## CONE Summary - Gas
|  |  |  | Simple Cycle |  |  |  | 1 x 1 Double Train Combined Cycle
|  |  |  | EMAAC | SWMAAC | Rest of RTO | WMAAC | EMAAC | SWMAAC | Rest of RTO | WMAAC
1 | Net Summer ICAP | MW |  | 360.589 | 362.838 | 352.927 | 349.94 | 1170.73 | 1173.658 | 1144.094 | 1133.424
Gross Costs
2 | Overnight | 2026$ million |  | 325.299 | 307.089 | 311.425 | 317.007 | 1358.5466 | 1240.4946 | 1263.2786 | 1307.6186
3 | Installed (inc. IDC) | 2026$ million |  | 340.8395 | 321.8813 | 326.3601 | 332.2098 | 1469.6235 | 1342.7775 | 1366.9722 | 1414.9518
4 | First Year FOM | 2026$ million/yr |  | 9.4961 | 14.3602 | 13.534 | 10.9435 | 36.8264 | 52.6437 | 46.7545 | 38.7783
Unitized Costs
5 | Overnight | 2026$/kW | = [2] / [1] | 902.1323 | 846.3529 | 882.4063 | 905.8896 | 1160.4269 | 1056.9473 | 1104.1738 | 1153.6888
6 | Installed (inc. IDC) | 2026$/kW | = [3] / [1] | 945.2299 | 887.1213 | 924.724 | 949.3335 | 1255.3052 | 1144.096 | 1194.8076 | 1248.387
7 | Levelized FOM | 2026$/kW-yr |  | 32.7 | 43.8 | 44.6 | 38.8 | 39 | 49.3 | 47.1 | 42.4
8 | After-Tax WACC | % |  | 7.927% | 7.994% | 7.958% | 7.958% | 7.927% | 7.994% | 7.958% | 7.958%
9 | Effective Charge Rate | % |  | 11.67% | 11.57% | 11.62% | 11.61% | 12.38% | 12.24% | 12.32% | 12.32%
10 | Levelized CONE | 2026$/ICAP MW-yr | = [5] x [9] + [7] | 138000 | 141700 | 147100 | 144000 | 182700 | 178700 | 183100 | 184500
11 | Levelized CONE | 2026$/ICAP MW-day | = [10] / 365 | 377.9573 | 388.3036 | 403.1201 | 394.6565 | 500.6185 | 489.5733 | 501.6575 | 505.5227

## Capital Costs - Gas
| CONE Area |  |  |  | CONE Area
| 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4
| EMAAC | SWMAAC | Rest of RTO | WMAAC | EMAAC | SWMAAC | Rest of RTO | WMAAC
Capital Costs (in $millions) | 361 MW | 363 MW | 353 MW | 350 MW | 1171 MW | 1174 MW | 1144 MW | 1133 MW
Owner Furnished Equipment
Gas Turbines | 78.555 | 78.555 | 78.555 | 78.555 | 155.271 | 155.271 | 155.271 | 155.271
HRSG / SCR | 33.531 | 33.531 | 33.531 | 33.531 | 80.719 | 80.719 | 80.719 | 80.719
Steam Turbines | 0 | 0 | 0 | 0 | 84.755 | 84.755 | 84.755 | 84.755
Sales Tax | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Owner Furnished Equipment | 112.086 | 112.086 | 112.086 | 112.086 | 320.745 | 320.745 | 320.745 | 320.745
EPC Costs
Equipment
Condenser | 0 | 0 | 0 | 0 | 61.66 | 61.66 | 61.66 | 61.66
Other Equipment | 24.141 | 24.141 | 24.141 | 24.141 | 86.34 | 86.34 | 86.34 | 86.34
Construction Labor | 50.571 | 37.849 | 40.627 | 44.979 | 365.528 | 283.274 | 297.064 | 330.467
Other Labor | 16.403 | 15.385 | 15.607 | 15.955 | 75.542 | 68.961 | 70.064 | 72.737
Materials | 8.107 | 8.107 | 8.107 | 8.107 | 75.461 | 75.461 | 75.461 | 75.461
Sales Tax | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
EPC Contractor Fee | 21.131 | 19.757 | 20.057 | 20.527 | 98.528 | 89.644 | 91.133 | 94.741
EPC Contingency | 23.244 | 21.733 | 22.063 | 22.58 | 108.38 | 98.609 | 100.247 | 104.215
Total EPC Costs | 143.597 | 126.972 | 130.602 | 136.289 | 871.439 | 763.949 | 781.969 | 825.621
Non-EPC Costs
Project Development | 12.784 | 11.953 | 12.134 | 12.419 | 59.609 | 54.235 | 55.136 | 57.318
Mobilization and Start-Up | 2.557 | 2.391 | 2.427 | 2.484 | 11.922 | 10.847 | 11.027 | 11.464
Net Start-Up Fuel Costs | -0.551 | -0.555 | 0.123 | -0.532 | -13.918 | -13.994 | -9.784 | -13.49
Electrical Interconnection | 7.793 | 7.843 | 7.629 | 7.563 | 25.305 | 25.368 | 24.729 | 24.499
Gas Interconnection | 33.748 | 33.748 | 33.748 | 33.748 | 33.748 | 33.748 | 33.748 | 33.748
Land | 0.366 | 0.295 | 0.164 | 0.306 | 2.196 | 1.77 | 0.984 | 1.836
Fuel Inventories | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Non-Fuel Inventories | 1.278 | 1.195 | 1.213 | 1.242 | 5.961 | 5.423 | 5.514 | 5.732
Owner's Contingency | 4.638 | 4.55 | 4.595 | 4.578 | 9.986 | 9.392 | 9.708 | 9.689
Emission Reduction Credit | 0 | 0 | 0 | 0 | 2.3086 | 2.3086 | 2.3086 | 2.3086
Financing Fees | 7.003 | 6.611 | 6.704 | 6.824 | 29.245 | 26.703 | 27.194 | 28.148
Total Non-EPC Costs | 69.616 | 68.031 | 68.737 | 68.632 | 166.3626 | 155.8006 | 160.5646 | 161.2526
Total Capital Costs | 325.299 | 307.089 | 311.425 | 317.007 | 1358.5466 | 1240.4946 | 1263.2786 | 1307.6186
Overnight Capital Costs ($million) | 325.299 | 307.089 | 311.425 | 317.007 | 1358.5466 | 1240.4946 | 1263.2786 | 1307.6186
Overnight Capital Costs ($/kW) | 902.1323 | 846.3529 | 882.4063 | 905.8896 | 1160.4269 | 1056.9473 | 1104.1738 | 1153.6888
Installed Cost ($/kW) | 945.2299 | 887.1213 | 924.724 | 949.3335 | 1255.3052 | 1144.096 | 1194.8076 | 1248.387 | Note: You must update Installed Cost values on Capital Costs_Nominal$ sheet.

## O&M Costs - Gas
| CONE Area |  |  |  | CONE Area
| 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4
O&M Costs | EMAAC | SWMAAC | Rest of RTO | WMAAC | EMAAC | SWMAAC | Rest of RTO | WMAAC
| 361 MW | 363 MW | 353 MW | 350 MW | 1171 MW | 1174 MW | 1144 MW | 1133 MW
Fixed O&M (2026$ million)
LTSA Fixed Payments | 0.346 | 0.346 | 0.346 | 0.346 | 0.824 | 0.824 | 0.824 | 0.824
Labor | 1.156 | 1.241 | 0.883 | 0.91 | 5.202 | 5.581 | 3.974 | 4.095
Maintenance and Minor Repairs | 0.53 | 0.543 | 0.485 | 0.489 | 6.561 | 6.717 | 5.998 | 6.058
Administrative and General | 0.249 | 0.263 | 0.205 | 0.21 | 1.378 | 1.441 | 1.168 | 1.188
Asset Management | 0.545 | 0.589 | 0.407 | 0.417 | 1.577 | 1.697 | 1.177 | 1.203
Property Taxes | 0.323 | 4.087 | 2.169 | 0.317 | 2.958 | 16.362 | 9.501 | 2.913
Insurance | 1.952 | 1.843 | 1.869 | 1.902 | 8.151 | 7.443 | 7.58 | 7.846
Firm Gas Contract | 4.3591 | 5.4142 | 7.136 | 6.3175 | 10.0254 | 12.4417 | 16.3925 | 14.5063
Working Capital | 0.036 | 0.034 | 0.034 | 0.035 | 0.15 | 0.137 | 0.14 | 0.145
Total Fixed O&M (2026$ million) | 9.4961 | 14.3602 | 13.534 | 10.9435 | 36.8264 | 52.6437 | 46.7545 | 38.7783
Levelized Fixed O&M (2026$/MW-yr) | 26300 | 39600 | 38300 | 31300 | 31500 | 44900 | 40900 | 34200
Variable O&M (2026$/MWh)
Major Maintenance - Hours Based | 0 | 0 | 0 | 0 | 1.3232 | 1.3189 | 1.3529 | 1.3654
Consumables, Waste Disposal, Other VOM | 1.1894 | 1.184 | 1.146 | 1.2161 | 0.75679 | 0.75535 | 0.76679 | 0.77098
Total Variable O&M (2026$/MWh) | 1.1894 | 1.184 | 1.146 | 1.2161 | 2.08 | 2.0742 | 2.1197 | 2.1364
Major Maintenance - Starts Based ($/factored start, per turbine) | 21169.9298 | 21169.9298 | 21169.9298 | 21169.9298 | 0 | 0 | 0 | 0

## CONE Summary - BESS
4-Hour Battery Storage
|  |  |  | EMAAC | SWMAAC | Rest of RTO | WMAAC
| Net Summer ICAP | MW |  | 200 | 200 | 200 | 200
Gross Costs
1 | Overnight | $m |  | 327.5821 | 312.3585 | 315.6574 | 320.9925
2 | Installed (inc. IDC) | $m |  | 345.0924 | 329.1944 | 332.5957 | 338.2171
3 | First Year FOM | $m/yr |  | 7.062 | 8.961 | 6.711 | 6.746
4 | Year 5 Augmentation | $m |  | 30.5163 | 30.5163 | 30.5163 | 30.5163
5 | Year 10 Augmentation | $m |  | 33.0565 | 33.0565 | 33.0565 | 33.0565
6 | Net Summer ICAP | MW |  | 200 | 200 | 200 | 200
Unitized Costs
7 | Overnight | $/kW | = [1] / [6] | 1637.9103 | 1561.7926 | 1578.287 | 1604.9626
8 | Installed (inc. IDC) | $/kW | = [2] / [6] | 1725.4619 | 1645.9718 | 1662.9785 | 1691.0855
9 | Levelized Fixed Costs | $/kW-yr |  | 66.1247 | 68.5566 | 63.9256 | 64.1426
10 | After-Tax WACC | % |  | 7.927% | 7.994% | 7.958% | 7.958%
11 | Effective Charge Rate | % |  | 11.07% | 11.03% | 11.05% | 11.05%
12 | Updated CONE | $/MW-yr | = [7] x [11] + [9] | 247400 | 240900 | 238400 | 241500
13 | Updated CONE | $/MW-day | = [12] / 365 | 677.8082 | 660 | 653.1507 | 661.6438

## Capital Costs - BESS
CONE Area
| 1 | 2 | 3 | 4
| EMAAC | SWMAAC | Rest of RTO | WMAAC
Capital Costs (in $millions) | 200 MW | 200 MW | 200 MW | 200 MW
EPC Costs
BESS Equipment
Batteries and Enclosures | 193.5161 | 193.5161 | 193.5161 | 193.5161
PCS and BOP Equipment | 28.9639 | 28.9639 | 28.9639 | 28.9639
Project Management | 11.7944 | 9.412 | 9.9557 | 10.7684
Construction & Materials | 58.7389 | 46.8742 | 49.582 | 53.6293
Sales Tax | 0 | 0 | 0 | 0
EPC Contractor Fee | Included | Included | Included | Included
EPC Contingency | Included | Included | Included | Included
Optional Augmentation | 0 | 0 | 0 | 0
Total EPC Costs | 293.0133 | 278.7662 | 282.0177 | 286.8778
Non-EPC Costs
Project Development | 14.6508 | 13.9385 | 14.1013 | 14.344
Mobilization and Start-Up | 2.9304 | 2.7873 | 2.8199 | 2.8692
Owner's Contingency | 11.1235 | 11.1235 | 11.1235 | 11.1235
Spare Parts Inventories | Included | Included | Included | Included
Electrical Interconnection | 4.121 | 4.121 | 4.121 | 4.121
Land | 0.42 | 0.338 | 0.187 | 0.352
Working Capital | 0.036 | 0.034 | 0.035 | 0.035
Financing Fees | 1.287 | 1.25 | 1.252 | 1.27
Total Non-EPC Costs | 34.5687 | 33.5923 | 33.6397 | 34.1147
Total Capital Costs | 327.5821 | 312.3585 | 315.6574 | 320.9925
Overnight Capital Costs ($million) | 327.5821 | 312.3585 | 315.6574 | 320.9925
Overnight Capital Costs ($/kW) | 1637.9103 | 1561.7926 | 1578.287 | 1604.9626
Installed Capital Costs ($/kW) | 1725.4619 | 1645.9718 | 1662.9785 | 1691.0855 | Note: You must update Installed Cost values on Capital Costs_Nominal$ sheet.
Installed Capital Costs ($/kWh) | 409.4776 | 390.4482 | 394.5718 | 401.2406

## O&M Costs - BESS
CONE Area
|  | 1 | 2 | 3 | 4
| O&M Costs | EMAAC | SWMAAC | Rest of RTO | WMAAC
|  | 200 MW | 200 MW | 200 MW | 200 MW
Fixed O&M Components
| O&M Contract Fixed Payments | 2.679 | 2.679 | 2.679 | 2.679
| BOP and Substation O&M | 0.125 | 0.1 | 0.105 | 0.114
| Station Load / Aux Load | 0.396 | 0.316 | 0.334 | 0.362
| Miscellaneous Owner Costs | 0.299 | 0.239 | 0.253 | 0.273
| Operating Insurance | 1.31 | 1.249 | 1.263 | 1.284
| Land Lease or Property Taxes | 2.253 | 4.378 | 2.077 | 2.034
| Fixed O&M (2026$ million) | 7.062 | 8.961 | 6.711 | 6.746
| Fixed O&M ($/kW-yr) | 35.31 | 44.805 | 33.555 | 33.73
Augmentation
| Year 5 Costs (2031$ million) | 30.5163 | 30.5163 | 30.5163 | 30.5163
| Year 10 Costs (2036$ million) | 33.0565 | 33.0565 | 33.0565 | 33.0565
| Levelized Augmentation Costs ($/kW-yr) | 22.3419 | 22.3151 | 22.3295 | 22.3295
| Total Levelized Fixed Costs ($/kW-yr) | 57.6519 | 67.1201 | 55.8845 | 56.0595
| Variable O&M (2026$/MWh) | 0 | 0 | 0 | 0
$/KW-yr | CONE With Levelized Augmentation Cost | 249.3783 | 242.5813 | 240.1634 | 243.359
$/KW-yr | CONE Without Levelized Augmentation Cost | 227.0364 | 220.2661 | 217.8339 | 221.0296
| Levelized Augmentation Cost ($/kW-Yr) | 22.3419 | 22.3151 | 22.3295 | 22.3295

## Summary Table (kW-yr)
|  | Simple Cycle |  |  |  | Combined Cycle |  |  |  | BESS
|  | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4
|  | EMAAC | SWMAAC | RTO | WMAAC | EMAAC | SWMAAC | RTO | WMAAC | EMAAC | SWMAAC | RTO | WMAAC
Gross Costs
Overnight | ($m) | 325.299 | 307.089 | 311.425 | 317.007 | 1358.5466 | 1240.4946 | 1263.2786 | 1307.6186 | 327.5821 | 312.3585 | 315.6574 | 320.9925
Installed | ($m) | 340.8395 | 321.8813 | 326.3601 | 332.2098 | 1469.6235 | 1342.7775 | 1366.9722 | 1414.9518 | 345.0924 | 329.1944 | 332.5957 | 338.2171
First Year FOM | ($m/yr) | 9.4961 | 14.3602 | 13.534 | 10.9435 | 36.8264 | 52.6437 | 46.7545 | 38.7783 | 7.062 | 8.961 | 6.711 | 6.746
Net Summer ICAP | (MW) | 360.589 | 362.838 | 352.927 | 349.94 | 1170.73 | 1173.658 | 1144.094 | 1133.424 | 200 | 200 | 200 | 200
Unitized Costs
Overnight | ($/kW) | 902.1323 | 846.3529 | 882.4063 | 905.8896 | 1160.4269 | 1056.9473 | 1104.1738 | 1153.6888 | 1637.9103 | 1561.7926 | 1578.287 | 1604.9626
Installed | ($/kW) | 945.2299 | 887.1213 | 924.724 | 949.3335 | 1255.3052 | 1144.096 | 1194.8076 | 1248.387 | 1725.4619 | 1645.9718 | 1662.9785 | 1691.0855
Levelized FOM | ($/kW-yr) | 32.6541 | 43.838 | 44.5852 | 38.7667 | 39.0039 | 49.3025 | 47.1005 | 42.4124 | 66.1247 | 68.5566 | 63.9256 | 64.1426 | Update with Values Below
After-Tax WACC | (%) | 7.927% | 7.994% | 7.958% | 7.958% | 7.927% | 7.994% | 7.958% | 7.958% | 7.927% | 7.994% | 7.958% | 7.958%
Levelized Gross CONE
Level-Nominal | ($/kW-yr) | 137.9544 | 141.7308 | 147.1388 | 144.0496 | 182.7258 | 178.6943 | 183.105 | 184.5158 | 247.3978 | 240.8964 | 238.352 | 241.517
Note: Update by copying and pasting values from CONE summary tables in CC, CT and BESS sheets because of the CC/CT/BESS switch on the CONE_Calculations tab
Operating Costs (Levelized FOM) | $/kW-year | 32.6541 | 43.838 | 44.5852 | 38.7667 | 39.0039 | 49.3025 | 47.1005 | 42.4124 | 66.1247 | 68.5566 | 63.9256 | 64.1426 | << Inputs from 'CONE Calculations' cell F51 as First Year Revenue Req. Also see results matrix from CONE_Calculations cell E103

## CT CONE Results
| MW | 360.589 | 362.838 | 352.927 | 349.94
PJM Simple-Cycle 2022/23 CONE Summary
CONE Area
|  | 1 | 2 | 3 | 4
Reference CT Plant |  | EMAAC | SWMAAC | RTO | WMAAC
Gross Costs
Overnight Costs | ($m) | 327.5821 | 312.3585 | 315.6574 | 320.9925 | #N/A
Installed Costs | ($m) | 345.0924 | 329.1944 | 332.5957 | 338.2171 | #N/A
First Year FOM Costs | ($m/yr) | 9.4961 | 14.3602 | 13.534 | 10.9435
Net Summer ICAP | (MW) | 360.589 | 362.838 | 352.927 | 349.94
Unitized Costs
Overnight Costs | ($/kW) | 908.4638 | 860.876 | 894.3986 | 917.2787
Installed Capital Costs | ($/kW) | 957.0241 | 907.2764 | 942.3923 | 966.5003
First Year FOM Costs | ($/kW-yr) | 26.335 | 39.5774 | 38.3478 | 31.2725
After-Tax WACC | (%) | 7.927% | 7.994% | 7.958% | 7.958% | #N/A
Levelized Gross CONE
Level-Nominal CONE | ($/kW-yr) | 247.3978 | 240.8964 | 238.352 | 241.517 | #N/A

## CC CONE Results
| MW | 1170.73 | 1173.658 | 1144.094 | 1133.424
PJM Combined-Cycle 2022/23 CONE Summary
CONE Area
|  | 1 | 2 | 3 | 4 | 5
Reference CC Plant |  | EMAAC | SWMAAC | RTO | WMAAC | Dominion
Gross Costs
Overnight Costs | ($m) | 327.5821 | 312.3585 | 315.6574 | 320.9925 | #N/A
Installed Costs | ($m) | 345.0924 | 329.1944 | 332.5957 | 338.2171 | #N/A
First Year FOM Costs | ($m/yr) | 36.8264 | 52.6437 | 46.7545 | 38.7783
Net Summer ICAP | (MW) | 1170.73 | 1173.658 | 1144.094 | 1133.424
Unitized Costs
Overnight Costs | ($/kW) | 279.8101 | 266.141 | 275.9016 | 283.206
Installed Capital Costs | ($/kW) | 294.7668 | 280.4858 | 290.7066 | 298.403
First Year FOM Costs | ($/kW-yr) | 31.4559 | 44.8544 | 40.8659 | 34.2134
After-Tax WACC | (%) | 7.927% | 7.994% | 7.958% | 7.958% | #N/A
Levelized Gross CONE
Level-Nominal CONE | ($/kW-yr) | 247.3978 | 240.8964 | 238.352 | 241.517 | #N/A

## BESS CONE Results
| Rated Output Power | 200 | 200 | 200 | 200
PJM Battery Energy Storage System 2022/23 CONE Summary
CONE Area
|  | 1 | 2 | 3 | 4 | 5
Reference CC Plant |  | EMAAC | SWMAAC | RTO | WMAAC | Dominion
Gross Costs
Overnight Costs | ($m) | 327.5821 | 312.3585 | 315.6574 | 320.9925 | #N/A
Installed Costs | ($m) | 345.0924 | 329.1944 | 332.5957 | 338.2171 | #N/A
First Year FOM Costs | ($m/yr) | 7.062 | 8.961 | 6.711 | 6.746
Net Summer ICAP | (MW) | 200 | 200 | 200 | 200
Unitized Costs
Overnight Costs | ($/kW) | 1637.9103 | 1561.7926 | 1578.287 | 1604.9626
Installed Capital Costs | ($/kW) | 1725.4619 | 1645.9718 | 1662.9785 | 1691.0855
First Year FOM Costs | ($/kW-yr) | 35.31 | 44.805 | 33.555 | 33.73
After-Tax WACC | (%) | 7.927% | 7.994% | 7.958% | 7.958% | #N/A
Levelized Gross CONE
Level-Nominal CONE | ($/kW-yr) | 247.3978 | 240.8964 | 238.352 | 241.517 | #N/A

## CONE_Calculations
|  | Online Years | 2026 | 2027 | 2028
Assumptions
1 | Select Options
| Select Technology >>> | BESS | Single Cycle | Combined Cycle | BESS
| Select Region >>> | 1 | 1 | 2 | 3 | 4
| Levelization Method >>> | Level-Nominal | 0% | Level-Real | Level-Nominal
| Levelized Revenue Requirements ($/kW-yr) | 247.3978
| Levelized Revenue Requirements ($/MW-day) | 677.8023
| Plant Capacity (MW) - Max Summer | 200 | 1_BESS
| Installed Cost ($m) | 345.0924
| Depreciable Cost ($m) | 333.2525 |  |  |  | LTSA Cost Scenario >> | VOM
| Installed Cost ($/kW) | 1725.4619
| Depreciable Cost ($/kW) | 1666.2626
| Overnight Cost | 327.5821
| Online Year | 2026
2 | Financial Assumptions
| Economic Life (years) | 20
| Debt Fraction (%) | 55%
| Debt Rate (%) | 4.7%
| Equity Rate (%) | 13.6%
| Federal Tax Rate (%) | 21%
| State Tax Rate (%) | 11.5%
| Total Income Tax Rate (%) | 30.09%
| Tax Depreciation Schedule | 7yr MACRS | 7yr MACRS | 15yr MACRS | 20yr MACRS
| Bonus Depreciation % | 20% | 20% | 0% | 0%
| Annual Inflation Rate (%) | 2.912%
| ATWACC Nominal (%) | 7.927%
| ATWACC Real (%) | 4.874%
| Interest During Construction (%) | 4.7%
| Construction Debt Fraction (%) | 55%
Calculations
Note: All dollar numbers are in nominal $.
|  | (1+ATWACC)/(1+Price_Growth)-1 = | 7.927%
|  | Present Value | First Year Revenue Req. | First Year Revenue Req.
|  | EOY 0 | MOY 1 | MOY 1
|  | ($m) | ($m/yr) | ($/kW-yr)
| (+) Investment Costs | 345.0924 | 48.1301 | 240.6504
| (+) Operating Costs | 94.8227 | 13.2249 | 66.1247
| (-) Depreciation Tax Shield | -85.1469 | -11.8754 | -59.3772
| Total | 354.7682 | 49.4796 | 247.3978
Summary of Cash Flows
| Project Year | EOY | MOY | MOY | MOY | MOY | MOY | MOY | MOY | MOY | MOY | MOY | MOY | MOY | MOY | MOY | MOY | MOY | MOY | MOY | MOY | MOY | MOY | MOY | MOY | MOY | MOY | MOY | MOY | MOY | MOY | MOY | MOY | MOY | MOY | MOY | MOY | MOY | MOY | MOY | MOY | MOY | MOY | MOY | MOY | MOY | MOY | MOY | MOY | MOY | MOY | MOY
|  | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50
| Revenue Requirement ($/kW-yr) |  | 247.3978 | 247.3978 | 247.3978 | 247.3978 | 247.3978 | 247.3978 | 247.3978 | 247.3978 | 247.3978 | 247.3978 | 247.3978 | 247.3978 | 247.3978 | 247.3978 | 247.3978 | 247.3978 | 247.3978 | 247.3978 | 247.3978 | 247.3978 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Revenue Requirement ($m) |  | 49.4796 | 49.4796 | 49.4796 | 49.4796 | 49.4796 | 49.4796 | 49.4796 | 49.4796 | 49.4796 | 49.4796 | 49.4796 | 49.4796 | 49.4796 | 49.4796 | 49.4796 | 49.4796 | 49.4796 | 49.4796 | 49.4796 | 49.4796 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fixed O&M ($m) |  | 7.062 | 7.2676 | 7.4792 | 7.697 | 7.9211 | 38.668 | 8.389 | 8.6333 | 8.8846 | 9.1433 | 42.466 | 9.6835 | 9.9654 | 10.2556 | 10.5542 | 46.5111 | 11.1777 | 11.5031 | 11.838 | 12.1827 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Operating Costs ($m) |  | 7.062 | 7.2676 | 7.4792 | 7.697 | 7.9211 | 38.668 | 8.389 | 8.6333 | 8.8846 | 9.1433 | 42.466 | 9.6835 | 9.9654 | 10.2556 | 10.5542 | 46.5111 | 11.1777 | 11.5031 | 11.838 | 12.1827 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Tax Depreciation (%) |  | 25% | 21.43% | 15.31% | 10.93% | 8.75% | 8.74% | 8.75% | 1.09% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| Tax Depreciation ($m) |  | 133.301 | 57.1328 | 40.8168 | 29.1396 | 23.3277 | 23.301 | 23.3277 | 2.906 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Income Tax ($m) ALL-EQUITY |  | -27.3423 | -4.4889 | 0.35608 | 3.8036 | 5.4847 | -3.7575 | 5.344 | 11.4143 | 12.213 | 12.1352 | 2.11 | 11.9727 | 11.8878 | 11.8005 | 11.7107 | 0.89305 | 11.5231 | 11.4252 | 11.3245 | 11.2208 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| All-Equity Cash Flow ($m) | -345.0924 | 69.7599 | 46.7009 | 41.6443 | 37.979 | 36.0738 | 14.569 | 35.7466 | 29.4319 | 28.3819 | 28.2011 | 4.9035 | 27.8234 | 27.6263 | 27.4235 | 27.2147 | 2.0754 | 26.7788 | 26.5512 | 26.3171 | 26.0761 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Net Present Value Discounted at ATWACC ($m) | 0: 345.0924
TRUE
| Interest Payments ($m) |  | 4.4091 | 7.4613 | 6.8456 | 6.3117 | 5.8303 | 5.36 | 5.4083 | 4.913 | 4.5416 | 4.168 | 3.7694 | 3.9415 | 3.5347 | 3.1007 | 2.6376 | 2.1432 | 2.2595 | 1.7464 | 1.1985 | 0.61318 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Taxable Income ($m) |  | -95.2925 | -22.3822 | -5.662 | 6.3313 | 12.4005 | -17.8495 | 12.3546 | 33.0273 | 36.0533 | 36.1683 | 3.2442 | 35.8546 | 35.9795 | 36.1233 | 36.2878 | 0.82519 | 36.0424 | 36.2301 | 36.4431 | 36.6837 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Net Income Tax ($m) |  | -28.6688 | -6.7337 | -1.7034 | 1.9048 | 3.7307 | -5.37 | 3.7169 | 9.9363 | 10.8466 | 10.8812 | 0.97601 | 10.7869 | 10.8244 | 10.8677 | 10.9172 | 0.24826 | 10.8434 | 10.8998 | 10.9639 | 11.0363 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| ROE Payments ($m) |  | 10.2233 | 17.6647 | 16.2069 | 14.9431 | 13.8033 | 12.6898 | 12.8042 | 11.6315 | 10.7523 | 9.8677 | 8.9241 | 9.3314 | 8.3684 | 7.341 | 6.2446 | 5.0741 | 5.3494 | 4.1346 | 2.8374 | 1.4517 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Discretionary Cash ($m) |  | 56.4539 | 23.8197 | 20.6513 | 18.6231 | 18.1942 | -1.8683 | 19.1612 | 14.3655 | 14.4543 | 15.4193 | -6.6559 | 15.7363 | 16.7867 | 17.9146 | 19.1259 | -4.4972 | 19.8497 | 21.1957 | 22.6418 | 24.1957 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Debt Balance ($m) |  | 189.8008 | 158.7512 | 145.6503 | 134.2921 | 124.0495 | 114.0427 | 115.0702 | 104.5316 | 96.6305 | 88.6807 | 80.2 | 83.8608 | 75.2058 | 65.9731 | 56.1201 | 45.6008 | 48.0743 | 37.157 | 25.4994 | 13.0464 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interest Payments ($m) |  | 4.4091 | 7.4613 | 6.8456 | 6.3117 | 5.8303 | 5.36 | 5.4083 | 4.913 | 4.5416 | 4.168 | 3.7694 | 3.9415 | 3.5347 | 3.1007 | 2.6376 | 2.1432 | 2.2595 | 1.7464 | 1.1985 | 0.61318 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Principal Repayment ($m) | -189.8008 | 31.0497 | 13.1008 | 11.3582 | 10.2427 | 10.0068 | -1.0276 | 10.5387 | 7.901 | 7.9499 | 8.4806 | -3.6608 | 8.655 | 9.2327 | 9.853 | 10.5193 | -2.4735 | 10.9173 | 11.6576 | 12.453 | 13.3076 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total Payments to Debt Holders ($m) | -189.8008 | 35.4588 | 20.5621 | 18.2038 | 16.5544 | 15.8371 | 4.3325 | 15.947 | 12.814 | 12.4915 | 12.6486 | 0.10864 | 12.5964 | 12.7674 | 12.9537 | 13.1569 | -0.33022 | 13.1768 | 13.404 | 13.6514 | 13.9208 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Net Present Value Discounted at Debt Rate ($m) | 0: 189.9075
TRUE
| Equity Balance ($m) |  | 155.2916 | 129.8873 | 119.1685 | 109.8754 | 101.495 | 93.3076 | 94.1484 | 85.5258 | 79.0613 | 72.5569 | 65.6182 | 68.6134 | 61.532 | 53.978 | 45.9165 | 37.3098 | 39.3335 | 30.4012 | 20.8631 | 10.6743 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| ROE Payments ($m) |  | 10.2233 | 17.6647 | 16.2069 | 14.9431 | 13.8033 | 12.6898 | 12.8042 | 11.6315 | 10.7523 | 9.8677 | 8.9241 | 9.3314 | 8.3684 | 7.341 | 6.2446 | 5.0741 | 5.3494 | 4.1346 | 2.8374 | 1.4517 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Dividend Payments ($m) | -155.2916 | 25.4043 | 10.7188 | 9.2931 | 8.3804 | 8.1874 | -0.84072 | 8.6225 | 6.4645 | 6.5044 | 6.9387 | -2.9952 | 7.0814 | 7.554 | 8.0616 | 8.6067 | -2.0237 | 8.9324 | 9.5381 | 10.1888 | 10.8881 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total Payments to Equity Holders ($m) | -155.2916 | 35.6276 | 28.3835 | 25.5 | 23.3234 | 21.9907 | 11.8491 | 21.4267 | 18.096 | 17.2568 | 16.8064 | 5.9289 | 16.4128 | 15.9224 | 15.4026 | 14.8513 | 3.0504 | 14.2817 | 13.6726 | 13.0262 | 12.3398 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Net Present Value Discounted at Equity Rate ($m) | 0: 155.3094
TRUE
| Debt Fraction (%) |  | 55% | 55% | 55% | 55% | 55% | 55% | 55% | 55% | 55% | 55% | 55% | 55% | 55% | 55% | 55% | 55% | 55% | 55% | 55% | 55% | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Results Matrix
|  |  | CONE Area | Overnight | Installed | CONE | IDC | Installed | ATWAAC | First Year Revenue Req. | CONE
|  |  |  | $m | $m | $/kW-yr | $m | $/kW | % | $/kW-yr | ($/MW-day)
|  |  |  | 327.5821 | 345.0924 | 247.3978 | 17.5103 | 1725.4619 | 7.927% | 66.1247 | 677.8023
|  |  | 1 | 327.5821 | 345.0924 | 247.3978 | 17.5103 | 1725.4619 | 7.927% | 66.1247 | 677.8023
|  |  | 2 | 312.3585 | 329.1944 | 240.8964 | 16.8358 | 1645.9718 | 7.994% | 68.5566 | 659.9901
|  |  | 3 | 315.6574 | 332.5957 | 238.352 | 16.9383 | 1662.9785 | 7.958% | 63.9256 | 653.0192
|  |  | 4 | 320.9925 | 338.2171 | 241.517 | 17.2246 | 1691.0855 | 7.958% | 64.1426 | 661.6905
|  |  | 5 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A

## Construction Costs
| Months To |  | Construction Assumptions |  |  |  | Date of Construction Assumptions
| Completion |  | CONE Area >>> | 1 |  |  | Year >>> | 2022
| 16 |  | Technology >>> | BESS |  |  | Month >>> | 6
|  |  | Debt Ratio >>> | 55% |  |  | Day >>> | 1
|  |  | Interest During Construction >>> | 4.7%
|  |  | ATWACC >>> | 7.927%
|  | Capital Cost (Nominal $m) = | 327.5821
|  | Non-depreciable Cost (Nominal $m) = | 0.42
|  | Month Of Construction = | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40
|  | Date = | 2021-03-01 | 2021-04-01 | 2021-05-01 | 2021-06-01 | 2021-07-01 | 2021-08-01 | 2021-09-01 | 2021-10-01 | 2021-11-01 | 2021-12-01 | 2022-01-01 | 2022-02-01 | 2022-03-01 | 2022-04-01 | 2022-05-01 | 2022-06-01 | 2022-07-01 | 2022-08-01 | 2022-09-01 | 2022-10-01 | 2022-11-01 | 2022-12-01 | 2023-01-01 | 2023-02-01 | 2023-03-01 | 2023-04-01 | 2023-05-01 | 2023-06-01 | 2023-07-01 | 2023-08-01 | 2023-09-01 | 2023-10-01 | 2023-11-01 | 2023-12-01 | 2024-01-01 | 2024-02-01 | 2024-03-01 | 2024-04-01 | 2024-05-01 | 2024-06-01
|  | Cash Flow (%) | 0.96% | 1.55% | 37.26% | 1.784% | 1.869% | 2.133% | 2.529% | 2.918% | 3.146% | 3.1% | 2.746% | 30.55% | 1.397% | 0.7056% | 0.2227% | 7.126% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Capital Cost Cash Flow ($m) = | 3.1448 | 5.0785 | 122.0662 | 5.8457 | 6.1238 | 6.986 | 8.2836 | 9.5582 | 10.3044 | 10.1554 | 8.9947 | 100.0799 | 4.5766 | 2.3114 | 0.72953 | 23.3432 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Non-Depreciable Assets ($m) = | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0.3835% | << Monthly debt rate | Interest During Construction ($m) = | 0 | 0.0066327 | 0.017358 | 0.27485 | 0.28775 | 0.30128 | 0.31665 | 0.33479 | 0.35565 | 0.37813 | 0.40035 | 0.42017 | 0.63213 | 0.64312 | 0.64935 | 0.65226 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | IDC + Depreciable Assets ($m) = | 3.1448 | 5.0851 | 122.0836 | 6.1205 | 6.4116 | 7.2873 | 8.6002 | 9.893 | 10.6601 | 10.5335 | 9.3951 | 100.5001 | 5.2088 | 2.9545 | 1.3789 | 23.9954 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Cumulative Dollars Spent ($m) = | 3.1448 | 8.2299 | 130.3135 | 136.4341 | 142.8456 | 150.1329 | 158.7332 | 168.6261 | 179.2862 | 189.8197 | 199.2148 | 299.7149 | 304.9237 | 307.8782 | 309.2571 | 333.2525 | 333.2525 | 333.2525 | 333.2525 | 333.2525 | 333.2525 | 333.2525 | 333.2525 | 333.2525 | 333.2525 | 333.2525 | 333.2525 | 333.2525 | 333.2525 | 333.2525 | 333.2525 | 333.2525 | 333.2525 | 333.2525 | 333.2525 | 333.2525 | 333.2525 | 333.2525 | 333.2525 | 333.2525
|  | Overnight Cost ($m Nominal) = | 2021-03-01: 327.5821
0.6378% | << Monthly ATWAAC | Installed Cost ($m) = | 2021-03-01: 345.0924
|  | Depreciable Cost ($m) = | 2021-03-01: 333.2525

## Capital Costs_Nominal$
|  |  | Number of year to online date>> | 5 |  | 1_CT | 2_CT | 3_CT | 4_CT | 1_CC | 2_CC | 3_CC | 4_CC
|  |  | Number of months in a year >> | 12 |  | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4
[6 empty] | CT | CT | CT | CT | CC | CC | CC | CC
| Months Prior |  |  |  | Escalate to middle of drawdown schedule >> | 4.4167 | 4.4167 | 4.4167 | 4.4167 | 4 | 4 | 4 | 4
| 7 |  |  |  | Escalation for electric interconnection (7 months prior to online year) >> | 4.4167 | 4.4167 | 4.4167 | 4.4167 | 4.4167 | 4.4167 | 4.4167 | 4.4167
| 8 |  |  |  | Escalation for gas interconnection (8 months prior to online year) >> | 4.3333 | 4.3333 | 4.3333 | 4.3333 | 4.3333 | 4.3333 | 4.3333 | 4.3333 | 3.6667
[6 empty] | Reference Year Overnight Costs (2026$) |  |  |  | Reference Year Overnight Costs (2026$)
[6 empty] | CONE Area |  |  |  | CONE Area
|  |  | Annual Escalation Rate | Monthly Escalation Rate |  | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 |  |  | Personal vs. Real property breakdown
|  | Capital Costs | (%/yr) | (%/mo) |  | EMAAC | SWMAAC | Rest of RTO | WMAAC | EMAAC | SWMAAC | Rest of RTO | WMAAC
Depreciable (1 = Yes) |  |  | Inflation Adder | Monthly Escalation Rate |  | Frame-Type Combustion Turbine | Frame-Type Combustion Turbine | Frame-Type Combustion Turbine | Frame-Type Combustion Turbine | Combined Cycle Dry ACC | Combined Cycle Dry ACC | Combined Cycle Dry ACC | Combined Cycle Dry ACC |  |  | Real/Personal Tax
[6 empty] | 360.589 | 362.838 | 352.927 | 349.94 | 1170.73 | 1173.658 | 1144.094 | 1133.424
Owner Furnished Equipment
1 |  | Gas Turbines | 0% | 0.2394% |  | 78555000 | 78555000 | 78555000 | 78555000 | 155271000 | 155271000 | 155271000 | 155271000 |  |  | P | Gas Turbines | Turbine
1 |  | HRSG / SCR | 0% | 0.2394% |  | 33531000 | 33531000 | 33531000 | 33531000 | 80719000 | 80719000 | 80719000 | 80719000 |  |  | P | HRSG/SCR | Material
1 |  | Steam Turbines | 0% | 0.2394% |  | 0 | 0 | 0 | 0 | 84755000 | 84755000 | 84755000 | 84755000 |  |  | P |  | Material
1 |  | Sales Tax |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | P | OFE Sales Tax
|  | Total Owner Furnished Equipment |  |  |  | 112086000 | 112086000 | 112086000 | 112086000 | 320745000 | 320745000 | 320745000 | 320745000
EPC Costs
Equipment
1 |  | Condenser | 0% | 0.2394% |  | 0 | 0 | 0 | 0 | 61660000 | 61660000 | 61660000 | 61660000 |  |  | P |  | Material
1 |  | Other Equipment | 0% | 0.2394% |  | 24141000 | 24141000 | 24141000 | 24141000 | 86340000 | 86340000 | 86340000 | 86340000 |  |  | P |  | Material
|  | Equipment Subtotal |  |  |  | 24141000 | 24141000 | 24141000 | 24141000 | 148000000 | 148000000 | 148000000 | 148000000 |  |  |  | Equipment
1 |  | Construction Labor | 1.6% | 0.3684% |  | 50571000 | 37849000 | 40627000 | 44979000 | 365528000 | 283274000 | 297064000 | 330467000 |  |  | P | Labor | Labor
1 |  | Other Labor | 1.6% | 0.3684% |  | 16403000 | 15385000 | 15607000 | 15955000 | 75542000 | 68961000 | 70064000 | 72737000 |  |  | P | Labor | Labor
1 |  | Materials | 0% | 0.2394% |  | 8107000 | 8107000 | 8107000 | 8107000 | 75461000 | 75461000 | 75461000 | 75461000 |  |  | R | Materials | Material
1 |  | Sales Tax |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | P | EPC Sales Tax
1 |  | EPC Contractor Fee |  |  |  | 21131000 | 19757000 | 20057000 | 20527000 | 98528000 | 89644000 | 91133000 | 94741000 |  |  | P | EPC Contractor Fee | Labor
1 |  | EPC Contingency |  |  |  | 23244000 | 21733000 | 22063000 | 22580000 | 108380000 | 98609000 | 100247000 | 104215000 |  |  | P | EPC Contingency | Material
|  | Total EPC Costs |  |  |  | 143597000 | 126972000 | 130602000 | 136289000 | 871439000 | 763949000 | 781969000 | 825621000
|  | Total Project Costs |  |  |  | 255683000 | 239058000 | 242688000 | 248375000 | 1192184000 | 1084694000 | 1102714000 | 1146366000
Non-EPC Costs
1 |  | Project Development |  |  |  | 12784000 | 11953000 | 12134000 | 12419000 | 59609000 | 54235000 | 55136000 | 57318000 |  |  | P | Project Development | Labor
1 |  | Mobilization and Start-Up |  |  |  | 2557000 | 2391000 | 2427000 | 2484000 | 11922000 | 10847000 | 11027000 | 11464000 |  |  | P | Mobilization and Start-up | Labor
1 |  | Net Start-Up Fuel Costs |  |  |  | -551000 | -555000 | 123000 | -532000 | -13918000 | -13994000 | -9784000 | -13490000 |  |  | P | Net Start-up Fuel Costs | Material
1 |  | Electrical Interconnection | 0.2% | 0.2557% |  | 7793000 | 7843000 | 7629000 | 7563000 | 25305000 | 25368000 | 24729000 | 24499000 |  |  | P | Electrical Interconnection | Material
1 |  | Gas Interconnection | 0.2% | 0.2557% |  | 33748000 | 33748000 | 33748000 | 33748000 | 33748000 | 33748000 | 33748000 | 33748000 |  |  | P | Gas Interconnection | Material
0 |  | Land | 0% | 0.2394% |  | 366000 | 295000 | 164000 | 306000 | 2196000 | 1770000 | 984000 | 1836000 |  |  | R | Land | Material
1 |  | Fuel Inventories | 6% | 0.7139% |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | P | Inventories | Material
1 |  | Non-Fuel Inventories |  |  |  | 1278000 | 1195000 | 1213000 | 1242000 | 5961000 | 5423000 | 5514000 | 5732000 |  |  | P | Inventories | Material
1 |  | Owner's Contingency |  |  |  | 4638000 | 4550000 | 4595000 | 4578000 | 9986000 | 9392000 | 9708000 | 9689000 |  |  | P | Owner's Contingency | Material
|  | Emission Reduction Credit |  |  |  | 0 | 0 | 0 | 0 | 2308607.398 | 2308607.398 | 2308607.398 | 2308607.398
|  | Subtotal - Non-EPC Costs w/o Financing Fees |  |  |  | 62613000 | 61420000 | 62033000 | 61808000 | 137117607.398 | 129097607.398 | 133370607.398 | 133104607.398
1 |  | Financing Fees |  |  |  | 7003000 | 6611000 | 6704000 | 6824000 | 29245000 | 26703000 | 27194000 | 28148000 |  |  | P | Financing Fees | Material
|  | Total Non-EPC Costs |  |  |  | 69616000 | 68031000 | 68737000 | 68632000 | 166362607.398 | 155800607.398 | 160564607.398 | 161252607.398
|  | Total Capital Costs |  |  |  | 325299000 | 307089000 | 311425000 | 317007000 | 1358546607.398 | 1240494607.398 | 1263278607.398 | 1307618607.398
|  | Overnight Capital Costs ($) |  |  |  | 325299000 | 307089000 | 311425000 | 317007000 | 1358546607.398 | 1240494607.398 | 1263278607.398 | 1307618607.398
|  | Overnight Capital Costs ($/kW) |  |  |  | 902.1323 | 846.3529 | 882.4063 | 905.8896 | 1160.4269 | 1056.9473 | 1104.1738 | 1153.6888
|  | Installed Cost ($/kW) |  |  |  | 945.2299 | 887.1213 | 924.724 | 949.3335 | 1255.3052 | 1144.096 | 1194.8076 | 1248.387 |  | Note: Copied from cells CONE Calculations J107:J110 (confirm technology is correct)
|  | Non-Depreciable Costs ($) |  |  |  | 366000 | 295000 | 164000 | 306000 | 2196000 | 1770000 | 984000 | 1836000

## BESS_Capital Costs_Nominal$
|  |  | Number of year to online date>> | 5 |  | 1_BESS | 2_BESS | 3_BESS | 4_BESS
|  |  | Number of months in a year >> | 12 |  | 1 | 2 | 3 | 4
[6 empty] | BESS | BESS | BESS | BESS
| Months Prior |  |  |  | Escalate to middle of drawdown schedule >> | 4.3333 | 4.3333 | 4.3333 | 4.3333
| 7 |  |  |  | Escalation for electric interconnection (7 months prior to online year) >> | 4.4167 | 4.4167 | 4.4167 | 4.4167
| 8 |  |  |  | Escalation for gas interconnection (8 months prior to online year) >> | 4.3333 | 4.3333 | 4.3333 | 4.3333 | 3.6667
Reference Year Overnight Costs (2026$)
CONE Area
|  |  | Annual Escalation Rate | Monthly Escalation Rate |  | 1 | 2 | 3 | 4 |  |  | Personal vs. Real property breakdown
|  | Capital Costs | (%/yr) | (%/mo) |  | EMAAC | SWMAAC | Rest of RTO | WMAAC
Depreciable (1 = Yes) |  |  | Inflation Adder | Monthly Escalation Rate |  | Lithium-Ion 4-hour Batteries | Lithium-Ion 4-hour Batteries | Lithium-Ion 4-hour Batteries | Lithium-Ion 4-hour Batteries |  |  | Real/Personal Tax
[6 empty] | 200 | 200 | 200 | 200
EPC Costs
1 |  | Batteries and Enclosures | -3.222% | -0.0259% |  | 193516068.7544 | 193516068.7544 | 193516068.7544 | 193516068.7544 |  |  | P | Equipment | Material
1 |  | PCS and BOP Equipment | -3.222% | -0.0259% |  | 28963943.74 | 28963943.74 | 28963943.74 | 28963943.74 |  |  | P | Equipment | Material
|  | BESS Equipment Subtotal |  |  |  | 222480012.4944 | 222480012.4944 | 222480012.4944 | 222480012.4944
1 |  | Project Management | -3.222% | -0.0259% |  | 11794373.3951 | 9411996.5976 | 9955742.0846 | 10768449.6835 |  |  | P | Labor | Labor
1 |  | Construction & Materials | -3.222% | -0.0259% |  | 58738917.7656 | 46874195.8798 | 49581971.4464 | 53629328.301 |  |  | R | Materials | Material
1 |  | Sales Tax |  | 0.2394% |  | 0 | 0 | 0 | 0 |  |  | P | EPC Sales Tax | Material
1 |  | EPC Contractor Fee |  |  |  | Included | Included | Included | Included |  |  | P | EPC Contractor Fee | Material
1 |  | EPC Contingency |  |  |  | Included | Included | Included | Included |  |  | P | EPC Contingency Fee | Material
|  | Subtotal - EPC Costs w/o Augmentation |  |  |  | 293013303.6551 | 278766204.9718 | 282017726.0254 | 286877790.4788
1 |  | Optional Augmentation to Maintain Nameplate over 15 Years | -3.222% | -0.0259% |  | 0 | 0 | 0 | 0
|  | Total EPC Costs |  |  |  | 293013303.6551 | 278766204.9718 | 282017726.0254 | 286877790.4788
Non-EPC Costs
1 |  | Project Development | -3.222% | -0.0259% |  | 14650837.8474 | 13938473.0466 | 14101271.0967 | 14343988.1894 |  |  | P | Project Development | Labor
1 |  | Mobilization and Start-Up | -3.222% | -0.0259% |  | 2930364.9004 | 2787299.9474 | 2819859.5574 | 2869192.2998 |  |  | P | Mobilization and Start-up | Labor
1 |  | Owner's Contingency | -3.222% | -0.0259% |  | 11123546.7635 | 11123546.7635 | 11123546.7635 | 11123546.7635
1 |  | Spare Parts Inventories | -3.222% | -0.0259% |  | Included | Included | Included | Included |  |  | P | Inventories | Material
1 |  | Electrical Interconnection | 0% | 0.2394% |  | 4121000 | 4121000 | 4121000 | 4121000 |  |  | P | Electrical Interconnection | Material
0 |  | Land | 0% | 0.2394% |  | 420000 | 338000 | 187000 | 352000 |  |  | R | Land | Material
1 |  | Working Capital | 0% | 0.2394% |  | 36000 | 34000 | 35000 | 35000 |  |  | P | Working Capital | Material
[12 empty] | P | Owner's Contingency | Material
|  | Subtotal - Non-EPC Costs w/o Financing Fees |  |  |  | 33281749.5113 | 32342319.7575 | 32387677.4175 | 32844727.2527
1 |  | Financing Fees |  |  |  | 1287000 | 1250000 | 1252000 | 1270000 |  |  | P | Financing Fees | Material
|  | Total Non-EPC Costs |  |  |  | 34568749.5113 | 33592319.7575 | 33639677.4175 | 34114727.2527
|  | Total Capital Costs |  |  |  | 327582053.1663 | 312358524.7293 | 315657403.443 | 320992517.7316
|  | Overnight Capital Costs ($) |  |  |  | 327582053.1663 | 312358524.7293 | 315657403.443 | 320992517.7316
|  | Overnight Capital Costs ($/kW) |  |  |  | 1637.9103 | 1561.7926 | 1578.287 | 1604.9626
|  | Battery Energy Capital Costs ($/kWh) |  |  |  | 409.4776 | 390.4482 | 394.5718 | 401.2406
|  | Installed Cost ($/kW) |  |  |  | 1725.4619 | 1645.9718 | 1662.9785 | 1691.0855 |  | Note: Copied from cells CONE Calculations J107:J110 (confirm technology is correct)
|  | Non-Depreciable Costs ($) |  |  |  | 420000 | 338000 | 187000 | 352000

## Capital Cost Escalation
Number of Months to Escalate
Cost Estimate Year Dollars | 2021 |  |  |  | CT | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 53 | 54 | 55 | 56 | 57 | 58 | 59 | 60 | 61 | 62 | 63 | 64 | 65 | 66 | 67 | 68 | 69 | 70 | 71 | 72 | 73 | 74 | 75 | 76 | 77 | 78 | 79 | 80
Future Estimate Year Dollars | 2026 |  |  |  | CC | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 53 | 54 | 55 | 56 | 57 | 58 | 59 | 60 | 61 | 62 | 63 | 64 | 65 | 66 | 67 | 68
[5 empty] | BESS | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 53 | 54 | 55 | 56 | 57 | 58 | 59 | 60 | 61 | 62 | 63 | 64 | 65 | 66 | 67 | 68 | 69 | 70 | 71 | 72 | 73 | 74 | 75 | 76 | 77 | 78 | 79 | 80 | 81 | 82 | 83 | 84
|  |  |  | Months to Completion |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | Total in Nominal $ | Cost in 2021$
|  |  | CT | 20 |  | 0.3635% | 0.4325% | 2.61% | 0.8045% | 1.755% | 1.111% | 2.176% | 2.887% | 4.029% | 6.697% | 8.136% | 10.41% | 11.57% | 12.27% | 11.49% | 10.16% | 7.709% | 4.285% | 0.9052% | 0.2016% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  |  | CC | 32 |  | 0.01% | 0.05% | 0.05% | 1.69% | 1.65% | 0.24% | 0.36% | 1.45% | 1.53% | 1.28% | 1.36% | 1.44% | 2.75% | 3.89% | 4.24% | 4.84% | 5.33% | 6.24% | 6.36% | 6.22% | 6.4% | 6.07% | 6.22% | 6.21% | 5.87% | 5.78% | 4.93% | 4.16% | 2.38% | 0.71% | 0.17% | 0.12% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  |  | BESS | 16 |  | 0.96% | 1.55% | 37.26% | 1.784% | 1.869% | 2.133% | 2.529% | 2.918% | 3.146% | 3.1% | 2.746% | 30.55% | 1.397% | 0.7056% | 0.2227% | 7.126% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  |  | Simple Cycle |  | Monthly Escalation Rate
CT_EMAAC_Gas Turbines | CT | EMAAC |  | Gas Turbines | 0.2394% | 277625.1539 | 331128.0428 | 2002838.4592 | 618924.6765 | 1353284.0377 | 858536.3005 | 1686497.1728 | 2242255.6714 | 3137004.932 | 5226833.7064 | 6364953.7993 | 8161214.758 | 9095047.8182 | 9671378.7289 | 9074520.7415 | 8043753.0508 | 6117948.9116 | 3408589.0012 | 721882.4521 | 161171.8148 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 78555389.2296 | 69250000
CT_EMAAC_HRSG / SCR | CT | EMAAC |  | HRSG / SCR | 0.2394% | 118502.4428 | 141339.7935 | 854898.2199 | 264183.8645 | 577640.2533 | 366460.486 | 719870.0546 | 957091.858 | 1339009.6041 | 2231039.0591 | 2716838.0196 | 3483560.0131 | 3882160.4181 | 4128163.4182 | 3873398.5725 | 3433422.2679 | 2611405.633 | 1454933.4502 | 308130.7034 | 68795.1127 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33530843.2447 | 29558900
CT_EMAAC_Condenser | CT | EMAAC |  | Condenser | 0.2394% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CT_EMAAC_Steam Turbines | CT | EMAAC |  | Steam Turbines | 0.2394% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CT_EMAAC_Other Equipment | CT | EMAAC |  | Other Equipment | 0.2394% | 85318.9204 | 101761.266 | 615506.2417 | 190206.0547 | 415887.1466 | 263842.7724 | 518289.1969 | 689083.2133 | 964054.8428 | 1606294.6843 | 1956058.3 | 2508079.7706 | 2795062.5148 | 2972178.7826 | 2788754.1959 | 2471981.795 | 1880149.5069 | 1047517.2353 | 221846.7261 | 49530.8334 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24141403.9995 | 21281700
CT_EMAAC_Construction Labor | CT | EMAAC |  | Construction Labor | 0.3684% | 176045.7443 | 210242.7498 | 1273295.8863 | 393984.884 | 862559.5107 | 547919.957 | 1077711.2627 | 1434697.3059 | 2009780.8357 | 3352976.6564 | 4088325.352 | 5248840.1663 | 5856954.8515 | 6236107.9954 | 5858781.2407 | 5199967.8824 | 3960099.7544 | 2209191.0021 | 468471.807 | 104728.388 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50570683.2329 | 41657600
CT_EMAAC_Other Labor | CT | EMAAC |  | Other Labor | 0.3684% | 57100.2573 | 68192.0211 | 412992.2199 | 127788.5946 | 279770.296 | 177717.2783 | 349554.547 | 465342.6054 | 651870.3608 | 1087534.5529 | 1326044.151 | 1702455.9454 | 1899697.3223 | 2022675.2571 | 1900289.7097 | 1686604.27 | 1284454.3095 | 716548.8445 | 151948.352 | 33968.5456 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16402549.4404 | 13511600
CT_EMAAC_Materials | CT | EMAAC |  | Materials | 0.2394% | 28651.7177 | 34173.3703 | 206698.7134 | 63874.8141 | 139662.8211 | 88603.4257 | 174051.379 | 231407.2611 | 323747.9689 | 539424.3341 | 656881.6146 | 842260.9333 | 938635.2021 | 998114.2166 | 936516.7485 | 830138.5459 | 631389.9968 | 351776.2292 | 74500.3539 | 16633.3968 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8107143.0433 | 7146800
__
CT_SWMAAC_Gas Turbines | CT | SWMAAC |  | Gas Turbines | 0.2394% | 277625.1539 | 331128.0428 | 2002838.4592 | 618924.6765 | 1353284.0377 | 858536.3005 | 1686497.1728 | 2242255.6714 | 3137004.932 | 5226833.7064 | 6364953.7993 | 8161214.758 | 9095047.8182 | 9671378.7289 | 9074520.7415 | 8043753.0508 | 6117948.9116 | 3408589.0012 | 721882.4521 | 161171.8148 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 78555389.2296 | 69250000
CT_SWMAAC_HRSG / SCR | CT | SWMAAC |  | HRSG / SCR | 0.2394% | 118502.4428 | 141339.7935 | 854898.2199 | 264183.8645 | 577640.2533 | 366460.486 | 719870.0546 | 957091.858 | 1339009.6041 | 2231039.0591 | 2716838.0196 | 3483560.0131 | 3882160.4181 | 4128163.4182 | 3873398.5725 | 3433422.2679 | 2611405.633 | 1454933.4502 | 308130.7034 | 68795.1127 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33530843.2447 | 29558900
CT_SWMAAC_Condenser | CT | SWMAAC |  | Condenser | 0.2394% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CT_SWMAAC_Steam Turbines | CT | SWMAAC |  | Steam Turbines | 0.2394% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CT_SWMAAC_Other Equipment | CT | SWMAAC |  | Other Equipment | 0.2394% | 85318.9204 | 101761.266 | 615506.2417 | 190206.0547 | 415887.1466 | 263842.7724 | 518289.1969 | 689083.2133 | 964054.8428 | 1606294.6843 | 1956058.3 | 2508079.7706 | 2795062.5148 | 2972178.7826 | 2788754.1959 | 2471981.795 | 1880149.5069 | 1047517.2353 | 221846.7261 | 49530.8334 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24141403.9995 | 21281700
CT_SWMAAC_Construction Labor | CT | SWMAAC |  | Construction Labor | 0.3684% | 131760.8849 | 157355.5264 | 952994.3106 | 294876.7502 | 645579.9591 | 410088.9725 | 806609.6128 | 1073794.6966 | 1504214.1599 | 2509524.857 | 3059894.2807 | 3928477.9518 | 4383619.4797 | 4667395.4605 | 4384986.4349 | 3891899.6443 | 2963924.2346 | 1653462.0732 | 350626.2539 | 78383.6333 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37849469.1767 | 31178500
CT_SWMAAC_Other Labor | CT | SWMAAC |  | Other Labor | 0.3684% | 53557.5869 | 63961.1846 | 387368.9496 | 119860.2087 | 262412.5117 | 166691.1678 | 327867.1394 | 436471.361 | 611426.3776 | 1020060.6626 | 1243772.4133 | 1596830.4962 | 1781834.4292 | 1897182.4459 | 1782390.0632 | 1581962.3061 | 1204762.9296 | 672092.0151 | 142521.0226 | 31861.0357 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15384886.3068 | 12673300
CT_SWMAAC_Materials | CT | SWMAAC |  | Materials | 0.2394% | 28651.7177 | 34173.3703 | 206698.7134 | 63874.8141 | 139662.8211 | 88603.4257 | 174051.379 | 231407.2611 | 323747.9689 | 539424.3341 | 656881.6146 | 842260.9333 | 938635.2021 | 998114.2166 | 936516.7485 | 830138.5459 | 631389.9968 | 351776.2292 | 74500.3539 | 16633.3968 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8107143.0433 | 7146800
__
CT_Rest of RTO_Gas Turbines | CT | Rest of RTO |  | Gas Turbines | 0.2394% | 277625.1539 | 331128.0428 | 2002838.4592 | 618924.6765 | 1353284.0377 | 858536.3005 | 1686497.1728 | 2242255.6714 | 3137004.932 | 5226833.7064 | 6364953.7993 | 8161214.758 | 9095047.8182 | 9671378.7289 | 9074520.7415 | 8043753.0508 | 6117948.9116 | 3408589.0012 | 721882.4521 | 161171.8148 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 78555389.2296 | 69250000
CT_Rest of RTO_HRSG / SCR | CT | Rest of RTO |  | HRSG / SCR | 0.2394% | 118502.4428 | 141339.7935 | 854898.2199 | 264183.8645 | 577640.2533 | 366460.486 | 719870.0546 | 957091.858 | 1339009.6041 | 2231039.0591 | 2716838.0196 | 3483560.0131 | 3882160.4181 | 4128163.4182 | 3873398.5725 | 3433422.2679 | 2611405.633 | 1454933.4502 | 308130.7034 | 68795.1127 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33530843.2447 | 29558900
CT_Rest of RTO_Condenser | CT | Rest of RTO |  | Condenser | 0.2394% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CT_Rest of RTO_Steam Turbines | CT | Rest of RTO |  | Steam Turbines | 0.2394% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CT_Rest of RTO_Other Equipment | CT | Rest of RTO |  | Other Equipment | 0.2394% | 85318.9204 | 101761.266 | 615506.2417 | 190206.0547 | 415887.1466 | 263842.7724 | 518289.1969 | 689083.2133 | 964054.8428 | 1606294.6843 | 1956058.3 | 2508079.7706 | 2795062.5148 | 2972178.7826 | 2788754.1959 | 2471981.795 | 1880149.5069 | 1047517.2353 | 221846.7261 | 49530.8334 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24141403.9995 | 21281700
CT_Rest of RTO_Construction Labor | CT | Rest of RTO |  | Construction Labor | 0.3684% | 141430.0128 | 168902.889 | 1022928.752 | 316515.9568 | 692955.1358 | 440182.9016 | 865801.7739 | 1152593.9417 | 1614599.2649 | 2693683.5841 | 3284441.2639 | 4216764.9943 | 4705306.5836 | 5009907.1533 | 4706773.8514 | 4177502.4278 | 3181428.5612 | 1774799.5725 | 376356.5767 | 84135.7302 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40627010.9275 | 33466500
CT_Rest of RTO_Other Labor | CT | Rest of RTO |  | Other Labor | 0.3684% | 54331.3707 | 64885.2764 | 392965.5389 | 121591.9127 | 266203.7682 | 169099.4713 | 332604.0645 | 442777.367 | 620260.0807 | 1034798.1901 | 1261742.0604 | 1619901.0196 | 1807577.8334 | 1924592.3633 | 1808141.495 | 1604818.0184 | 1222168.9796 | 681802.197 | 144580.1232 | 32321.3543 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15607162.4845 | 12856400
CT_Rest of RTO_Materials | CT | Rest of RTO |  | Materials | 0.2394% | 28651.7177 | 34173.3703 | 206698.7134 | 63874.8141 | 139662.8211 | 88603.4257 | 174051.379 | 231407.2611 | 323747.9689 | 539424.3341 | 656881.6146 | 842260.9333 | 938635.2021 | 998114.2166 | 936516.7485 | 830138.5459 | 631389.9968 | 351776.2292 | 74500.3539 | 16633.3968 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8107143.0433 | 7146800
__
CT_WMAAC_Gas Turbines | CT | WMAAC |  | Gas Turbines | 0.2394% | 277625.1539 | 331128.0428 | 2002838.4592 | 618924.6765 | 1353284.0377 | 858536.3005 | 1686497.1728 | 2242255.6714 | 3137004.932 | 5226833.7064 | 6364953.7993 | 8161214.758 | 9095047.8182 | 9671378.7289 | 9074520.7415 | 8043753.0508 | 6117948.9116 | 3408589.0012 | 721882.4521 | 161171.8148 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 78555389.2296 | 69250000
CT_WMAAC_HRSG / SCR | CT | WMAAC |  | HRSG / SCR | 0.2394% | 118502.4428 | 141339.7935 | 854898.2199 | 264183.8645 | 577640.2533 | 366460.486 | 719870.0546 | 957091.858 | 1339009.6041 | 2231039.0591 | 2716838.0196 | 3483560.0131 | 3882160.4181 | 4128163.4182 | 3873398.5725 | 3433422.2679 | 2611405.633 | 1454933.4502 | 308130.7034 | 68795.1127 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33530843.2447 | 29558900
CT_WMAAC_Condenser | CT | WMAAC |  | Condenser | 0.2394% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CT_WMAAC_Steam Turbines | CT | WMAAC |  | Steam Turbines | 0.2394% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CT_WMAAC_Other Equipment | CT | WMAAC |  | Other Equipment | 0.2394% | 85318.9204 | 101761.266 | 615506.2417 | 190206.0547 | 415887.1466 | 263842.7724 | 518289.1969 | 689083.2133 | 964054.8428 | 1606294.6843 | 1956058.3 | 2508079.7706 | 2795062.5148 | 2972178.7826 | 2788754.1959 | 2471981.795 | 1880149.5069 | 1047517.2353 | 221846.7261 | 49530.8334 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24141403.9995 | 21281700
CT_WMAAC_Construction Labor | CT | WMAAC |  | Construction Labor | 0.3684% | 156579.8627 | 186995.6076 | 1132503.9177 | 350420.8484 | 767183.8381 | 487334.8799 | 958545.6455 | 1276058.7206 | 1787553.6194 | 2982228.4358 | 3636267.5226 | 4668460.894 | 5209334.5988 | 5546563.695 | 5210959.0389 | 4624992.5583 | 3522220.1961 | 1964914.4333 | 416671.5392 | 93148.2705 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 44978938.1225 | 37051400
CT_WMAAC_Other Labor | CT | WMAAC |  | Other Labor | 0.3684% | 55543.3925 | 66332.7342 | 401731.7967 | 124304.3797 | 272142.23 | 172871.7348 | 340023.7812 | 452654.8248 | 634096.815 | 1057882.4222 | 1289888.9462 | 1656037.6996 | 1847901.1994 | 1967526.0842 | 1848477.4351 | 1640618.2274 | 1249433.0709 | 697011.8101 | 147805.4102 | 33042.3776 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15955326.3718 | 13143200
CT_WMAAC_Materials | CT | WMAAC |  | Materials | 0.2394% | 28651.7177 | 34173.3703 | 206698.7134 | 63874.8141 | 139662.8211 | 88603.4257 | 174051.379 | 231407.2611 | 323747.9689 | 539424.3341 | 656881.6146 | 842260.9333 | 938635.2021 | 998114.2166 | 936516.7485 | 830138.5459 | 631389.9968 | 351776.2292 | 74500.3539 | 16633.3968 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8107143.0433 | 7146800
__
__
__ |  |  | Combined Cycle |  | Monthly Escalation Rate
__
CC_EMAAC_Gas Turbines | CC | EMAAC |  | Gas Turbines | 0.2394% | 14844.6906 | 74401.1796 | 74579.3321 | 2526817.3948 | 2472918.2843 | 360558.4942 | 542132.7685 | 2188818.8897 | 2315111.5666 | 1941463.0601 | 2067743.8537 | 2194618.2704 | 4201146.8289 | 5956942.8819 | 6508461.7863 | 7447260.2775 | 8220856.132 | 9647462.4469 | 9856535.5089 | 9662649.5363 | 9966082.6706 | 9474839.6897 | 9732227.0505 | 9739846.5789 | 9228631.0802 | 9108894.8857 | 7787955.1077 | 6587316.3252 | 3777729.1166 | 1129668.1211 | 271131.5857 | 191845.2748 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 155271490.6698 | 138500000
CC_EMAAC_HRSG / SCR | CC | EMAAC |  | HRSG / SCR | 0.2394% | 7717.0955 | 38677.8696 | 38770.4831 | 1313580.1619 | 1285560.4077 | 187438.3508 | 281830.7533 | 1137869.7477 | 1203523.7025 | 1009280.4356 | 1074928.2127 | 1140884.5882 | 2183989.6872 | 3096750.0902 | 3383460.2788 | 3871499.9277 | 4273658.0614 | 5015287.337 | 5123975.1382 | 5023182.4304 | 5180923.8432 | 4925548.4307 | 5059352.6905 | 5063313.745 | 4797555.5074 | 4735309.9767 | 4048612.0415 | 3424453.2521 | 1963873.6202 | 587264.294 | 140949.272 | 99731.8396 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80718753.2724 | 72000000
CC_EMAAC_Condenser | CC | EMAAC |  | Condenser | 0.2394% | 5895.0035 | 29545.5948 | 29616.3413 | 1003429.2904 | 982025.3115 | 143182.0735 | 215287.381 | 869206.0573 | 919358.3838 | 770978.1105 | 821125.7181 | 871509.0604 | 1668325.4555 | 2365572.9856 | 2584587.713 | 2957395.7781 | 3264599.908 | 3831122.2713 | 3914147.675 | 3837153.2455 | 3957650.158 | 3762571.7179 | 3864783.3052 | 3867809.1108 | 3664799.3459 | 3617250.6766 | 3092689.7539 | 2615901.7898 | 1500181.2376 | 448604.669 | 107669.5828 | 76184.0441 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61660158.7498 | 55000000
CC_EMAAC_Steam Turbines | CC | EMAAC |  | Steam Turbines | 0.2394% | 8102.9502 | 40611.763 | 40709.0073 | 1379259.17 | 1349838.4281 | 196810.2683 | 295922.291 | 1194763.2351 | 1263699.8876 | 1059744.4574 | 1128674.6234 | 1197928.8176 | 2293189.1716 | 3251587.5947 | 3552633.2927 | 4065074.924 | 4487340.9645 | 5266051.7038 | 5380173.8951 | 5274341.552 | 5439970.0354 | 5171825.8523 | 5312320.325 | 5316479.4322 | 5037433.2828 | 4972075.4755 | 4251042.6436 | 3595675.9147 | 2062067.3012 | 616627.5087 | 147996.7356 | 104718.4316 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84754690.936 | 75600000
CC_EMAAC_Other Equipment | CC | EMAAC |  | Other Equipment | 0.2394% | 8254.5054 | 41371.3534 | 41470.4165 | 1405056.4249 | 1375085.4061 | 200491.3492 | 301457.1338 | 1217109.7327 | 1287335.7559 | 1079565.6037 | 1149785.0191 | 1220334.5233 | 2336080.3024 | 3312404.3257 | 3619080.6932 | 4141106.881 | 4571270.8603 | 5364546.3746 | 5480803.0735 | 5372991.2736 | 5541717.6231 | 5268558.1506 | 5411680.3904 | 5415917.2883 | 5131651.9423 | 5065071.702 | 4330552.8856 | 3662928.3716 | 2100635.597 | 628160.7269 | 150764.8227 | 106677.0541 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86339917.5628 | 77014000
CC_EMAAC_Construction Labor | CC | EMAAC |  | Construction Labor | 0.3684% | 34109.1371 | 171173.9815 | 171804.5923 | 5828388.3879 | 5711402.1352 | 833809.9105 | 1255322.5418 | 5074787.3041 | 5374502.7443 | 4512880.6024 | 4812600.3459 | 5114467.1956 | 9803194.3978 | 13918150.8108 | 15226314.9578 | 17445014.2977 | 19281916.2774 | 22657113.9656 | 23177902.4577 | 22751205.6239 | 23495842.4063 | 22366434.2908 | 23003581.7508 | 23051208.2298 | 21869417.2511 | 21613443.4208 | 18502911.0102 | 15670522.8541 | 8998375.8536 | 2694278.8172 | 647485.6161 | 458732.453 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 365528295.6212 | 306589500
CC_EMAAC_Other Labor | CC | EMAAC |  | Other Labor | 0.3684% | 7049.1405 | 35375.5486 | 35505.8733 | 1204519.7226 | 1180342.8422 | 172318.7295 | 259430.3363 | 1048777.2929 | 1110717.7703 | 932651.2458 | 994592.6125 | 1056977.7094 | 2025970.1671 | 2876384.6946 | 3146735.5036 | 3605261.4177 | 3984883.4531 | 4682416.2722 | 4790044.6539 | 4701861.6576 | 4855751.4862 | 4622343.1649 | 4754018.7895 | 4763861.4818 | 4519627.4934 | 4466726.8446 | 3823890.886 | 3238537.4111 | 1859642.9176 | 556811.2071 | 133812.1523 | 94803.6147 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 75541644.0931 | 63361100
CC_EMAAC_Materials | CC | EMAAC |  | Materials | 0.2394% | 7214.4339 | 36158.5436 | 36245.1246 | 1228018.6585 | 1201824.0022 | 175229.3455 | 263473.3941 | 1063753.3374 | 1125130.8489 | 943539.833 | 1004911.5692 | 1066571.8029 | 2041733.0923 | 2895039.8323 | 3163074.8341 | 3619325.4782 | 3995288.5951 | 4688611.0238 | 4790219.3243 | 4695991.8615 | 4843458.6121 | 4604717.3609 | 4729806.1315 | 4733509.1783 | 4485061.3988 | 4426870.2999 | 3784901.1977 | 3201397.6846 | 1835954.5299 | 549012.1817 | 131768.3845 | 93235.6954 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 75461047.5905 | 67310200
__
CC_SWMAAC_Gas Turbines | CC | SWMAAC |  | Gas Turbines | 0.2394% | 14844.6906 | 74401.1796 | 74579.3321 | 2526817.3948 | 2472918.2843 | 360558.4942 | 542132.7685 | 2188818.8897 | 2315111.5666 | 1941463.0601 | 2067743.8537 | 2194618.2704 | 4201146.8289 | 5956942.8819 | 6508461.7863 | 7447260.2775 | 8220856.132 | 9647462.4469 | 9856535.5089 | 9662649.5363 | 9966082.6706 | 9474839.6897 | 9732227.0505 | 9739846.5789 | 9228631.0802 | 9108894.8857 | 7787955.1077 | 6587316.3252 | 3777729.1166 | 1129668.1211 | 271131.5857 | 191845.2748 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 155271490.6698 | 138500000
CC_SWMAAC_HRSG / SCR | CC | SWMAAC |  | HRSG / SCR | 0.2394% | 7717.0955 | 38677.8696 | 38770.4831 | 1313580.1619 | 1285560.4077 | 187438.3508 | 281830.7533 | 1137869.7477 | 1203523.7025 | 1009280.4356 | 1074928.2127 | 1140884.5882 | 2183989.6872 | 3096750.0902 | 3383460.2788 | 3871499.9277 | 4273658.0614 | 5015287.337 | 5123975.1382 | 5023182.4304 | 5180923.8432 | 4925548.4307 | 5059352.6905 | 5063313.745 | 4797555.5074 | 4735309.9767 | 4048612.0415 | 3424453.2521 | 1963873.6202 | 587264.294 | 140949.272 | 99731.8396 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80718753.2724 | 72000000
CC_SWMAAC_Condenser | CC | SWMAAC |  | Condenser | 0.2394% | 5895.0035 | 29545.5948 | 29616.3413 | 1003429.2904 | 982025.3115 | 143182.0735 | 215287.381 | 869206.0573 | 919358.3838 | 770978.1105 | 821125.7181 | 871509.0604 | 1668325.4555 | 2365572.9856 | 2584587.713 | 2957395.7781 | 3264599.908 | 3831122.2713 | 3914147.675 | 3837153.2455 | 3957650.158 | 3762571.7179 | 3864783.3052 | 3867809.1108 | 3664799.3459 | 3617250.6766 | 3092689.7539 | 2615901.7898 | 1500181.2376 | 448604.669 | 107669.5828 | 76184.0441 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61660158.7498 | 55000000
CC_SWMAAC_Steam Turbines | CC | SWMAAC |  | Steam Turbines | 0.2394% | 8102.9502 | 40611.763 | 40709.0073 | 1379259.17 | 1349838.4281 | 196810.2683 | 295922.291 | 1194763.2351 | 1263699.8876 | 1059744.4574 | 1128674.6234 | 1197928.8176 | 2293189.1716 | 3251587.5947 | 3552633.2927 | 4065074.924 | 4487340.9645 | 5266051.7038 | 5380173.8951 | 5274341.552 | 5439970.0354 | 5171825.8523 | 5312320.325 | 5316479.4322 | 5037433.2828 | 4972075.4755 | 4251042.6436 | 3595675.9147 | 2062067.3012 | 616627.5087 | 147996.7356 | 104718.4316 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84754690.936 | 75600000
CC_SWMAAC_Other Equipment | CC | SWMAAC |  | Other Equipment | 0.2394% | 8254.5054 | 41371.3534 | 41470.4165 | 1405056.4249 | 1375085.4061 | 200491.3492 | 301457.1338 | 1217109.7327 | 1287335.7559 | 1079565.6037 | 1149785.0191 | 1220334.5233 | 2336080.3024 | 3312404.3257 | 3619080.6932 | 4141106.881 | 4571270.8603 | 5364546.3746 | 5480803.0735 | 5372991.2736 | 5541717.6231 | 5268558.1506 | 5411680.3904 | 5415917.2883 | 5131651.9423 | 5065071.702 | 4330552.8856 | 3662928.3716 | 2100635.597 | 628160.7269 | 150764.8227 | 106677.0541 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86339917.5628 | 77014000
CC_SWMAAC_Construction Labor | CC | SWMAAC |  | Construction Labor | 0.3684% | 26433.6064 | 132654.9435 | 133143.6488 | 4516834.422 | 4426173.4197 | 646178.8499 | 972839.0921 | 3932815.1204 | 4165086.0206 | 3497353.4862 | 3729627.7213 | 3963565.9022 | 7597195.4775 | 10786169.0898 | 11799958.9156 | 13519387.4924 | 14942934.027 | 17558615.7703 | 17962211.9672 | 17631534.1163 | 18208606.3405 | 17333347.3301 | 17827118.4016 | 17864027.5616 | 16948173.3293 | 16749800.9268 | 14339227.2093 | 12144207.3396 | 6973484.1079 | 2087989.0793 | 501782.847 | 355504.5403 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 283273982.1026 | 237598100
CC_SWMAAC_Other Labor | CC | SWMAAC |  | Other Labor | 0.3684% | 6435.0993 | 32294.0323 | 32413.0046 | 1099595.6334 | 1077524.7685 | 157308.2773 | 236831.7095 | 957419.7169 | 1013964.6427 | 851409.2532 | 907954.9909 | 964905.8061 | 1849490.6372 | 2625826.7017 | 2872627.6162 | 3291211.9561 | 3637765.6278 | 4274537.3034 | 4372790.3218 | 4292288.8274 | 4432773.5206 | 4219697.0834 | 4339902.622 | 4348887.9306 | 4125928.8356 | 4077636.2911 | 3490796.9062 | 2956432.7833 | 1697651.9302 | 508308.1335 | 122155.9561 | 86545.3996 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 68961313.3185 | 57841800
CC_SWMAAC_Materials | CC | SWMAAC |  | Materials | 0.2394% | 7214.4339 | 36158.5436 | 36245.1246 | 1228018.6585 | 1201824.0022 | 175229.3455 | 263473.3941 | 1063753.3374 | 1125130.8489 | 943539.833 | 1004911.5692 | 1066571.8029 | 2041733.0923 | 2895039.8323 | 3163074.8341 | 3619325.4782 | 3995288.5951 | 4688611.0238 | 4790219.3243 | 4695991.8615 | 4843458.6121 | 4604717.3609 | 4729806.1315 | 4733509.1783 | 4485061.3988 | 4426870.2999 | 3784901.1977 | 3201397.6846 | 1835954.5299 | 549012.1817 | 131768.3845 | 93235.6954 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 75461047.5905 | 67310200
__
CC_Rest of RTO_Gas Turbines | CC | Rest of RTO |  | Gas Turbines | 0.2394% | 14844.6906 | 74401.1796 | 74579.3321 | 2526817.3948 | 2472918.2843 | 360558.4942 | 542132.7685 | 2188818.8897 | 2315111.5666 | 1941463.0601 | 2067743.8537 | 2194618.2704 | 4201146.8289 | 5956942.8819 | 6508461.7863 | 7447260.2775 | 8220856.132 | 9647462.4469 | 9856535.5089 | 9662649.5363 | 9966082.6706 | 9474839.6897 | 9732227.0505 | 9739846.5789 | 9228631.0802 | 9108894.8857 | 7787955.1077 | 6587316.3252 | 3777729.1166 | 1129668.1211 | 271131.5857 | 191845.2748 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 155271490.6698 | 138500000
CC_Rest of RTO_HRSG / SCR | CC | Rest of RTO |  | HRSG / SCR | 0.2394% | 7717.0955 | 38677.8696 | 38770.4831 | 1313580.1619 | 1285560.4077 | 187438.3508 | 281830.7533 | 1137869.7477 | 1203523.7025 | 1009280.4356 | 1074928.2127 | 1140884.5882 | 2183989.6872 | 3096750.0902 | 3383460.2788 | 3871499.9277 | 4273658.0614 | 5015287.337 | 5123975.1382 | 5023182.4304 | 5180923.8432 | 4925548.4307 | 5059352.6905 | 5063313.745 | 4797555.5074 | 4735309.9767 | 4048612.0415 | 3424453.2521 | 1963873.6202 | 587264.294 | 140949.272 | 99731.8396 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80718753.2724 | 72000000
CC_Rest of RTO_Condenser | CC | Rest of RTO |  | Condenser | 0.2394% | 5895.0035 | 29545.5948 | 29616.3413 | 1003429.2904 | 982025.3115 | 143182.0735 | 215287.381 | 869206.0573 | 919358.3838 | 770978.1105 | 821125.7181 | 871509.0604 | 1668325.4555 | 2365572.9856 | 2584587.713 | 2957395.7781 | 3264599.908 | 3831122.2713 | 3914147.675 | 3837153.2455 | 3957650.158 | 3762571.7179 | 3864783.3052 | 3867809.1108 | 3664799.3459 | 3617250.6766 | 3092689.7539 | 2615901.7898 | 1500181.2376 | 448604.669 | 107669.5828 | 76184.0441 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61660158.7498 | 55000000
CC_Rest of RTO_Steam Turbines | CC | Rest of RTO |  | Steam Turbines | 0.2394% | 8102.9502 | 40611.763 | 40709.0073 | 1379259.17 | 1349838.4281 | 196810.2683 | 295922.291 | 1194763.2351 | 1263699.8876 | 1059744.4574 | 1128674.6234 | 1197928.8176 | 2293189.1716 | 3251587.5947 | 3552633.2927 | 4065074.924 | 4487340.9645 | 5266051.7038 | 5380173.8951 | 5274341.552 | 5439970.0354 | 5171825.8523 | 5312320.325 | 5316479.4322 | 5037433.2828 | 4972075.4755 | 4251042.6436 | 3595675.9147 | 2062067.3012 | 616627.5087 | 147996.7356 | 104718.4316 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84754690.936 | 75600000
CC_Rest of RTO_Other Equipment | CC | Rest of RTO |  | Other Equipment | 0.2394% | 8254.5054 | 41371.3534 | 41470.4165 | 1405056.4249 | 1375085.4061 | 200491.3492 | 301457.1338 | 1217109.7327 | 1287335.7559 | 1079565.6037 | 1149785.0191 | 1220334.5233 | 2336080.3024 | 3312404.3257 | 3619080.6932 | 4141106.881 | 4571270.8603 | 5364546.3746 | 5480803.0735 | 5372991.2736 | 5541717.6231 | 5268558.1506 | 5411680.3904 | 5415917.2883 | 5131651.9423 | 5065071.702 | 4330552.8856 | 3662928.3716 | 2100635.597 | 628160.7269 | 150764.8227 | 106677.0541 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86339917.5628 | 77014000
CC_Rest of RTO_Construction Labor | CC | Rest of RTO |  | Construction Labor | 0.3684% | 27720.3859 | 139112.5439 | 139625.0393 | 4736712.4863 | 4641638.1352 | 677634.631 | 1020196.5899 | 4124263.3106 | 4367841.0844 | 3667603.5425 | 3911184.8135 | 4156511.0307 | 7967024.539 | 11311236.3733 | 12374377.1657 | 14177506.9792 | 15670351.3066 | 18413363.6059 | 18836606.7375 | 18489831.5938 | 19094995.5105 | 18177129.1697 | 18694936.86 | 18733642.7462 | 17773205.0209 | 17565175.9129 | 15037256.2329 | 12735383.4934 | 7312951.0981 | 2189631.7242 | 526209.4765 | 372810.3883 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 297063669.5276 | 249164300
CC_Rest of RTO_Other Labor | CC | Rest of RTO |  | Other Labor | 0.3684% | 6538.0421 | 32810.6425 | 32931.5181 | 1117185.9546 | 1094762.0203 | 159824.7507 | 240620.3257 | 972735.6383 | 1030185.118 | 865029.3166 | 922479.6211 | 980341.4831 | 1879077.09 | 2667832.266 | 2918581.2748 | 3343861.7426 | 3695959.2617 | 4342917.4258 | 4442742.2058 | 4360952.9225 | 4503684.9607 | 4287199.9224 | 4409328.3988 | 4418457.4461 | 4191931.6563 | 4142866.5719 | 3546639.4695 | 3003727.0801 | 1724809.4068 | 516439.5802 | 124110.0949 | 87929.8735 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70064493.0815 | 58767100
CC_Rest of RTO_Materials | CC | Rest of RTO |  | Materials | 0.2394% | 7214.4339 | 36158.5436 | 36245.1246 | 1228018.6585 | 1201824.0022 | 175229.3455 | 263473.3941 | 1063753.3374 | 1125130.8489 | 943539.833 | 1004911.5692 | 1066571.8029 | 2041733.0923 | 2895039.8323 | 3163074.8341 | 3619325.4782 | 3995288.5951 | 4688611.0238 | 4790219.3243 | 4695991.8615 | 4843458.6121 | 4604717.3609 | 4729806.1315 | 4733509.1783 | 4485061.3988 | 4426870.2999 | 3784901.1977 | 3201397.6846 | 1835954.5299 | 549012.1817 | 131768.3845 | 93235.6954 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 75461047.5905 | 67310200
__
CC_WMAAC_Gas Turbines | CC | WMAAC |  | Gas Turbines | 0.2394% | 14844.6906 | 74401.1796 | 74579.3321 | 2526817.3948 | 2472918.2843 | 360558.4942 | 542132.7685 | 2188818.8897 | 2315111.5666 | 1941463.0601 | 2067743.8537 | 2194618.2704 | 4201146.8289 | 5956942.8819 | 6508461.7863 | 7447260.2775 | 8220856.132 | 9647462.4469 | 9856535.5089 | 9662649.5363 | 9966082.6706 | 9474839.6897 | 9732227.0505 | 9739846.5789 | 9228631.0802 | 9108894.8857 | 7787955.1077 | 6587316.3252 | 3777729.1166 | 1129668.1211 | 271131.5857 | 191845.2748 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 155271490.6698 | 138500000
CC_WMAAC_HRSG / SCR | CC | WMAAC |  | HRSG / SCR | 0.2394% | 7717.0955 | 38677.8696 | 38770.4831 | 1313580.1619 | 1285560.4077 | 187438.3508 | 281830.7533 | 1137869.7477 | 1203523.7025 | 1009280.4356 | 1074928.2127 | 1140884.5882 | 2183989.6872 | 3096750.0902 | 3383460.2788 | 3871499.9277 | 4273658.0614 | 5015287.337 | 5123975.1382 | 5023182.4304 | 5180923.8432 | 4925548.4307 | 5059352.6905 | 5063313.745 | 4797555.5074 | 4735309.9767 | 4048612.0415 | 3424453.2521 | 1963873.6202 | 587264.294 | 140949.272 | 99731.8396 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80718753.2724 | 72000000
CC_WMAAC_Condenser | CC | WMAAC |  | Condenser | 0.2394% | 5895.0035 | 29545.5948 | 29616.3413 | 1003429.2904 | 982025.3115 | 143182.0735 | 215287.381 | 869206.0573 | 919358.3838 | 770978.1105 | 821125.7181 | 871509.0604 | 1668325.4555 | 2365572.9856 | 2584587.713 | 2957395.7781 | 3264599.908 | 3831122.2713 | 3914147.675 | 3837153.2455 | 3957650.158 | 3762571.7179 | 3864783.3052 | 3867809.1108 | 3664799.3459 | 3617250.6766 | 3092689.7539 | 2615901.7898 | 1500181.2376 | 448604.669 | 107669.5828 | 76184.0441 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61660158.7498 | 55000000
CC_WMAAC_Steam Turbines | CC | WMAAC |  | Steam Turbines | 0.2394% | 8102.9502 | 40611.763 | 40709.0073 | 1379259.17 | 1349838.4281 | 196810.2683 | 295922.291 | 1194763.2351 | 1263699.8876 | 1059744.4574 | 1128674.6234 | 1197928.8176 | 2293189.1716 | 3251587.5947 | 3552633.2927 | 4065074.924 | 4487340.9645 | 5266051.7038 | 5380173.8951 | 5274341.552 | 5439970.0354 | 5171825.8523 | 5312320.325 | 5316479.4322 | 5037433.2828 | 4972075.4755 | 4251042.6436 | 3595675.9147 | 2062067.3012 | 616627.5087 | 147996.7356 | 104718.4316 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84754690.936 | 75600000
CC_WMAAC_Other Equipment | CC | WMAAC |  | Other Equipment | 0.2394% | 8254.5054 | 41371.3534 | 41470.4165 | 1405056.4249 | 1375085.4061 | 200491.3492 | 301457.1338 | 1217109.7327 | 1287335.7559 | 1079565.6037 | 1149785.0191 | 1220334.5233 | 2336080.3024 | 3312404.3257 | 3619080.6932 | 4141106.881 | 4571270.8603 | 5364546.3746 | 5480803.0735 | 5372991.2736 | 5541717.6231 | 5268558.1506 | 5411680.3904 | 5415917.2883 | 5131651.9423 | 5065071.702 | 4330552.8856 | 3662928.3716 | 2100635.597 | 628160.7269 | 150764.8227 | 106677.0541 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86339917.5628 | 77014000
CC_WMAAC_Construction Labor | CC | WMAAC |  | Construction Labor | 0.3684% | 30837.4404 | 154755.2328 | 155325.3563 | 5269338.2106 | 5163573.1018 | 753832.1281 | 1134913.9069 | 4588021.4001 | 4858988.5897 | 4080011.9373 | 4350983.0174 | 4623895.2565 | 8862886.8545 | 12583142.8872 | 13765829.9126 | 15771714.9758 | 17432424.1027 | 20483877.9459 | 20954713.1954 | 20568944.475 | 21242156.8262 | 20221079.8248 | 20797113.0665 | 20840171.2858 | 19771735.906 | 19540314.6974 | 16728139.8395 | 14167430.061 | 8135265.2847 | 2435847.678 | 585379.7775 | 414731.5316 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 330467375.7061 | 277181900
CC_WMAAC_Other Labor | CC | WMAAC |  | Other Labor | 0.3684% | 6787.4056 | 34062.0532 | 34187.5389 | 1159795.8605 | 1136516.6686 | 165920.5287 | 249797.6783 | 1009836.153 | 1069476.7782 | 898021.8704 | 957663.3518 | 1017732.0877 | 1950745.8195 | 2769584.4239 | 3029897.0973 | 3471397.9271 | 3836924.5823 | 4508557.9818 | 4612190.1177 | 4527281.3593 | 4675457.2529 | 4450715.3912 | 4577501.895 | 4586979.1277 | 4351813.5564 | 4300877.1107 | 3681909.6752 | 3118290.3966 | 1790594.3069 | 536136.7862 | 128843.7021 | 91283.553 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72736780.0378 | 61008500
CC_WMAAC_Materials | CC | WMAAC |  | Materials | 0.2394% | 7214.4339 | 36158.5436 | 36245.1246 | 1228018.6585 | 1201824.0022 | 175229.3455 | 263473.3941 | 1063753.3374 | 1125130.8489 | 943539.833 | 1004911.5692 | 1066571.8029 | 2041733.0923 | 2895039.8323 | 3163074.8341 | 3619325.4782 | 3995288.5951 | 4688611.0238 | 4790219.3243 | 4695991.8615 | 4843458.6121 | 4604717.3609 | 4729806.1315 | 4733509.1783 | 4485061.3988 | 4426870.2999 | 3784901.1977 | 3201397.6846 | 1835954.5299 | 549012.1817 | 131768.3845 | 93235.6954 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 75461047.5905 | 67310200
|  |  | Battery Storage |  | Monthly Escalation Rate
BESS_EMAAC_Batteries and Enclosures | BESS | EMAAC |  | Batteries and Enclosures | -0.0259% | 1861064.6775 | 3004647.313 | 72200592.4686 | 3456760.9667 | 3620283.2973 | 4128927.3784 | 4894548.8717 | 5646227.8765 | 6085466.8264 | 5995889.5963 | 5309264.3102 | 59058147.2829 | 2700026.2142 | 1363284.7649 | 430165.6696 | 13760771.2401 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 193516068.7544 | 196133500
BESS_EMAAC_PCS and BOP Equipment | BESS | EMAAC |  | PCS and BOP Equipment | -0.0259% | 278549.3368 | 449711.6766 | 10806409.5748 | 517380.447 | 541855.167 | 617984.9615 | 732577.0881 | 845082.4141 | 910824.2015 | 897416.9952 | 794648.3916 | 8839353.0641 | 404118.417 | 204045.6045 | 64383.771 | 2059602.6293 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28963943.74 | 29355700
BESS_EMAAC_Project Management | BESS | EMAAC |  | Project Management | -0.0259% | 113427.7472 | 183126.5618 | 4400465.3071 | 210681.8821 | 220648.2039 | 251648.9278 | 298311.8527 | 344125.0139 | 370895.6496 | 365436.117 | 323587.835 | 3599462.5436 | 164560.5843 | 83089.1701 | 26217.6395 | 838688.3593 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11794373.3951 | 11953900
BESS_EMAAC_Construction & Materials | BESS | EMAAC |  | Construction & Materials | -0.0259% | 564898.4384 | 912015.8991 | 21915413.4896 | 1049248.2586 | 1098883.0243 | 1253274.3524 | 1485667.3429 | 1713828.2989 | 1847152.734 | 1819962.9012 | 1611548.0317 | 17926220.1789 | 819552.7058 | 413804.7668 | 130570.3762 | 4176876.9667 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 58738917.7656 | 59533400
BESS_EMAAC_Optional Augmentation to Maintain Nameplate over 15 Years | BESS | EMAAC |  | Optional Augmentation to Maintain Nameplate over 15 Years | -0.0259% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BESS_EMAAC_Project Development | BESS | EMAAC |  | Project Development | -0.0259% | 140898.6705 | 227477.7534 | 5466208.4629 | 261706.662 | 274086.7148 | 312595.465 | 370559.6249 | 427468.218 | 460722.4003 | 453940.6303 | 401957.1656 | 4471211.8481 | 204415.3052 | 103212.4317 | 32567.2566 | 1041809.2378 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14650837.8474 | 14849000
BESS_EMAAC_Mobilization and Start-Up | BESS | EMAAC |  | Mobilization and Start-Up | -0.0259% | 28181.6319 | 45498.6146 | 1093315.3165 | 52344.8573 | 54821.0346 | 62523.3033 | 74116.916 | 85499.4011 | 92150.6855 | 90794.2402 | 80396.8471 | 894302.592 | 40885.8143 | 20643.8765 | 6513.89 | 208375.8796 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2930364.9004 | 2970000
BESS_EMAAC_Owner's Contingency | BESS | EMAAC |  | Owner's Contingency | -0.0259% | 106976.3359 | 172710.9026 | 4150180.7671 | 198698.9634 | 208098.4324 | 237335.9333 | 281344.8186 | 324552.2722 | 349800.2789 | 344651.2672 | 305183.1831 | 3394736.5058 | 155200.8991 | 78363.3211 | 24726.4631 | 790986.4198 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11123546.7635 | 11274000
BESS_SWMAAC_Batteries and Enclosures | BESS | SWMAAC |  | Batteries and Enclosures | -0.0259% | 1861064.6775 | 3004647.313 | 72200592.4686 | 3456760.9667 | 3620283.2973 | 4128927.3784 | 4894548.8717 | 5646227.8765 | 6085466.8264 | 5995889.5963 | 5309264.3102 | 59058147.2829 | 2700026.2142 | 1363284.7649 | 430165.6696 | 13760771.2401 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 193516068.7544 | 196133500
BESS_SWMAAC_PCS and BOP Equipment | BESS | SWMAAC |  | PCS and BOP Equipment | -0.0259% | 278549.3368 | 449711.6766 | 10806409.5748 | 517380.447 | 541855.167 | 617984.9615 | 732577.0881 | 845082.4141 | 910824.2015 | 897416.9952 | 794648.3916 | 8839353.0641 | 404118.417 | 204045.6045 | 64383.771 | 2059602.6293 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28963943.74 | 29355700
BESS_SWMAAC_Project Management | BESS | SWMAAC |  | Project Management | -0.0259% | 90516.1754 | 146136.3414 | 3511603.636 | 168125.6893 | 176078.8874 | 200817.6927 | 238055.0495 | 274614.2886 | 295977.4526 | 291620.7054 | 258225.469 | 2872397.5475 | 131320.555 | 66305.7681 | 20921.8689 | 669279.4708 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9411996.5976 | 9539300
BESS_SWMAAC_Construction & Materials | BESS | SWMAAC |  | Construction & Materials | -0.0259% | 450794.1423 | 727797.0641 | 17488701.2525 | 837309.7475 | 876918.7464 | 1000124.4442 | 1185576.1851 | 1367650.7236 | 1474044.8474 | 1452347.1111 | 1286030.131 | 14305288.3508 | 654010.5866 | 330220.0046 | 104196.3594 | 3333186.183 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 46874195.8798 | 47508200
BESS_SWMAAC_Optional Augmentation to Maintain Nameplate over 15 Years | BESS | SWMAAC |  | Optional Augmentation to Maintain Nameplate over 15 Years | -0.0259% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BESS_SWMAAC_Project Development | BESS | SWMAAC |  | Project Development | -0.0259% | 134047.7822 | 216417.1475 | 5200426.0863 | 248981.7506 | 260759.8505 | 297396.1974 | 352541.9773 | 406683.5151 | 438320.7859 | 431868.7645 | 382412.8816 | 4253808.9957 | 194476.0601 | 98193.954 | 30983.7453 | 991153.5526 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13938473.0466 | 14127000
BESS_SWMAAC_Mobilization and Start-Up | BESS | SWMAAC |  | Mobilization and Start-Up | -0.0259% | 26805.7609 | 43277.3017 | 1039937.9694 | 49789.3003 | 52144.5868 | 59470.8188 | 70498.4134 | 81325.188 | 87651.7463 | 86361.5247 | 76471.7485 | 850641.3544 | 38889.7055 | 19636.0105 | 6195.8718 | 198202.6464 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2787299.9474 | 2825000
BESS_SWMAAC_Owner's Contingency | BESS | SWMAAC |  | Owner's Contingency | -0.0259% | 106976.3359 | 172710.9026 | 4150180.7671 | 198698.9634 | 208098.4324 | 237335.9333 | 281344.8186 | 324552.2722 | 349800.2789 | 344651.2672 | 305183.1831 | 3394736.5058 | 155200.8991 | 78363.3211 | 24726.4631 | 790986.4198 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11123546.7635 | 11274000
BESS_Rest of RTO_Batteries and Enclosures | BESS | Rest of RTO |  | Batteries and Enclosures | -0.0259% | 1861064.6775 | 3004647.313 | 72200592.4686 | 3456760.9667 | 3620283.2973 | 4128927.3784 | 4894548.8717 | 5646227.8765 | 6085466.8264 | 5995889.5963 | 5309264.3102 | 59058147.2829 | 2700026.2142 | 1363284.7649 | 430165.6696 | 13760771.2401 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 193516068.7544 | 196133500
BESS_Rest of RTO_PCS and BOP Equipment | BESS | Rest of RTO |  | PCS and BOP Equipment | -0.0259% | 278549.3368 | 449711.6766 | 10806409.5748 | 517380.447 | 541855.167 | 617984.9615 | 732577.0881 | 845082.4141 | 910824.2015 | 897416.9952 | 794648.3916 | 8839353.0641 | 404118.417 | 204045.6045 | 64383.771 | 2059602.6293 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28963943.74 | 29355700
BESS_Rest of RTO_Project Management | BESS | Rest of RTO |  | Project Management | -0.0259% | 95745.4337 | 154578.8621 | 3714474.3669 | 177838.5684 | 186251.2349 | 212419.239 | 251807.855 | 290479.1775 | 313076.5242 | 308468.0811 | 273143.5507 | 3038340.3618 | 138907.1449 | 70136.354 | 22130.5574 | 707944.7729 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9955742.0846 | 10090400
BESS_Rest of RTO_Construction & Materials | BESS | Rest of RTO |  | Construction & Materials | -0.0259% | 476835.1088 | 769839.6223 | 18498968.7794 | 885678.5106 | 927575.5974 | 1057898.5027 | 1254063.2102 | 1446655.6248 | 1559195.8041 | 1536244.6575 | 1360320.066 | 15131660.0792 | 691790.731 | 349295.7806 | 110215.457 | 3525733.915 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 49581971.4464 | 50252600
BESS_Rest of RTO_Optional Augmentation to Maintain Nameplate over 15 Years | BESS | Rest of RTO |  | Optional Augmentation to Maintain Nameplate over 15 Years | -0.0259% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BESS_Rest of RTO_Project Development | BESS | Rest of RTO |  | Project Development | -0.0259% | 135613.4285 | 218944.8483 | 5261165.8261 | 251889.7982 | 263805.4635 | 300869.7142 | 356659.5838 | 411433.4818 | 443440.2684 | 436912.889 | 386879.3731 | 4303492.4731 | 196747.4942 | 99340.836 | 31345.6281 | 1002729.9904 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14101271.0967 | 14292000
BESS_Rest of RTO_Mobilization and Start-Up | BESS | Rest of RTO |  | Mobilization and Start-Up | -0.0259% | 27118.8902 | 43782.8419 | 1052085.9174 | 50370.9098 | 52753.7094 | 60165.5222 | 71321.9347 | 82275.1813 | 88675.6428 | 87370.3496 | 77365.0468 | 860578.0498 | 39343.9923 | 19865.3869 | 6268.2483 | 200517.934 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2819859.5574 | 2858000
BESS_Rest of RTO_Owner's Contingency | BESS | Rest of RTO |  | Owner's Contingency | -0.0259% | 106976.3359 | 172710.9026 | 4150180.7671 | 198698.9634 | 208098.4324 | 237335.9333 | 281344.8186 | 324552.2722 | 349800.2789 | 344651.2672 | 305183.1831 | 3394736.5058 | 155200.8991 | 78363.3211 | 24726.4631 | 790986.4198 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11123546.7635 | 11274000
BESS_WMAAC_Batteries and Enclosures | BESS | WMAAC |  | Batteries and Enclosures | -0.0259% | 1861064.6775 | 3004647.313 | 72200592.4686 | 3456760.9667 | 3620283.2973 | 4128927.3784 | 4894548.8717 | 5646227.8765 | 6085466.8264 | 5995889.5963 | 5309264.3102 | 59058147.2829 | 2700026.2142 | 1363284.7649 | 430165.6696 | 13760771.2401 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 193516068.7544 | 196133500
BESS_WMAAC_PCS and BOP Equipment | BESS | WMAAC |  | PCS and BOP Equipment | -0.0259% | 278549.3368 | 449711.6766 | 10806409.5748 | 517380.447 | 541855.167 | 617984.9615 | 732577.0881 | 845082.4141 | 910824.2015 | 897416.9952 | 794648.3916 | 8839353.0641 | 404118.417 | 204045.6045 | 64383.771 | 2059602.6293 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28963943.74 | 29355700
BESS_WMAAC_Project Management | BESS | WMAAC |  | Project Management | -0.0259% | 103561.3294 | 167197.4509 | 4017694.5104 | 192355.8947 | 201455.3043 | 229759.4562 | 272363.4455 | 314191.5872 | 338633.6016 | 333648.9618 | 295440.8176 | 3286366.3028 | 150246.4194 | 75861.7281 | 23937.12 | 765735.7534 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10768449.6835 | 10914100
BESS_WMAAC_Construction & Materials | BESS | WMAAC |  | Construction & Materials | -0.0259% | 515758.9715 | 832681.3283 | 20009032.3349 | 957976.0995 | 1003293.229 | 1144254.3419 | 1356431.8974 | 1564745.5552 | 1686472.3452 | 1661647.7055 | 1471362.4587 | 16366851.5481 | 748261.3366 | 377808.6579 | 119212.3014 | 3813538.1897 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 53629328.301 | 54354700
BESS_WMAAC_Optional Augmentation to Maintain Nameplate over 15 Years | BESS | WMAAC |  | Optional Augmentation to Maintain Nameplate over 15 Years | -0.0259% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BESS_WMAAC_Project Development | BESS | WMAAC |  | Project Development | -0.0259% | 137947.6646 | 222713.4204 | 5351723.2564 | 256225.4329 | 268346.1957 | 306048.4121 | 362798.5607 | 418515.2504 | 451072.9514 | 444433.22 | 393538.5059 | 4377566.0211 | 200133.996 | 101050.7329 | 31885.1624 | 1019989.4066 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14343988.1894 | 14538000
BESS_WMAAC_Mobilization and Start-Up | BESS | WMAAC |  | Mobilization and Start-Up | -0.0259% | 27593.3284 | 44548.8118 | 1070491.8991 | 51252.1364 | 53676.6224 | 61218.1031 | 72569.6942 | 83714.5652 | 90227.0012 | 88898.8722 | 78718.529 | 875633.649 | 40032.3057 | 20212.9269 | 6377.9098 | 204025.9454 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2869192.2998 | 2908000
BESS_WMAAC_Owner's Contingency | BESS | WMAAC |  | Owner's Contingency | -0.0259% | 106976.3359 | 172710.9026 | 4150180.7671 | 198698.9634 | 208098.4324 | 237335.9333 | 281344.8186 | 324552.2722 | 349800.2789 | 344651.2672 | 305183.1831 | 3394736.5058 | 155200.8991 | 78363.3211 | 24726.4631 | 790986.4198 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11123546.7635 | 11274000
Batteries and Enclosures |  | -1.5%
PCS and BOP Equipment |  | -1.5%
Project Management |  | -1.5%
Construction & Materials |  | -1.5%
Optional Augmentation to Maintain Nameplate over 15 Years |  | -1.5%
Project Development |  | -1.5%
Mobilization and Start-Up |  | -1.5%
Owner's Contingency |  | -1.5%

## Capital Costs
2021
Units | Reference Year Overnight Costs (2021$) |  |  |  | Reference Year Overnight Costs (2021$)
Location | EMAAC | SWMAAC | Rest of RTO | WMAAC | EMAAC | SWMAAC | Rest of RTO | WMAAC
Technology | Frame-Type Combustion Turbine | Frame-Type Combustion Turbine | Frame-Type Combustion Turbine | Frame-Type Combustion Turbine | Combined Cycle Dry ACC | Combined Cycle Dry ACC | Combined Cycle Dry ACC | Combined Cycle Dry ACC
Plant Capacity (MW) | 360.589 | 362.838 | 352.927 | 349.94 | 1170.73 | 1173.658 | 1144.094 | 1133.424
Project Costs
Owner Furnished Equipment
Gas Turbines | 69250000 | 69250000 | 69250000 | 69250000 | 138500000 | 138500000 | 138500000 | 138500000
HRSG / SCR | 29558900 | 29558900 | 29558900 | 29558900 | 72000000 | 72000000 | 72000000 | 72000000
Steam Turbines | 0 | 0 | 0 | 0 | 75600000 | 75600000 | 75600000 | 75600000
Sales Tax | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Owner Furnished Equipment | 98808900 | 98808900 | 98808900 | 98808900 | 286100000 | 286100000 | 286100000 | 286100000
EPC Costs
Equipment
Condenser | 0 | 0 | 0 | 0 | 55000000 | 55000000 | 55000000 | 55000000
Other Equipment | 21281700 | 21281700 | 21281700 | 21281700 | 77014000 | 77014000 | 77014000 | 77014000
Equipment Subtotal | 21281700 | 21281700 | 21281700 | 21281700 | 132014000 | 132014000 | 132014000 | 132014000
Construction Labor | 41657600 | 31178500 | 33466500 | 37051400 | 306589500 | 237598100 | 249164300 | 277181900
Other Labor | 13511600 | 12673300 | 12856400 | 13143200 | 63361100 | 57841800 | 58767100 | 61008500
Materials | 7146800 | 7146800 | 7146800 | 7146800 | 67310200 | 67310200 | 67310200 | 67310200
Sales Tax | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
EPC Contractor Fee | 18241000 | 17109000 | 17356000 | 17743000 | 85537000 | 78086000 | 79336000 | 82361000
EPC Contingency | 20065000 | 18820000 | 19092000 | 19518000 | 94091000 | 85895000 | 87269000 | 90598000
Total EPC Costs | 121904000 | 108209000 | 111199000 | 115884000 | 748903000 | 658745000 | 673861000 | 710474000
Total Project Costs | 220712900 | 207017900 | 210007900 | 214692900 | 1035003000 | 944845000 | 959961000 | 996574000
Non-EPC Costs
Project Development | 11036000 | 10351000 | 10500000 | 10735000 | 51750000 | 47242000 | 47998000 | 49829000
Mobilization and Start-Up | 2207000 | 2070000 | 2100000 | 2147000 | 10350000 | 9448000 | 9600000 | 9966000
Net Start-Up Fuel Costs | -551000 | -555000 | 123000 | -532000 | -13918000 | -13994000 | -9784000 | -13490000
Electrical Interconnection | 6807000 | 6850000 | 6663000 | 6606000 | 22102000 | 22157000 | 21599000 | 21398000
Gas Interconnection | 29552000 | 29552000 | 29552000 | 29552000 | 29552000 | 29552000 | 29552000 | 29552000
Land | 366000 | 295000 | 164000 | 306000 | 2196000 | 1770000 | 984000 | 1836000
Fuel Inventories | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Non-Fuel Inventories | 1104000 | 1035000 | 1050000 | 1073000 | 5175000 | 4724000 | 4800000 | 4983000
Owner's Contingency | 4042000 | 3968000 | 4012000 | 3991000 | 8577000 | 8072000 | 8380000 | 8326000
Emission Reduction Credit | 0 | 0 | 0 | 0 | 2000000 | 2000000 | 2000000 | 2000000
| 9.552% | 9.536% | 9.537% | 9.547% | 9.753% | 9.745% | 9.74% | 9.75%
Subtotal - Non-EPC Costs w/o Financing Fees | 54563000 | 53566000 | 54164000 | 53878000 | 117784000 | 110971000 | 115129000 | 114400000
Financing Fees | 1200000 | 1178000 | 1192000 | 1185000 | 2591000 | 2441000 | 2533000 | 2517000
Total Non-EPC Costs | 55763000 | 54744000 | 55356000 | 55063000 | 120375000 | 113412000 | 117662000 | 116917000
Overnight Capital Costs ($) | 276475900 | 261761900 | 265363900 | 269755900 | 1155378000 | 1058257000 | 1077623000 | 1113491000
Overnight Capital Costs ($/kW) | 766.7341 | 721.4291 | 751.8946 | 770.8633 | 986.8868 | 901.6741 | 941.9008 | 982.4135

## BESS_Capital Costs
2021
Units | Reference Year Overnight Costs (2021$)
Location | EMAAC | SWMAAC | Rest of RTO | WMAAC
Technology | Lithium-Ion 4-hour Batteries | Lithium-Ion 4-hour Batteries | Lithium-Ion 4-hour Batteries | Lithium-Ion 4-hour Batteries
Plant Nameplate Power (MW) | 200 | 200 | 200 | 200
Storage Duration | 4 | 4 | 4 | 4
Overbuild (%) | 22.33% | 22.33% | 22.33% | 22.33%
Gross Plant Capacity Installed (MWhDC) | 1029.9738 | 1029.9738 | 1029.9738 | 1029.9738
Gross BOL Capacity at POI (MWhAC) | 914.8227 | 914.8227 | 914.8227 | 914.8227
Project Costs
EPC Costs
Batteries and Enclosures | 196133500 | 196133500 | 196133500 | 196133500
PCS and BOP Equipment | 29355700 | 29355700 | 29355700 | 29355700
BESS Equipment Subtotal | 225489200 | 225489200 | 225489200 | 225489200
Project Management | 11953900 | 9539300 | 10090400 | 10914100
Construction & Materials | 59533400 | 47508200 | 50252600 | 54354700
Sales Tax | 0 | 0 | 0 | 0
EPC Contractor Fee | Included | Included | Included | Included
EPC Contingency | Included | Included | Included | Included
Subtotal - EPC Costs w/o Augmentation | 296977000 | 282537000 | 285832000 | 290758000
Optional Augmentation to Maintain Nameplate over 15 Years | 0 | 0 | 0 | 0
Total EPC Costs | 296977000 | 282537000 | 285832000 | 290758000
Non-EPC Costs
Project Development | 14849000 | 14127000 | 14292000 | 14538000
Mobilization and Start-Up | 2970000 | 2825000 | 2858000 | 2908000
Owner's Contingency | 11274000 | 11274000 | 11274000 | 11274000
Spare Parts Inventories | Included | Included | Included | Included
Electrical Interconnection | 3776000 | 3776000 | 3776000 | 3776000
Land | 420000 | 338000 | 187000 | 352000
Working Capital | 36000 | 34000 | 35000 | 35000
Subtotal - Non-EPC Costs w/o Financing Fees | 33325000 | 32374000 | 32422000 | 32883000
Financing Fees | 1333000 | 1295000 | 1297000 | 1315000
Total Non-EPC Costs | 34658000 | 33669000 | 33719000 | 34198000
Overnight Capital Costs ($) | 331635000 | 316206000 | 319551000 | 324956000
Battery Energy Capital Costs ($/kWh) | 414.5437 | 395.2575 | 399.4388 | 406.195
Battery Power Capacity Costs ($/kW) | 1658.175 | 1581.03 | 1597.755 | 1624.78

## O&M Costs_2026$
Online Year>> | 2026 |  |  | 1_CT | 2_CT | 3_CT | 4_CT | 1_CC | 2_CC | 3_CC | 4_CC
| FOM | 8760 | << # hours in a year | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4
| VOM | 75% | << CC Capacity factor | bar: 1_CT 1 to 4_CC 4
|  | 240 | << CT Starts/Year
[7 empty] | Major maintence FROM VOM SCENARIO>> | 1.2505 | 1.242 | 1.2765 | 1.2877 | ** Hard pasted VOM values used in FOM scenario
Scenario (Switch on KW-yr Tab):
VOM
|  |  |  | Reference Year Costs (2026$) |  |  |  | Reference Year Costs (2026$)
|  |  |  | CONE Area |  |  |  | CONE Area
|  |  |  | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4
| O&M Costs |  |  | EMAAC | SWMAAC | Rest of RTO | WMAAC | EMAAC | SWMAAC | Rest of RTO | WMAAC
|  | Annual Escalation Rate |  | Frame-Type Combustion Turbine | Frame-Type Combustion Turbine | Frame-Type Combustion Turbine | Frame-Type Combustion Turbine | Combined Cycle Dry ACC | Combined Cycle Dry ACC | Combined Cycle Dry ACC | Combined Cycle Dry ACC
|  |  | Average MW (Non-Ductfiring) | 371.104 | 373.52 | 362.319 | 359.551 | 1170.73 | 1173.658 | 1144.094 | 1133.424
Fixed O&M (2026$)
| LTSA | 2.912% |  | 346000 | 346000 | 346000 | 346000 | 824000 | 824000 | 824000 | 824000
| Labor | 4.512% |  | 1156000 | 1241000 | 883000 | 910000 | 5202000 | 5581000 | 3974000 | 4095000
| Maintenance and Minor Repairs | 2.912% |  | 530000 | 543000 | 485000 | 489000 | 6561000 | 6717000 | 5998000 | 6058000
| Administrative and General | 2.912% |  | 249000 | 263000 | 205000 | 210000 | 1378000 | 1441000 | 1168000 | 1188000
| Asset Management | 2.912% |  | 545000 | 589000 | 407000 | 417000 | 1577000 | 1697000 | 1177000 | 1203000
| Property Taxes |  |  | 323000 | 4087000 | 2169000 | 317000 | 2958000 | 16362000 | 9501000 | 2913000
| Insurance |  |  | 1952000 | 1843000 | 1869000 | 1902000 | 8151000 | 7443000 | 7580000 | 7846000
| Firm Gas Contract |  |  | 4359095.796 | 5414195.864 | 7135984.7728 | 6317505.3074 | 10025367.3269 | 12441680.5802 | 16392459.2302 | 14506339.5426
| Working Capital |  |  | 36000 | 34000 | 34000 | 35000 | 150000 | 137000 | 140000 | 145000
| Total Fixed O&M (2026$) |  |  | 9496095.796 | 14360195.864 | 13533984.7728 | 10943505.3074 | 36826367.3269 | 52643680.5802 | 46754459.2302 | 38778339.5426
| Total Fixed O&M (2026$/kW-year) |  |  | 26.335 | 39.5774 | 38.3478 | 31.2725 | 31.4559 | 44.8544 | 40.8659 | 34.2134
Variable O&M (2026$/MWh)
| Major Maintenance - Hours Based | 2.912% |  | 0 | 0 | 0 | 0 | 1.3232 | 1.3189 | 1.3529 | 1.3654
| Consumables, Waste Disposal, Other VOM | 2.912% |  | 1.1894 | 1.184 | 1.146 | 1.2161 | 0.75679 | 0.75535 | 0.76679 | 0.77098
| Total Variable O&M (2026$/MWh) |  |  | 1.1894 | 1.184 | 1.146 | 1.2161 | 2.08 | 2.0742 | 2.1197 | 2.1364
| Variable O&M - Starts Based ($/factored start, per turbine) | 2.912% |  | 21169.9298 | 21169.9298 | 21169.9298 | 21169.9298 | 0 | 0 | 0 | 0

## BESS_O&M Costs_2026$
Online Year>> | 2026 |  |  |  | 1_BESS | 2_BESS | 3_BESS | 4_BESS
| FOM | 8760 | << # hours in a year |  | 1 | 2 | 3 | 4
| VOM |  |  |  | BESS | BESS | BESS | BESS
|  |  |  | Major maintence FROM VOM SCENARIO>> | 1.2505 | 1.242 | 1.2765 | 1.2877 | ** Hard pasted VOM values used in FOM scenario
Scenario (Switch on KW-yr Tab):
VOM
Reference Year Costs (2026$)
CONE Area
[5 empty] | 1 | 2 | 3 | 4
| O&M Costs |  |  |  | EMAAC | SWMAAC | Rest of RTO | WMAAC
|  | Annual Escalation Rate |  |  | Lithium-Ion 4-hour Batteries | Lithium-Ion 4-hour Batteries | Lithium-Ion 4-hour Batteries | Lithium-Ion 4-hour Batteries
|  |  | Plant Nameplate Power (MW) |  | 200 | 200 | 200 | 200
|  |  | Storage Duration |  | 4 | 4 | 4 | 4
|  |  | Gross Plant Capacity Installed (MWhDC) |  | 1029.9738 | 1029.9738 | 1029.9738 | 1029.9738
Fixed O&M (2026$)
| O&M Contract Fixed Payments |  |  |  | 2679000 | 2679000 | 2679000 | 2679000
| BOP and Substation O&M | -0.3103% |  |  | 125000 | 100000 | 105000 | 114000
| Station Load / Aux Load | -0.3103% |  |  | 396000 | 316000 | 334000 | 362000
| Miscellaneous Owner Costs |  |  |  | 299000 | 239000 | 253000 | 273000
| Operating Insurance |  |  |  | 1310000 | 1249000 | 1263000 | 1284000
| Land Lease or Property Taxes |  |  |  | 2253000 | 4378000 | 2077000 | 2034000
| Year 5 Augmentation | -1.988% |  |  | 28760000 | 28760000 | 28760000 | 28760000
| Year 10 Augmentation | -0.7885% |  |  | 30564000 | 30564000 | 30564000 | 30564000
| Total Fixed O&M (2026$) |  |  |  | 7062000 | 8961000 | 6711000 | 6746000
| Total Fixed O&M ($/kWh-yr) |  |  |  | 8.8275 | 11.2012 | 8.3887 | 8.4325
| Total Fixed O&M ($/kW-yr) |  |  |  | 35.31 | 44.805 | 33.555 | 33.73
With Augmentation
| Total Fixed O&M (2026$) |  |  |  | 66386000 | 68285000 | 66035000 | 66070000
| Total Fixed O&M ($/kWh-yr) |  |  |  | 82.9825 | 85.3563 | 82.5438 | 82.5875
| Total Fixed O&M ($/kW-yr) |  |  |  | 331.93 | 341.425 | 330.175 | 330.35
Variable O&M (2026$/MWh)
| Included in FOM Above (Assumes 1 Cycle/Day) | -0.3103% |  |  | 0 | 0 | 0 | 0
| Total Variable O&M (2026$/MWh) |  |  |  | 0 | 0 | 0 | 0

## Annual FOM
[16 empty] | -0.3103% | -0.3951% | -0.4763% | -0.5568% | -0.6382% | -0.4107% | -0.2255% | -0.07227% | 0.05633% | 0.1655% | 0.259% | 0.3398% | 0.4101% | 0.4716% | 0.5256% | 0.5733%
|  |  | R | P | [11 empty] | 2026 |  |  |  |  | 2031 |  |  |  |  | 2036 |  |  |  |  | 2041
|  | Year | [13 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50
Annual Fixed O&M Costs (Nominal $million)
|  | FOM (excl. prop. tax, firm gas and working capital) | [13 empty] | 4.8087 | 4.9487 | 5.0927 | 5.241 | 5.3936 | 5.5507 | 5.7123 | 5.8786 | 6.0497 | 6.2259 | 6.4071 | 6.5937 | 6.7857 | 6.9832 | 7.1865 | 7.3958 | 7.6111 | 7.8327 | 8.0608 | 8.2955 | 8.537 | 8.7855 | 9.0413 | 9.3046 | 9.5755 | 9.8543 | 10.1412 | 10.4364 | 10.7403 | 11.053 | 11.3748 | 11.706 | 12.0468 | 12.3976 | 12.7585 | 13.13 | 13.5123 | 13.9057 | 14.3106 | 14.7272 | 15.156 | 15.5973 | 16.0514 | 16.5187 | 16.9997 | 17.4946 | 18.004 | 18.5282 | 19.0676 | 19.6228
|  | Augmentation | [13 empty] | 2031 6: 30.5163; 2036 11: 33.0565; 2041 16: 35.6497
|  | Property Tax | [13 empty] | 2.2533 | 2.3189 | 2.3865 | 2.4559 | 2.5275 | 2.601 | 2.6768 | 2.7547 | 2.8349 | 2.9174 | 3.0024 | 3.0898 | 3.1798 | 3.2723 | 3.3676 | 3.4657 | 3.5666 | 3.6704 | 3.7773 | 3.8873 | 4.0004 | 4.1169 | 4.2368 | 4.3601 | 4.4871 | 4.6177 | 4.7522 | 4.8905 | 5.0329 | 5.1795 | 5.3303 | 5.4854 | 5.6452 | 5.8095 | 5.9787 | 6.1527 | 6.3319 | 6.5162 | 6.7059 | 6.9012 | 7.1021 | 7.3089 | 7.5217 | 7.7407 | 7.9661 | 8.198 | 8.4367 | 8.6823 | 8.9351 | 9.1953
|  | Firm Gas (CC for SWMAAC Only) | [13 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Working Capital | [13 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Total FOM Cost | [13 empty] | 7.062 | 7.2676 | 7.4792 | 7.697 | 7.9211 | 38.668 | 8.389 | 8.6333 | 8.8846 | 9.1433 | 42.466 | 9.6835 | 9.9654 | 10.2556 | 10.5542 | 46.5111 | 11.1777 | 11.5031 | 11.838 | 12.1827 | 12.5374 | 12.9024 | 13.2781 | 13.6647 | 14.0626 | 14.472 | 14.8933 | 15.327 | 15.7732 | 16.2325 | 16.7051 | 17.1914 | 17.692 | 18.2071 | 18.7372 | 19.2827 | 19.8441 | 20.4219 | 21.0165 | 21.6284 | 22.2581 | 22.9062 | 23.5731 | 24.2594 | 24.9657 | 25.6926 | 26.4407 | 27.2105 | 28.0027 | 28.818
[16 empty] | 8.393 | 8.3556 | 8.3201 | 8.2863 | 8.2545 | 36.0601 | 8.1966 | 8.1707 | 8.1467 | 8.1249 | 36.9294 | 8.0876 | 8.0722 | 8.0591 | 8.0483 | 37.7547 | 8.0337 | 8.03 | 8.0289 | 8.0302 | 8.0342 | 8.0407 | 8.05 | 8.0968 | 8.2394 | 8.3849 | 8.5332 | 8.6845 | 8.8389 | 8.9963 | 9.1569 | 9.3207 | 9.4878 | 9.6582 | 9.832 | 10.0093 | 10.1901 | 10.3746 | 10.5627 | 10.7547 | 10.9504 | 11.1501 | 11.3537 | 11.5615 | 11.7734 | 11.9895 | 12.2099 | 12.4348 | 12.6642 | 12.8981
Property Tax Costs (Nominal $million)
| Area | Technology | Taxable Real | Taxable Personal | Real Rate | Personal Rate | Depreciation | Escalator | Assess. Ratio | Assess. Ratio | Dep. Floor |  | Real Tax Base | Personal Tax Base |  | Year 1 | Year 2 | Year 3 | Year 4 | Year 5 | Year 6 | Year 7 | Year 8 | Year 9 | Year 10 | Year 11 | Year 12 | Year 13 | Year 14 | Year 15 | Year 16 | Year 17 | Year 18 | Year 19 | Year 20 | Year 21 | Year 22 | Year 23 | Year 24 | Year 25 | Year 26 | Year 27 | Year 28 | Year 29 | Year 30 | Year 31 | Year 32 | Year 33 | Year 34 | Year 35 | Year 36 | Year 37 | Year 38 | Year 39 | Year 40 | Year 41 | Year 42 | Year 43 | Year 44 | Year 45 | Year 46 | Year 47 | Year 48 | Year 49 | Year 50
|  |  | ($m) | ($m) | % | % | (Personal) | (Real) | (Real) | (Personal) |  |  | ($m) | ($m)
1_CT | 1 | CT | 8.473 | 316.826 | 3.959% | 0% | 0% | 2.25% | 96.2% | 0% | 0% |  | 8.1514 | 0 |  | 0.32273 | 0.33213 | 0.3418 | 0.35175 | 0.36199 | 0.37253 | 0.38338 | 0.39454 | 0.40603 | 0.41785 | 0.43002 | 0.44254 | 0.45542 | 0.46868 | 0.48233 | 0.49637 | 0.51082 | 0.52569 | 0.541 | 0.55675 | 0.57296 | 0.58964 | 0.60681 | 0.62448 | 0.64266 | 0.66137 | 0.68063 | 0.70044 | 0.72084 | 0.74182 | 0.76342 | 0.78565 | 0.80852 | 0.83206 | 0.85629 | 0.88122 | 0.90688 | 0.93328 | 0.96045 | 0.98842 | 1.0172 | 1.0468 | 1.0773 | 1.1087 | 1.1409 | 1.1742 | 1.2083 | 1.2435 | 1.2797 | 1.317
2_CT | 2 | CT | 8.402 | 298.687 | 1.071% | 2.676% | 3.3% | 2.25% | 100% | 50% | 25% |  | 8.402 | 149.3435 |  | 4.0867 | 3.9569 | 3.8271 | 3.6973 | 3.5675 | 3.4379 | 3.3082 | 3.1786 | 3.0491 | 2.9196 | 2.7902 | 2.6609 | 2.5315 | 2.4023 | 2.2731 | 2.144 | 2.0149 | 1.8859 | 1.757 | 1.6281 | 1.4993 | 1.3705 | 1.2419 | 1.1492 | 1.1526 | 1.1561 | 1.1596 | 1.1632 | 1.1669 | 1.1707 | 1.1745 | 1.1785 | 1.1825 | 1.1866 | 1.1909 | 1.1952 | 1.1996 | 1.2041 | 1.2087 | 1.2134 | 1.2182 | 1.2232 | 1.2282 | 1.2334 | 1.2386 | 1.244 | 1.2495 | 1.2551 | 1.2609 | 1.2668
3_CT | 3 | CT | 8.271 | 303.154 | See below | [7 empty] | See below |  |  | 2.1685 | 2.0935 | 2.0186 | 1.9439 | 1.8694 | 1.795 | 1.7208 | 1.6468 | 1.573 | 1.4994 | 1.426 | 1.3529 | 1.2799 | 1.2072 | 1.1347 | 1.0624 | 0.99037 | 0.91859 | 0.84707 | 0.77582 | 0.70485 | 0.65432 | 0.66456 | 0.6751 | 0.68595 | 0.69712 | 0.70861 | 0.72044 | 0.73261 | 0.74513 | 0.75802 | 0.77129 | 0.78494 | 0.79898 | 0.81344 | 0.82832 | 0.84363 | 0.85939 | 0.8756 | 0.89229 | 0.90946 | 0.92714 | 0.94533 | 0.96404 | 0.98331 | 1.0031 | 1.0235 | 1.0445 | 1.0661 | 1.0884
4_CT | 4 | CT | 8.413 | 308.594 | 3.807% | 0% | 0% | 2.25% | 99% | 0% | 0% |  | 8.3289 | 0 |  | 0.31707 | 0.3263 | 0.3358 | 0.34558 | 0.35564 | 0.36599 | 0.37665 | 0.38762 | 0.3989 | 0.41052 | 0.42247 | 0.43477 | 0.44743 | 0.46045 | 0.47386 | 0.48766 | 0.50185 | 0.51647 | 0.5315 | 0.54698 | 0.5629 | 0.57929 | 0.59616 | 0.61352 | 0.63138 | 0.64976 | 0.66868 | 0.68815 | 0.70818 | 0.7288 | 0.75002 | 0.77186 | 0.79433 | 0.81746 | 0.84126 | 0.86575 | 0.89096 | 0.9169 | 0.9436 | 0.97107 | 0.99934 | 1.0284 | 1.0584 | 1.0892 | 1.1209 | 1.1535 | 1.1871 | 1.2217 | 1.2573 | 1.2939
1_CC | 1 | CC | 77.657 | 1278.581 | 3.959% | 0% | 0% | 2.25% | 96.2% | 0% | 0% |  | 74.7098 | 0 |  | 2.9579 | 3.044 | 3.1327 | 3.2239 | 3.3178 | 3.4143 | 3.5138 | 3.6161 | 3.7213 | 3.8297 | 3.9412 | 4.0559 | 4.174 | 4.2956 | 4.4206 | 4.5493 | 4.6818 | 4.8181 | 4.9584 | 5.1027 | 5.2513 | 5.4042 | 5.5616 | 5.7235 | 5.8901 | 6.0616 | 6.2381 | 6.4197 | 6.6066 | 6.799 | 6.9969 | 7.2007 | 7.4103 | 7.6261 | 7.8481 | 8.0766 | 8.3117 | 8.5537 | 8.8028 | 9.0591 | 9.3228 | 9.5943 | 9.8736 | 10.1611 | 10.4569 | 10.7614 | 11.0747 | 11.3972 | 11.729 | 12.0705
2_CC | 2 | CC | 77.231 | 1160.955 | 1.071% | 2.676% | 3.3% | 2.25% | 100% | 50% | 25% |  | 77.231 | 580.4775 |  | 16.3618 | 15.8677 | 15.3741 | 14.8809 | 14.3881 | 13.8958 | 13.4039 | 12.9125 | 12.4216 | 11.9312 | 11.4413 | 10.9518 | 10.4629 | 9.9746 | 9.4868 | 8.9995 | 8.5128 | 8.0267 | 7.5412 | 7.0563 | 6.5721 | 6.0884 | 5.6055 | 5.263 | 5.294 | 5.3257 | 5.3582 | 5.3914 | 5.4253 | 5.46 | 5.4954 | 5.5317 | 5.5688 | 5.6067 | 5.6455 | 5.6851 | 5.7256 | 5.7671 | 5.8094 | 5.8528 | 5.8971 | 5.9424 | 5.9887 | 6.036 | 6.0845 | 6.134 | 6.1846 | 6.2364 | 6.2893 | 6.3434
3_CC | 3 | CC | 76.445 | 1184.525 | See below | [7 empty] | See below |  |  | 9.5007 | 9.2374 | 8.9756 | 8.7154 | 8.4567 | 8.1997 | 7.9444 | 7.6909 | 7.4391 | 7.1892 | 6.9411 | 6.6951 | 6.451 | 6.209 | 5.9692 | 5.7315 | 5.4961 | 5.263 | 5.0323 | 4.804 | 4.5783 | 4.434 | 4.5287 | 4.6261 | 4.7264 | 4.8296 | 4.9358 | 5.0451 | 5.1576 | 5.2733 | 5.3925 | 5.5151 | 5.6412 | 5.7711 | 5.9047 | 6.0422 | 6.1837 | 6.3294 | 6.4792 | 6.6335 | 6.7922 | 6.9555 | 7.1236 | 7.2966 | 7.4747 | 7.6579 | 7.8465 | 8.0405 | 8.2402 | 8.4457
4_CC | 4 | CC | 77.297 | 1228.013 | 3.807% | 0% | 0% | 2.25% | 99% | 0% | 0% |  | 76.524 | 0 |  | 2.9132 | 2.998 | 3.0853 | 3.1751 | 3.2675 | 3.3627 | 3.4606 | 3.5613 | 3.665 | 3.7717 | 3.8815 | 3.9946 | 4.1109 | 4.2306 | 4.3537 | 4.4805 | 4.6109 | 4.7452 | 4.8833 | 5.0255 | 5.1718 | 5.3224 | 5.4774 | 5.6369 | 5.801 | 5.9699 | 6.1437 | 6.3226 | 6.5066 | 6.6961 | 6.891 | 7.0917 | 7.2982 | 7.5106 | 7.7293 | 7.9544 | 8.186 | 8.4243 | 8.6696 | 8.922 | 9.1818 | 9.4491 | 9.7242 | 10.0073 | 10.2987 | 10.5985 | 10.9071 | 11.2247 | 11.5515 | 11.8878
1_BESS | 1 | BESS | 59.1589 | 303.95 | 3.959% | 0% | 0% | 2.25% | 96.2% | 0% | 0% |  | 56.9138 | 0 |  | 2.2533 | 2.3189 | 2.3865 | 2.4559 | 2.5275 | 2.601 | 2.6768 | 2.7547 | 2.8349 | 2.9174 | 3.0024 | 3.0898 | 3.1798 | 3.2723 | 3.3676 | 3.4657 | 3.5666 | 3.6704 | 3.7773 | 3.8873 | 4.0004 | 4.1169 | 4.2368 | 4.3601 | 4.4871 | 4.6177 | 4.7522 | 4.8905 | 5.0329 | 5.1795 | 5.3303 | 5.4854 | 5.6452 | 5.8095 | 5.9787 | 6.1527 | 6.3319 | 6.5162 | 6.7059 | 6.9012 | 7.1021 | 7.3089 | 7.5217 | 7.7407 | 7.9661 | 8.198 | 8.4367 | 8.6823 | 8.9351 | 9.1953
2_BESS | 2 | BESS | 47.2122 | 289.397 | 1.071% | 2.676% | 3.3% | 2.25% | 100% | 50% | 25% |  | 47.2122 | 144.6985 |  | 4.3779 | 4.2615 | 4.1453 | 4.0294 | 3.9138 | 3.7984 | 3.6833 | 3.5685 | 3.454 | 3.3398 | 3.2259 | 3.1123 | 2.9991 | 2.8861 | 2.7735 | 2.6613 | 2.5493 | 2.4378 | 2.3266 | 2.2158 | 2.1053 | 1.9953 | 1.8856 | 1.8113 | 1.8302 | 1.8496 | 1.8695 | 1.8897 | 1.9105 | 1.9317 | 1.9534 | 1.9755 | 1.9982 | 2.0214 | 2.0451 | 2.0693 | 2.0941 | 2.1194 | 2.1453 | 2.1718 | 2.1989 | 2.2266 | 2.2549 | 2.2838 | 2.3134 | 2.3437 | 2.3747 | 2.4063 | 2.4387 | 2.4718
3_BESS | 3 | BESS | 49.769 | 292.711 | See below | [7 empty] | See below |  |  | 2.0772 | 2.1377 | 2.1999 | 2.264 | 2.3299 | 2.3978 | 2.4676 | 2.5394 | 2.6133 | 2.6894 | 2.7677 | 2.8483 | 2.9312 | 3.0166 | 3.1044 | 3.1948 | 3.2878 | 3.3836 | 3.4821 | 3.5834 | 3.6878 | 3.7951 | 3.9056 | 4.0194 | 4.1364 | 4.2568 | 4.3808 | 4.5083 | 4.6396 | 4.7746 | 4.9137 | 5.0567 | 5.2039 | 5.3555 | 5.5114 | 5.6719 | 5.837 | 6.0069 | 6.1818 | 6.3618 | 6.547 | 6.7377 | 6.9338 | 7.1357 | 7.3435 | 7.5573 | 7.7773 | 8.0037 | 8.2368 | 8.4766
4_BESS | 4 | BESS | 53.9813 | 297.682 | 3.807% | 0% | 0% | 2.25% | 99% | 0% | 0% |  | 53.4415 | 0 |  | 2.0344 | 2.0937 | 2.1546 | 2.2174 | 2.2819 | 2.3484 | 2.4167 | 2.4871 | 2.5595 | 2.634 | 2.7107 | 2.7897 | 2.8709 | 2.9545 | 3.0405 | 3.129 | 3.2201 | 3.3139 | 3.4103 | 3.5096 | 3.6118 | 3.717 | 3.8252 | 3.9366 | 4.0512 | 4.1691 | 4.2905 | 4.4154 | 4.544 | 4.6763 | 4.8125 | 4.9526 | 5.0968 | 5.2452 | 5.3979 | 5.555 | 5.7168 | 5.8832 | 6.0545 | 6.2308 | 6.4122 | 6.5989 | 6.791 | 6.9887 | 7.1922 | 7.4016 | 7.6171 | 7.8389 | 8.0671 | 8.302
RTO
[10 empty] | Ohio Tax Breakdown (CC): |  |  |  |  | Personal>> | 98% | 94% | 90% | 86% | 82% | 78% | 74% | 70% | 66% | 62% | 58% | 54% | 50% | 46% | 42% | 38% | 34% | 30% | 26% | 22% | 18% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15%
[13 empty] | Assessment % | Tax Rate % | Tax Base ($m)
[12 empty] | Real | 35% | 5.542% | 76.445 | 1.4829 | 1.5261 | 1.5705 | 1.6163 | 1.6633 | 1.7117 | 1.7616 | 1.8129 | 1.8656 | 1.92 | 1.9759 | 2.0334 | 2.0926 | 2.1535 | 2.2162 | 2.2808 | 2.3472 | 2.4155 | 2.4858 | 2.5582 | 2.6327 | 2.7093 | 2.7882 | 2.8694 | 2.9529 | 3.0389 | 3.1274 | 3.2184 | 3.3122 | 3.4086 | 3.5078 | 3.61 | 3.7151 | 3.8232 | 3.9345 | 4.0491 | 4.167 | 4.2883 | 4.4132 | 4.5417 | 4.6739 | 4.81 | 4.95 | 5.0941 | 5.2425 | 5.3951 | 5.5522 | 5.7138 | 5.8802 | 6.0514
[12 empty] | Personal | 24% | 5.542% | 1184.525 | 15.4412 | 14.811 | 14.1807 | 13.5505 | 12.9202 | 12.29 | 11.6597 | 11.0295 | 10.3992 | 9.7689 | 9.1387 | 8.5084 | 7.8782 | 7.2479 | 6.6177 | 5.9874 | 5.3572 | 4.7269 | 4.0967 | 3.4664 | 2.8361 | 2.3635 | 2.3635 | 2.3635 | 2.3635 | 2.3635 | 2.3635 | 2.3635 | 2.3635 | 2.3635 | 2.3635 | 2.3635 | 2.3635 | 2.3635 | 2.3635 | 2.3635 | 2.3635 | 2.3635 | 2.3635 | 2.3635 | 2.3635 | 2.3635 | 2.3635 | 2.3635 | 2.3635 | 2.3635 | 2.3635 | 2.3635 | 2.3635 | 2.3635
PA Tax (CC):
[13 empty] | Assessment % | Tax Rate % | Tax Base ($m)
[12 empty] | Real | 100% | 2.717% | 76.445 | 2.0772 | 2.1377 | 2.1999 | 2.264 | 2.3299 | 2.3978 | 2.4676 | 2.5394 | 2.6133 | 2.6894 | 2.7677 | 2.8483 | 2.9312 | 3.0166 | 3.1044 | 3.1948 | 3.2878 | 3.3836 | 3.4821 | 3.5834 | 3.6878 | 3.7951 | 3.9056 | 4.0194 | 4.1364 | 4.2568 | 4.3808 | 4.5083 | 4.6396 | 4.7746 | 4.9137 | 5.0567 | 5.2039 | 5.3555 | 5.5114 | 5.6719 | 5.837 | 6.0069 | 6.1818 | 6.3618 | 6.547 | 6.7377 | 6.9338 | 7.1357 | 7.3435 | 7.5573 | 7.7773 | 8.0037 | 8.2368 | 8.4766
Ohio Tax Breakdown (CT):
[15 empty] | Personal>> | 98% | 94% | 90% | 86% | 82% | 78% | 74% | 70% | 66% | 62% | 58% | 54% | 50% | 46% | 42% | 38% | 34% | 30% | 26% | 22% | 18% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15%
[13 empty] | Assessment % | Tax Rate % | Tax Base ($m)
[12 empty] | Real | 35% | 5.542% | 8.271 | 0.16045 | 0.16512 | 0.16992 | 0.17487 | 0.17996 | 0.1852 | 0.19059 | 0.19614 | 0.20185 | 0.20773 | 0.21378 | 0.22 | 0.22641 | 0.233 | 0.23979 | 0.24677 | 0.25395 | 0.26135 | 0.26895 | 0.27679 | 0.28484 | 0.29314 | 0.30167 | 0.31046 | 0.31949 | 0.3288 | 0.33837 | 0.34822 | 0.35836 | 0.36879 | 0.37953 | 0.39058 | 0.40195 | 0.41366 | 0.4257 | 0.43809 | 0.45085 | 0.46398 | 0.47748 | 0.49139 | 0.50569 | 0.52042 | 0.53557 | 0.55116 | 0.56721 | 0.58372 | 0.60072 | 0.61821 | 0.63621 | 0.65473
[12 empty] | Personal | 24% | 5.542% | 303.154 | 3.9519 | 3.7906 | 3.6293 | 3.468 | 3.3067 | 3.1454 | 2.9841 | 2.8228 | 2.6615 | 2.5002 | 2.3389 | 2.1776 | 2.0163 | 1.855 | 1.6937 | 1.5324 | 1.3711 | 1.2098 | 1.0485 | 0.88715 | 0.72585 | 0.60488 | 0.60488 | 0.60488 | 0.60488 | 0.60488 | 0.60488 | 0.60488 | 0.60488 | 0.60488 | 0.60488 | 0.60488 | 0.60488 | 0.60488 | 0.60488 | 0.60488 | 0.60488 | 0.60488 | 0.60488 | 0.60488 | 0.60488 | 0.60488 | 0.60488 | 0.60488 | 0.60488 | 0.60488 | 0.60488 | 0.60488 | 0.60488 | 0.60488
[10 empty] | PA Tax (CT): |  |  | Assessment % | Tax Rate % | Tax Base ($m)
[12 empty] | Real | 100% | 2.717% | 8.271 | 0.22475 | 0.23129 | 0.23802 | 0.24495 | 0.25209 | 0.25943 | 0.26698 | 0.27475 | 0.28275 | 0.29098 | 0.29946 | 0.30818 | 0.31715 | 0.32638 | 0.33588 | 0.34566 | 0.35573 | 0.36608 | 0.37674 | 0.38771 | 0.399 | 0.41062 | 0.42257 | 0.43488 | 0.44754 | 0.46057 | 0.47398 | 0.48778 | 0.50198 | 0.51659 | 0.53164 | 0.54711 | 0.56304 | 0.57944 | 0.59631 | 0.61367 | 0.63154 | 0.64992 | 0.66885 | 0.68832 | 0.70836 | 0.72898 | 0.75021 | 0.77205 | 0.79453 | 0.81766 | 0.84147 | 0.86597 | 0.89118 | 0.91713

## Property Tax for appendix
|  |  | Real Property Tax |  |  | Personal Property Tax
|  |  | Nominal Tax Rate | Assessment Ratio | Effective Tax Rate | Nominal Tax Rate | Assessment Ratio | Effective Tax Rate | Depreciation
|  |  | [a] | [b] | [a] X [b] | [c] | [d] | [c] X [d] | [e]
|  |  | (%) | (%) | (%) | (%) | (%) | (%)
1 | EMAAC
| New Jersey | [1] | 3.959% | 96.2% | 3.809% | n/a | n/a | n/a | n/a
| Gloucester |  | 3.72% | 98.47% | 3.663% | n/a | n/a | n/a | n/a
| Camden |  | 4.198% | 93.94% | 3.944% | n/a | n/a | n/a | n/a
2 | SWMAAC
| Maryland | [2] | 1.071% | 100% | 1.1% | 2.676% | 50% | 1.338% | 3.3%
| Charles |  | 1.141% | 100% | 1.2% | 2.853% | 50% | 1.426%
| Prince George's |  | 1% | 100% | 1% | 2.5% | 50% | 1.25%
3 | RTO
| Ohio | [3] | 5.542% | 35% | 1.94% | 5.542% | 24% | 1.33% | follow annual report "SchC-NewProd (NG)"
| Trumbull |  | 6.642% | 35% | 2.325% | 6.642% | 24% | 1.594%
| Carroll |  | 4.443% | 35% | 1.555% | 4.443% | 24% | 1.066%
| Pennsylvania | [4] | 2.717% | 100% | 2.717% | n/a | n/a | n/a | n/a
| Lawrence |  | 2.717% | 100% | 2.717% | n/a | n/a | n/a
4 | WMAAC
| Pennsylvania | [5] | 3.807% | 99% | 3.769% | n/a | n/a | n/a | n/a
| Luzerne |  | 2.481% | 97% | 2.407% | n/a | n/a | n/a
| Lycoming |  | 2.519% | 100% | 2.519% | n/a | n/a | n/a
| Bradford |  | 6.42% | 100% | 6.42% | n/a | n/a | n/a
Sources and Notes:
[1a],[1b] New Jersey rates estimated based on the average effective tax rates from Gloucester and Camden counties. For Gloucester County see:
https://tax1.co.monmouth.nj.us/cgi-bin/prc6.cgi?&ms_user=monm&passwd=data&srch_type=0&adv=0&out_type=0&district=0801
For Camden county see:
https://www.camdencounty.com/wp-content/uploads/2020/11/04CAMDEN.2021-Ratios.pdf
https://www.camdencounty.com/wp-content/uploads/2020/11/2021-County-Tax-Rates.pdf
[1c],[1d] No personal property tax assessed on power plants in New Jersey; NJ Rev Stat § 54:4-1 (2016).
[2a],[2c] Maryland tax rates estimated based on average county tax rates in Charles county and Prince George's county in 2017-2018. Data obtained from Maryland
Department of Assessments & Taxation website:
https://dat.maryland.gov/Documents/statistics/Taxrates_2021.pdf
[2d] MD Tax-Prop Code § 7-237 (2016)
[2e] Phone conversation with representative at Charles County Treasury Department.
[3a],[3c] Ohio rates estimated based on the average effective tax rates from Trumbull and Carroll counties. For Trumbull county see:
http://auditor.co.trumbull.oh.us/pdfs/2020%20RATE%20OF%20TAXATION.pdf
For Caroll County see:
http://www.carrollcountyauditor.us/auditorsadvisory/Rates%20of%20Taxation%202020.pdf
[3b],[3d] Assessment ratios for real property and personal property taxes found on pages 124 and 129:
http://www.tax.ohio.gov/Portals/0/communications/publications/annual_reports/2016AnnualReport/2016AnnualReport.pdf
[3e] Depreciation schedules for utility assets found in Form U-El by Ohio Department of Taxation:
http://www.tax.ohio.gov/portals/0/forms/public_utility_excise/2017/PUE_UEL.xls
[4a] Pennsylvania county tax rates for RTO based on the county of Lawrence, available at:
https://lawrencecountypa.gov/wp-content/uploads/2021/07/2021-millage.pdf
[4b] Pennsylvania assessment ratios available at:
http://www.revenue.pa.gov/FormsandPublications/FormsforIndividuals/Documents/Realty%20Transfer%20Tax/clr_factor_current.pdf
[4c]-[4e] According to Pennsylvania Legislator's Municipal Deskbook Taxation & Finance (Real Estate Assessment Process, pg. 1), only real estate tax assessed by local governments.
[5a] Pennsylvania county tax rates for WMAAC based on average effective tax rate between Luzerne, Lycoming, and Bradford counties:
https://www.luzernecounty.org/DocumentCenter/View/26403/2021-MILLAGES-JULY
https://www.lyco.org/Portals/1/Assessment/Documents/2021%20Millage.pdf?ver=2021-01-29-090920-517
https://bradfordcountypa.org/wp-content/uploads/2021/09/Bradford-County-Mill-Rates.pdf
[5b] Pennsylvania assessment ratios available at:
http://www.revenue.pa.gov/FormsandPublications/FormsforIndividuals/Documents/Realty%20Transfer%20Tax/clr_factor_current.pdf
Note assessment ratios above 100% are capped at 100% in our calculations.
[5c]-[5e] According to Pennsylvania Legislator's Municipal Deskbook Taxation & Finance (Real Estate Assessment Process, pg. 1), only real estate tax assessed by local governments.

## Additional Estimates
Note: All values highlighted in the following color are used:
Working Capital
| 11.9% | << Approx. Capital Charge Rate for CC
| WC Needed (% of Overnight Costs) >> | 0.5048%
| Financing Costs on WC (Annual Rate) >> | 2.189%
Firm Gas
| EMAAC | SWMAAC | Rest of RTO | WMAAC
Firm Gas for CC ACC ($/year): | 10025367.3269 | 12441680.5802 | 16392459.2302 | 14506339.5426 | << Year 2026$. Do NOT increase with inflation
Firm Gas for CC Wet ($/year): | 10024922.9155 | 12442615.262 | 16393004.8564 | 14507246.7202
Firm Gas for CT ($/year): | 4359095.796 | 5414195.864 | 7135984.7728 | 6317505.3074
Startup Fuel Cost (in $million) | <<From Net Start Up Workbook
| EMAAC | SWMAAC | Rest of RTO | WMAAC
CT
Fuel Oil | 0.29153 | -0.55506 | 0.9775 | 0.28227
No Fuel Oil | -0.55146 | -0.55505 | 0.12348 | -0.5318
CC
Wet and Firm Gas | -14.2759 | -14.3543 | -10.1136 | -13.8504
ACC and Firm Gas | -13.9175 | -13.9939 | -9.7836 | -13.4901
CT
No Fuel Oil | -0.55146 | -0.55505 | 0.12348 | -0.5318
CC
ACC and Firm Gas | -13.9175 | -13.9939 | -9.7836 | -13.4901
Land cost (in 2022$)
1000000 | << Million converter
| Price | Gas CT | Gas CC |  | Gas CT | Gas CC
| ($/acre) | (acres) | (acres) |  | ($m) | ($m)
EMAAC | 36600 | 10 | 60 |  | 0.366 | 2.196
SWMAAC | 29500 | 10 | 60 |  | 0.295 | 1.77
RTO | 16400 | 10 | 60 |  | 0.164 | 0.984
WMAAC | 30600 | 10 | 60 |  | 0.306 | 1.836
Notes:
It is assumed that land is bought in 2022, i.e., 6 months to 1 year before the start of construction.
Electrical Interconnection Cost (in 2021$)
Plant Size | Observations |  | Capacity Weighted Average
| (count) |  | (2021$m) | (2021$/kW)
< 500 MW | 5 |  | 7.2334 | 18.3267
500-750 MW | 5 |  | 12.1543 | 20.7405
> 750 MW | 7 |  | 23.9297 | 18.2524
Capacity Weighted Average | 17 |  | 18.7873 | 18.8787
Gas Interconnection Cost (in 2021$)
Gas Lateral Project |  | State | In-Service Year |  | Pipeline Width | Pipeline Length | Pipeline Cost | Pipeline Cost | Pipeline Cost | Meter Station | Station Cost | Substation Cost
[5 empty] | (inches) | (miles) | ($m in service year) | (2021$m) | ($m/mile) | (Y/N) | ($m in service year) | (2021$m)
Panda Power Lateral Project |  | TX | 2014 |  | 16 | 16.5 | 26.3 | 31.0496 | 1.8818 | Y | 2.2104 | 2.6096
Woodbridge lateral |  | NJ | 2015 |  | 20 | 2.4 | 32 | 36.8935 | 15.3723 | Y | 3.4545 | 3.9828
Rock Springs Expansion |  | PA,MD | 2016 |  | 20 | 11 | 80 | 90.072 | 8.1884 | Y | 3.2579 | 3.6681
Western Kentucky Lateral Project |  | KY | 2016 |  | 24 | 22.5 | 81 | 91.1979 | 4.0532 | Y | 4.768 | 5.3683
UGI Sunbury Pipeline |  | PA | 2017 |  | 20 | 35 | 178 | 195.7131 | 5.5918 | Y |  | 0
Willis Lateral Project |  | TX | 2020 |  | 24 | 19 | 96.178 | 98.4863 | 5.1835 | Y | 4.3448 | 4.4491
Average | [5 empty] | 17.7333 |  | 90.5687 | 5.1073 |  |  | 4.0156
Income and Sales Taxes
| CONE Area |  | Representative State |  | Corporate Income Tax Rate | Sales Tax Rate
1 | Eastern MAAC |  | New Jersey |  | 11.5% | 0%
2 | Southwest MAAC |  | Maryland |  | 8.25% | 0%
3 | Rest of RTO |  | Pennsylvania |  | 9.99% | 0%
4 | Western MAAC |  | Pennsylvania |  | 9.99% | 0%
Note: Sales tax rate of 0% due to equipment being sales tax exempt.
Fuel Oil Price (in 2021$)
| EMAAC | SWMAAC | Rest of RTO | WMAAC
CT | 13.824 | 13.824 | 13.824 | 13.824
CC | 13.824 | 13.824 | 13.824 | 13.824
Note on A2: Author: Carried over from the 2014 analysis to the 2018. We will keep it the same for now
Note on M77: Author: Exhibit K 'Cost of Facilities' does not break out costs for each individual station

## Tax_depreciation
Source: | MACRS from IRS website
| https://www.irs.gov/pub/irs-pdf/p946.pdf |  |  |  | Page 71 -> 3-, 5-, 7-, 10-, 15-, and 20-Year Property Mid-Quarter Convention Placed in Service in First Quarter
Year | 5yr MACRS | 7yr MACRS | 10yr MACRS | 15yr MACRS | 20yr MACRS | 5yr SLD | 10yr SLD | 20yr SLD | 30yr SLD | 40yr SLD | 50yr SLD
1 | 35% | 25% | 17.5% | 8.75% | 6.563% | 20% | 10% | 5% | 3.333% | 2.5% | 2%
2 | 26% | 21.43% | 16.5% | 9.13% | 7% | 20% | 10% | 5% | 3.333% | 2.5% | 2%
3 | 15.6% | 15.31% | 13.2% | 8.21% | 6.482% | 20% | 10% | 5% | 3.333% | 2.5% | 2%
4 | 11.01% | 10.93% | 10.56% | 7.39% | 5.996% | 20% | 10% | 5% | 3.333% | 2.5% | 2%
5 | 11.01% | 8.75% | 8.45% | 6.65% | 5.546% | 20% | 10% | 5% | 3.333% | 2.5% | 2%
6 | 1.38% | 8.74% | 6.76% | 5.99% | 5.13% | 0% | 10% | 5% | 3.333% | 2.5% | 2%
7 | 0% | 8.75% | 6.55% | 5.9% | 4.746% | 0% | 10% | 5% | 3.333% | 2.5% | 2%
8 | 0% | 1.09% | 6.55% | 5.91% | 4.459% | 0% | 10% | 5% | 3.333% | 2.5% | 2%
9 | 0% | 0% | 6.56% | 5.9% | 4.459% | 0% | 10% | 5% | 3.333% | 2.5% | 2%
10 | 0% | 0% | 6.55% | 5.91% | 4.459% | 0% | 10% | 5% | 3.333% | 2.5% | 2%
11 | 0% | 0% | 0.82% | 5.9% | 4.459% | 0% | 0% | 5% | 3.333% | 2.5% | 2%
12 | 0% | 0% | 0% | 5.91% | 4.46% | 0% | 0% | 5% | 3.333% | 2.5% | 2%
13 | 0% | 0% | 0% | 5.9% | 4.459% | 0% | 0% | 5% | 3.333% | 2.5% | 2%
14 | 0% | 0% | 0% | 5.91% | 4.46% | 0% | 0% | 5% | 3.333% | 2.5% | 2%
15 | 0% | 0% | 0% | 5.9% | 4.459% | 0% | 0% | 5% | 3.333% | 2.5% | 2%
16 | 0% | 0% | 0% | 0.74% | 4.46% | 0% | 0% | 5% | 3.333% | 2.5% | 2%
17 | 0% | 0% | 0% | 0% | 4.459% | 0% | 0% | 5% | 3.333% | 2.5% | 2%
18 | 0% | 0% | 0% | 0% | 4.46% | 0% | 0% | 5% | 3.333% | 2.5% | 2%
19 | 0% | 0% | 0% | 0% | 4.459% | 0% | 0% | 5% | 3.333% | 2.5% | 2%
20 | 0% | 0% | 0% | 0% | 4.46% | 0% | 0% | 5% | 3.333% | 2.5% | 2%
21 | 0% | 0% | 0% | 0% | 0.565% | 0% | 0% | 0% | 3.333% | 2.5% | 2%
22 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 3.333% | 2.5% | 2%
23 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 3.333% | 2.5% | 2%
24 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 3.333% | 2.5% | 2%
25 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 3.333% | 2.5% | 2%
26 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 3.333% | 2.5% | 2%
27 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 3.333% | 2.5% | 2%
28 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 3.333% | 2.5% | 2%
29 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 3.333% | 2.5% | 2%
30 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 3.333% | 2.5% | 2%
31 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 2.5% | 2%
32 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 2.5% | 2%
33 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 2.5% | 2%
34 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 2.5% | 2%
35 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 2.5% | 2%
36 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 2.5% | 2%
37 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 2.5% | 2%
38 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 2.5% | 2%
39 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 2.5% | 2%
40 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 2.5% | 2%
41 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 2%
42 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 2%
43 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 2%
44 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 2%
45 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 2%
46 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 2%
47 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 2%
48 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 2%
49 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 2%
50 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 2%
TOTAL | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100%

## ATB 2021 Utility-Scale BESS
Utility-Scale Battery Storage | [10 empty] | https://atb.nrel.gov/electricity/2021/utility-scale_battery_storage
Inputs
|  |  | Take me to: | [6 empty] | Calculated
| X | Assumptions
| Technology |  | Basis Year: |  | 2019
All values are given in 2019 U.S. dollars, using the Consumer Price Index (BLS, 2020) for dollar year conversions. Projections use an inflation assumption of 2.5% per year.
Utility Scale Battery Storage
Representative Li-Ion Battery Storage, 60 MW, 240 MWh storage (4 hours)
Reference: Battery Storage cost values from C. Augustine and N. Blair, “Energy Storage Futures Study Storage Technology Modeling Input Data Report,” NREL/TP-5700-78694. Golden, CO: National Renewable Energy Laboratory. https://www.nrel.gov/docs/fy21osti/78694.pdf.
|  |  | Capital Cost ($/kWh) | Battery Energy Capital Cost ($/kWh)
[5 empty] | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050
|  |  |  | Advanced | 290.4132 | 276.6247 | 252.8768 | 232.133 | 211.3892 | 190.6454 | 169.9016 | 159.0358 | 147.1822 | 136.3164 | 125.4506 | 114.5848 | 112.6092 | 110.6336 | 107.6702 | 105.6946 | 103.719 | 100.7556 | 98.78 | 96.8044 | 94.8288 | 91.8654 | 89.8898 | 87.9142 | 85.9386 | 82.9752 | 80.9996 | 79.024 | 77.0484 | 74.085 | 72.1094 | 70.1338
|  |  |  | Moderate | 290.4132 | 276.6247 | 259.2083 | 241.792 | 224.3757 | 206.9593 | 189.543 | 180.9925 | 172.4421 | 163.8916 | 155.3411 | 146.7907 | 144.5335 | 142.2764 | 140.0193 | 137.7621 | 135.505 | 133.2478 | 130.9907 | 128.7335 | 126.4764 | 124.2192 | 121.9621 | 119.705 | 117.4478 | 115.1907 | 112.9335 | 110.6764 | 108.4192 | 106.1621 | 103.9049 | 101.6478
|  |  |  | Conservative | 290.4132 | 276.6247 | 266.706 | 258.8036 | 251.889 | 243.9866 | 236.0842 | 227.5397 | 218.9953 | 210.4508 | 201.9063 | 193.3619 | 193.3619 | 193.3619 | 193.3619 | 193.3619 | 193.3619 | 193.3619 | 193.3619 | 193.3619 | 193.3619 | 193.3619 | 193.3619 | 193.3619 | 193.3619 | 193.3619 | 193.3619 | 193.3619 | 193.3619 | 193.3619 | 193.3619 | 193.3619
Battery Power Capital Cost ($/kW)
[5 empty] | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050
|  |  |  | Advanced | 272.6328 | 256.7855 | 238.0598 | 218.3038 | 198.5478 | 178.7918 | 159.0358 | 149.1578 | 138.292 | 128.414 | 118.536 | 107.6702 | 105.6946 | 103.719 | 101.7434 | 99.7678 | 96.8044 | 94.8288 | 92.8532 | 90.8776 | 88.902 | 86.9264 | 84.9508 | 81.9874 | 80.0118 | 78.0362 | 76.0606 | 74.085 | 72.1094 | 70.1338 | 68.1582 | 65.1948
|  |  |  | Moderate | 272.6328 | 256.7855 | 244.9797 | 233.1739 | 221.3681 | 209.5623 | 197.7565 | 197.5914 | 197.4263 | 197.2612 | 197.0962 | 196.9311 | 196.1585 | 195.3859 | 194.6133 | 193.8407 | 193.0681 | 192.2955 | 191.5229 | 190.7503 | 189.9777 | 189.2051 | 188.4325 | 187.6599 | 186.8873 | 186.1147 | 185.3421 | 184.5696 | 183.797 | 183.0244 | 182.2518 | 181.4792
|  |  |  | Conservative | 272.6328 | 256.7855 | 250.9012 | 242.9988 | 236.0842 | 229.1696 | 222.255 | 219.2916 | 216.3282 | 213.3648 | 210.4014 | 207.438 | 207.438 | 207.438 | 207.438 | 207.438 | 207.438 | 207.438 | 207.438 | 207.438 | 207.438 | 207.438 | 207.438 | 207.438 | 207.438 | 207.438 | 207.438 | 207.438 | 207.438 | 207.438 | 207.438 | 207.438
Total System Cost ($/kW) = Battery Energy Cost ($/kWh) * Storage Duration (hr) + Battery Power Cost ($/kW)
Future Projections
All values are given in 2019 U.S. dollars, using the Consumer Price Index (BLS, 2020) for dollar year conversions. Projections use an inflation assumption of 2.5% per year.
For 15-year life (values in 2019$):
[5 empty] | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050
| Techno-Economic Cost and Performance Parameters |  | CAPEX ($/kW) | 2Hr Battery Storage - Advanced | 853.4592 | 810.0348 | 743.8134 | 682.5698 | 621.3262 | 560.0826 | 498.839 | 467.2294 | 432.6564 | 401.0468 | 369.4372 | 336.8398 | 330.913 | 324.9862 | 317.0838 | 311.157 | 304.2424 | 296.34 | 290.4132 | 284.4864 | 278.5596 | 270.6572 | 264.7304 | 257.8158 | 251.889 | 243.9866 | 238.0598 | 232.133 | 226.2062 | 218.3038 | 212.377 | 205.4624
|  |  |  | 2Hr Battery Storage - Moderate | 853.4592 | 810.0348 | 763.3964 | 716.7579 | 670.1194 | 623.4809 | 576.8425 | 559.5765 | 542.3105 | 525.0444 | 507.7784 | 490.5124 | 485.2256 | 479.9387 | 474.6518 | 469.3649 | 464.078 | 458.7911 | 453.5043 | 448.2174 | 442.9305 | 437.6436 | 432.3567 | 427.0698 | 421.783 | 416.4961 | 411.2092 | 405.9223 | 400.6354 | 395.3485 | 390.0617 | 384.7748
|  |  |  | 2Hr Battery Storage - Conservative | 853.4592 | 810.0348 | 784.3132 | 760.606 | 739.8622 | 717.1428 | 694.4234 | 674.3711 | 654.3187 | 634.2664 | 614.214 | 594.1617 | 594.1617 | 594.1617 | 594.1617 | 594.1617 | 594.1617 | 594.1617 | 594.1617 | 594.1617 | 594.1617 | 594.1617 | 594.1617 | 594.1617 | 594.1617 | 594.1617 | 594.1617 | 594.1617 | 594.1617 | 594.1617 | 594.1617 | 594.1617
|  |  |  | 4Hr Battery Storage - Advanced | 1434.2856 | 1363.2842 | 1249.567 | 1146.8358 | 1044.1046 | 941.3734 | 838.6422 | 785.301 | 727.0208 | 673.6796 | 620.3384 | 566.0094 | 556.1314 | 546.2534 | 532.4242 | 522.5462 | 511.6804 | 497.8512 | 487.9732 | 478.0952 | 468.2172 | 454.388 | 444.51 | 433.6442 | 423.7662 | 409.937 | 400.059 | 390.181 | 380.303 | 366.4738 | 356.5958 | 345.73
|  |  |  | 4Hr Battery Storage - Moderate | 1434.2856 | 1363.2842 | 1281.8131 | 1200.3419 | 1118.8707 | 1037.3996 | 955.9284 | 921.5615 | 887.1946 | 852.8276 | 818.4607 | 784.0938 | 774.2926 | 764.4915 | 754.6903 | 744.8891 | 735.088 | 725.2868 | 715.4856 | 705.6844 | 695.8833 | 686.0821 | 676.2809 | 666.4797 | 656.6786 | 646.8774 | 637.0762 | 627.2751 | 617.4739 | 607.6727 | 597.8715 | 588.0704
|  |  |  | 4Hr Battery Storage - Conservative | 1434.2856 | 1363.2842 | 1317.7252 | 1278.2132 | 1243.6402 | 1205.116 | 1166.5918 | 1129.4505 | 1092.3092 | 1055.168 | 1018.0267 | 980.8854 | 980.8854 | 980.8854 | 980.8854 | 980.8854 | 980.8854 | 980.8854 | 980.8854 | 980.8854 | 980.8854 | 980.8854 | 980.8854 | 980.8854 | 980.8854 | 980.8854 | 980.8854 | 980.8854 | 980.8854 | 980.8854 | 980.8854 | 980.8854
|  |  |  | 6Hr Battery Storage - Advanced | 2015.112 | 1916.5336 | 1755.3206 | 1611.1018 | 1466.883 | 1322.6642 | 1178.4454 | 1103.3726 | 1021.3852 | 946.3124 | 871.2396 | 795.179 | 781.3498 | 767.5206 | 747.7646 | 733.9354 | 719.1184 | 699.3624 | 685.5332 | 671.704 | 657.8748 | 638.1188 | 624.2896 | 609.4726 | 595.6434 | 575.8874 | 562.0582 | 548.229 | 534.3998 | 514.6438 | 500.8146 | 485.9976
|  |  |  | 6Hr Battery Storage - Moderate | 2015.112 | 1916.5336 | 1800.2298 | 1683.9259 | 1567.622 | 1451.3182 | 1335.0143 | 1283.5465 | 1232.0787 | 1180.6108 | 1129.143 | 1077.6752 | 1063.3597 | 1049.0443 | 1034.7288 | 1020.4134 | 1006.0979 | 991.7824 | 977.467 | 963.1515 | 948.836 | 934.5206 | 920.2051 | 905.8897 | 891.5742 | 877.2587 | 862.9433 | 848.6278 | 834.3123 | 819.9969 | 805.6814 | 791.366
|  |  |  | 6Hr Battery Storage - Conservative | 2015.112 | 1916.5336 | 1851.1372 | 1795.8204 | 1747.4182 | 1693.0892 | 1638.7602 | 1584.53 | 1530.2998 | 1476.0695 | 1421.8393 | 1367.6091 | 1367.6091 | 1367.6091 | 1367.6091 | 1367.6091 | 1367.6091 | 1367.6091 | 1367.6091 | 1367.6091 | 1367.6091 | 1367.6091 | 1367.6091 | 1367.6091 | 1367.6091 | 1367.6091 | 1367.6091 | 1367.6091 | 1367.6091 | 1367.6091 | 1367.6091 | 1367.6091
|  |  |  | 8Hr Battery Storage - Advanced | 2595.9384 | 2469.783 | 2261.0742 | 2075.3678 | 1889.6614 | 1703.955 | 1518.2486 | 1421.4442 | 1315.7496 | 1218.9452 | 1122.1408 | 1024.3486 | 1006.5682 | 988.7878 | 963.105 | 945.3246 | 926.5564 | 900.8736 | 883.0932 | 865.3128 | 847.5324 | 821.8496 | 804.0692 | 785.301 | 767.5206 | 741.8378 | 724.0574 | 706.277 | 688.4966 | 662.8138 | 645.0334 | 626.2652
|  |  |  | 8Hr Battery Storage - Moderate | 2595.9384 | 2469.783 | 2318.6465 | 2167.5099 | 2016.3734 | 1865.2368 | 1714.1003 | 1645.5315 | 1576.9628 | 1508.394 | 1439.8253 | 1371.2566 | 1352.4268 | 1333.5971 | 1314.7673 | 1295.9376 | 1277.1078 | 1258.2781 | 1239.4483 | 1220.6186 | 1201.7888 | 1182.9591 | 1164.1293 | 1145.2996 | 1126.4698 | 1107.6401 | 1088.8103 | 1069.9806 | 1051.1508 | 1032.3211 | 1013.4913 | 994.6616
|  |  |  | 8Hr Battery Storage - Conservative | 2595.9384 | 2469.783 | 2384.5492 | 2313.4276 | 2251.1962 | 2181.0624 | 2110.9286 | 2039.6094 | 1968.2903 | 1896.9711 | 1825.652 | 1754.3328 | 1754.3328 | 1754.3328 | 1754.3328 | 1754.3328 | 1754.3328 | 1754.3328 | 1754.3328 | 1754.3328 | 1754.3328 | 1754.3328 | 1754.3328 | 1754.3328 | 1754.3328 | 1754.3328 | 1754.3328 | 1754.3328 | 1754.3328 | 1754.3328 | 1754.3328 | 1754.3328
|  |  |  | 10Hr Battery Storage - Advanced | 3176.7648 | 3023.0324 | 2766.8278 | 2539.6338 | 2312.4398 | 2085.2458 | 1858.0518 | 1739.5158 | 1610.114 | 1491.578 | 1373.042 | 1253.5182 | 1231.7866 | 1210.055 | 1178.4454 | 1156.7138 | 1133.9944 | 1102.3848 | 1080.6532 | 1058.9216 | 1037.19 | 1005.5804 | 983.8488 | 961.1294 | 939.3978 | 907.7882 | 886.0566 | 864.325 | 842.5934 | 810.9838 | 789.2522 | 766.5328
|  |  |  | 10Hr Battery Storage - Moderate | 3176.7648 | 3023.0324 | 2837.0632 | 2651.0939 | 2465.1247 | 2279.1554 | 2093.1862 | 2007.5165 | 1921.8469 | 1836.1772 | 1750.5076 | 1664.8379 | 1641.4939 | 1618.1499 | 1594.8058 | 1571.4618 | 1548.1177 | 1524.7737 | 1501.4297 | 1478.0856 | 1454.7416 | 1431.3975 | 1408.0535 | 1384.7095 | 1361.3654 | 1338.0214 | 1314.6774 | 1291.3333 | 1267.9893 | 1244.6452 | 1221.3012 | 1197.9572
|  |  |  | 10Hr Battery Storage - Conservative | 3176.7648 | 3023.0324 | 2917.9612 | 2831.0348 | 2754.9742 | 2669.0356 | 2583.097 | 2494.6889 | 2406.2808 | 2317.8727 | 2229.4646 | 2141.0565 | 2141.0565 | 2141.0565 | 2141.0565 | 2141.0565 | 2141.0565 | 2141.0565 | 2141.0565 | 2141.0565 | 2141.0565 | 2141.0565 | 2141.0565 | 2141.0565 | 2141.0565 | 2141.0565 | 2141.0565 | 2141.0565 | 2141.0565 | 2141.0565 | 2141.0565 | 2141.0565
|  |  | ATB Annual Escalation Rate (real) |  |  |  |  | -6.356% | -6.787% | -7.282% | -7.853% | -3.595% | -3.729% | -3.874% | -4.03% | -4.199% | -1.25% | -1.266% | -1.282% | -1.299% | -1.316% | -1.333% | -1.351% | -1.37% | -1.389% | -1.408% | -1.429%
|  |  | Annual Escalation (real) |  |  |  |  | -1.5% | -1.5% | -1.5% | -7.853% | -3.595% | -3.729% | -3.874% | -4.03% | -4.199% | -1.25% | -1.266% | -1.282% | -1.299% | -1.316% | -1.333% | -1.351% | -1.37% | -1.389% | -1.408% | -1.429%
|  |  | Index Value (2021 = 100) in 2021$ |  |  |  | 100 | 98.5 | 97.0225 | 95.5672 | 88.0619 | 84.8959 | 81.73 | 78.5641 | 75.3981 | 72.2322 | 71.3293 | 70.4264 | 69.5235 | 68.6206 | 67.7177 | 66.8148 | 65.9119 | 65.009 | 64.1061 | 63.2031 | 62.3002
|  |  | NREL Index (2021 = 100) in 2021$ |  |  |  | 100 | 93.6441 | 87.2881 | 80.9322 | 74.5763 | 71.8952 | 69.214 | 66.5329 | 63.8518 | 61.1707 | 60.4061 | 59.6414 | 58.8768 | 58.1121 | 57.3475 | 56.5829 | 55.8182 | 55.0536 | 54.289 | 53.5243 | 52.7597
|  |  | Average Escalation from 2021 (real) |  |  |  |  | -1.5% | -1.5% | -1.5% | -3.128% | -3.222% | -3.307% | -3.388% | -3.468% | -3.55% | -3.322% | -3.137% | -2.984% | -2.855% | -2.746% | -2.652% | -2.572% | -2.501% | -2.44% | -2.386% | -2.338%
-2.44%
|  |  | Index Value (2021 = 100) in Nominal$ |  | 2021: 100; 2022: 100.47; 2023: 100.9422; 2024: 101.4166; 2025: 95.321; 2026: 93.732; 2027: 92.0413; 2028: 90.2454; 2029: 88.3409; 2030: 86.3241; 2031: 86.95; 2032: 87.5663; 2033: 88.1726; 2034: 88.768; 2035: 89.352; 2036: 89.9239
|  |  | NREL Index (2021 = 100) in Nominal$ |  | 2021: 100; 2022: 95.5169; 2023: 90.8146; 2024: 85.8859; 2025: 80.7238; 2026: 79.3781; 2027: 77.9462; 2028: 76.4254; 2029: 74.8126; 2030: 73.1046; 2031: 73.6346; 2032: 74.1566; 2033: 74.67; 2034: 75.1743; 2035: 75.6688; 2036: 76.1531
|  |  | Fixed Operation and Maintenance Expenses ($/kW-yr) | 2Hr Battery Storage - Advanced | 21.3365 | 20.2509 | 18.5953 | 17.0642 | 15.5332 | 14.0021 | 12.471 | 11.6807 | 10.8164 | 10.0262 | 9.2359 | 8.421 | 8.2728 | 8.1247 | 7.9271 | 7.7789 | 7.6061 | 7.4085 | 7.2603 | 7.1122 | 6.964 | 6.7664 | 6.6183 | 6.4454 | 6.2972 | 6.0997 | 5.9515 | 5.8033 | 5.6552 | 5.4576 | 5.3094 | 5.1366
|  |  |  | 2Hr Battery Storage - Moderate | 21.3365 | 20.2509 | 19.0849 | 17.9189 | 16.753 | 15.587 | 14.4211 | 13.9894 | 13.5578 | 13.1261 | 12.6945 | 12.2628 | 12.1306 | 11.9985 | 11.8663 | 11.7341 | 11.602 | 11.4698 | 11.3376 | 11.2054 | 11.0733 | 10.9411 | 10.8089 | 10.6767 | 10.5446 | 10.4124 | 10.2802 | 10.1481 | 10.0159 | 9.8837 | 9.7515 | 9.6194
|  |  |  | 2Hr Battery Storage - Conservative | 21.3365 | 20.2509 | 19.6078 | 19.0152 | 18.4966 | 17.9286 | 17.3606 | 16.8593 | 16.358 | 15.8567 | 15.3554 | 14.854 | 14.854 | 14.854 | 14.854 | 14.854 | 14.854 | 14.854 | 14.854 | 14.854 | 14.854 | 14.854 | 14.854 | 14.854 | 14.854 | 14.854 | 14.854 | 14.854 | 14.854 | 14.854 | 14.854 | 14.854
|  |  |  | 4Hr Battery Storage - Advanced | 35.8571 | 34.0821 | 31.2392 | 28.6709 | 26.1026 | 23.5343 | 20.9661 | 19.6325 | 18.1755 | 16.842 | 15.5085 | 14.1502 | 13.9033 | 13.6563 | 13.3106 | 13.0637 | 12.792 | 12.4463 | 12.1993 | 11.9524 | 11.7054 | 11.3597 | 11.1128 | 10.8411 | 10.5942 | 10.2484 | 10.0015 | 9.7545 | 9.5076 | 9.1618 | 8.9149 | 8.6433
|  |  |  | 4Hr Battery Storage - Moderate | 35.8571 | 34.0821 | 32.0453 | 30.0085 | 27.9718 | 25.935 | 23.8982 | 23.039 | 22.1799 | 21.3207 | 20.4615 | 19.6023 | 19.3573 | 19.1123 | 18.8673 | 18.6222 | 18.3772 | 18.1322 | 17.8871 | 17.6421 | 17.3971 | 17.1521 | 16.907 | 16.662 | 16.417 | 16.1719 | 15.9269 | 15.6819 | 15.4368 | 15.1918 | 14.9468 | 14.7018
|  |  |  | 4Hr Battery Storage - Conservative | 35.8571 | 34.0821 | 32.9431 | 31.9553 | 31.091 | 30.1279 | 29.1648 | 28.2363 | 27.3077 | 26.3792 | 25.4507 | 24.5221 | 24.5221 | 24.5221 | 24.5221 | 24.5221 | 24.5221 | 24.5221 | 24.5221 | 24.5221 | 24.5221 | 24.5221 | 24.5221 | 24.5221 | 24.5221 | 24.5221 | 24.5221 | 24.5221 | 24.5221 | 24.5221 | 24.5221 | 24.5221
|  |  |  | 6Hr Battery Storage - Advanced | 50.3778 | 47.9133 | 43.883 | 40.2775 | 36.6721 | 33.0666 | 29.4611 | 27.5843 | 25.5346 | 23.6578 | 21.781 | 19.8795 | 19.5337 | 19.188 | 18.6941 | 18.3484 | 17.978 | 17.4841 | 17.1383 | 16.7926 | 16.4469 | 15.953 | 15.6072 | 15.2368 | 14.8911 | 14.3972 | 14.0515 | 13.7057 | 13.36 | 12.8661 | 12.5204 | 12.1499
|  |  |  | 6Hr Battery Storage - Moderate | 50.3778 | 47.9133 | 45.0057 | 42.0981 | 39.1906 | 36.283 | 33.3754 | 32.0887 | 30.802 | 29.5153 | 28.2286 | 26.9419 | 26.584 | 26.2261 | 25.8682 | 25.5103 | 25.1524 | 24.7946 | 24.4367 | 24.0788 | 23.7209 | 23.363 | 23.0051 | 22.6472 | 22.2894 | 21.9315 | 21.5736 | 21.2157 | 20.8578 | 20.4999 | 20.142 | 19.7841
|  |  |  | 6Hr Battery Storage - Conservative | 50.3778 | 47.9133 | 46.2784 | 44.8955 | 43.6855 | 42.3272 | 40.969 | 39.6132 | 38.2575 | 36.9017 | 35.546 | 34.1902 | 34.1902 | 34.1902 | 34.1902 | 34.1902 | 34.1902 | 34.1902 | 34.1902 | 34.1902 | 34.1902 | 34.1902 | 34.1902 | 34.1902 | 34.1902 | 34.1902 | 34.1902 | 34.1902 | 34.1902 | 34.1902 | 34.1902 | 34.1902
|  |  |  | 8Hr Battery Storage - Advanced | 64.8985 | 61.7446 | 56.5269 | 51.8842 | 47.2415 | 42.5989 | 37.9562 | 35.5361 | 32.8937 | 30.4736 | 28.0535 | 25.6087 | 25.1642 | 24.7197 | 24.0776 | 23.6331 | 23.1639 | 22.5218 | 22.0773 | 21.6328 | 21.1883 | 20.5462 | 20.1017 | 19.6325 | 19.188 | 18.5459 | 18.1014 | 17.6569 | 17.2124 | 16.5703 | 16.1258 | 15.6566
|  |  |  | 8Hr Battery Storage - Moderate | 64.8985 | 61.7446 | 57.9662 | 54.1877 | 50.4093 | 46.6309 | 42.8525 | 41.1383 | 39.4241 | 37.7099 | 35.9956 | 34.2814 | 33.8107 | 33.3399 | 32.8692 | 32.3984 | 31.9277 | 31.457 | 30.9862 | 30.5155 | 30.0447 | 29.574 | 29.1032 | 28.6325 | 28.1617 | 27.691 | 27.2203 | 26.7495 | 26.2788 | 25.808 | 25.3373 | 24.8665
|  |  |  | 8Hr Battery Storage - Conservative | 64.8985 | 61.7446 | 59.6137 | 57.8357 | 56.2799 | 54.5266 | 52.7732 | 50.9902 | 49.2073 | 47.4243 | 45.6413 | 43.8583 | 43.8583 | 43.8583 | 43.8583 | 43.8583 | 43.8583 | 43.8583 | 43.8583 | 43.8583 | 43.8583 | 43.8583 | 43.8583 | 43.8583 | 43.8583 | 43.8583 | 43.8583 | 43.8583 | 43.8583 | 43.8583 | 43.8583 | 43.8583
|  |  |  | 10Hr Battery Storage - Advanced | 79.4191 | 75.5758 | 69.1707 | 63.4908 | 57.811 | 52.1311 | 46.4513 | 43.4879 | 40.2528 | 37.2894 | 34.3261 | 31.338 | 30.7947 | 30.2514 | 29.4611 | 28.9178 | 28.3499 | 27.5596 | 27.0163 | 26.473 | 25.9298 | 25.1395 | 24.5962 | 24.0282 | 23.4849 | 22.6947 | 22.1514 | 21.6081 | 21.0648 | 20.2746 | 19.7313 | 19.1633
|  |  |  | 10Hr Battery Storage - Moderate | 79.4191 | 75.5758 | 70.9266 | 66.2773 | 61.6281 | 56.9789 | 52.3297 | 50.1879 | 48.0462 | 45.9044 | 43.7627 | 41.6209 | 41.0373 | 40.4537 | 39.8701 | 39.2865 | 38.7029 | 38.1193 | 37.5357 | 36.9521 | 36.3685 | 35.7849 | 35.2013 | 34.6177 | 34.0341 | 33.4505 | 32.8669 | 32.2833 | 31.6997 | 31.1161 | 30.5325 | 29.9489
|  |  |  | 10Hr Battery Storage - Conservative | 79.4191 | 75.5758 | 72.949 | 70.7759 | 68.8744 | 66.7259 | 64.5774 | 62.3672 | 60.157 | 57.9468 | 55.7366 | 53.5264 | 53.5264 | 53.5264 | 53.5264 | 53.5264 | 53.5264 | 53.5264 | 53.5264 | 53.5264 | 53.5264 | 53.5264 | 53.5264 | 53.5264 | 53.5264 | 53.5264 | 53.5264 | 53.5264 | 53.5264 | 53.5264 | 53.5264 | 53.5264
|  |  | Variable Operation and Maintenance Expenses ($/MWh) | 2Hr Battery Storage - Advanced | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | 2Hr Battery Storage - Moderate | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | 2Hr Battery Storage - Conservative | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | 4Hr Battery Storage - Advanced | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | 4Hr Battery Storage - Moderate | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | 4Hr Battery Storage - Conservative | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | 6Hr Battery Storage - Advanced | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | 6Hr Battery Storage - Moderate | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | 6Hr Battery Storage - Conservative | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | 8Hr Battery Storage - Advanced | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | 8Hr Battery Storage - Moderate | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | 8Hr Battery Storage - Conservative | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | 10Hr Battery Storage - Advanced | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | 10Hr Battery Storage - Moderate | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | 10Hr Battery Storage - Conservative | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Round-Trip Efficiency | 2Hr Battery Storage - Advanced | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85%
|  |  |  | 2Hr Battery Storage - Moderate | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85%
|  |  |  | 2Hr Battery Storage - Conservative | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85%
|  |  |  | 4Hr Battery Storage - Advanced | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85%
|  |  |  | 4Hr Battery Storage - Moderate | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85%
|  |  |  | 4Hr Battery Storage - Conservative | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85%
|  |  |  | 6Hr Battery Storage - Advanced | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85%
|  |  |  | 6Hr Battery Storage - Moderate | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85%
|  |  |  | 6Hr Battery Storage - Conservative | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85%
|  |  |  | 8Hr Battery Storage - Advanced | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85%
|  |  |  | 8Hr Battery Storage - Moderate | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85%
|  |  |  | 8Hr Battery Storage - Conservative | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85%
|  |  |  | 10Hr Battery Storage - Advanced | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85%
|  |  |  | 10Hr Battery Storage - Moderate | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85%
|  |  |  | 10Hr Battery Storage - Conservative | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85%
|  |  | Capacity Factor (%) | 2Hr Battery Storage - Advanced | 8.3% | 8.3% | 8.3% | 8.3% | 8.3% | 8.3% | 8.3% | 8.3% | 8.3% | 8.3% | 8.3% | 8.3% | 8.3% | 8.3% | 8.3% | 8.3% | 8.3% | 8.3% | 8.3% | 8.3% | 8.3% | 8.3% | 8.3% | 8.3% | 8.3% | 8.3% | 8.3% | 8.3% | 8.3% | 8.3% | 8.3% | 8.3%
|  |  |  | 2Hr Battery Storage - Moderate | 8.3% | 8.3% | 8.3% | 8.3% | 8.3% | 8.3% | 8.3% | 8.3% | 8.3% | 8.3% | 8.3% | 8.3% | 8.3% | 8.3% | 8.3% | 8.3% | 8.3% | 8.3% | 8.3% | 8.3% | 8.3% | 8.3% | 8.3% | 8.3% | 8.3% | 8.3% | 8.3% | 8.3% | 8.3% | 8.3% | 8.3% | 8.3%
|  |  |  | 2Hr Battery Storage - Conservative | 8.3% | 8.3% | 8.3% | 8.3% | 8.3% | 8.3% | 8.3% | 8.3% | 8.3% | 8.3% | 8.3% | 8.3% | 8.3% | 8.3% | 8.3% | 8.3% | 8.3% | 8.3% | 8.3% | 8.3% | 8.3% | 8.3% | 8.3% | 8.3% | 8.3% | 8.3% | 8.3% | 8.3% | 8.3% | 8.3% | 8.3% | 8.3%
|  |  |  | 4Hr Battery Storage - Advanced | 16.7% | 16.7% | 16.7% | 16.7% | 16.7% | 16.7% | 16.7% | 16.7% | 16.7% | 16.7% | 16.7% | 16.7% | 16.7% | 16.7% | 16.7% | 16.7% | 16.7% | 16.7% | 16.7% | 16.7% | 16.7% | 16.7% | 16.7% | 16.7% | 16.7% | 16.7% | 16.7% | 16.7% | 16.7% | 16.7% | 16.7% | 16.7%
|  |  |  | 4Hr Battery Storage - Moderate | 16.7% | 16.7% | 16.7% | 16.7% | 16.7% | 16.7% | 16.7% | 16.7% | 16.7% | 16.7% | 16.7% | 16.7% | 16.7% | 16.7% | 16.7% | 16.7% | 16.7% | 16.7% | 16.7% | 16.7% | 16.7% | 16.7% | 16.7% | 16.7% | 16.7% | 16.7% | 16.7% | 16.7% | 16.7% | 16.7% | 16.7% | 16.7%
|  |  |  | 4Hr Battery Storage - Conservative | 16.7% | 16.7% | 16.7% | 16.7% | 16.7% | 16.7% | 16.7% | 16.7% | 16.7% | 16.7% | 16.7% | 16.7% | 16.7% | 16.7% | 16.7% | 16.7% | 16.7% | 16.7% | 16.7% | 16.7% | 16.7% | 16.7% | 16.7% | 16.7% | 16.7% | 16.7% | 16.7% | 16.7% | 16.7% | 16.7% | 16.7% | 16.7%
|  |  |  | 6Hr Battery Storage - Advanced | 24.9% | 24.9% | 24.9% | 24.9% | 24.9% | 24.9% | 24.9% | 24.9% | 24.9% | 24.9% | 24.9% | 24.9% | 24.9% | 24.9% | 24.9% | 24.9% | 24.9% | 24.9% | 24.9% | 24.9% | 24.9% | 24.9% | 24.9% | 24.9% | 24.9% | 24.9% | 24.9% | 24.9% | 24.9% | 24.9% | 24.9% | 24.9%
|  |  |  | 6Hr Battery Storage - Moderate | 24.9% | 24.9% | 24.9% | 24.9% | 24.9% | 24.9% | 24.9% | 24.9% | 24.9% | 24.9% | 24.9% | 24.9% | 24.9% | 24.9% | 24.9% | 24.9% | 24.9% | 24.9% | 24.9% | 24.9% | 24.9% | 24.9% | 24.9% | 24.9% | 24.9% | 24.9% | 24.9% | 24.9% | 24.9% | 24.9% | 24.9% | 24.9%
|  |  |  | 6Hr Battery Storage - Conservative | 24.9% | 24.9% | 24.9% | 24.9% | 24.9% | 24.9% | 24.9% | 24.9% | 24.9% | 24.9% | 24.9% | 24.9% | 24.9% | 24.9% | 24.9% | 24.9% | 24.9% | 24.9% | 24.9% | 24.9% | 24.9% | 24.9% | 24.9% | 24.9% | 24.9% | 24.9% | 24.9% | 24.9% | 24.9% | 24.9% | 24.9% | 24.9%
|  |  |  | 8Hr Battery Storage - Advanced | 33.2% | 33.2% | 33.2% | 33.2% | 33.2% | 33.2% | 33.2% | 33.2% | 33.2% | 33.2% | 33.2% | 33.2% | 33.2% | 33.2% | 33.2% | 33.2% | 33.2% | 33.2% | 33.2% | 33.2% | 33.2% | 33.2% | 33.2% | 33.2% | 33.2% | 33.2% | 33.2% | 33.2% | 33.2% | 33.2% | 33.2% | 33.2%
|  |  |  | 8Hr Battery Storage - Moderate | 33.2% | 33.2% | 33.2% | 33.2% | 33.2% | 33.2% | 33.2% | 33.2% | 33.2% | 33.2% | 33.2% | 33.2% | 33.2% | 33.2% | 33.2% | 33.2% | 33.2% | 33.2% | 33.2% | 33.2% | 33.2% | 33.2% | 33.2% | 33.2% | 33.2% | 33.2% | 33.2% | 33.2% | 33.2% | 33.2% | 33.2% | 33.2%
|  |  |  | 8Hr Battery Storage - Conservative | 33.2% | 33.2% | 33.2% | 33.2% | 33.2% | 33.2% | 33.2% | 33.2% | 33.2% | 33.2% | 33.2% | 33.2% | 33.2% | 33.2% | 33.2% | 33.2% | 33.2% | 33.2% | 33.2% | 33.2% | 33.2% | 33.2% | 33.2% | 33.2% | 33.2% | 33.2% | 33.2% | 33.2% | 33.2% | 33.2% | 33.2% | 33.2%
|  |  |  | 10Hr Battery Storage - Advanced | 41.5% | 41.5% | 41.5% | 41.5% | 41.5% | 41.5% | 41.5% | 41.5% | 41.5% | 41.5% | 41.5% | 41.5% | 41.5% | 41.5% | 41.5% | 41.5% | 41.5% | 41.5% | 41.5% | 41.5% | 41.5% | 41.5% | 41.5% | 41.5% | 41.5% | 41.5% | 41.5% | 41.5% | 41.5% | 41.5% | 41.5% | 41.5%
|  |  |  | 10Hr Battery Storage - Moderate | 41.5% | 41.5% | 41.5% | 41.5% | 41.5% | 41.5% | 41.5% | 41.5% | 41.5% | 41.5% | 41.5% | 41.5% | 41.5% | 41.5% | 41.5% | 41.5% | 41.5% | 41.5% | 41.5% | 41.5% | 41.5% | 41.5% | 41.5% | 41.5% | 41.5% | 41.5% | 41.5% | 41.5% | 41.5% | 41.5% | 41.5% | 41.5%
|  |  |  | 10Hr Battery Storage - Conservative | 41.5% | 41.5% | 41.5% | 41.5% | 41.5% | 41.5% | 41.5% | 41.5% | 41.5% | 41.5% | 41.5% | 41.5% | 41.5% | 41.5% | 41.5% | 41.5% | 41.5% | 41.5% | 41.5% | 41.5% | 41.5% | 41.5% | 41.5% | 41.5% | 41.5% | 41.5% | 41.5% | 41.5% | 41.5% | 41.5% | 41.5% | 41.5%
?
?
?
?
?
?
?
?
?
?
?
?
Future Projections
Future Projections
Assumptions
Data Sources
Future Projections

## Capital Costs Data BESS
1000000
| Units |  | Reference Year Overnight Costs (2021$)
| Location | Annual Real Escalation Rate | EMAAC | SWMAAC | Rest of RTO | WMAAC
| Technology | (%/yr) | Lithium-Ion 4-hour Batteries | Lithium-Ion 4-hour Batteries | Lithium-Ion 4-hour Batteries | Lithium-Ion 4-hour Batteries | Comments (Please describe assumptions for each line item)
| Plant Nameplate Power (MW) |  | 200 | 200 | 200 | 200
| Storage Duration |  | 4 | 4 | 4 | 4
| Overbuild (%) | 11.18% | 22.33% | 22.33% | 22.33% | 22.33%
257.4934 | Gross Plant Capacity Installed (MWhDC) | 112.6% | 1029.9738 | 1029.9738 | 1029.9738 | 1029.9738
228.7057 | Gross BOL Capacity at POI (MWhAC) | 88.82% | 914.8227 | 914.8227 | 914.8227 | 914.8227
200 | Rated Capacity | 100% | 800 | 800 | 800 | 800
Project Costs
EPC Costs
| Batteries and Enclosures |  | 196133500 | 196133500 | 196133500 | 196133500 | 66.65% of Total EPC Costs per project cost data
| PCS and BOP Equipment |  | 29355700 | 29355700 | 29355700 | 29355700 | 9.80% of Total EPC Costs per project cost data
| BESS Equipment Subtotal |  | 225489200 | 225489200 | 225489200 | 225489200
| Project Management |  | 11953900 | 9539300 | 10090400 | 10914100 | 4.02% of Total EPC Costs per project cost data
| Construction & Materials |  | 59533400 | 47508200 | 50252600 | 54354700 | 19.53% of Total EPC Costs per project cost data
Sales Tax
| EPC Contractor Fee |  | Included | Included | Included | Included
| EPC Contingency |  | Included | Included | Included | Included
| Total EPC Costs |  | 296976500 | 282536700 | 285832200 | 290758000 | Levelized $/kWh Value x Gross Plant Capacity Installed (MWh) x Regional Adjustment Factor
| Augmentation Costs to Maintain Nameplate over 15 Years (assuming 2 augmentations) |  | 63596616.5248 | 63596616.5248 | 63596616.5248 | 63596616.5248 | $228.5/kWh Augmentation Value x 2 Augmentations x 123,597 Gross kWh per Augmentation. Value given in 2021 $USD does not account for battery cost escalation which may impact price at the time of augmentation. Given $/kWh value may be escalated according to NREL "4Hr Battery Storage - Moderate" projections for battery energy storage CAPEX for 5 and 10 year augmentations.
Share | Non-EPC Costs
5% | Project Development |  | 14848800 | 14126800 | 14291600 | 14537900 | 5% of Total EPC Costs Per BESS Cost Assumptions
1% | Mobilization and Start-Up |  | 2969800 | 2825400 | 2858300 | 2907600 | 1% of Total EPC Costs Per BESS Cost Assumptions
5% | Owner's Contingency |  | 11274500 | 11274500 | 11274500 | 11274500 | 5% applied to the BESS Equipment Subtotal only
| Spare Parts Inventories |  | Included | Included | Included | Included | Assume these are included in EPC Costs Per BESS Cost Assumptions
| Electrical Interconnection |  | 3775749.0187 | 3775749.0187 | 3775749.0187 | 3775749.0187
| Land |  | 420000 | 338400 | 187200 | 351600
| Working Capital |  | 36165.2006 | 34469.7647 | 34856.6996 | 35435.0628
| Subtotal - Non-EPC Costs w/o Financing Fees |  | 29093100 | 28226700 | 28424400 | 28720000
4% | Financing Fees |  | 1163700 | 1129100 | 1137000 | 1148800 | 4% of Subtotal Non-EPC Costs Per BESS Cost Assumptions
| Total Non-EPC Costs |  | 30256800 | 29355800 | 29561400 | 29868800
| Overnight Capital Costs ($) |  | 327233300 | 311892500 | 315393600 | 320626800 | Sum of EPC and Non-EPC Costs (not including Augmentation)
| Battery Energy Capital Costs ($/kWh) |  | 409.0416 | 389.8656 | 394.242 | 400.7835 | Overnight Capital Costs ($) / Nameplate Capacity Installed (kW) x Storage Duration (hours)
| Battery Power Capacity Costs ($/kW) |  | 1636.1665 | 1559.4625 | 1576.968 | 1603.134 | Overnight Capital Costs ($) / Nameplate Capacity Installed (kW)
Values estimated by S&L
Calculated by % of other costs based on values in the Cost Assumptions tab.
Values estimated by Brattle
Note on B40: Author: Brattle should calculate this since we did for CCs and CTs

## O&M Costs BESS
| Year of Cost >> | 2021
Reference Year O&M Costs (2021$)
| EMAAC | SWMAAC | Rest of RTO | WMAAC
O&M Costs | Lithium-Ion 4-hour Batteries | Lithium-Ion 4-hour Batteries | Lithium-Ion 4-hour Batteries | Lithium-Ion 4-hour Batteries | Comments (Please describe assumptions for each line item)
Fixed O&M
O&M Contract Fixed Payments | 2679200 | 2679200 | 2679200 | 2679200 | Levelized $/kWh Value x Gross Plant Capacity Installed (MWh) x Regional Adjustment Factor
BOP and Substation O&M | 126800 | 101200 | 107000 | 115800
Station Load / Aux Load | 402500 | 321200 | 339700 | 367500
Miscellaneous Owner Costs | 299200 | 238700 | 252500 | 273100
Operating Insurance | 1308900 | 1247600 | 1261600 | 1282500
Land Lease or Property Taxes
Fixed O&M ($/kWh-yr) | 8.0651 | 7.3664 | 7.5258 | 7.7642 | Total Fixed O&M Costs ($) / Nameplate Capacity Installed (kW) x Storage Duration (hours)
Fixed O&M ($/kW-yr) | 32.2605 | 29.4655 | 30.103 | 31.057 | Total Fixed O&M Costs ($) / Nameplate Capacity Installed (kW)
Augmentation
Year 5 Augmentation in 2031 | 31798308.2624 | 31798308.2624 | 31798308.2624 | 31798308.2624
Year 10 Augmentation in 2036 | 31798308.2624 | 31798308.2624 | 31798308.2624 | 31798308.2624
Variable O&M
Included in FOM Above (Assumes 1 Cycle/Day) | 0 | 0 | 0 | 0
Values estimated by S&L
Calculated by % of other costs based on values in the Cost Assumptions tab.
Values estimated by Brattle
1. All operating costs have been allocated to the Fixed O&M cost with noted exclusions
2. No augmentation or performance maintenance has been included in the Fixed O&M costs
3. Property Taxes apply to land only, exlcudes tangible property tax
4. Misc. Owner Costs may include but are not limited to maintenance and repair of interconnecting facilities, environmental compliance and monitoring, possessory interest tax, asset management, and owner administration, fees and taxes

## Cost Assumptions BESS
Study | To convert MW >> | 1000 | 1_BESS | 2_BESS | 3_BESS | 4_BESS
| To convert millions >> | 1000000 | 1 | 2 | 3 | 4
| To convert days to hours >> | 24 | BESS | BESS | BESS | BESS
|  |  | EMAAC | SWMAAC | Rest of RTO | WMAAC
| Assumptions | Units | Lithium-Ion 4-hour Batteries | Lithium-Ion 4-hour Batteries | Lithium-Ion 4-hour Batteries | Lithium-Ion 4-hour Batteries | Comments
Plant Characteristics
| Chemistry | -- | Lithium-Ion | Lithium-Ion | Lithium-Ion | Lithium-Ion
| Rated Output Power (POI Rating) | MWac | 200 | 200 | 200 | 200
| Storage Duration | hours | 4 | 4 | 4 | 4
| Design Life (amortization period) | years | 15 | 15 | 15 | 15
| Rated Output Frequency | Hz | 60 | 60 | 60 | 60
| EFOR (annual) | % | 2% | 2% | 2% | 2%
AC Losses
| Line Loss GSU to POI | % | 0.05% | 0.05% | 0.05% | 0.05%
| GSU Loss | % | 0.5% | 0.5% | 0.5% | 0.5%
| Auxuliary Load | % | 3% | 3% | 3% | 3%
| Line Loss PCS XFMR to GSU | % | 0.3% | 0.3% | 0.3% | 0.3%
| PCS XFMR Loss | % | 0.73% | 0.73% | 0.73% | 0.73%
| Total AC Loss (for PCS Inverter Sizing) | % | 4.58% | 4.58% | 4.58% | 4.58%
| Gross Inverter Output Power Required | MWac | 209.5997 | 209.5997 | 209.5997 | 209.5997
| Inverter Power | MW | 2.65 | 2.65 | 2.65 | 2.65
| Inverter Loss | % | 1.6% | 1.6% | 1.6% | 1.6%
| Battery Capacity Losses |  | 213.0078
| Battery Capacity Loss (1st year) | % | 4% | 4% | 4% | 4%
| Annual Degradation (after 1st year) | % | 2% | 2% | 2% | 2%
| Augmentation Period | yrs | 5 | 5 | 5 | 5
| Battery Capacity Loss (at 1st aug) | % | 12% | 12% | 12% | 12%
| Maximum State of Charge | % | 100% | 100% | 100% | 100%
| Minimum State of Charge | % | 5% | 5% | 5% | 5%
| Total Output Restriction at BOL | % | 11.18% | 11.18% | 11.18% | 11.18%
| Gross Energy Initial Installation | MWh | 1029.9738 | 1029.9738 | 1029.9738 | 1029.9738
| Gross MWh Overbuild | % | 22.33% | 22.33% | 22.33% | 22.33%
| Number of Augmentations | - | 2 | 2 | 2 | 2
| Gross MWh per Augmentation | MWh | 123.5969 | 123.5969 | 123.5969 | 123.5969
| Equivalent Forced Outage Rate - Demand Based | EFORd | 2% | 2% | 2% | 2%
Capital Costs
| EPC Contractor Fee | % of other EPC costs | 10% | 10% | 10% | 10%
| EPC Contingency | % of other EPC costs | 10% | 10% | 10% | 10%
| Project Development Cost | % of EPC costs | 5% | 5% | 5% | 5%
| Mobilization and Start-Up Cost | % of EPC costs | 1% | 1% | 1% | 1%
| Spare Parts Inventories | % of EPC costs | Included | Included | Included | Included | Assumes any spare parts inventories are included with the EPC contracted equipment supply.
| Owner Contingency | % of BESS Equipment Costs | 5% | 5% | 5% | 5%
| Financing Fees | % of Non-EPC Total | 4% | 4% | 4% | 4%
| Other Labor | % of EPC costs | 8% | 8% | 8% | 8%
| Construction Debt Financing | % | 55% | 55% | 55% | 55%
| Electric Interconnection | 2021$m | 3.7757 | 3.7757 | 3.7757 | 3.7757
| Per kW cost | 2021$/kW | 18.8787 | 18.8787 | 18.8787 | 18.8787
| Substation | 2021$m
| Land | $m | 0.42 | 0.3384 | 0.1872 | 0.3516
| Land Purchase Cost | $/acre | 35000 | 28200 | 15600 | 29300
| Acreage | acre | 12 | 12 | 12 | 12 | Based on 1.2 acres/100 MWh Gross per S&L experience. Note: 2021 Analysis group reference lists 9-12 acres for similarly sized BESS which were inclusive of laydown and parking requirements during construction.
| Sales Tax Rates | % | 0% | 0% | 0% | 0% | It is assumed that the project owner would receive a tax exemption certificate for capital purchases. Construction supplies and consumables would be taxable. As applicable, consumable material unit costs in the EPC estimates account for sales tax.
| State Income Tax Rates | % | 11.5% | 8.25% | 9.99% | 9.99%
| Depreciation Schedule |  | 7yr MACRS | 7yr MACRS | 7yr MACRS | 7yr MACRS
O&M Costs
| Insurance | % of Overnight Capital Costs | 0.4% | 0.4% | 0.4% | 0.4%
Values estimated by S&L
Calculated by % of other costs based on values in the Cost Assumptions tab.
Values estimated by Brattle
From 2018 report.

## Capital Costs Data
1000000
|  | LIVE |  |  |  | LIVE |  |  |  | Fuel Oil |  |  |  | No Fuel Oil
Units |  | Reference Year Overnight Costs (2021$) |  |  |  | Reference Year Overnight Costs (2021$) |  |  |  | Reference Year Overnight Costs (2021$) |  |  |  | Reference Year Overnight Costs (2021$) |  |  |  | Reference Year Overnight Costs (2021$) |  |  |  | Reference Year Overnight Costs (2021$)
Location | Annual Real Escalation Rate | EMAAC | SWMAAC | Rest of RTO | WMAAC | EMAAC | SWMAAC | Rest of RTO | WMAAC | EMAAC | SWMAAC | Rest of RTO | WMAAC | EMAAC | SWMAAC | Rest of RTO | WMAAC | EMAAC | SWMAAC | Rest of RTO | WMAAC | EMAAC | SWMAAC | Rest of RTO | WMAAC
Technology | (%/yr) | Frame-Type Combustion Turbine | Frame-Type Combustion Turbine | Frame-Type Combustion Turbine | Frame-Type Combustion Turbine | Combined Cycle Gas Turbine | Combined Cycle Gas Turbine | Combined Cycle Gas Turbine | Combined Cycle Gas Turbine | Frame-Type Combustion Turbine | Frame-Type Combustion Turbine | Frame-Type Combustion Turbine | Frame-Type Combustion Turbine | Frame-Type Combustion Turbine | Frame-Type Combustion Turbine | Frame-Type Combustion Turbine | Frame-Type Combustion Turbine | Combined Cycle Wet Cooling Tower | Combined Cycle Wet Cooling Tower | Combined Cycle Wet Cooling Tower | Combined Cycle Wet Cooling Tower | Combined Cycle Dry ACC | Combined Cycle Dry ACC | Combined Cycle Dry ACC | Combined Cycle Dry ACC | Comments
Plant Capacity (MW) |  | 360.589 | 362.838 | 352.927 | 349.94 | 1170.73 | 1173.658 | 1144.094 | 1133.424 | [8 empty] | 1055.6378 | 1062.8413 | 1034.1655 | 1025.1268 | 1045.022 | 1052.1531 | 1023.7657 | 1014.8178
Project Costs
Owner Furnished Equipment
Gas Turbines | 0% | 69250000 | 69250000 | 69250000 | 69250000 | 138500000 | 138500000 | 138500000 | 138500000 | 71850000 | 71850000 | 71850000 | 71850000 | 69250000 | 69250000 | 69250000 | 69250000 | 138500000 | 138500000 | 138500000 | 138500000 | 138500000 | 138500000 | 138500000 | 138500000 | *Provided by S&L
HRSG / SCR | 0% | 29558900 | 29558900 | 29558900 | 29558900 | 72000000 | 72000000 | 72000000 | 72000000 | 32000000 | 32000000 | 32000000 | 32000000 | 29558900 | 29558900 | 29558900 | 29558900 | 72000000 | 72000000 | 72000000 | 72000000 | 72000000 | 72000000 | 72000000 | 72000000 | *Provided by S&L
Steam Turbines | 0% |  |  |  |  | 75600000 | 75600000 | 75600000 | 75600000 | [8 empty] | 79800000 | 79800000 | 79800000 | 79800000 | 75600000 | 75600000 | 75600000 | 75600000 | *Provided by S&L
Sales Tax |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Owner Furnished Equipment |  | 98808900 | 98808900 | 98808900 | 98808900 | 286100000 | 286100000 | 286100000 | 286100000 | [8 empty] | 290300000 | 290300000 | 290300000 | 290300000 | 286100000 | 286100000 | 286100000 | 286100000
EPC Costs
Equipment
Condenser | 0% |  |  |  |  | 55000000 | 55000000 | 55000000 | 55000000 | [8 empty] | 7050000 | 7050000 | 7050000 | 7050000 | 55000000 | 55000000 | 55000000 | 55000000 | *Provided by S&L
Other Equipment | 0% | 21281700 | 21281700 | 21281700 | 21281700 | 77014000 | 77014000 | 77014000 | 77014000 | 23351400 | 23351400 | 23351400 | 23351400 | 21281700 | 21281700 | 21281700 | 21281700 | 91384100 | 91384100 | 91384100 | 91384100 | 77014000 | 77014000 | 77014000 | 77014000 | *Provided by S&L
Equipment Subtotal |  | 21281700 | 21281700 | 21281700 | 21281700 | 132014000 | 132014000 | 132014000 | 132014000 | [8 empty] | 98434100 | 98434100 | 98434100 | 98434100 | 132014000 | 132014000 | 132014000 | 132014000
Construction Labor | 1.6% | 41657600 | 31178500 | 33466500 | 37051400 | 306589500 | 237598100 | 249164300 | 277181900 | 40568600 | 30358900 | 32689000 | 36171800 | 41657600 | 31178500 | 33466500 | 37051400 | 280280100 | 215412700 | 226448900 | 250850200 | 306589500 | 237598100 | 249164300 | 277181900 | *Provided by S&L
Other Labor | 1.6% | 13511600 | 12673300 | 12856400 | 13143200 | 63361100 | 57841800 | 58767100 | 61008500 | 14020800 | 13204000 | 13390400 | 13669000 | 13511600 | 12673300 | 12856400 | 13143200 | 59965400 | 54776000 | 55658900 | 57611000 | 63361100 | 57841800 | 58767100 | 61008500 | *Provided by S&L
Materials | 0% | 7146800 | 7146800 | 7146800 | 7146800 | 67310200 | 67310200 | 67310200 | 67310200 | 7488800 | 7488800 | 7488800 | 7488800 | 7146800 | 7146800 | 7146800 | 7146800 | 80552400 | 80552400 | 80552400 | 80552400 | 67310200 | 67310200 | 67310200 | 67310200 | *Provided by S&L
Sales Tax |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
EPC Contractor Fee |  | 11315660 | 10183920 | 10431030 | 10818200 | 64127480 | 56676410 | 57925560 | 60951460 | [8 empty] | 59123200 | 52117600 | 53309500 | 55944800 | 64127500 | 56676500 | 57925600 | 60951500
EPC Contingency |  | 12447226 | 11202312 | 11474133 | 11900020 | 70540228 | 62344051 | 63718116 | 67046606 | [8 empty] | 65035600 | 57329300 | 58640400 | 61539300 | 70540300 | 62344100 | 63718200 | 67046700
Total EPC Costs |  | 107360586 | 93666532 | 96656563 | 101341320 | 703942508 | 613784561 | 628899276 | 665512666 | [8 empty] | 643390800 | 558622100 | 573044200 | 604931800 | 703942600 | 613784700 | 628899400 | 665512800
Total Project Costs |  | 206169486 | 192475432 | 195465463 | 200150220 | 990042508 | 899884561 | 914999276 | 951612666
Non-EPC Costs
Project Development Cost |  | 10308474.3 | 9623771.6 | 9773273.15 | 10007511 | 49502125.4 | 44994228.05 | 45749963.8 | 47580633.3
Mobilization and Start-Up Cost |  | 2061694.86 | 1924754.32 | 1954654.63 | 2001502.2 | 9900425.08 | 8998845.61 | 9149992.76 | 9516126.66
Owner's Contingency |  | 3965990.7057 | 3892211.0773 | 3936592.8395 | 3915380.0087 | 8502799.1106 | 7998208.041 | 8306098.0432 | 8252019.7422
Non-Fuel Inventories |  | 1030847.43 | 962377.16 | 977327.315 | 1000751.1 | 4950212.54 | 4499422.805 | 4574996.38 | 4758063.33
Net Start-Up Fuel Costs |  | -551455.3189 | -555045.4608 | 123481.7935 | -531796.9843 | -13917542.1157 | -13993940.8962 | -9783641.1247 | -13490054.0262 | [16 empty] | *From Additional Estimates (converted to millions)
Electrical Interconnection | 0.2% | 6807467.8145 | 6849926.1122 | 6662818.8696 | 6606428.058 | 22101913.2431 | 22157190.2087 | 21599058.9888 | 21397622.7787 | [16 empty] | *From Cost Assumptions (converted to millions)
Gas Interconnection | 0.2% | 29551854.7353 | 29551854.7353 | 29551854.7353 | 29551854.7353 | 29551854.7353 | 29551854.7353 | 29551854.7353 | 29551854.7353 | [16 empty] | *From Cost Assumptions (converted to millions)
Land | 0% | 366000 | 295000 | 164000 | 306000 | 2196000 | 1770000 | 984000 | 1836000 | [16 empty] | *From Cost Assumptions (converted to millions)
Fuel Inventories | 6% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [16 empty] | *From Cost Assumptions (converted to millions)
Emission Reduction Credits |  | 0 | 0 | 0 | 0 | 2000000 | 2000000 | 2000000 | 2000000 | [8 empty] | 2000000 | 2000000 | 2000000 | 2000000 | 2000000 | 2000000 | 2000000 | 2000000
Subtotal - Non-EPC Costs w/o Financing Fees |  | 53540874.5266 | 52544849.544 | 53144003.3328 | 52857630.1177 | 114787787.9933 | 107975808.5539 | 112132323.5826 | 111402266.5199
Financing Fees
Total Non-EPC Costs |  | 53540874.5266 | 52544849.544 | 53144003.3328 | 52857630.1177 | 114787787.9933 | 107975808.5539 | 112132323.5826 | 111402266.5199
Overnight Capital Costs ($) |  | 259710360.5266 | 245020281.544 | 248609466.3328 | 253007850.1177 | 1104830295.9933 | 1007860369.5539 | 1027131599.5826 | 1063014932.5199
Overnight Capital Costs ($/kW) |  | 720.2393 | 675.2884 | 704.4218 | 723.0035 | 943.7106 | 858.7343 | 897.7685 | 937.8793
Values estimated by S&L
Calculated by % of other costs based on values in the Cost Assumptions tab.
Values estimated by Brattle
From 2018 report.
DUAL FUEL CATEGORIES |  | Total Delta | Total Delta | Total Delta | Total Delta | Total Delta | Total Delta | Total Delta | Total Delta
Combustion Turbines w/ Accessories |  | 4400134.0961 | 0 | 4292744.9886 | 4284677.8947 | 4367294.8837 | 4241022.1767 | 4268719.2558 | 4261314.2326
SCR w/ Exhaust Stack |  | 904643.7195 | 0 | 849720.8659 | 845595.0488 | 55491.5674 | 50863.0986 | 51031.1476 | 51398.3116
Water Supply |  | 644838.1142 | 0 | 574314.5193 | 567916.4803 | 93983.1349 | 84726.1973 | 85062.2952 | 85796.6232
Field Erected Tanks |  | 3924000 | 0 | 3924000 | 3924000 | 36707.0578 | 32739.7988 | 32883.8408 | 33198.5528
Fire Protection |  | 100000 | 0 | 100000 | 100000 | 67000 | 67000 | 67000 | 67000
BOP Piping |  | 508763.8256 | 0 | 401099.6665 | 425529.6345 | 2700000 | 2700000 | 2700000 | 2700000
Foundations |  | 265729.4246 | 0 | 209040.8786 | 204815.7635 | 400000 | 400000 | 400000 | 400000
Site Preparation, Drainage, & Yard Work |  | 186130.5696 | 0 | 161721.0968 | 162747.6894 | 15882.34 | 13860.0439 | 14303.6211 | 14185.0274
Consumables |  | 46343.8387 | 0 | 46343.8387 | 46343.8387 | 386180.3611 | 312097.4857 | 314787.2629 | 320664.0586
Freight, Duties, Taxes, Etc. |  | 237094 | 0 | 237094 | 237094 | 77309.7968 | 60376.5682 | 60991.3744 | 62334.642
[6 empty] | 45011.708 | 42499.466 | 42336.638 | 43066.1
Total Direct Project Costs |  | 11217677.5883 | 0 | 10796079.8543 | 10798720.35 | 12383.781 | 10499.5995 | 10377.4785 | 10924.575
[6 empty] | 334312.1278 | 273923.1545 | 276115.738 | 280906.2332
Indirect Project Costs | [5 empty] | 29440.375 | 29440.375 | 29440.375 | 29440.375
Engineering, Procurement, & Project Services |  | 673060.6553 | 0 | 647764.7913 | 647923.221 | 84963.375 | 84963.375 | 84963.375 | 84963.375
Construction Management/Field Engineering |  | 224353.5518 | 0 | 215921.5971 | 215974.407
S-U/Commissioning |  | 112176.7759 | 0 | 107960.7985 | 107987.2035 | 8705960.5086 | 8404011.3393 | 8438012.4024 | 8445192.1064
EPC Contractor's Fee |  | 1467272.2286 | 0 | 1412127.2449 | 1412472.6218
Contingency @ 10% |  | 1369454.08 | 0 | 1317985.4286 | 1318307.7803 | 522357.6305 | 504240.6804 | 506280.7441 | 506711.5264
[6 empty] | 174119.2102 | 168080.2268 | 168760.248 | 168903.8421
Total EPC Project Cost for DF |  | 15063994.8798 | 0 | 14497839.7148 | 14501385.5836 | 87059.6051 | 84040.1134 | 84380.124 | 84451.9211
[6 empty] | 1138739.6345 | 1099244.6832 | 1103692.0222 | 1104631.1275
[6 empty] | 1062823.6589 | 1025961.7043 | 1030112.5541 | 1030989.0524
[6 empty] | 11691060.2478 | 11285578.7473 | 11331238.0949 | 11340879.5759

## Cost Assumptions
To convert MW >> | 1000 | 1_CT | 2_CT | 3_CT | 4_CT | 1_CC | 2_CC | 3_CC | 4_CC
To convert millions >> | 1000000 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4
To convert days to hours >> | 24 | CT | CT | CT | CT | CC | CC | CC | CC | CT | CT | CT | CT
| 1_CT: LIVE; 1_CC: LIVE | Fuel Oil |  |  |  | No Fuel Oil |  |  |  | Wet Cooling |  |  |  | Dry Cooling
|  | EMAAC | SWMAAC | Rest of RTO | WMAAC | EMAAC | SWMAAC | Rest of RTO | WMAAC | EMAAC | SWMAAC | Rest of RTO | WMAAC | EMAAC | SWMAAC | Rest of RTO | WMAAC | EMAAC | SWMAAC | Rest of RTO | WMAAC | EMAAC | SWMAAC | Rest of RTO | WMAAC
Assumptions | Units | Frame-Type Combustion Turbine | Frame-Type Combustion Turbine | Frame-Type Combustion Turbine | Frame-Type Combustion Turbine | Combined Cycle Dry ACC | Combined Cycle Dry ACC | Combined Cycle Dry ACC | Combined Cycle Dry ACC | Frame-Type Combustion Turbine | Frame-Type Combustion Turbine | Frame-Type Combustion Turbine | Frame-Type Combustion Turbine | Frame-Type Combustion Turbine | Frame-Type Combustion Turbine | Frame-Type Combustion Turbine | Frame-Type Combustion Turbine | Combined Cycle Wet Cooling Tower | Combined Cycle Wet Cooling Tower | Combined Cycle Wet Cooling Tower | Combined Cycle Wet Cooling Tower | Combined Cycle Dry ACC | Combined Cycle Dry ACC | Combined Cycle Dry ACC | Combined Cycle Dry ACC | Comments
Plant Characteristics
Net Plant Capacity without Duct Firing
Net Plant Capacity - Max Summer | MW | 360.589 | 362.838 | 352.927 | 349.94 | 1043.36 | 1046.766 | 1020.405 | 1011.076 | 360.589 | 362.838 | 352.927 | 349.94 | 360.589 | 362.838 | 352.927 | 349.94 | 1055.6378 | 1062.8413 | 1034.1655 | 1025.1268 | 1043.36 | 1046.766 | 1020.405 | 1011.076 |  | 1011.076 | 1046.766
Net Plant Capacity - Average (ISO) | MW | 371.104 | 373.52 | 362.319 | 359.551 | 1070.776 | 1077.26 | 1045.734 | 1037.833 | 371.104 | 373.52 | 362.319 | 359.551 | 371.104 | 373.52 | 362.319 | 359.551 | 1081.0748 | 1087.616 | 1056.3278 | 1048.1904 | 1070.776 | 1077.26 | 1045.734 | 1037.833
Net Plant Capacity with Duct Firing
Net Plant Capacity - Max Summer | MW | -- | -- | -- | -- | 1170.73 | 1173.658 | 1144.094 | 1133.424 | -- | -- | -- | -- | -- | -- | -- | -- | 1185.2245 | 1192.4202 | 1160.2393 | 1149.8484 | 1170.73 | 1173.658 | 1144.094 | 1133.424 |  | 1133.424 | 1173.658
Net Plant Capacity - Average (ISO) | MW | -- | -- | -- | -- | 1196.655 | 1203.115 | 1168.281 | 1159.172 | -- | -- | -- | -- | -- | -- | -- | -- | 1211.318 | 1217.999 | 1183.0083 | 1173.5116 | 1196.655 | 1203.115 | 1168.281 | 1159.172
Net Plant Heat Rate without Duct Firing
Net Plant Heat Rate - Max Summer | Btu/kWh, HHV | 9320 | 9317 | 9304 | 9311 | 6365 | 6383 | 6359 | 6368 | 9320 | 9317 | 9304 | 9311 | 9320 | 9317 | 9304 | 9311 | 6290.9993 | 6286.193 | 6274.3948 | 6280.9792 | 6365 | 6383 | 6359 | 6368 |  | 6359 | 6383
Net Plant Capacity - Average (ISO) | Btu/kWh, HHV | 9187 | 9187 | 9190 | 9191 | 6292 | 6295 | 6292 | 6292 | 9187 | 9187 | 9190 | 9191 | 9187 | 9187 | 9190 | 9191 | 6232.5465 | 6234.6674 | 6229.0011 | 6230.1234 | 6292 | 6295 | 6292 | 6292
Net Plant Heat Rate with Duct Firing
Net Plant Heat Rate - Max Summer | Btu/kWh, HHV | -- | -- | -- | -- | 6602 | 6619 | 6593 | 6601 | -- | -- | -- | -- | -- | -- | -- | -- | 6520.973 | 6515.3426 | 6501.4715 | 6507.1185 | 6602 | 6619 | 6593 | 6601 |  | 6593 | 6619
Net Plant Capacity - Average (ISO) | Btu/kWh, HHV | -- | -- | -- | -- | 6540 | 6540 | 6535 | 6534 | -- | -- | -- | -- | -- | -- | -- | -- | 6460.4418 | 6460.3698 | 6453.3508 | 6453.9246 | 6540 | 6540 | 6535 | 6534
Start-Up Time * | minutes | 21 | 21 | 21 | 21 | 120 | 120 | 120 | 120 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120
Start-Up Fuel Consumption * | mmBtu/start | 461.6236 | 464.6289 | 450.843 | 447.4473 | 8084.7871 | 8137.622 | 7895.71 | 7836.0543 | 461.6236 | 464.6289 | 450.843 | 447.4473 | 461.6236 | 464.6289 | 450.843 | 447.4473 | 8085.4189 | 8137.1088 | 7895.8407 | 7836.4267 | 8084.7871 | 8137.622 | 7895.71 | 7836.0543
Equivalent Forced Outage Rate - Demand Based | EFORd | 2.2% | 2.2% | 2.2% | 2.2% | 2% | 2% | 2% | 2% | 2.2% | 2.2% | 2.2% | 2.2% | 2.2% | 2.2% | 2.2% | 2.2% | 2% | 2% | 2% | 2% | 2% | 2% | 2% | 2%
Capital Costs
EPC Contractor Fee | % of other EPC costs | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10%
EPC Contingency | % of other EPC costs | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10%
Project Development Cost | % of EPC costs | 5% | 5% | 5% | 5% | 5% | 5% | 5% | 5% | 5% | 5% | 5% | 5% | 5% | 5% | 5% | 5% | 5% | 5% | 5% | 5% | 5% | 5% | 5% | 5%
Mobilization and Start-Up Cost | % of EPC costs | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1%
Non-Fuel Inventories | % of EPC costs | 0.5% | 0.5% | 0.5% | 0.5% | 0.5% | 0.5% | 0.5% | 0.5% | 0.5% | 0.5% | 0.5% | 0.5% | 0.5% | 0.5% | 0.5% | 0.5% | 0.5% | 0.5% | 0.5% | 0.5% | 0.5% | 0.5% | 0.5% | 0.5%
Owner's Contingency | % of other Owner's costs | 8% | 8% | 8% | 8% | 8% | 8% | 8% | 8% | 8% | 8% | 8% | 8% | 8% | 8% | 8% | 8% | 8% | 8% | 8% | 8% | 8% | 8% | 8% | 8%
Financing Fees | % of Non-EPC Total | 4% | 4% | 4% | 4% | 4% | 4% | 4% | 4% | 4% | 4% | 4% | 4% | 4% | 4% | 4% | 4% | 4% | 4% | 4% | 4% | 4% | 4% | 4% | 4%
Other Labor | % of EPC Costs | 8% | 8% | 8% | 8% | 8% | 8% | 8% | 8% | 8% | 8% | 8% | 8% | 8% | 8% | 8% | 8% | 8% | 8% | 8% | 8% | 8% | 8% | 8% | 8%
Construction Debt Financing | % | 55% | 55% | 55% | 55% | 55% | 55% | 55% | 55% | 55% | 55% | 55% | 55% | 55% | 55% | 55% | 55%
Electric Interconnection | 2021$m | 6.8075 | 6.8499 | 6.6628 | 6.6064 | 22.1019 | 22.1572 | 21.5991 | 21.3976 | 6.8075 | 6.8499 | 6.6628 | 6.6064 | 6.8075 | 6.8499 | 6.6628 | 6.6064
Per kW cost | 2021$/kW | 18.8787 | 18.8787 | 18.8787 | 18.8787 | 18.8787 | 18.8787 | 18.8787 | 18.8787 | 18.8787 | 18.8787 | 18.8787 | 18.8787 | 18.8787 | 18.8787 | 18.8787 | 18.8787
Gas Interconnection | 2021$m | 29.5519 | 29.5519 | 29.5519 | 29.5519 | 29.5519 | 29.5519 | 29.5519 | 29.5519 | 29.5519 | 29.5519 | 29.5519 | 29.5519 | 29.5519 | 29.5519 | 29.5519 | 29.5519
Pipeline Cost | 2021$/mile | 5.1073 | 5.1073 | 5.1073 | 5.1073 | 5.1073 | 5.1073 | 5.1073 | 5.1073 | 5.1073 | 5.1073 | 5.1073 | 5.1073 | 5.1073 | 5.1073 | 5.1073 | 5.1073 | [8 empty] | *Assumed - Hasn't changed from 2018 Brattle report (should be 5 miles).
Miles | miles | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5
Substation | 2021$m | 4.0156 | 4.0156 | 4.0156 | 4.0156 | 4.0156 | 4.0156 | 4.0156 | 4.0156 | 4.0156 | 4.0156 | 4.0156 | 4.0156 | 4.0156 | 4.0156 | 4.0156 | 4.0156
Land | $m | 0.366 | 0.295 | 0.164 | 0.306 | 2.196 | 1.77 | 0.984 | 1.836 | 0.366 | 0.295 | 0.164 | 0.306 | 0.366 | 0.295 | 0.164 | 0.306
Land Purchase Cost | $/acre | 36600 | 29500 | 16400 | 30600 | 36600 | 29500 | 16400 | 30600 | 36600 | 29500 | 16400 | 30600 | 36600 | 29500 | 16400 | 30600
Acreage | acre | 10 | 10 | 10 | 10 | 60 | 60 | 60 | 60 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
Sales Tax Rates | [9 empty] | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | bar: 1000 to 4_CC
State Income Tax Rates | % | 11.5% | 8.25% | 9.99% | 9.99% | 11.5% | 8.25% | 9.99% | 9.99% | 11.5% | 8.25% | 9.99% | 9.99% | 11.5% | 8.25% | 9.99% | 9.99%
Fuel Oil Inventory Cost | 1000: $; 1_CT: 0; 2_CT: 0; 3_CT: 0; 4_CT: 0 | 3497274.4638 | 3364769.1335 | 3408543.9751 | 3380479.3075
Days of Fuel Oil Inventory | 1000: days; 1_CT: 0; 2_CT: 0; 3_CT: 0; 4_CT: 0 | 3 | 3 | 3 | 3
Capacity Factor for Inventory Days | [9 empty] | 100% | 100% | 100% | 100% | bar: 1000 to 4_CC
Fuel Oil Price | 1000: $/mmBtu; 1_CT: 0; 2_CT: 0; 3_CT: 0; 4_CT: 0 | 13.824 | 13.824 | 13.824 | 13.824
Fuel Oil Heating Value | 1000: Btu/gallon; 1_CT: 0; 2_CT: 0; 3_CT: 0; 4_CT: 0 | 140000 | 140000 | 140000 | 140000
Fuel Oil Inventory | 1000: gallons; 1_CT: 0; 2_CT: 0; 3_CT: 0; 4_CT: 0 | 1807040 | 1738574.5608 | 1761193 | 1746692
Fuel Oil Price | 1000: $/gallon; 1_CT: 0; 2_CT: 0; 3_CT: 0; 4_CT: 0 | 1.9354 | 1.9354 | 1.9354 | 1.9354
Depreciation Schedule |  | 15yr MACRS | 15yr MACRS | 15yr MACRS | 15yr MACRS | 20yr MACRS | 20yr MACRS | 20yr MACRS | 20yr MACRS | 15yr MACRS | 15yr MACRS | 15yr MACRS | 15yr MACRS
O&M Costs
Natural Gas Consumed During Start* | mmBtu/start, per Unit | 461.6236 | 464.6289 | 450.843 | 447.4473 | 8084.7871 | 8137.622 | 7895.71 | 7836.0543 | 461.6236 | 464.6289 | 450.843 | 447.4473 | 461.6236 | 464.6289 | 450.843 | 447.4473 | 8085.4189 | 8137.1088 | 7895.8407 | 7836.4267 | 8084.7871 | 8137.622 | 7895.71 | 7836.0543 | See comments for Start-up Fuel Consumption above
Insurance | % of Overnight Capital Costs | 0.6% | 0.6% | 0.6% | 0.6% | 0.6% | 0.6% | 0.6% | 0.6% | 0.6% | 0.6% | 0.6% | 0.6% | 0.6% | 0.6% | 0.6% | 0.6% | 0.6% | 0.6% | 0.6% | 0.6% | 0.6% | 0.6% | 0.6% | 0.6%
Values estimated by S&L
Calculated by % of other costs based on values in the Cost Assumptions tab.
Values estimated by Brattle
From 2018 report.
*Simple Cycle Start: Simple cycle start assumes conventional cold start of the CTG with purge credit.
** Combined Cycle Start: Combined cycle start assumes a warm start, with purge credit, and ramping of the combustion turbines to minimum emission compliant load before loading the steam turbine (rapid response lite start).
Gas Testing
Fuel Use | mmBtu | 1636479.575 | 1647133.5552 | 1598261.5728 | 1586223.9557 | 6468335.1156 | 6509687.0376 | 6316672.5836 | 6269141.3459 | 1636479.575 | 1647133.5552 | 1598261.5728 | 1586223.9557 | 1636479.575 | 1647133.5552 | 1598261.5728 | 1586223.9557 | 6468335.1156 | 6509687.0376 | 6316672.5836 | 6269141.3459 | 6468335.1156 | 6509687.0376 | 6316672.5836 | 6269141.3459
Startup Days | full-load days | 20 | 20 | 20 | 20 | 40 | 40 | 40 | 40 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40
Fuel Oil Testing
Fuel Use | 1000: mmBtu; 1_CT: 0; 2_CT: 0; 3_CT: 0; 4_CT: 0 | 84328.512 | - | 82189.008 | 81512.304
Startup Days | 1000: full-load days; 1_CT: 0; 2_CT: 0; 3_CT: 0; 4_CT: 0 | 1 | - | 1 | 1
Energy Revenue Credit
Energy Production | MWh | 178129.92 | 179289.6 | 173913.12 | 172584.48 | 1027944.96 | 1034169.6 | 1003904.64 | 996319.68 | 187036.416 | 179289.6 | 182608.776 | 181213.704 | 178129.92 | 179289.6 | 173913.12 | 172584.48 | 1037831.8253 | 1044111.3529 | 1014074.7185 | 1006262.7902 | 1027944.96 | 1034169.6 | 1003904.64 | 996319.68
Labor
Total Construction Labor Hours | hours | 260918.2765 | 238252.7406 | 225597.5776 | 258762.3737 | 1240715.5963 | 1148989.634 | 1179562.7767 | 1230523.4597 | 260918.2765 | 238252.7406 | 225597.5776 | 258762.3737 | 260918.2765 | 238252.7406 | 225597.5776 | 258762.3737

## O&M Costs
[5 empty] | Year of Cost >> | 2021
[5 empty] | LIVE |  |  |  | Wet Cooling |  |  |  | Dry Cooling
| Reference Year O&M Costs (2021$) |  |  |  | Reference Year O&M Costs (2021$) |  |  |  | Reference Year O&M Costs (2021$) |  |  |  | Reference Year O&M Costs (2021$)
| EMAAC | SWMAAC | Rest of RTO | WMAAC | EMAAC | SWMAAC | Rest of RTO | WMAAC | EMAAC | SWMAAC | Rest of RTO | WMAAC | EMAAC | SWMAAC | Rest of RTO | WMAAC
O&M Costs | Frame-Type Combustion Turbine | Frame-Type Combustion Turbine | Frame-Type Combustion Turbine | Frame-Type Combustion Turbine | Combined Cycle Gas Turbine | Combined Cycle Gas Turbine | Combined Cycle Gas Turbine | Combined Cycle Gas Turbine | Combined Cycle Wet Cooling Tower | Combined Cycle Wet Cooling Tower | Combined Cycle Wet Cooling Tower | Combined Cycle Wet Cooling Tower | Combined Cycle Dry ACC | Combined Cycle Dry ACC | Combined Cycle Dry ACC | Combined Cycle Dry ACC | Comments (Please describe assumptions for each line item)
Fixed O&M
Major Maintenance - LTSA Fixed Payments | 300000 | 300000 | 300000 | 300000 | 714000 | 714000 | 714000 | 714000 | 714000 | 714000 | 714000 | 714000 | 714000 | 714000 | 714000 | 714000 | Fixed component of LTSA for CTs only. Independent of unit operating hours or starts.
Labor | 927000 | 995000 | 708000 | 730000 | 4172000 | 4476000 | 3187000 | 3284000 | 4172000 | 4476000 | 3187000 | 3284000 | 4172000 | 4476000 | 3187000 | 3284000 | Routine staffing for all shifts. Simple cycle plants are primarily peakers. Combined cycle plants run intermediate to base load.
Consumables | [16 empty] | Former "fixed" consumables category now included within Maintenance and Minor Repairs.
Maintenance, Supplies, and Minor Repairs | 459000 | 470000 | 420000 | 424000 | 5684000 | 5819000 | 5196000 | 5248000 | 5684000 | 5819000 | 5196000 | 5248000 | 5684000 | 5819000 | 5196000 | 5248000 | Covers routine maintenance, supplies, and services not under the scope of the LTSA or BOP major maintenance activities.
Administrative and General | 216000 | 228000 | 178000 | 182000 | 1194000 | 1248000 | 1012000 | 1029000 | 1195000 | 1250000 | 1013000 | 1030000 | 1194000 | 1248000 | 1012000 | 1029000 | Typical costs for legal, audit, tax, accounting, finance, human resources, and relatived services.
Asset Management | 472000 | 510000 | 353000 | 361000 | 1366000 | 1470000 | 1020000 | 1042000 | 1382000 | 1493000 | 1034000 | 1056000 | 1366000 | 1470000 | 1020000 | 1042000 | Typical costs for fuel procurement, power marketing, energy management, and related services.
Insurance
Property Taxes
Firm Gas Contract
Variable O&M
CT Major Maintenance - (If Hours Based) |  |  |  |  | 1.1463 | 1.1426 | 1.1721 | 1.1829 | 1.133 | 1.1253 | 1.1565 | 1.1667 | 1.1463 | 1.1426 | 1.1721 | 1.1829 | Variable component of LTSA for CTs only if frequency of major maintenance events is based on hours of CT operation. Covers the cost of required combustion inspections, hot gas path inspections, and major inspections, normalized to a $/MWh basis.
BOP Major Maintenance | [16 empty] | Major maintenance for steam turbine and HRSG, normalized to a $/MWh basis. Timing may coincide with CT major maintenance outage events, but at different frequencies.
Consumables, Waste Disposal, and Other VOM | 1.0304 | 1.0257 | 0.99281 | 1.0536 | 0.65563 | 0.65437 | 0.66429 | 0.66792 | 0.65115 | 0.64857 | 0.65905 | 0.66247 | 0.65563 | 0.65437 | 0.66429 | 0.66792 | Covers SCR catalyst replacement and disposal, CO catalyst, ammonia, water supply, water treatment, and other chemicals and consumables.
Variable O&M Total - If Hours Based ($/MWh) |  |  |  |  | 1.8019 | 1.7969 | 1.8364 | 1.8508 | 1.7841 | 1.7739 | 1.8155 | 1.8292 | 1.8019 | 1.7969 | 1.8364 | 1.8508
CT Major Maintenance - If Starts Based ($/factored start, per turbine) | 18340 | 18340 | 18340 | 18340 | [12 empty] | Variable component of LTSA for CTs only if frequency of major maintenance events is based on the number of CT starts. Covers the cost of required combustion inspections, hot gas path inspections, and major inspections, normalized to a $/factored start, per turbine basis.
Values estimated by S&L
Calculated by % of other costs based on values in the Cost Assumptions tab.
Values estimated by Brattle
*CT Major Maintenance (hours based) - Applicable to combined cycles only. Combined cycle operating profile is assumed to be a base loaded unit.
**CT Major Maintenance (starts based) - Applicable to simple cycles only. Simple cycle operating profile is assumed to be a peaker unit.

## Capital Drawdown Schedule
| Technology | Mon. Until | 50% of | Construction Month
|  | Completion | Drawdown | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | Total
CT | Frame-Type Combustion Turbine | 20 | 13 | 0.3635% | 0.4325% | 2.61% | 0.8045% | 1.755% | 1.111% | 2.176% | 2.887% | 4.029% | 6.697% | 8.136% | 10.41% | 11.57% | 12.27% | 11.49% | 10.16% | 7.709% | 4.285% | 0.9052% | 0.2016% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 100%
CC | Combined Cycle Gas Turbine | 32 | 20 | 0.01% | 0.05% | 0.05% | 1.69% | 1.65% | 0.24% | 0.36% | 1.45% | 1.53% | 1.28% | 1.36% | 1.44% | 2.75% | 3.89% | 4.24% | 4.84% | 5.33% | 6.24% | 6.36% | 6.22% | 6.4% | 6.07% | 6.22% | 6.21% | 5.87% | 5.78% | 4.93% | 4.16% | 2.38% | 0.71% | 0.17% | 0.12% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 100%
BESS | Lithium-Ion 4-hour Batteries | 16 | 8 | 0.96% | 1.55% | 37.26% | 1.784% | 1.869% | 2.133% | 2.529% | 2.918% | 3.146% | 3.1% | 2.746% | 30.55% | 1.397% | 0.7056% | 0.2227% | 7.126% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 100%