## Setup (hidden)
Enter Stakeholder Committee Name in cell A2:
OC Special Session: Outage Coordination
Enter issue title (use title from Issue Tracking if applicable) in cell A5:
Outage Coordination

## 1. Interest Identification
OC Special Session: Outage Coordination
Outage Coordination
Interest Identification
Instructions: List interests of all parties on this page.
1 | Effective coordination between transmission and generation outages
2 | Transparency around scheduled transmission outage information (and outage changes)
3 | Transparency around scheduled generation outage information (and outage changes)
4 | Enhancements to transmission outage submittal, evaluation and approval processes
5 | Consistency of communication and transparency around transmission outages
6 | Consistent use of the existing TERM process for transmission ratings change submittal, evaluation, and approval
7 | Transparency around transmission ratings changes (TERM process) and use of special notices
8 | Consideration of transmission outage impacts on market congestion
9 | Membership education about the processes for outage submittal, evaluation, and approval
10 | Improve the modeling of outages
11 | Improve or develop opportunities for outage acceleration
12 | Increase coordination between Planning and Operations for RTEP related projects
13 | Evaluation should include reliability and economic criteria
14
15
16
17
18
19
20

## 2. Options Matrix- Design Comp.
OC Special Session: Outage Coordination
Outage Coordination
OPTIONS MATRIX
Solution Options2
# | Design Components1 | Priority | Status Quo | A | B | C | D | E
A | Transparency
| Transmission Outage Information |  | PJM publicly shares transmission outage through PJM's OASIS site. For each transmission outage request, PJM includes the following information: • Ticket Number • Transmission Zone • Equipment • Equipment Outage Dates • Equipment Status • At Risk flag • Ticket History • Outage Type • Cause Type • Availability • Previous Ticket Status | Status Quo + indication if an outage has been evaluated by PJM | Enhance transparency of OASIS and eDART. Enhancements include Status Quo + ‘On Time’ status of each ticket + PJM Evaluated Timestamp for Risk Flag that gets updated at each review
| OASIS Information and Data Requests |  | The information that PJM is required to post on the PJM OASIS website is driven by PJM OATT and focuses on the need to share transmission outage and outage acceleration information. Additionally, PJM is multiple requirements to share transmission service information on the OASIS application by NAESB standard WEQ-001 and WEQ-002. However, PJM is not limited to only providing that information and provides additional details as necessary. Stakeholders can also submit one-time data requests by filling out the Data Request Form available through the link below. https://www.pjm.com/markets-and-operations/form-data-request/one-time-data-requests.aspx | Status Quo | Expand upon detail and organization of information provided thru OASIS to ensure line ratings and special notices are timely, accurate and easily accessed via standardized formats/methods so that all market participants are equally informed. Currently information available in OASIS is often posted in different locations and in awkward file configurations without user interfaces/API's. Availability must include development and inclusion of a proper user interface (UI) to replace current long format and/or compressed flat files. Transparency into facility rating methodology consistent with FERC 881 should be added to OASIS.
| Generation Outage Information |  | Due to the market sensitive nature of generation outages, PJM does not publically post individual Generation Outage Information. However, PJM does post aggregated generator outage information on Dataminer. PJM has visibility into all generation outage requests. Additionally, each TO has visibility into generation outage requests within their zone. | Status Quo | Status Quo
| Rating Change Information |  | Changes to facilities ratings must be requested by the Transmission Owner. PJM evaluates all rating change requests and implements them as close to the indicated Start Date as possible. For Temporary tickets, PJM restores the permanent ratings as close to the indicated End Date as possible in coordination with the TO. On daily basis, PJM posts the effective thermal ratings for all reportable facilities within the PJM operational footprint that are not deemed market sensitive. On or before July 12, 2025, FERC Order 881 will change the sharing obligation to include 10 days of hourly projections for PJM Thermal Transmission Facility Ratings. PJM will also share Ambient-Adjusted Rating Exceptions and Temporary overrides for relevant facilities as well as Operational Planning Seasonal projections for upcoming 12 months. Thermal ratings database will include a 5 year historic record, including rating effective duration, and nature and basis of any Exceptions & Temporary (conditional) ratings. PJM’s filing under Docket No. ER22-2359-000 around FERC Order 881 can be found on the PJM site under Home > Library > Filings & Orders. | Status Quo | All stakeholders must have the ability to access information related to transmission line derates. PJM must post ratings changes upon receipt to OASIS/eDART with notifications/alerts/derates/rationale clearly visible on the posting sites and various data feeds. PJM to provide end dates for derates & rationale for derates timely and clearly visible and in a consistent and uniform format on posting sites and datafeeds. (suitable replacement for ratings changes file(s)
| Outage Acceleration |  | PJM posts outages eligible for Outage Acceleration on the Outage Acceleration site in OASIS. Eligibility is determined as outages causing at least an estimated $500,000 in FTR revenue inadequacy. Market Participant requests for Acceleration are kept confidential. For outages affecting interconnection of a generator to the transmission system, there is no expected congestion revenue inadequacy requirement, nor is information posted on OASIS. | Status Quo | Status Quo |  |  |  | High
| Switching Solutions |  | PJM shares a list of potential switching solutions that can be applied by PJM and the TO during certain system conditions to mitigate constraints and eliminate or reduce off-cost operation. PJM's procedures state that, if possible, all non-cost options, including switching, should be taken prior to initiating off-cost operations. | Status Quo | PJM should incorporate a "flag" indicating PJM reviewed and approved a switching solution. Each switching solution should have a valid start and end date associated with its intended use. Further, PJM should perform timely page updates as well as routine custodial activities to ensure timely and accurate descriptions. This will improve transparency for market participants so that all market participants are equally informed of PJM's review.
B | Transmission and Generation Outage Coordination
| Bottled Generation Outage Coordination |  | PJM requires TOs to coordinate transmission outage requests with impacted generators if the transmission outage forces an area generator off line. The TO is responsible for notifying the generator no later than six weeks prior to start of the transmission outage. | Status Quo | Status Quo
| Nuclear Generator Coordination |  | If a transmission outage involves opening a Nuclear Generator Unit Breaker, the PJM TOs shall align the transmission outage with the generator outage. In the event that the outage request cannot be delayed until the next unit outage, the nuclear station should be given at least six weeks notice. | Status Quo | Status Quo
| Stability Limit Impact Coordination |  | For areas and units with pre-identified stability concerns, PJM makes the stability limits available through PJM Manual 3B (CEII access required). In addition, PJM utilizes its online Transient Stability Assessment (TSA) tool to determine the limits based on actual and project system topology. PJM communicates the applicable limits to the impacted units as quickly as possible and prior to Day Ahead market submission when practical. | Status Quo | Status Quo
| Outage Conflict Coordination |  | PJM resolves potential outage conflicts based on system reliability. PJM performs the following activities: • Reviews the transmission and generator maintenance schedules to coordinate major transmission and generator outages and communicates with submitting PJM Members to assist in attempting to minimize anticipated constrained operations. • Recommends adjustments to transmission outage schedules throughout the year to coincide with planned generator outages within the PJM RTO and surrounding Balancing Authorities. • Communicates with submitting PJM Members to assist in attempting to minimize the forecast PJM RTO production cost based on anticipated market-based prices. | Status Quo | Status Quo
C | RTEP Outage Coordination Process |  | PJM TOs submit transmission outage requests that are required to support RTEP work. PJM's Operations Planning evaluates the outages by confirming their duration, expected outage timeframe and impact to the reliability of the system. If no uncontrollable reliability issues are found, PJM approves the outage. | PJM Planning and Operations Planning staff will review the approved RTEP projects to identify projects that may require extended outages. Operations Planning will review specific projects with member Operations Planning staff to confirm if extended outages may be required to implement the RTEP project and to assess the impact of the outages. If the outages are expected to create significant operational issues, mitigation strategies including upgrades to limiting facilities, will be considered. | Status Quo
D | Minimizing Impact of Outages on PJM Markets
Transmission Outages
| i. Late Outages |  | A transmission outage submitted as 'Late', per PJM Manual 3 Section 4.2.1, may be denied if it jeopardizes system reliability or causes congestion requiring off-cost operations | Status Quo | Status Quo
| ii. Peak Period Maintenance Season |  | Per PJM Manual 3 Section 4.2.6, Transmission Owners should avoid scheduling outages in excess of 5 days in duration with a restoration time greater than 72 hours between June 15 - September 15 and January 1 - February 28 due to the risk of other unexpected forced outages during peak periods. | Status Quo | Status Quo
| iii. Outage Conflict Coordination |  | PJM resolves potential outage conflicts based on system reliability, however, those actions also result in minimizing the impact on PJM Markets. PJM performs the following activities: • Reviews the transmission and generator maintenance schedules to coordinate major transmission and generator outages and communicates with submitting PJM Members to assist in attempting to minimize anticipated constrained operations. • Recommends adjustments to transmission outage schedules throughout the year to coincide with planned generator outages within the PJM RTO and surrounding Balancing Authorities. • Communicates with submitting PJM Members to assist in attempting to minimize the forecast PJM RTO production cost based on anticipated market-based prices. | Status Quo | Status Quo
Generation Outages
| i. Unit Startup Notification |  | The Unit Startup Notification procedure, as described in PJM Manual 10 Section 1.4, allows PJM to place units in a state of readiness so they can be brought online within 48 hours for anticipated shortage of operating capacity, stability issues or constrained operations. | Status Quo | Status Quo
| ii. Peak Period Maintenance Season |  | PJM does not allow Planned Outages of generation resources to be scheduled during PJM Peak Period Maintenance Season, defined as weeks containing the 24th - 36th Wednesday of the calendar year. (PJM Manual 10 Section 2.2) Maintenance outages are only allowed with a maximum duration of 9 consecutive days, 5 week days plus the weekend on each end. (PJM Manual 10 Section 2.3) | Status Quo | Status Quo
| Outage Acceleration Eligibility |  | Outages that qualify for this process include the planned outages that will exceed five days and are estimated to cause more than $500,000 in congestion revenue inadequacy. Also qualifying for this process are forced outages projected to last into the month of the analysis window and are estimated to cause more than $500,000 in congestion revenue inadequacy. Planned and forced outages affecting the interconnection of a generating unit to the transmission system qualify for outage acceleration regardless of expected congestion revenue inadequacy. | Status Quo | Status Quo
Instructions:
*Implementation should consider timing for both PJM and stakeholders (added as standard component based on Stakeholder feedback- 2015)
1Design Components - each is an "attribute" or "component" of any proposed solution. Consensus of the group should be sought on selection of a set of solution criteria.
2Solution Options - each is a solution alternative elicited from the stakeholder group that meet one of the specific solution criteria.
To complete the matrix:
1. Elicit from the stakeholder group a set of components (attributes) desired for any proposed solution. Enter a short label for each in the Design Components column.
2. If needed, enter a more detailed description of each criteria on the "Design Component Details" tab (2a).
3. Using informal feedback from the participants, rate each component's priority in the final solution as "high/medium/low"
4. Elicit from the stakeholder group potential solution alternative(s) for each component. Enter a short label for each in the Solution Options columns.
5. If needed, enter a more detailed description of each potential solution option on the "Option Details" tab 2b.
6. Once the matrix is filled out, the group will attempt to select a single solution alternative (column) for each component (row) to form a solution "package", to be documented in tab 3, "Packages Matrix".
Example: cells 1B, 2C, 3A, 4B, 5D could make up a solution package.

## 2a. Design Component Details
OC Special Session: Outage Coordination
Outage Coordination
COMPONENT DETAILS
Instructions: Complete this form as needed. Design components should be populated from the Options Matrix.
Design Component | Detailed Description
1 | <enter detailed description of this component>
2 | <enter detailed description of this component>
3 | <enter detailed description of this component>
4 | <enter detailed description of this component>
5 | <enter detailed description of this component>

## 2b. Option Details
OC Special Session: Outage Coordination
Outage Coordination
SOLUTION OPTION DETAILS
Instructions: Complete this form as needed, including more detailed / expansive descriptions of options than the Options Matrix allows.
Cell # | Detailed Description
Corresponding cell number from Options Matrix (ex. 1A, 1B, 2A, etc.) | <enter detailed description of this option>

## 3. Package Matrix
OC Special Session: Outage Coordination
Outage Coordination
PACKAGE/ PROPOSAL MATRIX
Packages
# | Design Components | Priority | Status Quo | A | B | C | D | E
1 | Transparency
2 | Transmission Outage Information |  | PJM publicly shares transmission outage through PJM's OASIS site. For each transmission outage request, PJM includes the following information: • Ticket Number • Transmission Zone • Equipment • Equipment Outage Dates • Equipment Status • At Risk flag • Ticket History • Outage Type • Cause Type • Availability • Previous Ticket Status | Status Quo + indication if an outage has been evaluated by PJM | Enhance transparency of OASIS and eDART. Enhancements include Status Quo + ‘On Time’ status of each ticket + PJM Evaluated Timestamp for Risk Flag that gets updated at each review
3 | OASIS Information and Data Requests |  | The information that PJM is required to post on the PJM OASIS website is driven by PJM OATT and focuses on the need to share transmission outage and outage acceleration information. Additionally, PJM is multiple requirements to share transmission service information on the OASIS application by NAESB standard WEQ-001 and WEQ-002. However, PJM is not limited to only providing that information and provides additional details as necessary. Stakeholders can also submit one-time data requests by filling out the Data Request Form available through the link below. https://www.pjm.com/markets-and-operations/form-data-request/one-time-data-requests.aspx | Status Quo | Expand upon detail and organization of information provided thru OASIS to ensure line ratings and special notices are timely, accurate and easily accessed via standardized formats/methods so that all market participants are equally informed. Currently information available in OASIS is often posted in different locations and in awkward file configurations without user interfaces/API's. Availability must include development and inclusion of a proper user interface (UI) to replace current long format and/or compressed flat files. Transparency into facility rating methodology consistent with FERC 881 should be added to OASIS.
4 | Generation Outage Information |  | Due to the market sensitive nature of generation outages, PJM does not publically post individual Generation Outage Information. However, PJM does post aggregated generator outage information on Dataminer. PJM has visibility into all generation outage requests. Additionally, each TO has visibility into generation outage requests within their zone. | Status Quo | Status Quo
5 | Rating Change Information |  | Changes to facilities ratings must be requested by the Transmission Owner. PJM evaluates all rating change requests and implements them as close to the indicated Start Date as possible. For Temporary tickets, PJM restores the permanent ratings as close to the indicated End Date as possible in coordination with the TO. On daily basis, PJM posts the effective thermal ratings for all reportable facilities within the PJM operational footprint that are not deemed market sensitive. On or before July 12, 2025, FERC Order 881 will change the sharing obligation to include 10 days of hourly projections for PJM Thermal Transmission Facility Ratings. PJM will also share Ambient-Adjusted Rating Exceptions and Temporary overrides for relevant facilities as well as Operational Planning Seasonal projections for upcoming 12 months. Thermal ratings database will include a 5 year historic record, including rating effective duration, and nature and basis of any Exceptions & Temporary (conditional) ratings. PJM’s filing under Docket No. ER22-2359-000 around FERC Order 881 can be found on the PJM site under Home > Library > Filings & Orders. | Status Quo | All stakeholders must have the ability to access information related to transmission line derates. PJM must post ratings changes upon receipt to OASIS/eDART with notifications/alerts/derates/rationale clearly visible on the posting sites and various data feeds. PJM to provide end dates for derates & rationale for derates timely and clearly visible and in a consistent and uniform format on posting sites and datafeeds. (suitable replacement for ratings changes file(s)
6 | Outage Acceleration |  | PJM posts outages eligible for Outage Acceleration on the Outage Acceleration site in OASIS. Eligibility is determined as outages causing at least an estimated $500,000 in FTR revenue inadequacy. Market Participant requests for Acceleration are kept confidential. For outages affecting interconnection of a generator to the transmission system, there is no expected congestion revenue inadequacy requirement, nor is information posted on OASIS. | Status Quo | Status Quo
7 | Switching Solutions |  | PJM shares a list of potential switching solutions that can be applied by PJM and the TO during certain system conditions to mitigate constraints and eliminate or reduce off-cost operation. PJM's procedures state that, if possible, all non-cost options, including switching, should be taken prior to initiating off-cost operations. | Status Quo | PJM should incorporate a "flag" indicating PJM reviewed and approved a switching solution. Each switching solution should have a valid start and end date associated with its intended use. Further, PJM should perform timely page updates as well as routine custodial activities to ensure timely and accurate descriptions. This will improve transparency for market participants so that all market participants are equally informed of PJM's review.
8 | Transmission and Generation Outage Coordination
9 | Bottled Generation Outage Coordination |  | PJM requires TOs to coordinate transmission outage requests with impacted generators if the transmission outage forces an area generator off line. The TO is responsible for notifying the generator no later than six weeks prior to start of the transmission outage. | Status Quo | Status Quo |  |  |  | Low
10 | Nuclear Generator Coordination |  | If a transmission outage involves opening a Nuclear Generator Unit Breaker, the PJM TOs shall align the transmission outage with the generator outage. In the event that the outage request cannot be delayed until the next unit outage, the nuclear station should be given at least six weeks notice. | Status Quo | Status Quo |  |  |  | Low - Medium
| Stability Limit Impact Coordination |  | For areas and units with pre-identified stability concerns, PJM makes the stability limits available through PJM Manual 3B (CEII access required). In addition, PJM utilizes its online Transient Stability Assessment (TSA) tool to determine the limits based on actual and project system topology. PJM communicates the applicable limits to the impacted units as quickly as possible and prior to Day Ahead market submission when practical. | Status Quo | Status Quo |  |  |  | Low - High
| Outage Conflict Coordination |  | PJM resolves potential outage conflicts based on system reliability. PJM performs the following activities: • Reviews the transmission and generator maintenance schedules to coordinate major transmission and generator outages and communicates with submitting PJM Members to assist in attempting to minimize anticipated constrained operations. • Recommends adjustments to transmission outage schedules throughout the year to coincide with planned generator outages within the PJM RTO and surrounding Balancing Authorities. • Communicates with submitting PJM Members to assist in attempting to minimize the forecast PJM RTO production cost based on anticipated market-based prices. | Status Quo | Status Quo |  |  |  | Medium
| RTEP Outage Coordination Process |  | PJM TOs submit transmission outage requests that are required to support RTEP work. PJM's Operations Planning evaluates the outages by confirming their duration, expected outage timeframe and impact to the reliability of the system. If no uncontrollable reliability issues are found, PJM approves the outage. | PJM Planning and Operations Planning staff will review the approved RTEP projects to identify projects that may require extended outages. Operations Planning will review specific projects with member Operations Planning staff to confirm if extended outages may be required to implement the RTEP project and to assess the impact of the outages. If the outages are expected to create significant operational issues, mitigation strategies including upgrades to limiting facilities, will be considered. | Status Quo |  |  |  | Medium - High
| Minimizing Impact of Outages on PJM Markets | [7 empty] | High
Transmission Outages
| i. Late Outages |  | A transmission outage submitted as 'Late', per PJM Manual 3 Section 4.2.1, may be denied if it jeopardizes system reliability or causes congestion requiring off-cost operations | Status Quo | Status Quo
| ii. Peak Period Maintenance Season |  | Per PJM Manual 3 Section 4.2.6, Transmission Owners should avoid scheduling outages in excess of 5 days in duration with a restoration time greater than 72 hours between June 15 - September 15 and January 1 - February 28 due to the risk of other unexpected forced outages during peak periods. | Status Quo | Status Quo
| iii. Outage Conflict Coordination |  | PJM resolves potential outage conflicts based on system reliability, however, those actions also result in minimizing the impact on PJM Markets. PJM performs the following activities: • Reviews the transmission and generator maintenance schedules to coordinate major transmission and generator outages and communicates with submitting PJM Members to assist in attempting to minimize anticipated constrained operations. • Recommends adjustments to transmission outage schedules throughout the year to coincide with planned generator outages within the PJM RTO and surrounding Balancing Authorities. • Communicates with submitting PJM Members to assist in attempting to minimize the forecast PJM RTO production cost based on anticipated market-based prices. | Status Quo | Status Quo
Generation Outages
| i. Unit Startup Notification |  | The Unit Startup Notification procedure, as described in PJM Manual 10 Section 1.4, allows PJM to place units in a state of readiness so they can be brought online within 48 hours for anticipated shortage of operating capacity, stability issues or constrained operations. | Status Quo | Status Quo
| ii. Peak Period Maintenance Season |  | PJM does not allow Planned Outages of generation resources to be scheduled during PJM Peak Period Maintenance Season, defined as weeks containing the 24th - 36th Wednesday of the calendar year. (PJM Manual 10 Section 2.2) Maintenance outages are only allowed with a maximum duration of 9 consecutive days, 5 week days plus the weekend on each end. (PJM Manual 10 Section 2.3) | Status Quo | Status Quo
| Outage Acceleration Eligibility |  | Outages that qualify for this process include the planned outages that will exceed five days and are estimated to cause more than $500,000 in congestion revenue inadequacy. Also qualifying for this process are forced outages projected to last into the month of the analysis window and are estimated to cause more than $500,000 in congestion revenue inadequacy. Planned and forced outages affecting the interconnection of a generating unit to the transmission system qualify for outage acceleration regardless of expected congestion revenue inadequacy. | Status Quo | Status Quo
Instructions:
1. Copy over design component, priority, and status quo columns from options matrix
2. Complete individual packages in columns by selecting individual component options from the options matrix.

## 3a. Package Details
OC Special Session: Outage Coordination
Outage Coordination
PACKAGE / PROPOSAL DETAILS
Instructions: Complete this form as needed, including more detailed / expansive descriptions of package components than the Package Matrix allows.
Package Solutions2
| A | B | C | D | E
1 | <enter detailed description of this component> | <enter detailed description of this component> | <enter detailed description of this component> | <enter detailed description of this component> | <enter detailed description of this component>
2 | <enter detailed description of this component> | <enter detailed description of this component> | <enter detailed description of this component> | <enter detailed description of this component> | <enter detailed description of this component>
3 | <enter detailed description of this component> | <enter detailed description of this component> | <enter detailed description of this component> | <enter detailed description of this component> | <enter detailed description of this component>
4 | <enter detailed description of this component> | <enter detailed description of this component> | <enter detailed description of this component> | <enter detailed description of this component> | <enter detailed description of this component>
5 | <enter detailed description of this component> | <enter detailed description of this component> | <enter detailed description of this component> | <enter detailed description of this component> | <enter detailed description of this component>

## Parking Lot
OC Special Session: Outage Coordination
Outage Coordination
PARKING LOT
Instructions: Use this space to document any items not specific to another topic area.
Description

## Revision History
OC Special Session: Outage Coordination
Outage Coordination
Revision History
Current Spreadsheet Version:
Instructions: Document all version changes to this matrix for easy identification of changes.
Version | Posting Date | Description of changes
1
2
3