## Appendix
Region | UpgradeId | Description | Transmission Owner | Immediate Need | Project Submittal Number | Drivers | Required In-Service Date | Revised In-Service Date | Status | Initial TEAC Cost ($M) | Latest TEAC Cost ($M) | Board Approval Date | Issue Category
PJM SOUTH | b3800.375 | Construct new Woodside – Goose Creek 500 kV line for ~3 miles on single circuit monopole structures within the Doubs – Goose Creek Corridor.? (DOM Portion) | Dominion |  |  | Baseline Load Growth Deliverability & Reliability |  |  | PL | 15.6 |  |  | Scope/Cost Change
PJM WEST | b3800.129 | Construct 500 kV Line from existing structure MVF1-101 on the Doubs – Millville 138 kV Line, around Doubs Substation, and into the entrance of the Doubs – Goose Creek Corridor.? (~2 miles) | APS |  |  | Baseline Load Growth Deliverability & Reliability |  |  | PL | 115.3 |  |  | Scope/Cost Change
PJM WEST | b3800.128 | Construct new Woodside – Goose Creek 500 kV line for ~15 miles on single circuit monopole structures within the Doubs – Goose Creek Corridor.? (FE Portion) | APS |  |  | Baseline Load Growth Deliverability & Reliability |  |  | PL | 13.2 |  |  | Scope/Cost Change
PJM SOUTH | b3854.1 | Replace over duty Carson 230kV circuit breakers 200272 and 24972-3 with an interrupting rating of 63 kA | Dominion | X |  | Short Circuit | 6/1/2025 |  | PL | 1.25 |  |  | New Upgrade
PJM SOUTH | b3853.1 | Replace over duty Ladysmith CT 230kV circuit breakers SX1272 and SX3472 with an interrupting rating of 63 kA | Dominion | X |  | Short Circuit | 6/1/2025 |  | PL | 1.25 |  |  | New Upgrade
PJM MA | b3849.1 | Perform all necessary engineering design and evaluation to increase Fairlawn 69kV GIS from 50kA to 55kA. | PSEG | X |  | TO Criteria Violation | 6/1/2028 |  | PL | 1.49 |  |  | New Upgrade
PJM WEST | b3007.1 | Reconductor the Blairsville East to Social Hall 138 kV line and upgrade terminal equipment - AP portion. 4.8 miles total. The new conductor will be 636 ACSS replacing the existing 636 ACSR conductor. At Social Hall, meters, relays, bus conductor, a wavetrap, circuit breaker and disconnects will be replaced. | APS | X |  | Generator Deactivation | 6/1/2021 |  | Cancelled | 3.135 | 3.135 | 7/31/2018 | Cancelled
PJM MA | b3007.2 | Reconductor the Blairsville East to Social Hall 138 kV line and upgrade terminal equipment - PENELEC portion. 4.8 miles total. The new conductor will be 636 ACSS replacing the existing 636 ACSR conductor. At Blairsville East, the wave trap and breaker disconnects will be replaced. | PENELEC | X |  | Generator Deactivation | 6/1/2021 |  | Cancelled | 3.135 | 3.135 | 7/31/2018 | Cancelled
PJM MA | b3728.2 | Replace 4 meters and bus work inside Peach Bottom substation on the 500 kV Line 5012 (Conastone-Peach Bottom). | PECO |  |  | Baseline Load Growth Deliverability & Reliability | 12/1/2027 |  | Cancelled | 3.8 | 3.8 | 12/6/2022 | Cancelled
PJM MA | b3728.1 | Upgrade two Breaker bushings on the 500 kV Line 5012 (Conastone-Peach Bottom) at Conastone substation. | BGE |  |  | Baseline Load Growth Deliverability & Reliability | 12/1/2027 |  | Cancelled | 2 | 2 | 12/6/2022 | Cancelled
PJM MA | b3737.22 | Construct the Larrabee Collector station AC switchyard, composed of a 230 kV 3 x breaker and a half substation with a nominal current rating of 4000 A and four single phase 500/230 kV 480 MVA autotransformers to step up the voltage for connection to the Smithburg substation. Procure land adjacent to the AC switchyard, and prepare the site for construction of future AC to DC converters for future interconnection of DC circuits from offshore wind generation. Land should be suitable to accommodate installation of four individual converters to accommodate circuits with equivalent rating of 1400 MVA at 400 kV.Additional scope includes prebuild extension work, and three sets of AC collector lines from the LCS to the offshore wind converter station area. | MAOD |  | 2021_SAA-550, DENL | Public Policy | 12/31/2027 |  | EP | 121.3 | 217.1 | 12/6/2022 | Scope/Cost Change
PJM WEST | b3800.119 | New 500 kV transmission line from Woodside substation to Aspen substation (in DOM zone). (NEET Portion) | NEET |  | 2022-W3-853 | Baseline Load Growth Deliverability & Reliability | 6/1/2027 |  | Cancelled | 71.72 |  | 12/11/2023 | Scope/Cost Change
PJM MA | b3800.2 | Break the existing TMI-Peach Bottom 500 kV line and reterminate into adjacent Otter Creek 500 kV Switchyard. | ME |  | 2022-W3-374, DENL | Baseline Load Growth Deliverability & Reliability | 6/1/2027 |  | EP | 7.03 | 7.43 | 12/11/2023 | Scope/Cost Change
PJM MA | b3800.39 | Red Lion - Hope Creek 500 kV - Replace four 500kV breakers and the stranded bus at Red Lion 500 kV substation | DPL |  | 2022-W3-344 | Baseline Load Growth Deliverability & Reliability | 6/1/2027 |  | EP | 4 | 6 | 12/11/2023 | Scope/Cost Change
PJM MA | b3800.3 | Build New 500kV AC line from the new Otter Creek (Chanceford) 500 kV switchyard – towards PA/MD border ~12.5 miles Ø Rebuild the existing Otter Creek - Conastone 230 kV line to become a double-circuit 500 kV line, operate Conastone circuit at 230 kV initially | PPL |  | 2022-W3-374 | Baseline Load Growth Deliverability & Reliability | 6/1/2027 |  | EP | 83.3 | 102.8 | 12/11/2023 | Scope/Cost Change
PJM WEST | b3811.1 | Expand Haumesser Road 138 kV substation as a 4 circuit breaker ring bus. | ComEd |  | 2023-W1-972 | Baseline Load Growth Deliverability & Reliability | 12/1/2028 |  | PL | 15.91 |  |  | New Upgrade
PJM WEST | b3811.2 | Add one 138 kV circuit breaker at H-452 to complete a three circuit breaker ring bus. | ComEd |  | 2023-W1-972 | Baseline Load Growth Deliverability & Reliability | 12/1/2028 |  | PL | 1.98 |  |  | New Upgrade
PJM WEST | b3811.3 | Rebuild 3 miles of 138 kV line 11323 from Haumesser Road to the H-452 tap with double circuit towers. Cut the H-452 tap over to the 2nd circuit from Haumesser Road. Both circuits to use twisted pair 556 ACSR Parakeet conductor. | ComEd |  | 2023-W1-972 | Baseline Load Growth Deliverability & Reliability | 12/1/2028 |  | PL | 10.22 |  |  | New Upgrade
PJM WEST | b3812.1 | Reconductor 345 kV lines 11620 & 11622 from Elwood to Goodings Grove. | ComEd |  | 2023-W1-35 | Baseline Load Growth Deliverability & Reliability | 6/1/2028 |  | PL | 56.18 |  |  | New Upgrade
PJM WEST | b3812.2 | Upgrade Goodings Grove 345 kV circuit breakers, disconnects, and associated equipment. | ComEd |  | 2023-W1-35 | Baseline Load Growth Deliverability & Reliability | 6/1/2028 |  | PL | 5.16 |  |  | New Upgrade
PJM WEST | b3812.3 | Upgrade station conductor at Elwood 345 kV. | ComEd |  | 2023-W1-35 | Baseline Load Growth Deliverability & Reliability | 6/1/2028 |  | PL | 0.5 |  |  | New Upgrade
PJM MA | b3800.5 | Peach Bottom-TMI 500 kV - Replace terminal equipment at Peach Bottom. | PECO |  | 2022-W3-374 | Baseline Load Growth Deliverability & Reliability | 6/1/2027 |  | EP | 0 | 2.5 | 12/11/2023 | Scope/Cost Change
PJM SOUTH | b3702 | Install one 13.5 Ohm series reactor to control the power flow on the 230 kV line #2054 from Charlottesville substation to Proffit Rd 230 kV line. | Dominion |  | 202021_1-651 | Congestion Relief - Economic | 6/1/2023 |  | Cancelled | 11.38 |  | 2/16/2022 | Cancelled
PJM SOUTH | b3850.1 | Rebuild approximately 13.51 miles of 500 kV line #588 from structure 588/184 inside Yadkin substation to structure 588/254 outside of Fentress substation. | Dominion | X |  | TO Criteria Violation | 6/1/2028 |  | PL | 78.6 |  |  | New Upgrade
PJM SOUTH | b3850.3 | At Fentress substation, since the new 500kV line will be using fiber, the wave trap will be removed and the line protection scheme will be updated. | Dominion | X |  | TO Criteria Violation | 6/1/2028 |  | PL | 0.14 |  |  | New Upgrade
PJM SOUTH | b3850.2 | Line #588 terminal equipment at Yadkin substation will be upgraded to a rating of 5000A. Since the new 500kV line will be using fiber, the wave trap will be removed and the line protection scheme will be updated. | Dominion | X |  | TO Criteria Violation | 6/1/2028 |  | PL | 0.962 |  |  | New Upgrade
PJM WEST | b3851.1 | Rebuild Allen –R.P. Mone 345kV line (18.6 miles). | AEP | X |  | Baseline Load Growth Deliverability & Reliability | 6/1/2027 |  | PL | 49.875 |  |  | New Upgrade
PJM WEST | b3851.2 | Rebuild R.P. Mone – Maddox Creek 345kV line (9.4 miles). | AEP | X |  | Baseline Load Growth Deliverability & Reliability | 6/1/2027 |  | PL | 39.034 |  |  | New Upgrade
PJM WEST | b3851.3 | Replace breakers 'B1' and 'B' at Maddox Creek. | AEP | X |  | Baseline Load Growth Deliverability & Reliability | 6/1/2027 |  | PL | 1.8 |  |  | New Upgrade
PJM WEST | b3851.4 | Replace two 345kV breakers 'M' and 'M2' at East Lima Station. | AEP | X |  | Baseline Load Growth Deliverability & Reliability | 6/1/2027 |  | PL | 1.761 |  |  | New Upgrade
PJM WEST | b3852.1 | Connect and energize a second 765/345 kV bank at Vassell station. | AEP | X |  | Baseline Load Growth Deliverability & Reliability | 6/1/2027 |  | PL | 30.829 |  |  | New Upgrade
PJM WEST | b3852.2 | Replace 765 kV breaker D at Maliszewski station. | AEP | X |  | Baseline Load Growth Deliverability & Reliability | 6/1/2027 |  | PL | 2.9 |  |  | New Upgrade
PJM MA | b3855.3 | Replace the existing HPFF termination structure with a new XLPE termination structure to connect to spare GIS bay position at Jackson 230kV | PSEG |  | 2023-W2-627 | Baseline Load Growth Deliverability & Reliability | 6/1/2028 |  | PL | 0.82 |  |  | New Upgrade
PJM MA | b3800.53 | Construct a double-circuit 500kV line from the existing TMI-Peach Bottom 500kV right-of-way to the proposed Chanceford Switchyard approximately 1.0 miles in length | PPL |  |  | Baseline Load Growth Deliverability & Reliability | 6/1/2027 |  | PL | 12.59 | 12.59 |  | Scope/Cost Change
PJM WEST | b3847.2 | Add two 765 kV breakers to the reactors at Broadford station on the Baker and Jacksons Ferry 765 kV lines. | AEP | X |  | Baseline Load Growth Deliverability & Reliability | 6/1/2027 |  | PL | 29.05 |  |  | New Upgrade
PJM WEST | b3847.1 | Add a 765 kV breaker at Baker station for the reactor on the Broadford 765 kV line. | AEP | X |  | Baseline Load Growth Deliverability & Reliability | 6/1/2027 |  | PL | 23.37 |  |  | New Upgrade
PJM MA | b3855.2 | Expand a new 230kV bay at the existing Cedar Grove Station with one line position by adding two 230kV circuit breakers and associated disconnect switches | PSEG |  | 2023-W2-627 | Baseline Load Growth Deliverability & Reliability | 6/1/2028 |  | PL | 6.61 |  |  | New Upgrade
PJM WEST | b3847.3 | Add a 765 kV breaker to the reactor at Jefferson station on the Greentown 765 kV line. | AEP | X |  | Baseline Load Growth Deliverability & Reliability | 6/1/2027 |  | PL | 8.53 |  |  | New Upgrade
PJM MA | b3848.1 | Open East Rutherford 69kV Tie Breaker [26K] | PSEG | X |  | TO Criteria Violation | 6/1/2028 |  | PL | 2.14 |  |  | New Upgrade
PJM MA | b3855.1 | Build 4 miles New 230kV XLPE Circuit using (345kV rated 5000kcmil cable) from Jackson Road 230kV Station to Cedar Grove 230kV Station | PSEG |  | 2023-W2-627 | Baseline Load Growth Deliverability & Reliability | 6/1/2028 |  | PL | 77.15 |  |  | New Upgrade
PJM MA | b3848.2 | Move line U-775 [ East Rutherford to Hasbrouck Heights] currently on section 2 to section 7 of the ring bus. | PSEG | X |  | TO Criteria Violation | 6/1/2028 |  | PL | 0 |  |  | New Upgrade