## CT Heat Rate Curves
Minimum Load
Base Load
Peak Load
Fuel Cost = $4 mmBtu
VOM = $75/EOH
No Load Cost = No Load Fuel x Fuel Cost
= $ 2,359/hr

## CT Heat Input
Fitted Regression Line Equation
No Load Fuel = 578.23 mmBtu/hr
Minimum Load
Base Load
Peak Load

## CT
Combustion Turbine Heat Rate & Cost Curves
Heat Rate Curves
Output | Heat Input | Heat Rate | Incrementals
(MW) | (MBtu/hr) | (Btu/kWh) | (Btu/kWh)
0 | 578.23 |  |  | No Load
70 | 879.02 | 12557.4286 | 4297 | Min
90 | 1054.57 | 11717.4444 | 8777.5 | Base
100 | 1157.28 | 11572.8 | 10271 | Peak
Conditions at 59F
a= | 578.23 | (No Load Fuel) |  |  |  | Fuel Cost | 2.8 | $/mmBtu
b= | 0.8122 |  |  |  |  | VOM | 75 | $/EOH
c= | 0.0498 |  |  |  |  | PF | 1.02
Gas |  |  | Maintenance |  | Operating | Incremental | No Load = | 1651.4249 | $/hr
Net Gen | Heat Input | Heat Rate | Factor | Total Cost | Rate | Heat Rate |  | Incremental Cost
MW | MMBtu/Hr | Btu/Kwh |  | $/MWH | $/Hr | Btu/Kwh |  | $/MWH
0 | 578.23
70 | 879.104 | 12558.6286 | 1 | 36.9389 | 2585.721 | 4298.2 |  | 13.3471 | 13.3471
90 | 1054.708 | 11718.9778 | 1 | 34.3027 | 3087.246 | 8780.2 |  | 25.0763 | 25.0763
100 | 1157.45 | 11574.5 | 4 | 36.0568 | 3605.6772 | 10274.2 |  | 51.8431 | 51.8431

## CC PF Heat Rate Curves
Fuel Cost - $4/mmBtu
VOM Cost - $75/EOH
1 CT at Minimum
1 CT at Base
2 CT at Base
2 CT at Peak
No Load Cost = No Load Fuel x Fuel Cost
= $ 700/hr

## CC PF Heat Input
Fitted Regression Line Equation
No Load Fuel = 171.56 mmBtu/hr
1 CT at Minimum
1 CT at Base
2 CT at Base
2 CT at Peak

## CC 2 on 1 PF
2 on 1 Combined Cycle Heat Rate & Cost Curves
Output | Heat Input | Heat Rate | Incrementals
(MW) | (MBtu/hr) | (Btu/kWh) | (Btu/kWh)
0 | 578.23 |  |  | No Load
105 | 879.02 | 8371.619 | 2864.6667 | Min 1 CT
135 | 1054.57 | 7811.6296 | 5851.6667 | Base 1 CT
270 | 2109.14 | 7811.6296 | 7811.6296 | Base 2 CT
300 | 2314.56 | 7715.2 | 6847.3333 | Peak 2 CT
Conditions at 59F
a= | 171.56 | (No Load Fuel) |  |  |  | Fuel Cost | 4 | $/mmBtu
b= | 6.2856 |  |  |  |  | VOM | 75 | $/EOH
c= | 0.003 |  |  |  |  | PF | 1.02
Gas |  |  | Maintenance |  | Operating | Incremental | No Load = | 699.9648
Net Gen | Heat Input | Heat Rate | Factor | Total Cost | Rate | Heat Rate |  | Incremental Cost
MW | MMBtu/Hr | Btu/Kwh |  | $/MWH | $/Hr | Btu/Kwh |  | $/MWH
0 | 171.56
105 | 864.623 | 8234.5048 | 1 | 34.3111 | 3602.6618 | 6600.6 |  | 27.6447 | 27.6447
135 | 1074.791 | 7961.4148 | 1 | 33.0381 | 4460.1473 | 7005.6 |  | 28.5828 | 28.5828
270 | 2087.372 | 7731.0074 | 2 | 32.0981 | 8666.4778 | 7500.6 |  | 31.158 | 31.158
300 | 2327.24 | 7757.4667 | 8 | 33.6505 | 10095.1392 | 7590.6 |  | 34.1515 | 34.1515

## CC Maint History
2 on 1 Combined Cycle 20 Year Maintenance History
Year | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20
Escalation Factors | 659 | 631 | 604 | 578 | 596 | 546 | 515 | 493 | 465 | 441 | 438 | 425 | 415 | 389 | 383 | 375 | 363 | 358 | 346 | 334 | 322
VOM |  | 1753506.0531 | 1702433.0612 | 1652847.6323 | 1604706.4391 | 1557967.4166 | 1512589.7249 | 1468533.7135 | 1425760.8868 | 1384233.8707 | 1343916.3793 | 1304773.1838 | 1266770.0814 | 1229873.8654 | 1194052.2965 | 1159274.0743 | 1125508.81 | 1092727 | 1060900 | 1030000 | 1000000
CT Overhauls |  |  | 2300000 | 2200000 |  |  |  |  | 1900000 | 1800000 |  |  |  |  | 1600000 | 1500000
ST Overhauls | [10 empty] | 2000000
Major Inspections | [5 empty] | 550000 | 500000 |  |  |  |  | 450000 | 400000 |  |  |  |  | 350000 | 300000
Annual Cost with |  | 1753506.0531 | 4002433.0612 | 3852847.6323 | 1604706.4391 | 2107967.4166 | 2012589.7249 | 1468533.7135 | 3325760.8868 | 3184233.8707 | 3343916.3793 | 1754773.1838 | 1666770.0814 | 1229873.8654 | 2794052.2965 | 2659274.0743 | 1125508.81 | 1442727 | 1360900 | 1030000 | 1000000
Annual Cost without |  | 1753506.0531 | 1702433.0612 | 1652847.6323 | 1604706.4391 | 1557967.4166 | 1512589.7249 | 1468533.7135 | 1425760.8868 | 1384233.8707 | 1343916.3793 | 1304773.1838 | 1266770.0814 | 1229873.8654 | 1194052.2965 | 1159274.0743 | 1125508.81 | 1092727 | 1060900 | 1030000 | 1000000
Escalated with |  | 1831316.1473 | 4366893.0254 | 4392779.5669 | 1774331.4486 | 2544231.7354 | 2575333.2596 | 1963009.5683 | 4713282.6332 | 4758299.5937 | 5031143.5936 | 2720930.6545 | 2646750.563 | 2083513.8234 | 4807520.7922 | 4673230.9732 | 2043279.0793 | 2655746.0698 | 2592003.1792 | 2032245.509 | 2046583.8509
Escalated without |  | 1831316.1473 | 1857455.9393 | 1884475.0686 | 1774331.4486 | 1880403.8966 | 1935527.4343 | 1963009.5683 | 2020594.4611 | 2068503.6753 | 2022011.1735 | 2023165.9486 | 2011569.8401 | 2083513.8234 | 2054518.1812 | 2037230.9732 | 2043279.0793 | 2011472.3268 | 2020615.896 | 2032245.509 | 2046583.8509
Average Yearly Total Maintenance Cost (with OH) |  |  | 3112621.2533 |  | Before 6/1/2015
Average Yearly Total Maintenance Cost (without OH) |  |  | 1980091.2121 |  | After 6/1/2015
2 on 1 Combined Cycle Equivalent Service Hours
Number of Starts |  |  | 200 |  |  | Cyclic Starting Factor |  | 10
Total Operating Hours |  |  | 3200 |  |  | Cyclic Peaking Factor |  | 3
Number of Hours above Base Load |  |  | 100
Equivalent Service Hours (with CF) |  |  | 5500 |  | Before 6/1/2015
Operating Hours (without CF) |  |  | 3200 |  | After 6/1/2015
2 on 1 Combined Cycle Equivalent Maintenance Cost
Equivalent Hourly Maintenance Cost (with OH & CF) |  |  | $ | 565.9311 | /hour
Equivalent Hourly Maintenance Cost (without OH & CF) |  |  | $ | 618.7785 | /hour
Equivalent Hourly Maintenance Cost (without OH & with CF) |  |  | $ | 360.0166 | /hour
2 on 1 Combined Cycle Start Cost
Start Fuel |  | 2197.55 | mmBtu |  | Total Fuel Related Costs $ |  |  | 2.8 | /mmBtu |  | Performance Factor |  | 1.02
Station Service |  | 20 | MWh |  | Station Service Rate $ |  |  | 30.15 | /MWh
Net Generation during Start Period |  | 192.5 | MWh |  | Actual Cost of Unit $ |  |  | 30.15 | /MWh
Start Maintenance Adder (with OH & CF) | $ | 5659.3114
Start Maintenance Adder (without OH & CF) | $ | 0
Start Maintenance Adder (without OH & with CF) | $ | 3600.1658
Start Additional Labor Cost | $ | 0
Start Cost (with OH & CF) |  |  | $ | 6734.6392
Start Cost (without OH & CF) |  |  | $ | 1075.3278
Start Cost (without OH & with CF) |  |  | $ | 4675.4936
2 on 1 Combined Cycle Cost Schedule
a= | 171.56 | (No Load Fuel)
b= | 6.2856
c= | 0.003
[5 empty] | Operating | Operating | Operating
| No Load = $ | 999.6 | /hr |  | Rate | Rate | Rate |  | Incremental Cost
Gas |  |  | Operating CT |  | with | without | without OH |  | With | Without | without OH
Net Gen | Heat Input | Heat Rate | CTs | Mode | OH & CF | OH & CF | with CF |  | OH & CF | OH & CF | with CF
MW | MMBtu/Hr | Btu/Kwh |  |  | $/Hr | $/Hr | $/Hr |  | $/MWH | $/MWH | $/MWH
0 | 350
105 | 864.623 | 8234.5048 | 1 | Min | 3035.2944 | 3088.1418 | 2829.3799 |  | 19.3876 | 19.8909 | 17.4265
135 | 1074.791 | 7961.4148 | 1 | Base | 3635.5342 | 3688.3816 | 3429.6197 |  | 20.008 | 20.008 | 20.008
270 | 2087.372 | 7731.0074 | 2 | Base | 7093.3967 | 7199.0914 | 6681.5676 |  | 25.6138 | 26.0053 | 24.0885
300 | 2327.24 | 7757.4667 | 2 | Peak | 11174.0465 | 7884.1544 | 9526.7301 |  | 136.0217 | 22.8354 | 94.8388
Total Annual Maintenance Cost Recovered
|  | Recovered | Recovered | Recovered
|  | Through | Through | Through
|  | Starts | Base Hours | Peak Hours |  | Totals
|  | $ | $ | $ |  | $
Maintenance Cost Recovered ( with OH & CF) |  | 1131862.2739 | 1810979.6383 | 169779.3411 |  | 3112621.2533
Maintenance Cost Recovered ( without OH & CF) |  | 0 | 1980091.2121 | 0 |  | 1980091.2121
Maintenance Cost Recovered ( without OH & with CF) |  | 720033.168 | 1152053.0688 | 108004.9752 |  | 1980091.2121