## Requirements_status quo_DIRS
For Purposes of this matrix: DR – load reduction activity from DER or any type of load DER – a resource that can produce or inject electricity onto the grid (Generator, battery, etc) | Demand Response (DR) (No Injection) | Generation (Small Gen) | Dual Model (DR+DER, with injection)
High level requirement | Status Quo | Status Quo | Status Quo
Model Overview | Allows all technologies and methods that can change load to participate in the wholesale markets (Gen, Batteries, arc furnace curtailment, residential load control, etc.). The DR model only allows payment for change in load and does not compensate for injection past the retail meter (or in the case of a muni, the muni meter(s)) | Traditional model where all units go through the interconnection queue prior to participation in the wholesale markets. Units receive CIRs and may be a Capacity unit or an Energy Only unit. Some Capacity resources have capacity market must offer requirements. All capacity resources have energy market must offer requirements, market mitigation and are modelled in the EMS (state estimator). Some interconnection provisions allow for expedited processing in the queue. | DER that is oversized for the customer's retail load can participate as both DR and Gen at the same time. The portion used to offset load is handled with the DR model and the portion that injects is handled with the Generation model. One caveat- Regulation market, once interconnection study is done for the injection, the entire amount is handled under the DR rules.
Interconnection: study process around DER and DER aggregation. | No PJM Interconnection study process for DR, study process/requirements are at the utility/state level. DR in PJM needs to go through registration process. | Must go through PJM Interconnection queue. All capacity resources are Att N; 5MW or less inverter based and 2 MW or less synchronous are Att Y, and 10kW or less are Att BB | DR portion participates under DR rules, Gen (injection) portion participates under generation rules.
Jurisdiction: the Commission declined to exercise its jurisdiction over the interconnections of DERs to distribution facilities for the purpose of participating in RTO/ISO markets exclusively as part of a DER aggregation. | Jurisdiction over interconnection is at state level. | Sign WMPA or ISA | Portion that is Gen (Injection) would sign WMPA or ISA
Opt-in for Small Utilities: do not accept bids for aggregators in utilities < 4millon MWh/year unless utility allows opt-in. | All DR goes through EDC review process where each EDC is defined as "small" or "large" based on 4 million threshold. The EDC is responsible to interpret RERRA to approve or deny participation in the market. PJM publically posts all RERRA evidence used to approve, qualify or deny. | No opt-in review for generation resources. | Dual Model will go through the EDC review process.
Participation Model: all DER Aggregation to participate in markets under 1 or more participation model and accommodate physical and operational impacts. | DR (behind the meter DER, no injection) | Generator market rules, and ESR participation model | Behind the meter/DER that has the capability to inject can go through the interconnection process and have the injection amount treated as front of the meter generation (must offer, etc.). Regulation solely operates under DR model
Distribution Factors & Bidding Parameters: distributed energy resource aggregators give to the RTO/ISO the total distributed energy resource aggregation response that would be provided from each DER resource in the aggregation, and incorporate appropriate bidding parameters into its participation models. | CSPs have flexibility to aggregate to a resource and such aggregation opportunities vary a little by market. CSPs provide the individual customers that will be participating in the market prior to operations. Distribution factors provided to PJM after the fact. During the settlement process data is provided to detail how much load response was provided by each customer. To address bidding parameters, CSPs can use multi-point curve of aggregate offers. | Aggregation beyond the plant level is typically not allowed. Telemetry on each individual resource at the plant (distribution factor) is required. Bidding parameters available for resources in gen model. | DR portion participates under DR rules, Gen (injection) portion participates under generation rules.
Double Counting Services: limit the participation of resources in RTO/ISO markets through a distributed energy resource aggregator that are receiving compensation for the same services as part of another program. | End use customers may only be with one CSP in one market at any moment in time. Duplicate logic and automated dispute logic in place. Rules are set up to avoid double counting of retail cost savings vs wholesale revenue. | Only allow generator to participate as 1 market resource. | Demand response portion and injection portion accounted for separate
Information & Data Requirements: (1) Information and data that a distributed energy resource aggregator must provide about the physical and operational characteristics of its aggregation; (2) require distributed energy resource aggregators to provide a list of the individual resources in its aggregation; and (3) establish any necessary information that must be submitted for the individual distributed energy resources. | DR is required to provide which customer will provide the response, their load reduction capability and how they will provide the response (HVAC. Gen, Lighting, etc). | Physical and Operational data provided to PJM, aggregation data N/A at this time | DR is required to provide which customer will provide the response, how much response and how they will provide the response.
Metering & Telemetry: determine necessary metering for settlements and performance and telemetry for situational awareness and dispatch. | Metering: Capacity (end of 2 months after the event) and Energy (60days after event)- require hourly load data after the fact (DR Hub) for settlement and performance calculations. SR requires 1min data 2 business days after the event. Telemetry: Regulation participation requires RT telemetry. Hourly meter data is required upon request. Requirements found in M11 | Metering: Hourly data required in Power Meter for capacity, energy and ancillary services. Telemetry: Required for ancillary services and capacity resources and required for energy resources >10MW. Requirements found in M01 | DR portion participates under DR rules, Gen (injection) portion participates under generation rules. Requirements found in M11, M01
Locational Requirements: establish locational requirements for distributed energy resources to participate in a distributed energy resource aggregation that are as geographically broad as technically feasible, multi-node or single node aggregation. | Aggregation across geographic footprint based on market specific requirements and process (participation(min threshold), market offer, settlement and compliance). Energy market can be aggregated by zone by LSE (registration) and by zone (residual zonal aggregate) for the market offer. | Generating units that are connected to the system at the same electrical location may be aggregated and offered into the PJM market as a single unit. All individual nodes are studied and modeled with applicable resources. | DR portion participates under DR rules, Gen (injection) portion participates under generation rules.
Minimum & Maximum Size of Aggregation: Minimum size = 100kw, determine max capacity size if one is needed. | 100kw min size, no max size requirements | 100kw min size, no max size requirements | 100kw min size, no max size requirements
Maximum Capacity Requirements: propose a maximum capacity requirement for individual distributed energy resources participating in its markets through a distributed energy resource aggregation or, alternatively, to explain why such a requirement is not necessary. | 1 site over 100kw in an aggregation (no capacity size max on that 1 site), with exception process | No Max Capacity Size | 1 site over 100kw in an aggregation (no capacity size max on that 1 site)
Single Resource Aggregation: allow a single qualifying distributed energy resource to avail itself of the proposed distributed energy resource aggregation rules by serving as its own distributed energy resource aggregator. Can set size requirements for these resources. | Single customer may participate but would need to be a PJM member. | Single resources are allowed to participate in the market | DR portion participates under DR rules, Gen (injection) portion participates under generation rules.
Modifications to List of Resources in Aggregation: develop rules for modifying the list of resources in an aggregation and how they would be reported to PJM. | All customers are "registered" and then CSP can modify their offers or their aggregation (via Dispatch groups). Some modification (such as a change in customers providing service) will require a re-registration process. | All modifications (adding generation) need to go through PJM queue for study. Modeling or aggregation of resources in Markets is able to be performed during quarterly model updates (e.g. combined cycles). Unit modeling changes in the PJM Markets Gateway system (unit type, aggregation level), not including changes based on physical changes at the plant, can be made at the beginning of each quarter. | DR portion participates under DR rules, Gen (injection) portion participates under generation rules.
Types of Technology: make sure participation is technology neutral, allow heterogeneous and homogeneous aggregations. | DR can participate with anything that will reduce load - we do not differentiate based on how the load is reduced. For example, we treat batteries, mass market AC cycling and arc furnace curtailments the same | Aggregation currently only homogenous (hydro or combined cycle). | DR can participate with anything that will reduce load - we do not differentiate based on how the load is reduced. For example, we treat batteries, mass market AC cycling and arc furnace curtailments the same
Market Participation Agreements: new agreement in Tariff for aggregators. Attestation that the DER aggregator’s aggregation is compliant with the Tariff and operating procedures of the utility. | CSP must be a PJM member but does not sign a market participation agreement. - Certification (or provide attestations) is required for different market participation (e.g. for regulation with the capability to inject we require CSP to coordinate and get approval from the EDC that they meet the EDCs requirements). | Resources signs WMPA or ISA. Market Seller can sign a DOA to market the resource. Resource owner does not need to be a PJM Member, but Market Seller does. | DR portion participates under DR rules, Gen (injection) portion participates under generation rules.
Market Rules to address coordination between all parties (DO/TO/RTO/RERRA) - Distributed Utility Review: develop a process for utilities to review the individual DERs in the aggregation, if they can participate (double counting checks) and safe and reliable operations. - Coordinate Operations: data flows, line faults, outages, dispatch control - Role of RERRA: define their involvement | PJM has an automated process built to coordinate across all parties - this was expanded as part of 719A. We have detailed rules on how this works and who is responsible for what. This coordination has been active since 2007.