## Setup
Enter Stakeholder Committee Name in cell A2:
Reactive Power Compensation Task Force
Enter issue title (use title from Issue Tracking if applicable) in cell A5:
Reactive Rate Process

## Buckets
Compensation | Process | Operational Topics
(3) Estimate of Current Cost method used by FERC | (5) Coordination of PJM OATT disposition and FPA Section 203 approved timelines | (9) PJM defined demand for reactive power
(4) Independent Rate Expert |  | (10) Required location on the grid
(6) Competitive Markets | (8) Transparency | (14) Enhancing PJM's Ability of maintaining reliability
(16) Reducing financial risk to PJM and Members | (11) Retain the reactive revenues achieved at FERC | (2) Analysis of Operational side of house (testing RP)
(19) Compensation for non-synchronous resources | (12) Simple process going forward | (28) Understanding the reliability impacts of voltage support on the distribution side of the transmission wholesale meter if distribution level resources are no longer required to provide reactive or cannot receive compensation for reactive in PJM
(20) Compensation for service rendered and control of the unit | (13) Predictability of Reactive Revenues for resources | (29) PJM's ability to fulfill its role as Reliability Coordinator if generation level no longer is required to comply with PJM directives because no compensation comes under Schedule 2
(21) Compensation tied to actual cost or well defined "Replacement costs" that can be easily verified | (15) Easing of Administrative burden (Settlements and Testing)
(22) Obligation implies compensation directly | (17) Reducing uncertainty and increasing transparency in rate design & operations
(23) Ensuring opportunity for generators to reasonably recover costs associated with reactive power capability | (18) Eligibility requirements
(24) Compensation design commensurate with other FERC defined AS (Black Start, Synch Reserve, Regulation, Non-Spin) based on the cost to have the option available and compensation for actual use if it requires cost | (26) Transition mechanisms for existing rates to new constructs that may be approved
(25) Compensation comparability based on MVAR output | (30) If distrubution connected resources are not eligible for Schedule 2 compensation, will PJM still require these resources obligations in existing FERC - accepted ISA requirements and in future ISA's
(27) Inclusion of ancillary services opportunity costs
(7) No double counting of reactive revenues

## 1. Interest Identification
Reactive Power Compensation Task Force
Reactive Rate Process
Interest Identification
Instructions: List interests of all parties on this page.
1 | Overview of the RPCTF issue
2 | Analysis of Operational side of house (Testing Reactive Power)
3 | Estimate of Current Cost method used by FERC
4 | Independent Rate Expert
5 | Coordination of PJM OATT disposition and FPA Section 203 approval timelines.
6 | Competitive Markets
7 | No Double Counting
8 | Transparency
9 | PJM defined demand for reactive
10 | Required location on the grid
11 | Retain the Reactive Revenues achieved at FERC
12 | Simplified process going forward
13 | Predictability of Reactive Revenues for Resources
14 | Enhancing PJM's Ability of maintaining reliability
15 | Easing of Administrative Burden (Settlements and Testing)
16 | Reducing Financial Risk to PJM and Members
17 | Reducing Uncertainty and Increasing Transparency in rate design and operations
18 | Eligibility Requirements
19 | Compensation for non-synchronous resources
20 | Compensation for service rendered and control of the unit
21 | Compensation tied to actual cost or well defined. "Replacement costs" that can be easily verified.
22 | Obligation implies compensation directly
23 | Ensuring opportunity for generators to reasonably recover costs associated with reactive power capability
24 | Compensation design commensurate with other FERC defined AS (i.e. Black start, synch reserve, regulation, non-spin) based on the cost to have the option available, and compensation for actual use if it requires costs
25 | Compensation comparability based on MVAR output
26 | Transition mechanisms for existing rates to new constructs that may be approved
27 | Inclusion of ancillary services opportunity costs
28 | Understanding the reliability impacts of voltage support on the distribution side of the transmission wholesale meter if distribution level resources are no longer required to provide reactive or cannot receive compensation for reactive in PJM

## 2. Options Matrix- Design Comp.
Reactive Power Compensation Task Force
Reactive Rate Process
OPTIONS MATRIX
Solution Options2
# | Design Components1 | Priority | Status Quo | A | B | C | D | E | F | G | H | I | J | K | L | L
1 | Compensation Mechanism | High | Unit specific related/structured to the AEP methodology, FERC settlement proceedings, and filed rate. Payment via PJM Tariff Schedule 2- FERC Filed Rate | Unit-specific filed Rate | Flat Rate based on the facility's MVAR obligation under it's ISA | Included in Capacity Payment | Flat rate by technology type | Capacity plus adjustment | Capability independent flat rate | A resource-specific, i.e., generator, cost of service filed at FERC using the AEP methodology | A flat rate per MVAr that is differentiated by resource type, power factor and location determined using the AEP methodology with a requirement to update flat rates periodically, at least every three years. | Compensation solely through existing markets. | Streamlined AEP method. Two options: (A) unit-specific approach using AEP-based form; or (b) AEP-derived stated rate based on generation type
1A | Basis for Compensation | High | FERC Approved Capability | MVAR Capability Nameplate | MVAR Capability ISA | MVAR Capability Tested | Delivered MVAR-h (useful to regulating voltage) | Regulation Capability (Target Voltage Regulation) | Tested MVAR capability beyond the ISA obligation | MW capability (ICAP or MFO, if applicable) | Tested and validated MVAR capability beyond the ISA obligation | Tested and validated MVAR capability | Cost-of-Service rate recovery. | MVAR Capability Tested/Demonstrated | Reactive capability is part of the integrated generator.
1B | Treatment of leading vs. lagging capability. Lagging means injecting |  | No Difference | A: No different; B: Only lagging compensated; C: Different compensation for leading vs. lagging; D: Open for discussion
1C | Eligibility for Compensation | High | FERC Determined | Located inside PJM footprint | Physically connected to PJM designated transmission facilities | Located in an area that benefits from reactive capability | Performs capability testing | Must have automatic voltage regulation operating at all times except for planned outages. Requirement to be dispatched by PJM for reactive power as needed. | Must be modeled in PJM EMS and have all required telemetry | Any generating unit that provides reactive power service and has an ISA or WMPA with PJM would be eligible for compensation under Schedule 2. | FERC Determined with a requirement that resources file an annual report with FERC containing the financial and technical information that is used in the annual revenue requirement calculations, including the most recent power factor test results. Compensation should be adjusted automatically to reflect the power factor, if the demonstrated power factor is more than 0.01 higher than the power factor used to establish the current reactive power compensation (down only). Reactive power capability compensation should remain in place as long as a resource is providing reactive power capability. Once a resource is no longer providing reactive power capability, compensation should cease. | Physically connect to designated PJM Transmission Facilities. Must have automatic voltage regulation operating at all times and regulating voltage by exchanging more VARs in response to greater transmission voltage deviation from schedule except for planned outages. Requirement to be dispatched by PJM for reactive power as needed. Units operating on fixed power factor mode (including unity power factor) are not eligible for compensation. Requirement to be dispatched by PJM for reactive power as needed. Units operating on fixed power factor mode (including unity power factor) are not eligible for compensation. | FERC Determined
2 | Reactive Capability Verification/Testing | Low - High | Varies (Manual 14D - Attachment E) | Nameplate | Testing by PJM | Annual testing plus assessment of actual performance during ops | Assessment of actual performance during ops | Testing with adjustments calculated for grid conditions at the time of testing | Every 5-years testing/demonstration When internal generator conditions preclude testing (or demonstration within last 2 years) of full MVAR capability, only actual delivered MVAR will be eligible for flat rate payment. PJM reserves the right to require a retest if prior test capability is not reflected in actual operations. Limit 2 test per year | Power factor testing should be done at a defined real power output target value (for example, Summer Economic Maximum) while determining the reactive power capability target for the test and should occur at no less than the MOD-25 intervals. Testing must recognize that there may be seasonal or system conditions that pose limitations and which should be considered in analyzing test results. | Real time testing needs to be implemented. | Manufacturer's technical specifications should be deemed adequate to support use of nameplate capability particularly for new generation
3 | Delivery Point for Compensation and Related Purposes (e.g. Capability Testing) | Low - High | Varies (FERC Determined Delivery Point) | A: Exciter Terminals; B: POI; C: Match capability testing and ISA obligation; D: Nearest upstream PJM Transmission Facility bus; E: Exciter/Inverter Terminals; F: Nearest upstream PJM Transmission Facility bus (MVAR based on Telemetry); G: Not relevant. The issue is reactive capability of the generating unit. Delivery or absorbing/providing VARs is as needed on an ongoing basis directed by PJM
4 | Treatment of Resources interconnected at Distribution Level (i.e., not PJM monitored facilities) that makes wholesale sales of electric energy in interstate commerce the PJM energy market | Medium | Varies | A: Identical to Transmission Resources; B: Not Eligible; C: Proportional Allocation to account for high impedance between DER terminals and PJM transmission facilities (i.e. the distribution system); D: Not Eligible for PJM; E: Eligible for compensation under Schedule 2
5 | Treatment of Capacitors (and other standalone VAR equipment) located at Generator Sites | Medium | Varies | A: Included in plant MVAR capability; B: Excluded in Plant MVAR capability; C: Included in plant MVAR capability if they meet technical conditions e.g. fast enough autonomous response to be useful post-contingency; D: Included in plant reactive capability.; E: Eligible for recovery under either compensation mechanism discussed above. Eligible for compensation under Schedule 2
6 | Cost development rules for non-synchronous resources if applicable | Medium | Varies | A: Not Applicable; B: A resource-specific, cost of service using the AEP methodology.; C: A flat rate per MVAr that is differentiated by resource type, power factor and location determined using the AEP methodology with a requirement to update flat rates periodically, at least every three years.; D: Under Option A, the AEP-based form would be fuel neutral. Under Option B, A stated rate would be created for each generation type.
7 | Flat Rate Methodology | Medium - High | None | A: Follow the method of the NEISO approach for developing the flat rate; B: NY Approach; C: Avoided cost of SVC or similar; D: NEISO. Remove reactive revenue from Capacity Market pro forma modeling (i.e., remove from VRR CT Net CONE and Net ACR/MOPR Net CONE).; E: A flat rate per MVAr that is differentiated by resource type, power factor and location determined using the AEP methodology with a requirement to update flat rates periodically, at least every three years.; F: Based on current Schedule 2 reactive revenue/total gen MVAR capability; G: AEP-derived stated rate based on generation type
7A | Determinate used for flat rate |  | n/a | A: MVAR Capability beyond ISA obligation/requirement; B: All MVAR capability gets flat rate
8 | Performance incentive/penalty | Medium | None | A: Pass/fail/exceed with penalty/bonus structure; B: Overall performance score with tiered penalties for underperformance; C: Pass/fail with penalty; D: Overall performance score with tiered penalties for underperformance and bonus for over performance; E: Monthly pass/fail look back analysis of generator voltage control performance.; F: Monthly pass/fail look back analysis of generator voltage control performance. If voltage at regulated bus exceeds voltage schedule high/low limits for a 5 minute period, evaluate actual MVAR provided compared to expected MVAR. If actual MVAR is less than 90% of expected (lagging) or greater than 90% (leading), reactive flat rate revenues are withheld for following month and capability is reduced to match delivered. Generator may retest to increase capability. If voltage is consistently within voltage schedule, generator has assumed to pass test. Generators will only be evaluated when online. No compensation if AVR out of service for the month.; G: Monthly pass/fail look back analysis of generator voltage control performance. No compensation if AVR out of service for the month.
8a | AVR | Low | Defined in Manual 3, Sections 3.12 | A: In order to pass during an AVR outage must have a ticket and some demo that they can meet output.
9 | Eligibility for Reactive Services Uplift (Make Whole and Lost Opportunity Cost) | Low | Steam, CCGT, CTs, and Energy Storage Resources | A: All resources otherwise eligible for reactive capability compensation; B: Synchronous and non-synchronous resource eligible for uplift. Additionally, mechanism should be created to compensate inverter-based resources for providing reactive power when resource is not providing real power.; C: All resource types eligible for Reactive Services Uplift (Make Whole and Lost Opportunity Cost)
10 | Voltage schedule development process | Medium | Defined in Manual 3, Sections 3.11 | A: Set upon unit registration for reactive compensation if not already identified; B: A Voltage schedule controlling to a target voltage set by PJM with TO input. Generator Voltage Schedule is in Manual 3 section 3.11; AVR is in Generator Voltage Schedule is in Manual 3 section 3.12; C: No FERC has not required this
11 | Implementation |  | n/a | A: Capability payments only applies to new ISAs going forward; B: New reactive power compensation mechanisms should be applied prospectively following acceptance of PJM's FPA section 205 following by FERC. New reactive power compensation mechanism should not impact generating units that have rates on file with FERC, generating units that have a FPA section 205 filing pending at FERC at the time of filing, or projects that have a facilities study agreement signed by the interconnection customer ("excluded resources"). The reactive rates for these excluded resources are not being fixed under this stakeholder proposal but instead will continue to be determined by the Commission.; C: New reactive power compensation mechanism should be applied prospectively following acceptance of PJM's FPA section 205 following by FERC. New reactive power compensation mechanism should not impact generating units that have rates on file with FERC, generating units that have a FPA section 205 filing pending at FERC at the time of filing, or projects that have a facilities study agreement signed by the interconnection customer; D: New reactive power compensation mechanisms should be applied prospectively following acceptance of PJM's FPA section 205 filing. New reactive power compensation mechanism should not impact generating units that have existing rates on file with FERC.; E: As soon as practical. Need to address issue in Quad Review.

## 2a. Design Component Details
Reactive Power Compensation Task Force
Reactive Rate Process
COMPONENT DETAILS
Instructions: Complete this form as needed. Design components should be populated from the Options Matrix.
Design Component | Detailed Description
1 | <enter detailed description of this component>
2 | <enter detailed description of this component>
3 | <enter detailed description of this component>
4 | <enter detailed description of this component>
5 | <enter detailed description of this component>

## 2b. Option Details
Reactive Power Compensation Task Force
Reactive Rate Process
SOLUTION OPTION DETAILS
Instructions: Complete this form as needed, including more detailed / expansive descriptions of options than the Options Matrix allows.
Cell # | Detailed Description
11E | Physically connect to PJM Transmission Facilities. Must have automatic voltage regulation operating at all times except for planned outaged. Requirement to be dispatched by PJM for reactive power as needed.
13H | Every 5-years testing/demonstration When internal conditions preclude testing (or demonstration within last 2 years) of full MVAR capability, only actual delivered MVAR will be eligible for flat rate payment. PJM reserves the right to require a retest if prior test capability is not reflected in actual operations. Limit 2 test per year
20E | Monthly pass/fail look back analysis of generator voltage control performance. If voltage at regulated bus exceeds voltage schedule high/low limits for a 5 mimute period, evaluate actual MVAR provided compared to expected MVAR. If actual MVAR is less than 90% of expected (lagging) or greater than 90% (leading), reactive flat rate revenues are withheld for following month and capability is reduced to match delivered. Generator may retest to increase capability. If voltage is consistently within voltage schedule, generator has assumed to pass test. Generators will only be evaluated when online. No excuse for unit online but AVR not in service.

## 3. Package Matrix
Reactive Power Compensation Task Force
Reactive Rate Process
RPCTF PACKAGE/ PROPOSAL MATRIX
Packages
# | Design Components1 | Priority | Status Quo | A - ODEC | B - CEC | E - PJM-Full Capability | F - IMM | G - PJM-Capability Above Standard Obligation | H - IMM Flat Rate
* | Compensation Mechanism | High | Unit specific related/structured to the AEP methodology, FERC settlement proceedings, and filed rate. Payment via PJM Tariff Schedule 2- FERC Filed Rate | Flat Rate based on the facility's MVAR obligation under it's ISA | Streamlined AEP-derived stated (flat) rate based on generation type | Flat Rate | Compensation solely through existing markets. | Same as Package E - PJM-Full Capability | Flat rate
1 | Basis for Compensation | High | FERC Approved Capability | Facilities will be compensated according to their ISA requirements. Penalties for non-performance associated with its ISA obligation. Potential exist for bonus payments if PJM requests ( and the generator provides) MVARs beyond the Capability ISA's obligations. . | Cost-of-Service derived stated rate based on the AEP formula, which is the same methodology that has been applied in PJM and is how current rates are assigned to existing generation in PJM. Capability will be used FERC's approved AEP formula and will be tested for confirmation. | Capability based on average leading plus average lagging demonstrated capability. Monthly compensated MVAR Capability = product of: a) Avg (Qmax at Pmax, Qmax at Pmin) - Avg (Qmin at Pmax, Qmin at Pmin) b) flat rate in $/MVAR-month c) "Availability factor" (between zero and one) reflecting resource's availability to provide reactive power Capability (at 4 MVAR points) is set by event-based demonstration, except testing is used when insufficient events exist over the last 2 years (including for new units). Availability for synchronous resources is calculated monthly based on % of time unit is available previous month. Full reduction eDART outages will be used to determine availability. For inverter based resources availability will be determined based on PI data when resource is generating. If resource has "Q at night" or "wind free" capability, availability will be determined similar to synchronous resources (with outage tickets). | Reactive capability is part of the integrated generator. | Before transition--same as Package E-PJM-Full Capability. After transition--same as Package E, except only count capability above the standardized ISA obligation (i.e., 0.95 lead/lag at GSU high side). In particular, afte transition: Capability based on average leading plus average lagging demonstrated capability in excess of 0.95 leading/lagging at GSU high side. Monthly compensated MVAR Capability = product of the below, where QmaxO and QminO are the reactive capability values of the standardized ISA obligation as defined above. a) Avg (Qmax@Pmax minus QmaxO@Pmax, Qmax@Pmin minus QMaxO@Pmin) - Avg (Qmin@Pmax minus QMinO@Pmax, Qmin@Pmin minus QMinO@Pmin) b) flat rate in $/MVAR-month c) "Availability factor" (between zero and one) reflecting resource's availability to provide reactive power Capability (at 4 MVAR points) is set by event-based demonstration, except testing is used when insufficient events exist over the last 2 years (including for new units). Availability for synchronous resources is calculated monthly based on % of time unit is available previous month. Full reduction eDART outages will be used to determine availability. For inverter based resources availability will be determined based on PI data when resource is generating. If resource has "Q at night" or "wind free" capability, availability will be determined similar to synchronous resources (with outage tickets). | Capability based on average leading plus average lagging demonstrated capability. Monthly compensated MVAR Capability = product of: a) Avg (Qmax at Pmax, Qmax at Pmin) - Avg (Qmin at Pmax, Qmin at Pmin) b) flat rate in $/MVAR-month c) "Availability factor" (between zero and one) reflecting resource's availability to provide reactive power Capability (at 4 MVAR points) is set by event-based demonstration. Test result not to exceed Schedule 2 requirements. Availability for synchronous resources is calculated monthly based on % of time unit is available previous month. All eDART outages will be used to determine availability. For inverter based resources availability will be determined based on PI data when resource is generating. If resource has "Q at night" or "wind free" capability, availability will be determined based on review (with outage tickets).
2 | Treatment of leading vs. lagging capability. Lagging means injecting | High | No Difference | Compensation is based on the ISA requirement | PJM must adopt means to allow generation to test to confirm manufacturer's reactive capability. Testing limitations (system voltage, availability of renewable resource) must be taken into account if not based on manufacturer's nameplate rating to avoid a discriminatory result or impact on recovery based on cooperation or lack thereof by the interconnecting utility. Options include (1) PJM establishing telemetry to the low side or per feeder for wind and solar resources, (2) PJM allow units to abosrb VARs while other units provide VARs so the full range of VAR capability is validated, (3) PJM directs redispatch of local generation, cap banks and reactors to allow meaningful test. This is also needed to ensure that there is no opportunity for a utility to prefer its own generation or a particular technology type. | No difference | No difference | Same as Package E - PJM-Full Capability | No difference.
3 | Eligibility for Compensation | High | FERC Determined | Directly connected to the Located inside PJM footprint PJM transmission system and the facility is located within the PJM service territory (i.e. no pseudo-ties) . | Any generating unit or resource that has demonstrated reactive capability and has an ISA or WMPA with PJM would be eligible for compensation under Schedule 2. | * Physically connect to designated PJM Transmission Facilities. * Must have automatic voltage regulation operating at all times when online and regulating voltage by automatically exchanging more VARs in response to greater transmission voltage deviation from schedule except for planned outages. * Generation owner must be PJM Member or have an executed full responsibility DOA with a PJM Member * If in the course of performance assessment, PJM discovers that the resource can not meet ISA requirements due to internal plant limitations, PJM reserves the right to make the resource not eligible for compensation. If resource can not meet ISA requirement due to system limitation, compensation will be based on deliverable MVAR amount (see design component 1) * Requirement to be capable of being dispatched by PJM for reactive power as needed. Units operating on fixed power factor mode (including unity power factor) are not eligible for compensation. | FERC Determined | Same as Package E - PJM-Full Capability | Same as Package E - PJM-Full Capability
4 | Reactive Capability Verification/Testing | Low | Varies (Manual 14D - Attachment E) | Not required but PJM needs to verify the generator can satisfy the ISA requirements and is performing consistent with its ongoing obligations . | PJM must adopt means to allow generation to test to confirm manufacturer's reactive capability.Testing limitations (system voltage, availability of renewable resource) need to be taken into account if not based on nameplate rating to avoid a discriminatory result or impact on recovery based on cooperation or lack thereof by the interconnecting utility. Options include (1) PJM establishing telemetry to the low side or per feeder for wind and solar resources, (2) PJM allow units to abosrb VARs while other units provide VARs so the full range of VAR capability is validated, (3) PJM directs redispatch of local generation, cap banks and reactors to allow meaningful test. This is also needed to ensure that there is no opportunity for a utility to preference its own generation or a particular technology type. Verification of capability: Three-strike rule for non-performance similar to MISO's Schedule 2 section IV.A.1 " | Capability verification is by event-based demonstration. When insufficient events have been observed in preceding 2 years to validate capability, or with PJM approval based on gen owner request and explanation, generator is eligible for a test to verify capability. When insufficient events have been observed across 5 years, at least one test is required within the 5-year window. When internal generator or system conditions preclude testing or demonstration of full MVAR capability, only actual delivered MVAR will be eligible for flat rate payment. PJM reserves the right to require a retest if prior test capability is not reflected in actual operations. Limit 2 test per year. Units that share a Generator Step-Up transformer (GSU) must be tested as an aggregated unit at the same time unless they can provide evidence of not being limited by GSU. | Real time testing needs to be implemented. | Same as Package E - PJM-Full Capability | Capability verification is by event-based demonstration. Only actual delivered MVAR will be eligible for flat rate payment. Units that share a Generator Step-Up transformer (GSU) must be evaluated as an aggregated unit at the same time unless they can provide evidence of not being limited by GSU.
5 | Delivery Point for Compensation and Related Purposes (e.g. Capability Testing) | High | Varies (FERC Determined Delivery Point) | Interconnection point with PJM transmission system | Not relevant. Per FERC precedent, the issue is the reactive capability of the generating unit or resource.so it is available for reliability as needed on a day-to-day basis and for emergency needs of the transmission grid. Delivery or absorbing/providing VARs is as needed on an ongoing basis directed by PJM | High side of Generator Step-Up transformer (GSU), as measured by PJM State Estimator data | Match capability testing and ISA obligation | Same as Package E - PJM-Full Capability | Same as Package E - PJM-Full Capability
6 | Treatment of Resources interconnected at Distribution Level (i.e., not PJM monitored facilities) that makes wholesale sales of electric energy in interstate commerce the PJM energy market | Medium | Varies | Not eligible as these resources are not transmission level facilities | Eligible for compensation under Schedule 2 similar to the cost recovery of such devices in transmission owner transmission rates. Reactive support from capacitors and the like owned by generators or owned by transmission owners have no difference and should be treated the same. | Not eligible | Not eligible | Same as Package E - PJM-Full Capability | Not eligible
7 | Treatment of Capacitors (and other standalone VAR equipment) located at Generator Sites | High | Varies | Reactive capability not eligible for Schedule 2 reactive payments are for generating resources only and should not provide compensation associated with capacitors. | Eligible for compensation under Schedule 2 similar to the cost recovery of such devices in transmission owner transmission rates. | Included in plant MVAR capability if they meet technical conditions e.g. fast enough autonomous response to be useful post-contingency, equal to 500 milliseconds). | Included in plant reactive capability. | Same as Package E - PJM-Full Capability | Included in plant reactive capability.
8 | AVR |  | Defined by Manual 3 Section 3.12 | Defined by Manual 3 Section 3.12 | Defined by Manual 3 Section 3.12 | Defined by Manual 3 Section 3.12 AVR controller requirement including 500 millisecond response time: The eligible reactive capability of inverter-based resources must have a plant controller that automatically and immediately controls PJM-level voltage as directly measured on the high side of the generator step-up transformer. The full reactive capability of the plant must respond to a change in PJM voltage in 500 milliseconds or faster. Full reactive capability response means the reactive output of the plant can change from Qmin to Qmax when voltage swings below the voltage schedule within 0.5 seconds, and vice versa for swings to high voltage. A plant that demonstrates that it meets the default (or faster) reactive capability requirements of IEEE standard 2800 complies with this eligibility requirement. Documentation of compliance with this requirement must be provided at time of registration. The eligible reactive capability of synchronous resources must automatically and immediately respond to PJM-level voltage as directly measured near the generator terminals (or, by exception, on the high side of the generator step-up transformer). The full reactive capability of the plant must respond to a change in PJM voltage in 500 milliseconds or faster. Full reactive capability response means the reactive output of the plant can change from Qmin to Qmax when voltage swings below the voltage schedule within 0.5 seconds, and vice versa for swings to high voltage. Documentation of compliance with this requirement must be provided at time of registration. | Defined by Manual 3 Section 3.12 | Same as Package E - PJM-Full Capability | Defined by Manual 3 Section 3.12
9 | Cost development rules for non-synchronous resources if applicable | Medium | Varies | Not required | A stated rate would be created for each generation type using AEP formula. This will eliminate constant filings at FERC for each Project LLC or by utulity. | Not applicable | Varies Not applicable | Same as Package E - PJM-Full Capability | Not applicable.
10 | Flat Rate Methodology | High | None | MVAR Rate will be based on the PJM average reactive rate as of 1/1/22 (Total Reactive Compensation (approx.. $335 million)) divided by ( System MVAR capability based on nominal plant MW ratings of all units and a 95% Power Factor) | AEP-derived stated rate based on generation type. AEP-derived rate could be applied to new units based on either MFO MW, or MVAr capability. | MVAR Rate will be based on the PJM average reactive rate as of 1/1/22 (Total Reactive Compensation (approx.. $335 million)) divided by ( System MVAR capability based on nominal plant eDART Reportable MW ratings of all unitss, a 95% Power Factor at Pmax, and a rectangular D-curve) Draft rate = $367 m / 130,048 MVAR = $2822/MVAR/year | None | Same as Package E - PJM-Full Capability | Flat rate = $1,000/Mvar-year. Phase out over five years.
11 | Performance incentive/penalty | Medium | FERC Approved Capability | Facilities will be compensated according to their ISA requirements. Penalties for non-performance associated with its ISA obligation. Potential exist for bonus payments if PJM requests ( and the generator provides) MVARs beyond the Capability ISA's obligations. | FERC Approved Capability Three-strike rule for non-performance similar to MISO's Schedule 2 section IV.A.1 | Monthly event assessment, re-rating, and pass/fail look back analysis of generator voltage control performance. If voltage at regulated bus exceeds voltage schedule high/low limits for a 5 minute period (an "event interval"), evaluate actual MVAR compared to expected MVAR. If actual MVAR is less than 90% of expected (lagging) or greater than 90% (leading), reactive flat rate revenues are withheld for that month and capability is reduced to match delivered. Generator may only retest to increase capability with PJM approval upon valid justification of why unit has greater capability than during the event. If actual MVAR is greater than 110% of expected (lagging) or less than 110% (leading), capability is increased to match delivered. Capability derates and uprates apply the change in MVAR uniformly across the capability points of the Dcurve that are on the applicable leading or lagging side, including all such points from Pmin to Pmax. If voltage is consistently within voltage schedule, generator is assumed to pass assessment. Generators will only be evaluated when online. No compensation if AVR out of service for the month. | Monthly pass/fail look back analysis of generator voltage control performance. No compensation if AVR out of service for the month. | Same as Package E - PJM-Full Capability | Monthly event assessment, re-rating, and pass/fail look back analysis of generator voltage control performance. If voltage at regulated bus exceeds voltage schedule high/low limits for a 5 minute period (an "event interval"), evaluate actual MVAR compared to expected MVAR. If actual MVAR is less than 90% of expected (lagging) or greater than 90% (leading), reactive flat rate revenues are withheld for that month and capability is reduced to match delivered. If voltage is consistently within voltage schedule, generator is assumed to pass assessment. Generators will only be evaluated when online. No compensation if AVR out of service for the month.
12 | Eligibility for Reactive Services Uplift (Make Whole and Lost Opportunity Cost) | Low | Steam, CCGT, CTs, and Energy Storage Resources | Steam, CCGT, CTs, and Energy Storage Resources | Synchronous and non-synchronous resource need to be eligible for uplift to avoid discriminatory treatment. Uplift for opportunity costs for reneable resource is missing from PJM's Tariff and is a key piece for overall compensation for reactive support. Additionally, mechanism should be created to compensate inverter-based resources for providing reactive power when resource is not providing real power - an ability that synchronous generation does not necessarily have. | Synchronous and non-synchronous resource eligible for Reactive Services uplift. Inverter-based resources committed by PJM dispatch to provide reactive capability when the resource is not providing real power receive Reactive Services uplift using current rules for “condensing mode” as described in Tariff AttK Appendix Section 3.2.3B (i)). Inverter-based condensing mode Reactive Services uplift includes existing cost components (such as real power consumption) | All resource types eligible for Reactive Services Uplift (Make Whole and Lost Opportunity Cost) | Same as Package E - PJM-Full Capability | All resource types eligible for Reactive Services Uplift (Make Whole and Lost Opportunity Cost)
13 | Voltage schedule development process | Medium | Defined by Manual 3 Section 3.11 | Defined by Manual 3 Section 3.11 | No. FERC has not required this. Whether a facility has a voltage, power factor, or no voltage-related schedule should not impact compensation. So long as the resource is at PJM's disposal for reliability needs, that is what should govern. | A Voltage schedule controlling to a target voltage set by PJM with TO input. Generator Voltage Schedule is in Manual 3 section 3.11; AVR is in Generator Voltage Schedule is in Manual 3 section 3.12 | A Voltage schedule controlling to a target voltage set by PJM with TO input. Generator Voltage Schedule is in Manual 3 section 3.11; AVR is in Generator Voltage Schedule is in Manual 3 section 3.12 | Same as Package E - PJM-Full Capability | A Voltage schedule controlling to a target voltage set by PJM with TO input. Generator Voltage Schedule is in Manual 3 section 3.11; AVR is in Generator Voltage Schedule is in Manual 3 section 3.12
14 | Implementation |  | n/a | New reactive power compensation mechanisms should be applied prospectively following acceptance of PJM's FPA section 205 following by FERC. New reactive power compensation mechanism should not impact generating units that have rates on file with FERC, generating units that have a FPA section 205 filing pending at FERC at the time of filing, or projects that have a facilities study agreement signed by the interconnection customer ("excluded resources"). The reactive rates for these excluded resources are not being fixed under this stakeholder proposal but instead will continue to be determined by the Commission. Rate applicable to all units. A transition rate would be established for those units with existing FERC approved rates New reactive power compensation mechanism should be applied prospectively following acceptance of PJM's FPA section 205 following by FERC. | New reactive power compensation mechanism should be applied prospectively following acceptance of PJM's FPA section 205 following by FERC. New reactive power compensation mechanism should not impact generating units that have rates on file with FERC, generating units that have a FPA section 205 filing pending at FERC at the time of filing, or projects that have a facilities study agreement signed by the interconnection customer | To allow implementation time for performance assessment and re-rate process, new reactive power compensation mechanisms should be applied 18-24 months following acceptance of PJM's FPA section 205 filing. It would apply to all new resources and existing resources as they come off of their existing Schedule 2 rates. New reactive power compensation mechanism should not impact generating units that have existing and effective rates on file with FERC. | As soon as practical. Need to address issue in Quad Review. | Same as Package E - PJM-Full Capability, plus: transition mentioned in design component 1 ends after: Option I: 5 years. Option II: after 90% of existing Schedule 2 filed rates have rolled off (e.g., only 29 or fewer remain) | As soon as practicable. Applies to existing and new resources. VRR curve needs to be recalibrated to be consistent. Five year transition to zero adder.

## 3a. Package Details
Reactive Power Compensation Task Force
Reactive Rate Process
PACKAGE / PROPOSAL DETAILS
Instructions: Complete this form as needed, including more detailed / expansive descriptions of package components than the Package Matrix allows.
Package Solutions2
| A | B | C | D | E
1 | <enter detailed description of this component> | <enter detailed description of this component> | <enter detailed description of this component> | <enter detailed description of this component> | <enter detailed description of this component>
2 | <enter detailed description of this component> | <enter detailed description of this component> | <enter detailed description of this component> | <enter detailed description of this component> | <enter detailed description of this component>
3 | <enter detailed description of this component> | <enter detailed description of this component> | <enter detailed description of this component> | <enter detailed description of this component> | <enter detailed description of this component>
4 | <enter detailed description of this component> | <enter detailed description of this component> | <enter detailed description of this component> | <enter detailed description of this component> | <enter detailed description of this component>
5 | <enter detailed description of this component> | <enter detailed description of this component> | <enter detailed description of this component> | <enter detailed description of this component> | <enter detailed description of this component>

## Parking Lot
Reactive Power Compensation Task Force
Reactive Rate Process
PARKING LOT
Instructions: Use this space to document any items not specific to another topic area.
Description

## Revision History
Reactive Power Compensation Task Force
Reactive Rate Process
Revision History
Current Spreadsheet Version:
Instructions: Document all version changes to this matrix for easy identification of changes.
Version | Posting Date | Description of changes
1
2
3