## Key System Upgrades 2021_2022
System Upgrades With Potential Impact to Congestion June 2021 Through May 2022
Description | TO | Projected In-service Date
Reconductor and string open position and sixwire 6.2 miles of the Chemical - Capitol Hill 138 kV circuit | AEP | 2021-02-08
Reconductor Dequine - Meadow Lake 345 kV circuit #1 utilizing dual 954 ACSR 54/7 cardinal conductor | AEP | 2021-03-15
Reconductor the entire Dequine - Meadow Lake 345 kV circuit #2 | AEP | 2021-03-15
Reconductor the Port Union – Mulhauser 138kV line with 954ASCR bringing the summer ratings to A/B/C=300/300/300 MVA. | DEOK | 2021-05-03
Reconductor the Conastone to Graceton 230 kV 2323 & 2324 circuits. Replace 7 disconnect switches at Conastone Substation | BGE | 2021-05-21
Rebuild the Tanner Creek – Miami Fort 345kV line (DEOK portion) | DEOK | 2021-05-24
Upgrade terminal equipment at Yukon to increase rating on Yukon – AA2-161 (Robbins) 138 kV line | APS | 2021-06-01
Upgrade terminal equipment at Yukon to increase rating on Yukon – AA2-161 (Wycoff jct) 138 kV line | APS | 2021-06-01
Add 2nd W. Milton 138/69kV Xfr | DAY | 2021-06-01
Add 2nd W. Milton 345/138 Xfr | DAY | 2021-06-01
Add Bundle conductor on the Graceton-Bagley-Raphael Road 2305 & 2313 230kV circuits | BGE | 2021-06-06
Construct a 230/69kV station at Hillsdale Substation and tie to Paramus and Dumont at 69kV. Install a 69kV ring bus and one (1) 230/69kV transformer at Hillsdale. Construct a 69kV network between Paramus, Dumont, and Hillsdale Substation using existing 69kV circuits. | PSEG | 2021-06-30
Reconductor 0.3 miles of Tiltonsville-Windsor 138 kV into Tiltonsville station with 795 ACSS; string the vacant side of the 3.8 mile middle section using 556 ACSR and operate in a six wire configuration; rebuild the 0.9 mile section crossing from Ohio into the Windsor station in West Virginia, using 795 ACSS. | AEP | 2021-09-29
Reconductor the Maddox Creek - East Lima 345 kV circuit with 2-954 ACSS Cardinal conductor | AEP | 2021-11-18
Expand existing Chadwick station and install a second 138/69 kV transformer at a new 138 kV bus tied into the Bellefonte – Grangston 138 kV circuit. The 69 kV bus will be reconfigured into a ring bus arrangement to tie the new transformer into the existing 69 kV via installation of four 3000A 63 kA 69 kV circuit breakers. | AEP | 2021-11-19
Rebuild the Delaware – Hyatt 138 kV line (~ 4.3 miles) along with replacing conductors at both Hyatt and Delaware substations. | AEP | 2021-11-23
Construct a new Flint Run 500-138 kV substation as a 4-breaker ring bus with expansion plans for double-breaker-double-bus on the 500 kV bus and breaker-and-a-half on the 138 kV bus to provide EHV source to the Marcellus shale load growth area. Projected load growth of additional 160 MVA to current plan of 280 MVA, for a total load of 440 MVA served from Waldo Run substation. Construct additional 3-breaker string at Waldo Run 138 kV bus. Relocate the Sherwood #2 line terminal to the new string. Construct two single circuit Flint Run - Waldo Run 138 kV lines using 795 ACSR (approximately 3 miles). After terminal relocation on new 3-breaker string at Waldo Run, terminate new Flint Run 138 kV lines onto the two open terminals. Loop the Belmont-Harrison 500 kV line into and out of the new Flint Run 500 kV substation (less than 1 mile). Replace primary relaying and carrier sets on Belmont and Harrison 500 kV Remote End Substations. | APS | 2021-12-01
Replace breaker 822 at Beckjord 138kV substation to increase the rating from Pierce to Beckjord 138kV to 603MVA. | DEOK | 2021-12-15
Replace four Yukon 500/138 kV transformers with three transformers with higher rating and reconfigure 500 kV bus | APS | 2021-12-23
Reconductor Northwest – Northwest #2 115kV 110574 substation tie circuit with 2167 ACSR to achieve ratings of 400/462 MVA SN/SE | BGE | 2021-12-31
Re-conductor the entire 230 kV Line No.274 (Pleasant View – Ashburn – Beaumeade) using a higher capacity conductor with an approximate rating of 1572 MVA. | DOM | 2021-12-31
Replace the North Meshoppen #3 230/115kV transformer eliminating the old reactor and installing two breakers to complete a 230kV ring bus at North Meshoppen | PENELEC | 2021-12-31
Construct a 230/69kV station at Maywood. Purchase properties at Maywood to accommodate new construction. Extend Maywood 230kV bus and install one (1) 230kV breaker. Install one (1) 230/69kV transformer at Maywood. Install Maywood 69kV ring bus. Construct a 69kV network between Spring Valley Road, Hasbrouck Heights, and Maywood. | PSEG | 2022-03-31
Reconductor the entire Dequine - Eugene 345 kV circuit #1 | AEP | 2022-04-01
Highlighted upgrades will be modeled as in-service in annual ARR allocation and annual FTR auction
Note: See the Project Status & Cost Allocation page in the Planning section of the PJM web site for a complete list of all planned upgrades including up-to-date projections of in-service dates