## Sheet1
PJM 2016 RTEP Proposal Window #3 Tracking Spreadsheet
Proposal Window: | 2016 RTEP Proposal Window 3
Window Opening Date: | 2016-09-30
Window Closing Date: | 2016-10-31
Current Spreadsheet Version | V2 |  | V2 - 2/9/2017 - Updated to include previously redacted information that was subject to a subsequent window
Project ID | Upgrade/Greenfield | Proposing Entity | Project Cost ($M) | Target Zone(s) | kV Level(s) | Analysis Type | FG# | Major Components/Project Description
2016_3-1A | Upgrade | DEOK/AEP | 7.8 | AEP/DEOK | 345 | Winter Gen Deliv | 41 | This is a joint proposal between Duke Energy, Ohio & Kentucky (DEOK) and AEP. DEOK will replace the DEOK owned portion of the Tanners Creek to Miami Fort 345kV circuit (3.4 miles, double bundle) with two different types of conductor. Aluminum Conductor Composite Reinforced will be used for the Ohio River crossing with the balance of the circuit using Aluminum Conductor, Steel Supported. The rating for the Duke portion of the circuit will increase to 2151MVA. AEP will perform a sag study including a LiDAR survey on the AEP portion of the Tanners Creek to Miami Fort 345kV Circuit (0.36 miles, double bundle). A successful sag study will allow AEP's conductor to be operated at its Maximum Operating Temperature and thus increase the Summer Emergency rating from 1409 MVA to 1956 MVA. If the sag study determines the tie line cannot be operated at its MOT without additional improvements AEP will need to reconductor their portion of the line; which is expected to cost approximately $400,000.
2016_3-2A | Greenfield | Transource | 14.5 | AEP/DEOK | 345 | Winter Gen Deliv | 41 | Construct new greenfield 345kV Switch Station to be called Anson Station. The existing Tanners Creek-East Bend 345kV, East Bend-Terminal 345kV and Miami Fort-Terminal 345kV circuits will all be looped in and out of this station. The station will be comprised of six new 345kV breakers and will be configured in a ring bus.
2016_3-2B | Greenfield | Transource | 8.3 | AEP/ATSI | 138 | Winter Gen Deliv | 1,2,3 | Construct a new single circuit 138 kV line between Bryan Station and Stryker Station.
2016_3-2C | Greenfield | Transource | 44.9 | ATSI | 345/138 | Winter Gen Deliv | 393, 490, 386, 400, 493, 392, 489, 407, 504 | Construct a new double circuit 345 kV line between ATSI's Carlisle Station and a new station, Rocky River West, along the Avon Lake-Juniper 345 kV line. Also, construct a new Sheffield 138kV switching station.
2016_3-2D | Greenfield | Transource | 17.2 | AEP/ATSI | 138 | Winter Gen Deliv | 1,2,3 | Construct approximately 14 miles of new 138 kV line establishing a Lockwood Road – Stryker 138 kV Circuit.
2016_3-2E | Greenfield | Transource | 59.8 | AEP/DEOK | 345 | Winter Gen Deliv | 41 | Tap the Tanners Creek – Losantville 345 kV line by constructing a new 345kV station (York) and build a single circuit 345kV line to a new 345/138kV station (Coyote) next to the existing Wiley station
2016_3-3A | Greenfield | Nextera | 5.95 | AEP | 345 | Winter Gen Deliv | 123 | Add series reactor to Maddox Creek-E Lima 345 kV
2016_3-4A | Upgrade | AEP | 7.3 | AEP | 138 | Winter Gen Deliv; Winter Baseline Thermal | 394, 395, 396, 397, 398; N1-35 | Reconductor and string open position and sixwire 6.2 miles of the Capitol Hill to Chemical 138 kV
2016_3-4B | Upgrade | AEP | 15.5 | AEP | 345 | Winter Gen Deliv | 84 | Reconductor Kyger - Sporn No.2 circuit
2016_3-4C | Upgrade | AEP | 0.3 | AEP | 345 | Winter Gen Deliv | 84 | Six Wire Kyger - Sporn No.1 and No.2 Circuits Together
2016_3-4D | Upgrade | AEP | 18.2 | AEP | 345 | Winter Gen Deliv | 123 | Reconductor the Maddox Creek - East Lima 345 kV circuit with 2-954 ACSS Cardinal conductor.
2016_3-4E | Upgrade | AEP | 0.78 | AEP | 138 | Short Circuit | SC-4, SC-5 | Replace South Canton 138kV breakers L & L2 with 80kA breakers.
2016_3-4F | Upgrade | AEP | 67.7 | AEP | 345 | Winter Gen Deliv | 123 | Rebuild the Maddox Creek - East Lima 345 kV line utilizing BOLD construction.
2016_3-4G | Greenfield | AEP | 69.3 | AEP | 345 | Winter Gen Deliv | 123 | Construct a new 345 kV single circuit line between Maddox Creek and Southwest Lima stations.
2016_3-5A | Greenfield | NTD | 8.5 | ATSI | 138 | Winter Gen Deliv | 1,2,3 | Build a 138 kV line from the existing 138 kV City of Bryan substation to the existing 138 kV Stryker substation
2016_3-5B | Greenfield | NTD | 19 | ATSI | 138 | Winter Gen Deliv | 392, 393, 400, 407, 489, 490, 493, 504, 915 | Build a double circuit 138 kV line from the existing Fieldstone to Johnson 138 kV line and the Carlisle to National Bronze 138 kV line to a new switching station ("Butternut Ridge") interconnecting the existing Astor to Crystal 138 kV line and the Crestwood TP3 to Fowles 138 kV line. Reconfigure the existing Fieldstone to Johnson 138 kV line and the Carlisle to National Bronze 138 kV line to have a Johnson to National Bronze 138 kV line, a Fieldstone to Butternut Ridge 138 kV line and a Carlisle to Butternut Ridge 138 kV line.
2016_3-5C | Greenfield | NTD | 30 | AEP | 138 | Winter Gen Deliv; Winter Baseline Thermal | 394, 395, 396, 397, 398; N1-35 | Build a 138 kV switching station ("Campbells Branch") interconnecting the Amos to Lanham 138 kV line and the Sisson to Lanham 138 kV line. Build a 138 kV line from the new Campbells Branch 138 kV switching station to the existing 138 kV Coco switching station. One of the existing 138 kV lines from Campbells Branch to Lanham will be removed from service.
2016_3-5D | Greenfield | NTD | 34.5 | ATSI | 138 | Winter Gen Deliv | 386, 392, 393, 400, 407, 489, 490, 493, 504, 915 | Construct a double circuit 345 kV line to loop the existing 345 kV Avon Lake to Juniper transmission line into the existing 345 kV Carlisle substation
2016_3-5E | Greenfield | NTD | 19.8 | AEP/OVEC | 345 | Winter Gen Deliv | 84 | Build a 345/138 kV substation ("Poplar Ridge") interconnecting the Kyger Creek to Marquis 345 kV line, the Firebr to Gavin 138 kV line and the Rio Tap to Sporn 138 kV line
2016_3-5F | Greenfield | NTD | 12.4 | ATSI | 138 | Winter Gen Deliv | 386, 915 | Build a 138 kV switching station ("Middle Ridge") interconnecting the Carlisle to Concast 138 kV line and the Beaver to Henrietta 138 kV line. Build a 138 kV switching station ("West Ridge") interconnecting the Carlisle to Concast 138 kV line and the Murray to Gates 138 kV line.
2016_3-5G | Greenfield | NTD | 14.5 | AEP/DEOK | 345 | Winter Gen Deliv | 41 | Build a 345 kV switching station ("Second Creek") interconnecting the Tanners Creek to East Bend 345 kV line and the Miami Fort to Terminal 345 kV line
2016_3-5H | Greenfield | NTD | 6.1 | ATSI | 138 | Winter Gen Deliv | 1,2,3 | Build a 138 kV switching station ("Webb Run") interconnecting the Richland to Lockwood Road 138 kV line and the Richland LJ to Ridgeville 138 kV line
2016_3-6A | Upgrade | First Energy | 0.11 | ATSI | 138 | Winter Gen Deliv | 386, 915 | Beaver-Black River 138kV line replace the GCY51 relay at Beaver substation with SEL. Modify the existing RTU
2016_3-6B | Upgrade | First Energy | 13.4 | ATSI | 138 | Winter Gen Deliv | 400, 493, 407, 504 | Expand / Revise the scope of work for the existing PJM RTEP Project b2559 (ISD 2017) to create a bundled 795 ACSS double circuit tower line. Black River-Lorain Q2 138kV line ugrade. Rebuild/Reconductor approx. 6.5miles single 795ACSS/TW conductor between Black River to Charleston and Charleston to Lorain Q2 substaions (ISD 2017) with bundle 795Kcmil ACSS conductor. Terminal upgrades Upgrade 2000A wavetrap (ISD2017) at Black River, Lorain and Charleston substation to 3000A. The new Black River-Charleston and Charleston-Lorain Q2 138kV circuit winter (MVA) rating will be 679WN/753WE/459WLD (The limiting element is a substation conductor at Charleston)
2016_3-6C | Greenfield | First Energy | 30.3 | ATSI | 138 | Winter Gen Deliv | 400, 493, 407, 504 | Build a new switching sub (Detroit), a new 138kV line and network Lake Ave, Carlisle and Lorain 138kV substation. Detroit 138kV switching substation Construct new 138kV three circuit breakers ring bus switching substation on Carlisle-Lorain Q4 138kV line per FE standard. Lake Ave 138kV substation Build a new 138kV breaker bay with breaker and half configuration, a second breaker bay for future exit, to create a dedicated line exit for Lake Ave-Detroit 138kV line-per FE standard. Lake Ave-Detroit 138kV line Build a new 1.7miles single circuit line with 795Kcmil ACSR conductor from Lake Ave to National Bronze and rebuild/reconductor 0.7miles National Bronze tap with 795Kcmil ACSR conductor to extend the exiting Carlisle-Lorain Q4 138kV line to Lake Ave. Install fiber communication (OPGW) on the line (Lake Ave-National Bronze-Detroit). Install 2000A switches with whip at National Bronze sub new tap. Carlisle-Lorain Q4 138kV line Loop the Carlisle-Lorain Q4 138kV line in/out of the new Detroit switching substation. Rebuild (~2.8miles) Carlisle-Detroit 138kV line with 954Kcmil ACSR conductor and install fiber communication (OPGW). Replace poles and exiting switch on the Carlisle-Detroit 138kV line (~13.1miles) to install fiber communication (OPGW) reusing the existing conductor. Detroit-Lake Ave-Lorain Q4 Loop the Lake Ave-National Bronze-Lorain Q4 138kV line section in/out of the new Detroit switching substation Lorain-Upgrade line relaying at Lorain to Detroit substation, upgrade line drops at Lorain on Q4 line to Admiral and Detroit Substation. Terminal upgrade Carlisle-Upgrade line relaying at Lorain to Detroit sub and substation conductor (line drops) on Admiral Q4 and Detroit 138kV line exit Carlisle-Upgrade line relay at Carlisle to Detroit substation
2016_3-6D | Upgrade | First Energy | 3.2 | ATSI | 138 | Winter Gen Deliv | 393, 490, 392, 489 | Reconductor the Avon - Lorain 138kV line segment (~4.5miles) with 795Kcmil ACSS conductor. Upgrade the line drops at Avon. New ratings WN 521MVA/WE611MVA (Avon - Admiral) and WN 438MVA/WE459MVA (Admiral - Lorain)
2016_3-6E | Upgrade | First Energy | 9.1 | ATSI | 138 | Winter Gen Deliv | 1,2,3 | Eliminate three terminal line at Naomi Junction by constructing a double circuit line towards Wauseon substation. Wauseon substation will need to incorporate a new 138kV line exit by adding a 138kV breaker and relaying.
2016_3-6F | Upgrade | First Energy | 0.01 | ATSI | 345 | Short Circuit | SC-1 | Replace Mansfield Substation Breaker B57 with a breaker having 80 kA interrupt capability. Also replace associated gang-operated disconnect switches, D56 & D58. FirstEnergy is already planning to replace B57 (as well as four other remaining ITE "GA" breakers at Mansfield) and associated disconnect switches based on condition, and Breaker B57 is expected to be in service November of 2017.
2016_3-7A | Greenfield | PSEG | 55.9 | AEP | 345 | Winter Gen Deliv | 123 | Build a new 345kV Line from Maddox Creek to Southwest Lima