## N-1 Thermal
Note | APS and Dominion zones as a whole are quarantined pending Window 3 outcome and are not included in above results
Related to 2022 Window 3, pending window outcome
PJM N-1 Thermal Result (Light Load 2028 Case)
FG # | Fr Bus | Fr Name | To Bus | To Name | CKT | KVs | Areas | Rating | DC Ld(%) | AC Ld(%) | Cont Type | Contingency | Conductor/Transformer Rating (MVA) | PJM Accepting Proposals | Reasons for Exclusions | Comments
2023W1-N1-LLT1 | 231130 | CECIL138 | 231124 | GLASGOW | 1 | 138/138 | 235/235 | 348 | 125.2586 | 125.03 | Line_FB | 'PECO_P4_NOTTI895_SRT-A' | 309/378 (SN/SE) | NO | Below 200 kV Exclusion
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230/230 | 230/230 | 607 | 168.6656 | 167.12 | Line_FB | 'PECO_P4_PEACH235_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230/230 | 230/230 | 607 | 168.3361 | 167.1 | Line_FB | 'PJM_500_BG_P4_5_CNSTN_B_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230/230 | 230/230 | 607 | 168.5997 | 167.05 | Line_FB | 'PJM_500_BG_P4_5_CNSTN_C_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230/230 | 230/230 | 607 | 168.5997 | 167.05 | Single | 'PECO_P1-2_5012_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230/230 | 230/230 | 607 | 154.547 | 152.51 | Line_FB | 'PECO_P4_PEACH245_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230/230 | 230/230 | 607 | 169.7529 | 167.12 | Line_FB | 'PECO_P4_PEACH235_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230/230 | 230/230 | 607 | 169.4069 | 167.1 | Line_FB | 'PJM_500_BG_P4_5_CNSTN_B_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230/230 | 230/230 | 607 | 169.6705 | 167.05 | Line_FB | 'PJM_500_BG_P4_5_CNSTN_C_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230/230 | 230/230 | 607 | 169.6705 | 167.05 | Single | 'PECO_P1-2_5012_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230/230 | 230/230 | 607 | 155.6178 | 152.51 | Line_FB | 'PECO_P4_PEACH245_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230/230 | 230/230 | 628 | 160.6369 | 159.35 | Line_FB | 'PECO_P4_PEACH235_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230/230 | 230/230 | 628 | 160.3025 | 159.33 | Line_FB | 'PJM_500_BG_P4_5_CNSTN_B_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230/230 | 230/230 | 628 | 160.5573 | 159.28 | Line_FB | 'PJM_500_BG_P4_5_CNSTN_C_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230/230 | 230/230 | 628 | 160.5573 | 159.28 | Single | 'PECO_P1-2_5012_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230/230 | 230/230 | 628 | 146.9904 | 145.21 | Line_FB | 'PECO_P4_PEACH245_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 235463 | 01TANEY | 1 | 138/138 | 227/201 | 268 | 160.8955 | 157.07 | Line_FB | 'PJM_500_BG_P4_5_CNSTN_J_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 235463 | 01TANEY | 1 | 138/138 | 227/201 | 268 | 160.8955 | 157.07 | Single | 'PJM_500_BG_P1_5011_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 235463 | 01TANEY | 1 | 138/138 | 227/201 | 268 | 160.8209 | 156.99 | Line_FB | 'PEPCO_P4_PP40_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 235463 | 01TANEY | 1 | 138/138 | 227/201 | 221 | 131.9005 | 130.91 | Single | 'BASE CASE' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 235463 | 01TANEY | 1 | 138/138 | 227/201 | 268 | 135.4851 | 128.76 | Line_FB | 'PJM_500_BG_P4_5_CNSTN_C_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 235463 | 01TANEY | 1 | 138/138 | 227/201 | 268 | 135.4851 | 128.76 | Single | 'PECO_P1-2_5012_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 235463 | 01TANEY | 1 | 138/138 | 227/201 | 268 | 135.4478 | 128.75 | Line_FB | 'PECO_P4_PEACH235_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 235463 | 01TANEY | 1 | 138/138 | 227/201 | 268 | 135.5224 | 128.75 | Line_FB | 'PJM_500_BG_P4_5_CNSTN_B_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 235463 | 01TANEY | 1 | 138/138 | 227/201 | 268 | 123.2836 | 121.46 | Single | 'PEPCO_P1_5055_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 235463 | 01TANEY | 1 | 138/138 | 227/201 | 268 | 123.2836 | 121.46 | Single | 'AP_P1-2_PE-500-406T_SRT-SL' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 235463 | 01TANEY | 1 | 138/138 | 227/201 | 268 | 120.9328 | 119.88 | Tower | 'BG_P7_GRCTN_RAPHEL_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 235463 | 01TANEY | 1 | 138/138 | 227/201 | 268 | 120.8209 | 119.76 | Tower | 'BG_P7_CNSTN_NWEST2_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 235463 | 01TANEY | 1 | 138/138 | 227/201 | 268 | 119.4403 | 118.53 | Tower | 'BG_P7_NEAST_RPHLRD_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 235463 | 01TANEY | 1 | 138/138 | 227/201 | 268 | 119.7015 | 118.29 | Bus | 'AP_P2-2_WP-500-DRT16_SRT-SL' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 235463 | 01TANEY | 1 | 138/138 | 227/201 | 268 | 115.5597 | 114.53 | Tower | 'BG_P7_GRNITE_HIRDG_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 235463 | 01TANEY | 1 | 138/138 | 227/201 | 268 | 115.4104 | 114.41 | Bus | 'AP_P2-2_WP-138-074_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 235463 | 01TANEY | 1 | 138/138 | 227/201 | 268 | 115.3358 | 114.02 | Bus | 'AP_P2-2_WP-500-DRT17_SRT-SL' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 235463 | 01TANEY | 1 | 138/138 | 227/201 | 268 | 114.2537 | 113.28 | Tower | 'BG_P7_NWEST_GRNITE_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 235463 | 01TANEY | 1 | 138/138 | 227/201 | 268 | 114.291 | 113.1 | Bus | 'AP_P2-2_WP-500-DRT15_SRT-SL' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 235463 | 01TANEY | 1 | 138/138 | 227/201 | 268 | 112.3507 | 111.26 | Bus | 'DVP_P2-2: BREMO B1_SRT-L' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230/230 | 230/232 | 628 | 157.9299 | 157.06 | Line_FB | 'PECO_P4_PEACH235_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230/230 | 230/232 | 628 | 157.5955 | 157.04 | Line_FB | 'PJM_500_BG_P4_5_CNSTN_B_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230/230 | 230/232 | 628 | 157.8503 | 156.99 | Line_FB | 'PJM_500_BG_P4_5_CNSTN_C_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230/230 | 230/232 | 628 | 157.8503 | 156.99 | Single | 'PECO_P1-2_5012_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230/230 | 230/232 | 628 | 144.2834 | 142.9 | Line_FB | 'PECO_P4_PEACH245_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 205912 | AD1-020 TAP | 204544 | 27LINCOLN | 1 | 115/115 | 227/227 | 282 | 139.6099 | 139.35 | Line_FB | 'PJM_500_BG_P4_5_CNSTN_J_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 205912 | AD1-020 TAP | 204544 | 27LINCOLN | 1 | 115/115 | 227/227 | 282 | 139.6099 | 139.35 | Single | 'PJM_500_BG_P1_5011_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 205912 | AD1-020 TAP | 204544 | 27LINCOLN | 1 | 115/115 | 227/227 | 282 | 139.5745 | 139.28 | Line_FB | 'PEPCO_P4_PP40_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 205912 | AD1-020 TAP | 204544 | 27LINCOLN | 1 | 115/115 | 227/227 | 282 | 118.156 | 113.86 | Line_FB | 'PJM_500_BG_P4_5_CNSTN_C_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 205912 | AD1-020 TAP | 204544 | 27LINCOLN | 1 | 115/115 | 227/227 | 282 | 118.156 | 113.86 | Single | 'PECO_P1-2_5012_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 205912 | AD1-020 TAP | 204544 | 27LINCOLN | 1 | 115/115 | 227/227 | 282 | 118.156 | 113.85 | Line_FB | 'PECO_P4_PEACH235_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 205912 | AD1-020 TAP | 204544 | 27LINCOLN | 1 | 115/115 | 227/227 | 282 | 118.227 | 113.85 | Line_FB | 'PJM_500_BG_P4_5_CNSTN_B_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 205912 | AD1-020 TAP | 204544 | 27LINCOLN | 1 | 115/115 | 227/227 | 282 | 108.3688 | 106.83 | Single | 'ME_P1-2_ME-115-061_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 205912 | AD1-020 TAP | 204544 | 27LINCOLN | 1 | 115/115 | 227/227 | 282 | 107.8723 | 106.32 | Single | 'AP_P1-2_PE-500-406T_SRT-SL' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 205912 | AD1-020 TAP | 204544 | 27LINCOLN | 1 | 115/115 | 227/227 | 282 | 105.922 | 104.83 | Tower | 'BG_P7_GRCTN_RAPHEL_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 205912 | AD1-020 TAP | 204544 | 27LINCOLN | 1 | 115/115 | 227/227 | 282 | 105.8156 | 104.72 | Tower | 'BG_P7_CNSTN_NWEST2_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 205912 | AD1-020 TAP | 204544 | 27LINCOLN | 1 | 115/115 | 227/227 | 282 | 105.6383 | 104.08 | Bus | 'ME_P2-2_ME-115-0102A-8_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 205912 | AD1-020 TAP | 204544 | 27LINCOLN | 1 | 115/115 | 227/227 | 282 | 104.6454 | 103.61 | Tower | 'BG_P7_NEAST_RPHLRD_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 205912 | AD1-020 TAP | 204544 | 27LINCOLN | 1 | 115/115 | 227/227 | 282 | 104.8582 | 103.45 | Bus | 'AP_P2-2_WP-500-DRT16_SRT-SL' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 205912 | AD1-020 TAP | 204544 | 27LINCOLN | 1 | 115/115 | 227/227 | 282 | 101.3475 | 100 | Tower | 'BG_P7_GRNITE_HIRDG_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223938 | DICKH230 | 223937 | DICK 230 | 1 | 230/230 | 233/233 | 680 | 141.7353 | 138.8 | Line_FB | 'PEPCO_P4_PP19_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223938 | DICKH230 | 223937 | DICK 230 | 1 | 230/230 | 233/233 | 680 | 135.1324 | 132.32 | Single | 'PEPCO_P1_PP2_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223938 | DICKH230 | 223937 | DICK 230 | 1 | 230/230 | 233/233 | 680 | 128.7941 | 125.88 | Line_FB | 'DVP_P4-2: 51482_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223938 | DICKH230 | 223937 | DICK 230 | 1 | 230/230 | 233/233 | 680 | 128.7941 | 125.88 | Single | 'AP_P1-2_PE-500-407T_SRT-SL' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223938 | DICKH230 | 223937 | DICK 230 | 1 | 230/230 | 233/233 | 680 | 128.7941 | 125.88 | Single | 'DVP_P1-2: LN 514_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223938 | DICKH230 | 223937 | DICK 230 | 1 | 230/230 | 233/233 | 680 | 119.6912 | 116.77 | Line_FB | 'AP_P2-3_PE-500-019C_SRT-SL' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230/230 | 229/232 | 797 | 141.33 | 136.75 | Line_FB | 'PJM_500_BG_P4_5_CNSTN_B_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230/230 | 229/232 | 797 | 141.606 | 136.7 | Line_FB | 'PJM_500_BG_P4_5_CNSTN_C_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230/230 | 229/232 | 797 | 141.606 | 136.7 | Single | 'PECO_P1-2_5012_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230/230 | 229/232 | 797 | 141.5809 | 136.69 | Line_FB | 'PECO_P4_PEACH235_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230/230 | 229/232 | 797 | 133.212 | 128.41 | Line_FB | 'PECO_P4_PEACH245_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230/230 | 229/232 | 797 | 112.8231 | 111.34 | Line_FB | 'PJM_500_BG_P4_5_CNSTN_15_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230/230 | 229/232 | 797 | 109.8996 | 108.51 | Tower | 'BG_P7_GRCTN_CNSTN_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 204538 | 27STRABAN | 1 | 115/115 | 227/227 | 313 | 132.8754 | 133.82 | Line_FB | 'PJM_500_BG_P4_5_CNSTN_J_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 204538 | 27STRABAN | 1 | 115/115 | 227/227 | 313 | 132.8754 | 133.82 | Single | 'PJM_500_BG_P1_5011_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 204538 | 27STRABAN | 1 | 115/115 | 227/227 | 313 | 132.8115 | 133.75 | Line_FB | 'PEPCO_P4_PP40_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 204538 | 27STRABAN | 1 | 115/115 | 227/227 | 313 | 111.0863 | 107.89 | Line_FB | 'PJM_500_BG_P4_5_CNSTN_C_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 204538 | 27STRABAN | 1 | 115/115 | 227/227 | 313 | 111.0863 | 107.89 | Line_FB | 'PECO_P4_PEACH235_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 204538 | 27STRABAN | 1 | 115/115 | 227/227 | 313 | 111.0863 | 107.89 | Single | 'PECO_P1-2_5012_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 204538 | 27STRABAN | 1 | 115/115 | 227/227 | 313 | 111.1502 | 107.88 | Line_FB | 'PJM_500_BG_P4_5_CNSTN_B_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 204538 | 27STRABAN | 1 | 115/115 | 227/227 | 313 | 100.6709 | 100.26 | Single | 'AP_P1-2_PE-500-406T_SRT-SL' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 204538 | 27STRABAN | 1 | 115/115 | 227/227 | 313 | 100.6709 | 100.26 | Single | 'PEPCO_P1_5055_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230/230 | 233/345 | 1428 | 136.8487 | 133.78 | Single | 'DVP_P1-2: LN 514_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230/230 | 233/345 | 1428 | 136.8487 | 133.78 | Single | 'AP_P1-2_PE-500-407T_SRT-SL' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230/230 | 233/345 | 1428 | 136.8487 | 133.76 | Line_FB | 'DVP_P4-2: 51482_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230/230 | 233/345 | 1428 | 131.7297 | 128.65 | Line_FB | 'AP_P2-3_PE-500-019C_SRT-SL' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230/230 | 233/345 | 1428 | 105.6583 | 102.96 | Line_FB | 'DVP_P4-2: 560T571_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230/230 | 233/345 | 1428 | 105.4972 | 102.82 | Line_FB | 'DVP_P4-2: H2T560_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230/230 | 233/345 | 1428 | 105.4902 | 102.8 | Line_FB | 'DVP_P4-2: H1T560_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230/230 | 233/345 | 1428 | 105.3501 | 102.65 | Single | 'PEPCO_P1_5070_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223938 | DICKH230 | 223937 | DICK 230 | 2 | 230/230 | 233/233 | 680 | 135.1324 | 132.32 | Single | 'PEPCO_P1_PP1_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223938 | DICKH230 | 223937 | DICK 230 | 2 | 230/230 | 233/233 | 680 | 128.7941 | 125.88 | Line_FB | 'DVP_P4-2: 51482_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223938 | DICKH230 | 223937 | DICK 230 | 2 | 230/230 | 233/233 | 680 | 128.7941 | 125.88 | Single | 'AP_P1-2_PE-500-407T_SRT-SL' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223938 | DICKH230 | 223937 | DICK 230 | 2 | 230/230 | 233/233 | 680 | 128.7941 | 125.88 | Single | 'DVP_P1-2: LN 514_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223938 | DICKH230 | 223937 | DICK 230 | 2 | 230/230 | 233/233 | 680 | 119.6912 | 116.77 | Line_FB | 'AP_P2-3_PE-500-019C_SRT-SL' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 203981 | AD2-062_POI | 235188 | 01GREENE | 1 | 138/138 | 226/201 | 268 | 135.7463 | 131.39 | Line_FB | 'PJM_500_BG_P4_5_CNSTN_J_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 203981 | AD2-062_POI | 235188 | 01GREENE | 1 | 138/138 | 226/201 | 268 | 135.7463 | 131.39 | Single | 'PJM_500_BG_P1_5011_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 203981 | AD2-062_POI | 235188 | 01GREENE | 1 | 138/138 | 226/201 | 268 | 135.6343 | 131.29 | Line_FB | 'PEPCO_P4_PP40_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 203981 | AD2-062_POI | 235188 | 01GREENE | 1 | 138/138 | 226/201 | 268 | 129.8507 | 122.95 | Line_FB | 'PJM_500_BG_P4_5_CNSTN_C_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 203981 | AD2-062_POI | 235188 | 01GREENE | 1 | 138/138 | 226/201 | 268 | 129.8507 | 122.95 | Single | 'PECO_P1-2_5012_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 203981 | AD2-062_POI | 235188 | 01GREENE | 1 | 138/138 | 226/201 | 268 | 129.8507 | 122.94 | Line_FB | 'PECO_P4_PEACH235_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 203981 | AD2-062_POI | 235188 | 01GREENE | 1 | 138/138 | 226/201 | 268 | 129.9254 | 122.94 | Line_FB | 'PJM_500_BG_P4_5_CNSTN_B_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 203981 | AD2-062_POI | 235188 | 01GREENE | 1 | 138/138 | 226/201 | 221 | 117.9638 | 117.27 | Single | 'BASE CASE' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 203981 | AD2-062_POI | 235188 | 01GREENE | 1 | 138/138 | 226/201 | 268 | 109.3284 | 107.65 | Single | 'AP_P1-2_WP-500-DRT17_SRT-SL' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 203981 | AD2-062_POI | 235188 | 01GREENE | 1 | 138/138 | 226/201 | 268 | 109.3284 | 107.65 | Single | 'AP_P1-2_PE-500-001_SRT-SL' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 203981 | AD2-062_POI | 235188 | 01GREENE | 1 | 138/138 | 226/201 | 268 | 108.9179 | 107.28 | Bus | 'AP_P2-2_WP-500-DRT16_SRT-SL' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 203981 | AD2-062_POI | 235188 | 01GREENE | 1 | 138/138 | 226/201 | 268 | 107.3507 | 105.71 | Tower | 'AP_P7-1_PE-138-022T_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 203981 | AD2-062_POI | 235188 | 01GREENE | 1 | 138/138 | 226/201 | 268 | 107.3507 | 105.71 | Bus | 'AP_P2-2_PE-138-073_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 203981 | AD2-062_POI | 235188 | 01GREENE | 1 | 138/138 | 226/201 | 268 | 107.0896 | 105.69 | Bus | 'AP_P2-2_PE-138-003_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 203981 | AD2-062_POI | 235188 | 01GREENE | 1 | 138/138 | 226/201 | 268 | 107.1642 | 105.4 | Bus | 'ME_P2-2_ME-115-003_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 203981 | AD2-062_POI | 235188 | 01GREENE | 1 | 138/138 | 226/201 | 268 | 105.8209 | 104.78 | Tower | 'BG_P7_GRCTN_RAPHEL_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 203981 | AD2-062_POI | 235188 | 01GREENE | 1 | 138/138 | 226/201 | 268 | 105.6716 | 104.67 | Tower | 'BG_P7_CNSTN_NWEST2_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 203981 | AD2-062_POI | 235188 | 01GREENE | 1 | 138/138 | 226/201 | 268 | 104.8134 | 103.9 | Tower | 'BG_P7_NEAST_RPHLRD_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 203981 | AD2-062_POI | 235188 | 01GREENE | 1 | 138/138 | 226/201 | 268 | 103.8806 | 102.6 | Bus | 'AP_P2-2_WP-500-DRT17_SRT-SL' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 203981 | AD2-062_POI | 235188 | 01GREENE | 1 | 138/138 | 226/201 | 268 | 101.9776 | 101.11 | Tower | 'BG_P7_GRNITE_HIRDG_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204538 | 27STRABAN | 204529 | 27GERMANTN | 1 | 115/115 | 227/227 | 313 | 129.4888 | 131.09 | Line_FB | 'PJM_500_BG_P4_5_CNSTN_J_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204538 | 27STRABAN | 204529 | 27GERMANTN | 1 | 115/115 | 227/227 | 313 | 129.4888 | 131.09 | Single | 'PJM_500_BG_P1_5011_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204538 | 27STRABAN | 204529 | 27GERMANTN | 1 | 115/115 | 227/227 | 313 | 129.4249 | 131.02 | Line_FB | 'PEPCO_P4_PP40_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204538 | 27STRABAN | 204529 | 27GERMANTN | 1 | 115/115 | 227/227 | 313 | 107.6997 | 105.19 | Line_FB | 'PJM_500_BG_P4_5_CNSTN_C_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204538 | 27STRABAN | 204529 | 27GERMANTN | 1 | 115/115 | 227/227 | 313 | 107.6997 | 105.19 | Single | 'PECO_P1-2_5012_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204538 | 27STRABAN | 204529 | 27GERMANTN | 1 | 115/115 | 227/227 | 313 | 107.6997 | 105.18 | Line_FB | 'PECO_P4_PEACH235_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204538 | 27STRABAN | 204529 | 27GERMANTN | 1 | 115/115 | 227/227 | 313 | 107.7636 | 105.18 | Line_FB | 'PJM_500_BG_P4_5_CNSTN_B_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204529 | 27GERMANTN | 204530 | 27GERMANTN | 1 | 115/138 | 227/227 | 345 | 124.9855 | 127.74 | Line_FB | 'PJM_500_BG_P4_5_CNSTN_J_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204529 | 27GERMANTN | 204530 | 27GERMANTN | 1 | 115/138 | 227/227 | 345 | 124.9855 | 127.74 | Single | 'PJM_500_BG_P1_5011_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204529 | 27GERMANTN | 204530 | 27GERMANTN | 1 | 115/138 | 227/227 | 345 | 124.9275 | 127.67 | Line_FB | 'PEPCO_P4_PP40_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204529 | 27GERMANTN | 204530 | 27GERMANTN | 1 | 115/138 | 227/227 | 345 | 105.2464 | 104.06 | Line_FB | 'PJM_500_BG_P4_5_CNSTN_C_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204529 | 27GERMANTN | 204530 | 27GERMANTN | 1 | 115/138 | 227/227 | 345 | 105.2464 | 104.06 | Single | 'PECO_P1-2_5012_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204529 | 27GERMANTN | 204530 | 27GERMANTN | 1 | 115/138 | 227/227 | 345 | 105.2174 | 104.05 | Line_FB | 'PECO_P4_PEACH235_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204529 | 27GERMANTN | 204530 | 27GERMANTN | 1 | 115/138 | 227/227 | 345 | 105.2754 | 104.05 | Line_FB | 'PJM_500_BG_P4_5_CNSTN_B_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230/230 | 229/232 | 814 | 131.5848 | 127.07 | Line_FB | 'PJM_500_BG_P4_5_CNSTN_B_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230/230 | 229/232 | 814 | 132.113 | 126.98 | Line_FB | 'PJM_500_BG_P4_5_CNSTN_C_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230/230 | 229/232 | 814 | 132.113 | 126.98 | Single | 'PECO_P1-2_5012_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230/230 | 229/232 | 814 | 132.1007 | 126.96 | Line_FB | 'PECO_P4_PEACH235_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230/230 | 229/232 | 814 | 122.7641 | 117.83 | Line_FB | 'PECO_P4_PEACH245_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500/500 | 225/225 | 3369 | 128.3912 | 123.31 | Single | 'BASE CASE' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 221095 | ROCKRGE2 | 221098 | C.PIPE12 | 1 | 115/115 | 232/232 | 217 | 123.6866 | 123.3 | Tower | 'BG_P7_GRCTN_RAPHEL_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 221095 | ROCKRGE2 | 221098 | C.PIPE12 | 1 | 115/115 | 232/232 | 217 | 117.1429 | 117.47 | Tower | 'BG_P7_NEAST_RPHLRD_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204550 | 27ORRTANNA | 204544 | 27LINCOLN | 1 | 115/115 | 227/227 | 160 | 124.25 | 122.85 | Single | 'ME_P1-2_ME-115-068_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204550 | 27ORRTANNA | 204544 | 27LINCOLN | 1 | 115/115 | 227/227 | 160 | 122.6875 | 121.28 | Line_FB | 'ME_P2-3_ME-115-013B_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204550 | 27ORRTANNA | 204544 | 27LINCOLN | 1 | 115/115 | 227/227 | 160 | 122.5625 | 121.13 | Line_FB | 'ME_P2-3_ME-115-013A_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204550 | 27ORRTANNA | 204544 | 27LINCOLN | 1 | 115/115 | 227/227 | 160 | 120.3125 | 119.69 | Line_FB | 'ME_P2-3_ME-115-035A_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204550 | 27ORRTANNA | 204544 | 27LINCOLN | 1 | 115/115 | 227/227 | 160 | 118.75 | 118.12 | Line_FB | 'ME_P2-3_ME-115-035B_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204550 | 27ORRTANNA | 204544 | 27LINCOLN | 1 | 115/115 | 227/227 | 160 | 102.3125 | 100.33 | Single | 'ME_P1-2_ME-115-067_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208393 | FARO DC TIE | 208395 | FARO FF | 1 | 115/69 | 229/229 | 77 | 121.8182 | 122 | Single | 'BASE CASE' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208393 | FARO DC TIE | 208395 | FARO FF | 2 | 115/69 | 229/229 | 77 | 121.8182 | 121.99 | Single | 'BASE CASE' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 221098 | C.PIPE12 | 221090 | GLENARM2 | 1 | 115/115 | 232/232 | 217 | 119.7235 | 120.23 | Tower | 'BG_P7_GRCTN_RAPHEL_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 221098 | C.PIPE12 | 221090 | GLENARM2 | 1 | 115/115 | 232/232 | 217 | 113.1797 | 114.41 | Tower | 'BG_P7_NEAST_RPHLRD_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204539 | 27HUNTRSTN | 205912 | AD1-020 TAP | 1 | 115/115 | 227/227 | 282 | 120.2482 | 119.7 | Line_FB | 'PJM_500_BG_P4_5_CNSTN_J_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204539 | 27HUNTRSTN | 205912 | AD1-020 TAP | 1 | 115/115 | 227/227 | 282 | 120.2482 | 119.7 | Single | 'PJM_500_BG_P1_5011_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204539 | 27HUNTRSTN | 205912 | AD1-020 TAP | 1 | 115/115 | 227/227 | 282 | 120.1773 | 119.63 | Line_FB | 'PEPCO_P4_PP40_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 221096 | ROCKRGE1 | 221097 | C.PIPE11 | 1 | 115/115 | 232/232 | 217 | 118.8479 | 118.45 | Tower | 'BG_P7_GRCTN_RAPHEL_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 221096 | ROCKRGE1 | 221097 | C.PIPE11 | 1 | 115/115 | 232/232 | 217 | 112.3041 | 112.72 | Tower | 'BG_P7_NEAST_RPHLRD_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 221097 | C.PIPE11 | 221100 | GLENARM1 | 1 | 115/115 | 232/232 | 217 | 118.7097 | 118.44 | Tower | 'BG_P7_GRCTN_RAPHEL_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 221097 | C.PIPE11 | 221100 | GLENARM1 | 1 | 115/115 | 232/232 | 217 | 112.1659 | 112.7 | Tower | 'BG_P7_NEAST_RPHLRD_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200003 | BRIGHTON | 1 | 500/500 | 225/225 | 3099 | 118.6899 | 117.86 | Tower | 'BG_P7_CNSTN_NWEST2_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200003 | BRIGHTON | 1 | 500/500 | 225/225 | 3099 | 117.3153 | 116.53 | Tower | 'BG_P7_GRCTN_RAPHEL_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200003 | BRIGHTON | 1 | 500/500 | 225/225 | 3099 | 115.6825 | 114.93 | Tower | 'BG_P7_NEAST_RPHLRD_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200003 | BRIGHTON | 1 | 500/500 | 225/225 | 3099 | 113.1817 | 112.01 | Line_FB | 'PJM_500_BG_P4_5_CNSTN_13_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200003 | BRIGHTON | 1 | 500/500 | 225/225 | 3099 | 113.1333 | 111.96 | Line_FB | 'PJM_500_BG_P4_5_CNSTN_6_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200003 | BRIGHTON | 1 | 500/500 | 225/225 | 3099 | 111.494 | 110.51 | Line_FB | 'AP_P2-3_WP-500-465_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200003 | BRIGHTON | 1 | 500/500 | 225/225 | 3099 | 111.494 | 110.51 | Line_FB | 'AP_P2-3_WP-500-DRT20_SRT-SL' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200003 | BRIGHTON | 1 | 500/500 | 225/225 | 3099 | 111.494 | 110.51 | Bus | 'AP_P2-2_WP-500-DRT16_SRT-SL' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200003 | BRIGHTON | 1 | 500/500 | 225/225 | 3099 | 111.494 | 110.51 | Single | 'AP_P1-2_WP-500-DRT21_SRT-SL' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200003 | BRIGHTON | 1 | 500/500 | 225/225 | 3099 | 111.494 | 110.51 | Single | 'AP_P1-2_WP-500-005A_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200003 | BRIGHTON | 1 | 500/500 | 225/225 | 3099 | 111.5553 | 110.38 | Tower | 'BG_P7_GRNITE_HIRDG_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200003 | BRIGHTON | 1 | 500/500 | 225/225 | 3099 | 110.2581 | 109.06 | Tower | 'BG_P7_NWEST_GRNITE_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200003 | BRIGHTON | 1 | 500/500 | 225/225 | 3099 | 109.9968 | 108.97 | Line_FB | 'AP_P2-3_PE-500-015_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200003 | BRIGHTON | 1 | 500/500 | 225/225 | 3099 | 109.6644 | 108.67 | Single | 'AP_P1-2_WP-500-DRT17_SRT-SL' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200003 | BRIGHTON | 1 | 500/500 | 225/225 | 3099 | 109.6644 | 108.67 | Single | 'AP_P1-2_PE-500-001_SRT-SL' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200003 | BRIGHTON | 1 | 500/500 | 225/225 | 3099 | 109.1029 | 107.81 | Bus | 'PJM_500_BG_P2_CNSTN_230-S_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200003 | BRIGHTON | 1 | 500/500 | 225/225 | 3099 | 109.0868 | 107.79 | Bus | 'PJM_500_BG_P2_CNSTN_230-N_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200003 | BRIGHTON | 1 | 500/500 | 225/225 | 3099 | 108.3801 | 107.1 | Bus | 'AP_P2-2_WP-500-DRT17_SRT-SL' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200003 | BRIGHTON | 1 | 500/500 | 225/225 | 3099 | 107.5992 | 106.35 | Bus | 'AP_P2-2_WP-500-DRT15_SRT-SL' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 221090 | GLENARM2 | 221089 | WINDYED1 | 1 | 115/115 | 232/232 | 216 | 116.8981 | 117.4 | Tower | 'BG_P7_GRCTN_RAPHEL_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 221090 | GLENARM2 | 221089 | WINDYED1 | 1 | 115/115 | 232/232 | 216 | 110.2778 | 111.56 | Tower | 'BG_P7_NEAST_RPHLRD_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200004 | CNASTONE | 1 | 500/500 | 225/225 | 3949 | 121.2636 | 116.19 | Line_FB | 'PECO_P4_PEACH035_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200004 | CNASTONE | 1 | 500/500 | 225/225 | 3949 | 119.0251 | 114.59 | Line_FB | 'PJM_500_BG_P4_5_CNSTN_M_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200004 | CNASTONE | 1 | 500/500 | 225/225 | 3949 | 119.0251 | 114.59 | Single | 'PJM_500_BG_P1_5013_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200004 | CNASTONE | 1 | 500/500 | 225/225 | 3949 | 118.6781 | 113.97 | Tower | 'PECO_P7-1_220-0607_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200004 | CNASTONE | 1 | 500/500 | 225/225 | 3949 | 118.6781 | 113.97 | Line_FB | 'PECO_P4_PEACH675_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200004 | CNASTONE | 1 | 500/500 | 225/225 | 3949 | 116.2978 | 111.53 | Single | 'PECO_P1-2_220-07_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200004 | CNASTONE | 1 | 500/500 | 225/225 | 3949 | 116.1433 | 111.49 | Line_FB | 'PECO_P4_NOTTI55_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200004 | CNASTONE | 1 | 500/500 | 225/225 | 3949 | 116.0268 | 111.38 | Bus | 'PECO_P2-2_NOTT230B_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200004 | CNASTONE | 1 | 500/500 | 225/225 | 3949 | 116.0547 | 111.36 | Line_FB | 'PECO_P4_NOTTI785_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200004 | CNASTONE | 1 | 500/500 | 225/225 | 3949 | 115.7635 | 111.19 | Single | 'PECO_P1-2_220-08_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200004 | CNASTONE | 1 | 500/500 | 225/225 | 3949 | 115.4799 | 110.99 | Single | 'PECO_P1-2_220-93_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200004 | CNASTONE | 1 | 500/500 | 225/225 | 3949 | 114.7911 | 110.4 | Tower | 'PL_05_P71_000906_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200004 | CNASTONE | 1 | 500/500 | 225/225 | 3949 | 113.8516 | 109.59 | Bus | 'AP_P2-2_WP-500-DRT16_SRT-SL' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200004 | CNASTONE | 1 | 500/500 | 225/225 | 3949 | 113.2287 | 108.71 | Bus | 'AEP_P2-2_#6188_05HANG R 765_1_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200004 | CNASTONE | 1 | 500/500 | 225/225 | 3949 | 112.9577 | 108.55 | Bus | 'PL_05_P22_000674_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200004 | CNASTONE | 1 | 500/500 | 225/225 | 3949 | 112.9096 | 108.44 | Tower | 'PL_04_P71_001014_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200004 | CNASTONE | 1 | 500/500 | 225/225 | 3949 | 112.5196 | 108.1 | Bus | 'DVP_P2-2: BREMO B1_SRT-L' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200004 | CNASTONE | 1 | 500/500 | 225/225 | 3949 | 111.7929 | 107.38 | Tower | 'PL_04_P71_000904_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200004 | CNASTONE | 1 | 500/500 | 225/225 | 3949 | 111.7802 | 107.37 | Tower | 'PL_04_P71_001822_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200532 | 26ROXBURY | 203981 | AD2-062_POI | 1 | 138/138 | 226/226 | 268 | 119.0299 | 114.44 | Line_FB | 'PJM_500_BG_P4_5_CNSTN_J_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200532 | 26ROXBURY | 203981 | AD2-062_POI | 1 | 138/138 | 226/226 | 268 | 119.0299 | 114.44 | Single | 'PJM_500_BG_P1_5011_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200532 | 26ROXBURY | 203981 | AD2-062_POI | 1 | 138/138 | 226/226 | 268 | 118.9179 | 114.35 | Line_FB | 'PEPCO_P4_PP40_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200532 | 26ROXBURY | 203981 | AD2-062_POI | 1 | 138/138 | 226/226 | 268 | 113.1343 | 106 | Line_FB | 'PECO_P4_PEACH235_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200532 | 26ROXBURY | 203981 | AD2-062_POI | 1 | 138/138 | 226/226 | 268 | 113.1343 | 106 | Line_FB | 'PJM_500_BG_P4_5_CNSTN_C_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200532 | 26ROXBURY | 203981 | AD2-062_POI | 1 | 138/138 | 226/226 | 268 | 113.1343 | 106 | Single | 'PECO_P1-2_5012_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200532 | 26ROXBURY | 203981 | AD2-062_POI | 1 | 138/138 | 226/226 | 268 | 113.209 | 105.99 | Line_FB | 'PJM_500_BG_P4_5_CNSTN_B_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 205912 | AD1-020 TAP | 1 | 115/115 | 227/227 | 232 | 116.25 | 114.35 | Single | 'BASE CASE' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 221092 | FIVE.FOR | 221096 | ROCKRGE1 | 1 | 115/115 | 232/232 | 254 | 113.8189 | 114.21 | Tower | 'BG_P7_GRCTN_RAPHEL_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 221092 | FIVE.FOR | 221096 | ROCKRGE1 | 1 | 115/115 | 232/232 | 254 | 108.2283 | 109.08 | Tower | 'BG_P7_NEAST_RPHLRD_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208395 | FARO FF | 208393 | FARO DC TIE | 1 | 69/115 | 229/229 | 114 | 117.3684 | 114.18 | Tower | 'PL_05_P71_000906_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208395 | FARO FF | 208393 | FARO DC TIE | 1 | 69/115 | 229/229 | 114 | 109.386 | 105.43 | Line_FB | 'PJM_500_BG_P4_5_CNSTN_B_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208395 | FARO FF | 208393 | FARO DC TIE | 1 | 69/115 | 229/229 | 114 | 109.386 | 105.42 | Line_FB | 'PECO_P4_PEACH235_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208395 | FARO FF | 208393 | FARO DC TIE | 1 | 69/115 | 229/229 | 114 | 109.386 | 105.42 | Line_FB | 'PJM_500_BG_P4_5_CNSTN_C_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208395 | FARO FF | 208393 | FARO DC TIE | 1 | 69/115 | 229/229 | 114 | 109.386 | 105.42 | Single | 'PECO_P1-2_5012_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208395 | FARO FF | 208393 | FARO DC TIE | 1 | 69/115 | 229/229 | 114 | 105 | 101.65 | Line_FB | 'PECO_P4_PEACH245_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208395 | FARO FF | 208393 | FARO DC TIE | 1 | 69/115 | 229/229 | 114 | 102.5439 | 100.92 | Tower | 'BG_P7_GRCTN_RAPHEL_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230/230 | 229/229 | 814 | 116.4496 | 113.44 | Line_FB | 'PJM_500_BG_P4_5_CNSTN_B_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230/230 | 229/229 | 814 | 116.7076 | 113.39 | Line_FB | 'PJM_500_BG_P4_5_CNSTN_C_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230/230 | 229/229 | 814 | 116.7076 | 113.39 | Single | 'PECO_P1-2_5012_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230/230 | 229/229 | 814 | 116.6953 | 113.37 | Line_FB | 'PECO_P4_PEACH235_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230/230 | 229/229 | 814 | 108.2801 | 104.96 | Line_FB | 'PECO_P4_PEACH245_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200065 | PCHBTM2S | 200064 | PCHBTM1S | Z1 | 500/500 | 225/225 | 3198 | 118.7179 | 113.31 | Line_FB | 'PECO_P4_PEACH255_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500/500 | 225/225 | 2812 | 114.1821 | 112.69 | Single | 'BASE CASE' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208396 | FARO | 208395 | FARO FF | 1 | 69/69 | 229/229 | 240 | 111.5417 | 112.52 | Tower | 'PL_05_P71_000906_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208396 | FARO | 208395 | FARO FF | 1 | 69/69 | 229/229 | 240 | 103.9167 | 103.66 | Line_FB | 'PJM_500_BG_P4_5_CNSTN_B_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208396 | FARO | 208395 | FARO FF | 1 | 69/69 | 229/229 | 240 | 103.9167 | 103.66 | Line_FB | 'PJM_500_BG_P4_5_CNSTN_C_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208396 | FARO | 208395 | FARO FF | 1 | 69/69 | 229/229 | 240 | 103.9167 | 103.66 | Line_FB | 'PECO_P4_PEACH235_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208396 | FARO | 208395 | FARO FF | 1 | 69/69 | 229/229 | 240 | 103.9167 | 103.66 | Single | 'PECO_P1-2_5012_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 221092 | FIVE.FOR | 221095 | ROCKRGE2 | 1 | 115/115 | 232/232 | 254 | 110.748 | 110.64 | Tower | 'BG_P7_GRCTN_RAPHEL_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 221092 | FIVE.FOR | 221095 | ROCKRGE2 | 1 | 115/115 | 232/232 | 254 | 105.1575 | 105.64 | Tower | 'BG_P7_NEAST_RPHLRD_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 221058 | DOLFD T1 | 221055 | HARRIS1A | 1 | 115/115 | 232/232 | 189 | 109.3651 | 109.16 | Tower | 'BG_P7_NWEST_GRNITE_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208395 | FARO FF | 208393 | FARO DC TIE | 2 | 69/115 | 229/229 | 120 | 111.5 | 108.47 | Tower | 'PL_05_P71_000906_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208395 | FARO FF | 208393 | FARO DC TIE | 2 | 69/115 | 229/229 | 120 | 103.9167 | 100.15 | Line_FB | 'PJM_500_BG_P4_5_CNSTN_B_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208395 | FARO FF | 208393 | FARO DC TIE | 2 | 69/115 | 229/229 | 120 | 103.9167 | 100.15 | Line_FB | 'PECO_P4_PEACH235_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208395 | FARO FF | 208393 | FARO DC TIE | 2 | 69/115 | 229/229 | 120 | 103.9167 | 100.15 | Line_FB | 'PJM_500_BG_P4_5_CNSTN_C_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208395 | FARO FF | 208393 | FARO DC TIE | 2 | 69/115 | 229/229 | 120 | 103.9167 | 100.15 | Single | 'PECO_P1-2_5012_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208921 | SAHA 693 | 208551 | MANO | 1 | 69/69 | 229/229 | 99 | 105.4545 | 107.75 | Line_FB | 'PL_04_P42_000556_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208921 | SAHA 693 | 208551 | MANO | 1 | 69/69 | 229/229 | 99 | 105.4545 | 107.65 | Line_FB | 'PL_04_P42_000559_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208921 | SAHA 693 | 208551 | MANO | 1 | 69/69 | 229/229 | 99 | 105.4545 | 107.63 | Line_FB | 'PL_04_P42_000993_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208921 | SAHA 693 | 208551 | MANO | 1 | 69/69 | 229/229 | 99 | 105.4545 | 107.63 | Bus | 'PL_05_P22_000675_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208921 | SAHA 693 | 208551 | MANO | 1 | 69/69 | 229/229 | 99 | 105.8586 | 107.63 | Single | 'PL_04_P12_000256_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208921 | SAHA 693 | 208551 | MANO | 1 | 69/69 | 229/229 | 99 | 105.8586 | 107.61 | Tower | 'PL_05_P71_000906_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208394 | PPL-BGE TIE | 221092 | FIVE.FOR | 1 | 115/115 | 229/232 | 247 | 106.6397 | 107.35 | Tower | 'PL_05_P71_000906_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204538 | 27STRABAN | 204544 | 27LINCOLN | 1 | 115/115 | 227/227 | 257 | 107.4319 | 106.95 | Single | 'BASE CASE' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 221057 | DOLFD T0 | 221056 | HARRIS0A | 1 | 115/115 | 232/232 | 189 | 104.9735 | 105.12 | Tower | 'BG_P7_NWEST_GRNITE_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204514 | 27TMI | 204502 | 27JACKSON | 1 | 230/230 | 227/227 | 659 | 104.9165 | 104.95 | Line_FB | 'PJM_500_BG_P4_5_CNSTN_C_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204514 | 27TMI | 204502 | 27JACKSON | 1 | 230/230 | 227/227 | 659 | 104.9165 | 104.95 | Single | 'PECO_P1-2_5012_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204514 | 27TMI | 204502 | 27JACKSON | 1 | 230/230 | 227/227 | 659 | 104.9772 | 104.94 | Line_FB | 'PJM_500_BG_P4_5_CNSTN_B_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204514 | 27TMI | 204502 | 27JACKSON | 1 | 230/230 | 227/227 | 659 | 104.9014 | 104.93 | Line_FB | 'PECO_P4_PEACH235_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204529 | 27GERMANTN | 204538 | 27STRABAN | 1 | 115/115 | 227/227 | 257 | 103.3074 | 103.66 | Single | 'BASE CASE' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 204529 | 27GERMANTN | 1 | 138/115 | 227/227 | 287 | 101.5679 | 103.03 | Single | 'BASE CASE' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 221100 | GLENARM1 | 221088 | WINDYED2 | 1 | 115/115 | 232/232 | 254 | 101.0236 | 101.11 | Tower | 'BG_P7_GRCTN_RAPHEL_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220972 | GRANITE1 | 1 | 230/230 | 232/232 | 811 | 104.0074 | 101.1 | Line_FB | 'PEPCO_P4_PP40_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220972 | GRANITE1 | 1 | 230/230 | 232/232 | 811 | 103.7608 | 100.81 | Line_FB | 'PJM_500_BG_P4_5_CNSTN_J_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220972 | GRANITE1 | 1 | 230/230 | 232/232 | 811 | 103.7608 | 100.81 | Single | 'PJM_500_BG_P1_5011_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230/230 | 227/229 | 801 | 102.834 | 100.8 | Line_FB | 'PJM_500_BG_P4_5_CNSTN_B_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230/230 | 227/229 | 801 | 103.2709 | 100.72 | Line_FB | 'PJM_500_BG_P4_5_CNSTN_C_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230/230 | 227/229 | 801 | 103.2709 | 100.72 | Single | 'PECO_P1-2_5012_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230/230 | 227/229 | 801 | 103.2459 | 100.7 | Line_FB | 'PECO_P4_PEACH235_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220972 | GRANITE1 | 220953 | HOWARD12 | 1 | 230/230 | 232/232 | 772 | 103.2383 | 100.35 | Line_FB | 'PEPCO_P4_PP40_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 235463 | 01TANEY | 1 | 138/138 | 227/201 | 268 | 119.2537 | 117.7 | Single | 'AP_P2-1_WP-138-AD2062-A_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 235463 | 01TANEY | 1 | 138/138 | 227/201 | 268 | 117.4254 | 116.23 | Single | 'PN_P2-1_PN-115-117_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 235463 | 01TANEY | 1 | 138/138 | 227/201 | 268 | 115.1493 | 114.18 | Single | 'AP_P2-1_WP-138-0213-A_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 235463 | 01TANEY | 1 | 138/138 | 227/201 | 268 | 113.3582 | 112.26 | Single | 'PL_04_P21_000390_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 203981 | AD2-062_POI | 235188 | 01GREENE | 1 | 138/138 | 226/201 | 268 | 107.6119 | 105.79 | Single | 'AP_P2-1_PE-138-083_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 203981 | AD2-062_POI | 235188 | 01GREENE | 1 | 138/138 | 226/201 | 268 | 107.0896 | 105.69 | Single | 'AP_P2-1_PE-138-028_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 203981 | AD2-062_POI | 235188 | 01GREENE | 1 | 138/138 | 226/201 | 268 | 107.0522 | 105.25 | Single | 'ME_P2-1_ME-115-0002_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 203981 | AD2-062_POI | 235188 | 01GREENE | 1 | 138/138 | 226/201 | 268 | 106.6791 | 104.97 | Single | 'ME_P2-1_ME-115-0001_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200004 | CNASTONE | 1 | 500/500 | 225/225 | 3949 | 115.9686 | 111.37 | Single | 'PECO_P2-1_NOTT85_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200004 | CNASTONE | 1 | 500/500 | 225/225 | 3949 | 115.6673 | 111.16 | Single | 'PECO_P2-1_COOP220-08_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200004 | CNASTONE | 1 | 500/500 | 225/225 | 3949 | 115.5254 | 111.04 | Single | 'PECO_P2-1_COOP125_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200004 | CNASTONE | 1 | 500/500 | 225/225 | 3949 | 115.4242 | 110.94 | Single | 'BG_P21:TO:214084 COOPER 230 220964 GRACETON 230 1 _SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200003 | BRIGHTON | 1 | 500/500 | 225/225 | 3099 | 108.6705 | 107.46 | Single | 'BG_P21:TO:220962 NWEST311 230 220963 CONASTON 230 1 _SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200003 | BRIGHTON | 1 | 500/500 | 225/225 | 3099 | 108.6705 | 107.46 | Single | 'BG_P21:FROM:220962 NWEST311 230 220963 CONASTON 230 1 _SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200003 | BRIGHTON | 1 | 500/500 | 225/225 | 3099 | 108.6254 | 107.42 | Single | 'BG_P21:TO:220961 NWEST326 230 220963 CONASTON 230 1 _SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200003 | BRIGHTON | 1 | 500/500 | 225/225 | 3099 | 108.6254 | 107.42 | Single | 'BG_P21:FROM:220961 NWEST326 230 220963 CONASTON 230 1 _SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 205912 | AD1-020 TAP | 204544 | 27LINCOLN | 1 | 115/115 | 227/227 | 282 | 104.4681 | 102.87 | Single | 'AP_P2-1_WP-138-AD2062-A_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 205912 | AD1-020 TAP | 204544 | 27LINCOLN | 1 | 115/115 | 227/227 | 282 | 102.9433 | 101.4 | Single | 'PN_P2-1_PN-115-117_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204550 | 27ORRTANNA | 204544 | 27LINCOLN | 1 | 115/115 | 227/227 | 160 | 102.3125 | 100.33 | Single | 'ME_P2-1_ME-115-0003_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208395 | FARO FF | 208393 | FARO DC TIE | 1 | 69/115 | 229/229 | 114 | 101.6667 | 100.24 | Single | 'PL_04_P21_000390_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208395 | FARO FF | 208393 | FARO DC TIE | 1 | 69/115 | 229/229 | 114 | 101.6667 | 100.24 | Single | 'BG_P21:FROM:208071 PPL-BGE TIE 230 220964 GRACETON 230 1 _SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome

## N-1 Volt Mag
Note | APS and Dominion zones as a whole are quarantined pending Window 3 outcome and are not included in above results
Related to 2022 Window 3, pending window outcome
PJM N-1 Voltage Magnitude Result (Light Load 2028 Case)
FG# | Bus # | Name | KV | Area | ContVolt | BaseVolt | Upper/Lower Limit | Cont Type | Contingency | PJM Accepting Proposals | Reasons for Exclusions | Comments
2023W1-N1-LLVM1 | 217063 | WALDWICK | 345 | 231 | 1.0502 | 1.045 | 1.05 | Single | PS_P1-4_WALDWICK_345_SRT-A | YES
2023W1-N1-LLVM2 | 217063 | WALDWICK | 345 | 231 | 1.0508 | 1.045 | 1.05 | Line_FB | PS_P2-3_WALD_1-9_SRT-A | YES
2023W1-N1-LLVM3 | 217063 | WALDWICK | 345 | 231 | 1.0511 | 1.045 | 1.05 | Line_FB | PS_P2-3_WALD_1-9_LT_SRT-A | YES
2023W1-N1-LLVM4 | 217063 | WALDWICK | 345 | 231 | 1.0515 | 1.045 | 1.05 | Line_FB | PS_P2-3_WALD3_2-4_SRT-A | YES
2023W1-N1-LLVM5 | 217063 | WALDWICK | 345 | 231 | 1.0516 | 1.045 | 1.05 | Line_FB | PS_P2-3_WALD3_2-6_SRT-A | YES
2023W1-N1-LLVM6 | 217063 | WALDWICK | 345 | 231 | 1.0516 | 1.045 | 1.05 | Line_FB | PS_P2-3_WALD3_2-7_SRT-A | YES
2023W1-N1-LLVM7 | 217314 | HINCHAV_2 | 230 | 231 | 1.0515 | 1.0259 | 1.05 | Bus | PS_P2-2_HNCH_3_SRT-A | YES
2023W1-N1-LLVM8 | 217314 | HINCHAV_2 | 230 | 231 | 1.0516 | 1.0259 | 1.05 | Line_FB | PS_P2-3_HNCH_3-4_SRT-A | YES
2023W1-N1-LLVM9 | 217313 | HINCHAV_1 | 230 | 231 | 1.0515 | 1.026 | 1.05 | Bus | PS_P2-2_HNCH_3_SRT-A | YES
2023W1-N1-LLVM10 | 217313 | HINCHAV_1 | 230 | 231 | 1.0516 | 1.026 | 1.05 | Line_FB | PS_P2-3_HNCH_3-4_SRT-A | YES
2023W1-N1-LLVM11 | 217313 | HINCHAV_1 | 230 | 231 | 1.0519 | 1.026 | 1.05 | Bus | PS_P2-2_HNCH_2_SRT-A | YES
2023W1-N1-LLVM12 | 217313 | HINCHAV_1 | 230 | 231 | 1.0521 | 1.026 | 1.05 | Line_FB | PS_P2-3_HNCH_2-3_SRT-A | YES
2023W1-N1-LLVM13 | 217313 | HINCHAV_1 | 230 | 231 | 1.0526 | 1.026 | 1.05 | Line_FB | PS_P2-3_HNCH_2-3_LT_SRT-A | YES
2023W1-N1-LLVM14 | 217311 | HAWTHORN_2 | 230 | 231 | 1.0514 | 1.0291 | 1.05 | Bus | PS_P2-2_HNCH_3_SRT-A | YES
2023W1-N1-LLVM15 | 217311 | HAWTHORN_2 | 230 | 231 | 1.0515 | 1.0291 | 1.05 | Line_FB | PS_P2-3_HNCH_3-4_SRT-A | YES
2023W1-N1-LLVM16 | 217311 | HAWTHORN_2 | 230 | 231 | 1.0517 | 1.0291 | 1.05 | Bus | PS_P2-2_HNCH_2_SRT-A | YES
2023W1-N1-LLVM17 | 217311 | HAWTHORN_2 | 230 | 231 | 1.052 | 1.0291 | 1.05 | Line_FB | PS_P2-3_HNCH_2-3_SRT-A | YES
2023W1-N1-LLVM18 | 217311 | HAWTHORN_2 | 230 | 231 | 1.0523 | 1.0291 | 1.05 | Line_FB | PS_P2-3_HNCH_2-3_LT_SRT-A | YES
2023W1-N1-LLVM19 | 217311 | HAWTHORN_2 | 230 | 231 | 1.0541 | 1.0291 | 1.05 | Line_FB | PS_P2-3_HAWT_1-N_LT_SRT-A | YES
2023W1-N1-LLVM20 | 217311 | HAWTHORN_2 | 230 | 231 | 1.0541 | 1.0291 | 1.05 | Line_FB | PS_P2-3_HAWT_1-N_SRT-A | YES
2023W1-N1-LLVM21 | 217064 | WALDWICK_E | 230 | 231 | 1.0514 | 1.0307 | 1.05 | Bus | PS_P2-2_HNCH_3_SRT-A | YES
2023W1-N1-LLVM22 | 217064 | WALDWICK_E | 230 | 231 | 1.0516 | 1.0307 | 1.05 | Line_FB | PS_P2-3_HNCH_3-4_SRT-A | YES
2023W1-N1-LLVM23 | 217064 | WALDWICK_E | 230 | 231 | 1.0517 | 1.0307 | 1.05 | Bus | PS_P2-2_HNCH_2_SRT-A | YES
2023W1-N1-LLVM24 | 217064 | WALDWICK_E | 230 | 231 | 1.052 | 1.0307 | 1.05 | Line_FB | PS_P2-3_HNCH_2-3_SRT-A | YES
2023W1-N1-LLVM25 | 217064 | WALDWICK_E | 230 | 231 | 1.0523 | 1.0307 | 1.05 | Line_FB | PS_P2-3_HNCH_2-3_LT_SRT-A | YES
2023W1-N1-LLVM26 | 217064 | WALDWICK_E | 230 | 231 | 1.0539 | 1.0307 | 1.05 | Line_FB | PS_P2-3_HAWT_1-N_LT_SRT-A | YES
2023W1-N1-LLVM27 | 217064 | WALDWICK_E | 230 | 231 | 1.0539 | 1.0307 | 1.05 | Line_FB | PS_P2-3_HAWT_1-N_SRT-A | YES
2023W1-N1-LLVM28 | 217053 | HAWTHORN_1 | 230 | 231 | 1.0514 | 1.029 | 1.05 | Bus | PS_P2-2_HNCH_3_SRT-A | YES
2023W1-N1-LLVM29 | 217053 | HAWTHORN_1 | 230 | 231 | 1.0515 | 1.029 | 1.05 | Line_FB | PS_P2-3_HNCH_3-4_SRT-A | YES
2023W1-N1-LLVM30 | 217053 | HAWTHORN_1 | 230 | 231 | 1.0517 | 1.029 | 1.05 | Bus | PS_P2-2_HNCH_2_SRT-A | YES
2023W1-N1-LLVM31 | 217053 | HAWTHORN_1 | 230 | 231 | 1.052 | 1.029 | 1.05 | Line_FB | PS_P2-3_HNCH_2-3_SRT-A | YES
2023W1-N1-LLVM32 | 217053 | HAWTHORN_1 | 230 | 231 | 1.0523 | 1.029 | 1.05 | Line_FB | PS_P2-3_HNCH_2-3_LT_SRT-A | YES
2023W1-N1-LLVM33 | 217046 | FAIRLAWN | 230 | 231 | 1.0554 | 1.0412 | 1.05 | Line_FB | PS_P2-3_FLWN_3-4_SRT-A | YES
2023W1-N1-LLVM34 | 217046 | FAIRLAWN | 230 | 231 | 1.0555 | 1.0412 | 1.05 | Bus | PS_P2-2_FLWN_4_SRT-A | YES
2023W1-N1-LLVM35 | 217046 | FAIRLAWN | 230 | 231 | 1.0555 | 1.0412 | 1.05 | Line_FB | PS_P2-3_FLWN_4-5_SRT-A | YES
2023W1-N1-LLVM36 | 216971 | WALDWICK_O | 230 | 231 | 1.0546 | 1.0406 | 1.05 | Line_FB | PS_P2-3_FLWN_3-4_SRT-A | YES
2023W1-N1-LLVM37 | 216971 | WALDWICK_O | 230 | 231 | 1.0547 | 1.0406 | 1.05 | Bus | PS_P2-2_FLWN_4_SRT-A | YES
2023W1-N1-LLVM38 | 216971 | WALDWICK_O | 230 | 231 | 1.0547 | 1.0406 | 1.05 | Line_FB | PS_P2-3_FLWN_4-5_SRT-A | YES
2023W1-N1-LLVM39 | 200921 | 26FRANKLNB | 115 | 226 | 1.0545 | 1.0371 | 1.05 | Line_FB | PN_P2-3_PN-115-0426-1_SRT-A | NO | Below 200 kV Exclusion
2023W1-N1-LLVM40 | 200598 | 26WAYNE | 115 | 226 | 1.0556 | 1.0408 | 1.05 | Line_FB | PN_P2-3_PN-115-0426A-B_SRT-A | NO | Below 200 kV Exclusion
2023W1-N1-LLVM41 | 200598 | 26WAYNE | 115 | 226 | 1.0616 | 1.0408 | 1.05 | Line_FB | PN_P2-3_PN-115-0426-1_SRT-A | NO | Below 200 kV Exclusion
2023W1-N1-LLVM42 | 200011 | KEYSTONE | 500 | 225 | 1.1134 | 1.0504 | 1.1 | Single | PL_10_P21_000976_SRT-A | YES
2023W1-N1-LLVM43 | 220954 | HOWARD32 | 230 | 232 | 1.0945 | 1.0221 | 1.05 | Single | BG_P21:FROM:220954 HOWARD32 230 220974 PUMPHRY 230 1 _SRT-A | YES
N/A | 220978 | SNOW.R18 | 230 | 232 | 0.915 | 1.0182 | 0.92 | Single | BG_P21:TO:220941 H.RDGE16 230 220943 SNOW18TP 230 1 _SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 220978 | SNOW.R18 | 230 | 232 | 0.9165 | 1.0182 | 0.92 | Single | BG_P21:FROM:220941 H.RDGE16 230 220943 SNOW18TP 230 1 _SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 220952 | W.LAKE8A | 230 | 232 | 0.915 | 1.0181 | 0.92 | Single | BG_P21:TO:220941 H.RDGE16 230 220943 SNOW18TP 230 1 _SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 220952 | W.LAKE8A | 230 | 232 | 0.9165 | 1.0181 | 0.92 | Single | BG_P21:FROM:220941 H.RDGE16 230 220943 SNOW18TP 230 1 _SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 220948 | COLUMB18 | 230 | 232 | 0.915 | 1.0182 | 0.92 | Single | BG_P21:TO:220941 H.RDGE16 230 220943 SNOW18TP 230 1 _SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 220948 | COLUMB18 | 230 | 232 | 0.9165 | 1.0182 | 0.92 | Single | BG_P21:FROM:220941 H.RDGE16 230 220943 SNOW18TP 230 1 _SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 220943 | SNOW18TP | 230 | 232 | 0.915 | 1.0182 | 0.92 | Single | BG_P21:TO:220941 H.RDGE16 230 220943 SNOW18TP 230 1 _SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 220943 | SNOW18TP | 230 | 232 | 0.9165 | 1.0182 | 0.92 | Single | BG_P21:FROM:220941 H.RDGE16 230 220943 SNOW18TP 230 1 _SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 220941 | H.RDGE16 | 230 | 232 | 0.9165 | 1.0183 | 0.92 | Single | BG_P21:FROM:220941 H.RDGE16 230 220943 SNOW18TP 230 1 _SRT-A | NO | Related to 2022 Window 3, pending window outcome

## N-1 Volt Drop
Note | APS and Dominion zones as a whole are quarantined pending Window 3 outcome and are not included in above results
Related to 2022 Window 3, pending window outcome
PJM N-1 Voltage Drop Result (Light Load 2028)
FG# | Bus # | Name | KV | Area | ContVolt | BaseVolt | Vdrop(%) | Cont Type | Contingency | PJM Accepting Proposals | Reasons for Exclusions | Comment
N/A | 220978 | SNOW.R18 | 230 | 232 | 0.696 | 1.0182 | 32.22 | Single | BG_P21:TO:220941 H.RDGE16 230 220943 SNOW18TP 230 1 _SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 220978 | SNOW.R18 | 230 | 232 | 0.7009 | 1.0182 | 31.73 | Single | BG_P21:FROM:220941 H.RDGE16 230 220943 SNOW18TP 230 1 _SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 220952 | W.LAKE8A | 230 | 232 | 0.6952 | 1.0181 | 32.29 | Single | BG_P21:TO:220941 H.RDGE16 230 220943 SNOW18TP 230 1 _SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 220952 | W.LAKE8A | 230 | 232 | 0.7001 | 1.0181 | 31.8 | Single | BG_P21:FROM:220941 H.RDGE16 230 220943 SNOW18TP 230 1 _SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 220948 | COLUMB18 | 230 | 232 | 0.6956 | 1.0182 | 32.26 | Single | BG_P21:TO:220941 H.RDGE16 230 220943 SNOW18TP 230 1 _SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 220948 | COLUMB18 | 230 | 232 | 0.7006 | 1.0182 | 31.76 | Single | BG_P21:FROM:220941 H.RDGE16 230 220943 SNOW18TP 230 1 _SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 220943 | SNOW18TP | 230 | 232 | 0.6957 | 1.0182 | 32.25 | Single | BG_P21:TO:220941 H.RDGE16 230 220943 SNOW18TP 230 1 _SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 220943 | SNOW18TP | 230 | 232 | 0.7006 | 1.0182 | 31.76 | Single | BG_P21:FROM:220941 H.RDGE16 230 220943 SNOW18TP 230 1 _SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 220941 | H.RDGE16 | 230 | 232 | 0.7007 | 1.0183 | 31.76 | Single | BG_P21:FROM:220941 H.RDGE16 230 220943 SNOW18TP 230 1 _SRT-A | NO | Related to 2022 Window 3, pending window outcome