## GDDetail_2023W1-GD-LL550
****** PJM Generator Deliverability Detailed Report ****** PJM [TARA Ver 2302.2.0.3 PJMGD 2022 Reform RC2 64-bit - Mon Jul 17 16:29:40 2023]
FG Index [All Queue] | 550 | FG ID | 400 | Monitored Facility:235283 01WYCOFJ 138 254064 15CHESWK 138 1 / Contingency:AP_P2-3_WP-138-AA2-161-B5_SRT-A[Breaker]
Rating | Final DC %LD | Final AC %LD | DC¦AC | Base FG Flow | 50/50 MW | Regular Adder MW | SW Harmer | SW Helper | LTF Impact | DC Final Flow | AC Final Flow | Transfer Cap | 50¦50 Dispatch | Regular Adder Dispatch | SW Harmer Dispatch | SW Helper Dispatch | Ext Regular Adder Dispatch | Ext SW Harmer Dispatch
248 | 101.26 | 100.67 | AC | 246.72 | 0 | 0 | 0 | 0 | 4.39 | 251.11 | 249.7 | 860.3 | 0 | 0 | 0 | 0 | 0 | 0
Bus#¦LTF# | Gen¦LTF Name | Gen ID | Volt | Area | Category | PJT Status | Gen Class | EEFORD | Com.Prob | CIR | MWP Cap | MWP Energy | MWN Cap | MWN Energy | PGen | PNew | Ramping Factor | Flag | Dfax | Impact | FRMP | Cum Avai | Group ID | Study Unit? | MFO Limited?
22 | BlueGrass |  |  |  | LTF | [5 empty] | 173.3 | 0 | 0 | 0 |  | 173.3 | 1 | CLTF | 0.00435 | 0.7542 | 0.7542
18 | TRIMBLE |  |  |  | LTF | [5 empty] | 55.7 | 0 | 0 | 0 |  | 55.7 | 1 | CLTF | 0.00436 | 0.2425 | 0.2425
11 | Gibson |  |  |  | LTF | [5 empty] | 54.6 | 0 | 0 | 0 |  | 54.6 | 1 | CLTF | 0.00435 | 0.2375 | 0.2375
25 | MDU |  |  |  | LTF | [5 empty] | 0 | 0 | 0 | 0 |  | 0 | 1 | CLTF | 0.00436 | 0 | 0
17 | PRAIRIE |  |  |  | LTF | [5 empty] | 131.3 | 0 | 0 | 0 |  | 131.3 | 1 | CLTF | 0.00428 | 0.5621 | 0.5621
19 | CALDErWOOD |  |  |  | LTF | [5 empty] | 49.7 | 0 | 0 | 0 |  | 49.7 | 1 | CLTF | 0.00391 | 0.1942 | 0.1942
21 | CHEOAH |  |  |  | LTF | [5 empty] | 50 | 0 | 0 | 0 |  | 50 | 1 | CLTF | 0.0039 | 0.195 | 0.195
15 | CATAWBA |  |  |  | LTF | [5 empty] | 35 | 0 | 0 | 0 |  | 35 | 1 | CLTF | 0.00356 | 0.1245 | 0.1245
13 | HAMLET |  |  |  | LTF | [5 empty] | 57.8 | 0 | 0 | 0 |  | 57.8 | 1 | CLTF | 0.0034 | 0.1962 | 0.1962
1 | CBM North |  |  |  | LTF | [5 empty] | 93 | 0 | 0 | 0 |  | 93 | 1 | LTF/CBM | 0.00014 | 0.0135 | 0.0135
27 | MISO WIND |  |  |  | LTF | [5 empty] | 16783.3 | 0 | 0 | 0 |  | 16783.3 | 1 | CLTF | 0.00011 | 1.8722 | 1.8722
238105 | AF2-314 GEN | S1 | 25 | 201 | Gen |  | 86 | 0 | 1 |  | 10 | 0 | 0 | 0 | 5.4 |  |  |  | 0.01655 |  |  |  | AF2-314
254310 | AG1-086 GEN | B1 | 138 | 215 | Gen | New | 88 | 0 | 1 |  | 5.63 | 0 | 0 | 0 | 0 |  |  |  | -0.01297 |  |  |  | AG1-086 |  | MFO
254310 | AG1-086 GEN | S1 | 138 | 215 | Gen |  | 86 | 0 | 1 |  | 17.5 | 0 | 0 | 0 | 9.45 |  |  |  | -0.01297 |  |  |  | AG1-086 |  | MFO
254303 | AC2-168C | 1 | 23 | 215 | Gen |  | 83 | 0 | 1 |  | 20 | 0 | 0 | 0 | 10.6 |  |  |  | -0.01272 |  |  |  | AC2-168
254304 | AE2-114 C | 1 | 138 | 215 | Gen |  | 86 | 0 | 1 |  | 17.1 | 0 | 0 | 0 | 9.23 |  |  |  | -0.01216 |  |  |  | AE2-114
254305 | AE2-115 C | 1 | 138 | 215 | Gen |  | 86 | 0 | 1 |  | 17.1 | 0 | 0 | 0 | 9.23 |  |  |  | -0.01216 |  |  |  | AE2-115
235055 | AG1-141 C | S1 | 138 | 201 | Gen | New | 86 | 0 | 1 |  | 5 | 0 | 0 | 0 | 0 |  |  |  | 0.00992 |  |  |  | AG1-141
237043 | AE2-125 C | 1 | 25 | 201 | Gen |  | 86 | 0 | 1 |  | 13.8 | 0 | 0 | 0 | 7.45 |  |  |  | 0.00974 |  |  |  | AE2-125
237052 | AF1-210 C | 1 | 25 | 201 | Gen | New | 86 | 0 | 1 |  | 16 | 0 | 0 | 0 | 0 |  |  |  | 0.00659 |  |  |  | AF1-210
270322 | AE2-290 GEN | S1 | 0.6 | 205 | Gen |  | 86 | 0 | 1 |  | 101.32 | 0 | 0 | 0 | 54.71 |  |  |  | -0.00598 |  |  |  | AE2-290
241916 | 02Z1-035 | W1 | 69 | 202 | Gen |  | 77 | 0 | 1 |  | 18 | 0 | 0 | 0 | 5.76 |  |  |  | -0.00595 |  |  |  | Z1-035
270387 | AD2-014 GEN | S1 | 0.6 | 205 | Gen |  | 83 | 0 | 1 |  | 54 | 0 | 0 | 0 | 28.62 |  |  |  | -0.00586 |  |  |  | AD2-014
241801 | AE1-079 GEN | B1 | 69 | 202 | Gen | New | 88 | 0 | 1 |  | 4 | 0 | -4 | 0 | 0 |  |  |  | -0.00585 |  |  |  | AE1-079 |  | MFO
241985 | AE1-237 GEN | B1 | 69 | 202 | Gen | New | 88 | 0 | 1 |  | 4 | 0 | -4 | 0 | 0 |  |  |  | -0.00584 |  |  |  | AE1-237 |  | MFO
241982 | AE2-343 S C | B1 | 69 | 202 | Gen | New | 88 | 0 | 1 |  | 4 | 0 | -4 | 0 | 0 |  |  |  | -0.00584 |  |  |  | AE2-343 |  | MFO
241801 | AE1-079 GEN | S1 | 69 | 202 | Gen |  | 86 | 0 | 1 |  | 19.9 | 0 | 0 | 0 | 10.75 |  |  |  | -0.00585 |  |  |  | AE1-079 |  | MFO
241985 | AE1-237 GEN | S1 | 69 | 202 | Gen |  | 86 | 0 | 1 |  | 19.9 | 0 | 0 | 0 | 10.75 |  |  |  | -0.00584 |  |  |  | AE1-237 |  | MFO
241982 | AE2-343 S C | S1 | 69 | 202 | Gen |  | 86 | 0 | 1 |  | 17.9 | 0 | 0 | 0 | 9.67 |  |  |  | -0.00584 |  |  |  | AE2-343 |  | MFO
241967 | AE2-285 GEN | S1 | 69 | 202 | Gen |  | 86 | 0 | 1 |  | 50 | 0 | 0 | 0 | 27 |  |  |  | -0.00584 |  |  |  | AE2-285
238124 | AG1-029 G1 | S1 | 25 | 201 | Gen |  | 83 | 0 | 1 |  | 15 | 0 | 0 | 0 | 7.95 |  |  |  | -0.00561 |  |  |  | AG1-029
238125 | AG1-029 G2 | S2 | 25 | 201 | Gen |  | 83 | 0 | 1 |  | 15 | 0 | 0 | 0 | 7.95 |  |  |  | -0.00561 |  |  |  | AG1-029
241885 | AC2-103 C1 | W1 | 0.69 | 202 | Gen |  | 77 | 0 | 1 |  | 148.83 | 0 | 0 | 0 | 47.63 |  |  |  | -0.00547 |  |  |  | AC2-103
241886 | AC2-103 C2 | W2 | 0.69 | 202 | Gen |  | 77 | 0 | 1 |  | 148.83 | 0 | 0 | 0 | 47.63 |  |  |  | -0.00547 |  |  |  | AC2-103
236523 | 01WDPWR_K20 | W1 | 25 | 201 | Gen |  | 77 | 0 | 1 |  | 15 | 0 | 0 | 0 | 4.8 |  |  |  | 0.00527 |  |  |  | K20
235058 | AG1-386 C | B1 | 25 | 201 | Gen | New | 88 | 0 | 1 |  | 8.57 | 0 | -8.57 | 0 | 0 |  |  |  | -0.00511 |  |  |  | AG1-386 |  | MFO
235058 | AG1-386 C | S1 | 25 | 201 | Gen |  | 83 | 0 | 1 |  | 20 | 0 | 0 | 0 | 10.8 |  |  |  | -0.00511 |  |  |  | AG1-386 |  | MFO
240997 | 02BG10 | S1 | 69 | 202 | Gen | New | 83 | 0 | 1 |  | 20 | 0 | 0 | 0 | 0 |  |  |  | -0.00509 |  |  |  | G10
241996 | AE2-282_GEN | S1 | 0.64 | 202 | Gen |  | 86 | 0 | 1 |  | 68.67 | 0 | 0 | 0 | 37.08 |  |  |  | -0.00501 |  |  |  | AE2-282
270361 | AD1-070 GEN | S1 | 0.69 | 205 | Gen |  | 83 | 0 | 1 |  | 205 | 0 | 0 | 0 | 108.65 |  |  |  | -0.00499 |  |  |  | AD1-070
247522 | U1-059 C | W1 | 69 | 205 | Gen |  | 77 | 0 | 1 |  | 53.1 | 0 | 0 | 0 | 16.99 |  |  |  | -0.00488 |  |  |  | U1-059
247555 | W1-056 C | W1 | 69 | 205 | Gen |  | 77 | 0 | 1 |  | 66.7 | 0 | 0 | 0 | 21.34 |  |  |  | -0.00488 |  |  |  | W1-056
241960 | AC2-195 C | S1 | 0.42 | 202 | Gen |  | 86 | 0 | 1 |  | 99.96 | 0 | 0 | 0 | 53.98 |  |  |  | -0.00486 |  |  |  | AC2-195
270377 | AD1-106 GEN | S1 | 0.55 | 205 | Gen |  | 83 | 0 | 1 |  | 61.75 | 0 | 0 | 0 | 32.73 |  |  |  | -0.00486 |  |  |  | AD1-106
270297 | AD1-101 C | S1 | 0.39 | 205 | Gen |  | 83 | 0 | 1 |  | 50 | 0 | 0 | 0 | 26.5 |  |  |  | -0.00471 |  |  |  | AD1-101
247549 | V3-028 C | S1 | 345 | 205 | Gen |  | 86 | 0 | 1 |  | 150 | 0 | 0 | 0 | 81 |  |  |  | -0.00468 |  |  |  | V3-028
270317 | AD1-130_GEN | S1 | 0.63 | 205 | Gen |  | 86 | 0 | 1 |  | 170 | 0 | 0 | 0 | 91.8 |  |  |  | -0.00468 |  |  |  | V3-028
246936 | 05BLCK-1 C | W1 | 0.69 | 205 | Gen |  | 77 | 0 | 1 |  | 116 | 0 | 0 | 0 | 37.12 |  |  |  | -0.00466 |  |  |  | R60
246937 | 05BLCK-2 C | W1 | 0.69 | 205 | Gen |  | 77 | 0 | 1 |  | 116 | 0 | 0 | 0 | 37.12 |  |  |  | -0.00466 |  |  |  | R60
246938 | 05BLCK-3 C | W1 | 0.69 | 205 | Gen |  | 77 | 0 | 1 |  | 118 | 0 | 0 | 0 | 37.76 |  |  |  | -0.00466 |  |  |  | R60
270223 | U2-072_GEN1 | W1 | 0.69 | 205 | Gen |  | 77 | 0 | 1 |  | 50 | 0 | 0 | 0 | 16 |  |  |  | -0.00467 |  |  |  | U2-072
270224 | U2-072_GEN2 | W2 | 0.69 | 205 | Gen |  | 77 | 0 | 1 |  | 50 | 0 | 0 | 0 | 16 |  |  |  | -0.00467 |  |  |  | U2-072
270227 | U2-072_GEN3 | W3 | 0.69 | 205 | Gen |  | 77 | 0 | 1 |  | 50 | 0 | 0 | 0 | 16 |  |  |  | -0.00467 |  |  |  | U2-072
270228 | U2-072_GEN4 | W4 | 0.69 | 205 | Gen |  | 77 | 0 | 1 |  | 50 | 0 | 0 | 0 | 16 |  |  |  | -0.00467 |  |  |  | U2-072
270231 | U2-072_GEN5 | W5 | 0.69 | 205 | Gen |  | 77 | 0 | 1 |  | 50 | 0 | 0 | 0 | 16 |  |  |  | -0.00467 |  |  |  | U2-072
270391 | AE2-306 GEN | S1 | 0.63 | 205 | Gen |  | 86 | 0 | 1 |  | 30 | 0 | 0 | 0 | 16.2 |  |  |  | -0.00467 |  |  |  | AE2-306
270404 | AC1-167 GEN | S1 | 0.36 | 205 | Gen |  | 86 | 0 | 1 |  | 49.98 | 0 | 0 | 0 | 26.99 |  |  |  | -0.00467 |  |  |  | AC1-167
247965 | Y1-063 E | E | 34.5 | 205 | Gen | New | 88 | 0 | 1 |  | 4 | 0 | -4 | 0 | 0 |  |  |  | -0.00465 |  |  |  | Y1-063
270258 | AD1-119 C | S1 | 0.39 | 205 | Gen |  | 83 | 0 | 1 |  | 49.96 | 0 | 0 | 0 | 26.48 |  |  |  | -0.00465 |  |  |  | AD1-119
247607 | V1-011 GEN | W1 | 0.69 | 205 | Gen |  | 77 | 0 | 1 |  | 100 | 0 | 0 | 0 | 32 |  |  |  | -0.00465 |  |  |  | V1-011
253369 | AE2-303_GEN | S1 | 0.64 | 209 | Gen |  | 86 | 0 | 1 |  | 49.9 | 0 | 0 | 0 | 26.95 |  |  |  | -0.00462 |  |  |  | AE2-303
270284 | AF1-227 C1 | S1 | 0.6 | 205 | Gen |  | 86 | 0 | 1 |  | 112.25 | 0 | 0 | 0 | 60.61 |  |  |  | -0.00462 |  |  |  | AF1-227
270286 | AF1-227 C2 | S1 | 0.6 | 205 | Gen |  | 86 | 0 | 1 |  | 152.55 | 0 | 0 | 0 | 82.38 |  |  |  | -0.00462 |  |  |  | AF1-227
270287 | AF1-227 C3 | S1 | 0.63 | 205 | Gen |  | 86 | 0 | 1 |  | 106.38 | 0 | 0 | 0 | 57.45 |  |  |  | -0.00462 |  |  |  | AF1-227
246953 | 05TIMB G C | W1 | 0.69 | 205 | Gen |  | 77 | 0 | 1 |  | 149.4 | 0 | 0 | 0 | 47.81 |  |  |  | -0.00462 |  |  |  | R49
241973 | AD2-163_C1 | 1 | 0.6 | 202 | Gen |  | 86 | 0 | 1 |  | 90 | 0 | 0 | 0 | 48.6 |  |  |  | -0.0046 |  |  |  | AD2-163
241974 | AD2-163_C2 | 1 | 0.6 | 202 | Gen |  | 86 | 0 | 1 |  | 90 | 0 | 0 | 0 | 48.6 |  |  |  | -0.0046 |  |  |  | AD2-163
247521 | TR3_G114 | W1 | 0.69 | 205 | Gen |  | 77 | 0 | 1 |  | 99.6 | 0 | 0 | 0 | 31.87 |  |  |  | -0.0046
270191 | TR4_S_V150 | W1 | 0.72 | 205 | Gen |  | 77 | 0 | 1 |  | 75.9 | 0 | 0 | 0 | 24.29 |  |  |  | -0.0046
270246 | TR3_N_V150 | W3 | 0.72 | 205 | Gen |  | 77 | 0 | 1 |  | 25.2 | 0 | 0 | 0 | 8.06 |  |  |  | -0.0046 |  |  |  | V150
270247 | TR3_N_V136 | W2 | 0.65 | 205 | Gen |  | 77 | 0 | 1 |  | 25.2 | 0 | 0 | 0 | 8.06 |  |  |  | -0.0046 |  |  |  | V136
241955 | AC1-078 C | 1 | 0.6 | 202 | Gen |  | 83 | 0 | 1 |  | 196 | 0 | 0 | 0 | 103.88 |  |  |  | -0.0046 |  |  |  | AC1-078
241992 | AE2-217_GEN | S1 | 0.63 | 202 | Gen | New | 86 | 0 | 1 |  | 181.2 | 0 | 0 | 0 | 0 |  |  |  | -0.00459 |  |  |  | AE2-217
253378 | AE2-206_GEN | S1 | 0.39 | 209 | Gen |  | 83 | 0 | 1 |  | 146.3 | 0 | 0 | 0 | 77.54 |  |  |  | -0.0046 |  |  |  | AE2-206
253383 | AE2-342_GEN | S1 | 0.6 | 209 | Gen |  | 86 | 0 | 1 |  | 40 | 0 | 0 | 0 | 21.6 |  |  |  | -0.0046 |  |  |  | AE2-342
270349 | AD2-093_GEN | S1 | 0.63 | 205 | Gen |  | 86 | 0 | 1 |  | 226.5 | 0 | 0 | 0 | 122.31 |  |  |  | -0.00459 |  |  |  | AD2-093
244412 | 05WTRV SLR | S1 | 138 | 205 | Gen |  | 83 | 0 | 1 |  | 4.6 | 0 | 0 | 0 | 2.44 |  |  |  | -0.00457
247643 | Z2-116 C | 1C | 138 | 205 | Gen |  | 83 | 0 | 1 |  | 2.6 | 0 | 0 | 0 | 1.38 |  |  |  | -0.00455 |  |  |  | Z2-116
253388 | AE2-218 GEN | S1 | 0.63 | 209 | Gen | New | 86 | 0 | 1 |  | 178.18 | 0 | 0 | 0 | 0 |  |  |  | -0.00455 |  |  |  | AE2-218
270216 | AD2-079_C O | S1 | 0.63 | 205 | Gen |  | 86 | 0 | 1 |  | 20 | 0 | 0 | 0 | 10.8 |  |  |  | -0.00455 |  |  |  | AD2-079
241972 | AD1-140 GEN | 1 | 0.57 | 202 | Gen | New | 83 | 0 | 1 |  | 175 | 0 | 0 | 0 | 0 |  |  |  | -0.00454 |  |  |  | AD1-140
253325 | AC1-069 C | 1 | 0.36 | 209 | Gen |  | 86 | 0 | 1 |  | 49.9 | 0 | 0 | 0 | 26.95 |  |  |  | -0.00453 |  |  |  | AC1-069
253333 | AC1-068 C | 1 | 0.36 | 209 | Gen |  | 86 | 0 | 1 |  | 49.9 | 0 | 0 | 0 | 26.95 |  |  |  | -0.00453 |  |  |  | AC1-068
253338 | AC1-165 C | 1 | 0.36 | 209 | Gen |  | 86 | 0 | 1 |  | 49.9 | 0 | 0 | 0 | 26.95 |  |  |  | -0.00453 |  |  |  | AC1-165
253343 | AC1-166 C | 1 | 0.36 | 209 | Gen |  | 86 | 0 | 1 |  | 49.9 | 0 | 0 | 0 | 26.95 |  |  |  | -0.00453 |  |  |  | AC1-166
253420 | AE2-319_GEN | S1 | 0.6 | 209 | Gen |  | 86 | 0 | 1 |  | 100 | 0 | 0 | 0 | 54 |  |  |  | -0.00453 |  |  |  | AE2-319
244415 | 05OLIV SLR | S1 | 138 | 205 | Gen |  | 83 | 0 | 1 |  | 5 | 0 | 0 | 0 | 2.65 |  |  |  | -0.00453
270269 | AC2-059 C | S1 | 0.63 | 205 | Gen |  | 86 | 0 | 1 |  | 146.2 | 0 | 0 | 0 | 78.95 |  |  |  | -0.00452 |  |  |  | AC2-059
270273 | AD2-016 C | S1 | 0.63 | 205 | Gen |  | 86 | 0 | 1 |  | 274 | 0 | 0 | 0 | 147.96 |  |  |  | -0.00452 |  |  |  | AD2-016
270291 | AC1-194 C | S1 | 0.55 | 205 | Gen |  | 83 | 0 | 1 |  | 125 | 0 | 0 | 0 | 66.25 |  |  |  | -0.00451 |  |  |  | AC1-194
270201 | AC2-176 GEN | W1 | 0.69 | 205 | Gen |  | 77 | 0 | 1 |  | 130 | 0 | 0 | 0 | 41.6 |  |  |  | -0.0045 |  |  |  | AC2-176
270263 | AC1-001 C | 1 | 0.38 | 205 | Gen |  | 86 | 0 | 1 |  | 49.9 | 0 | 0 | 0 | 26.95 |  |  |  | -0.0045 |  |  |  | AC1-001
247536 | 05BLUFF P WF | W1 | 138 | 205 | Gen |  | 77 | 0 | 1 |  | 120 | 0 | 0 | 0 | 38.4 |  |  |  | -0.0045 |  |  |  | S71
253303 | V4-073 C | S1 | 69 | 209 | Gen |  | 83 | 0 | 1 |  | 2.05 | 0 | 0 | 0 | 1.09 |  |  |  | -0.0045 |  |  |  | V4-073
253349 | AC2-067 C | S1 | 0.38 | 209 | Gen |  | 83 | 0 | 1 |  | 57.5 | 0 | 0 | 0 | 30.48 |  |  |  | -0.0045 |  |  |  | AC2-067
253400 | AC2-068 GEN | S1 | 0.38 | 209 | Gen |  | 83 | 0 | 1 |  | 20.9 | 0 | 0 | 0 | 11.08 |  |  |  | -0.0045 |  |  |  | AC2-068
253415 | AE1-040 GEN | S1 | 0.6 | 209 | Gen |  | 86 | 0 | 1 |  | 48.64 | 0 | 0 | 0 | 26.27 |  |  |  | -0.00449 |  |  |  | AE1-040
270340 | AC2-060 GEN | S1 | 0.55 | 205 | Gen |  | 86 | 0 | 1 |  | 123.65 | 0 | 0 | 0 | 66.77 |  |  |  | -0.00449 |  |  |  | AC2-060
247642 | Z2-115 C | S1 | 12 | 205 | Gen |  | 83 | 0 | 1 |  | 2.5 | 0 | 0 | 0 | 1.33 |  |  |  | -0.00447 |  |  |  | Z2-115
270383 | AD1-128 GEN | S1 | 0.39 | 205 | Gen |  | 83 | 0 | 1 |  | 150 | 0 | 0 | 0 | 79.5 |  |  |  | -0.00447 |  |  |  | AD1-128
276164 | X3-005 C | 1 | 13.2 | 222 | Gen |  | 86 | 0 | 1 |  | 9 | 0 | 0 | 0 | 4.86 |  |  |  | -0.00447 |  |  |  | X3-005
276169 | Z1-107 E | BA | 34.5 | 222 | Gen | New | 88 | 0 | 1 |  | 20 | 0 | -20 | 0 | 0 |  |  |  | -0.00446 |  |  |  | Z1-107
276675 | AE2-062 E | 1 | 138 | 222 | Gen | New | 88 | 0 | 1 |  | 1 | 0 | -1 | 0 | 0 |  |  |  | -0.00446 |  |  |  | AE2-062
243795 | 05HDWTR1G C | W1 | 0.69 | 205 | Gen |  | 77 | 0 | 1 |  | 200 | 0 | 0 | 0 | 64 |  |  |  | -0.00447 |  |  |  | U2-090
246909 | 05MDL-1G C | W1 | 0.6 | 205 | Gen |  | 77 | 0 | 1 |  | 202 | 0 | 0 | 0 | 64.64 |  |  |  | -0.00447 |  |  |  | S06
246910 | 05MDL-2G C | W1 | 12 | 205 | Gen |  | 77 | 0 | 1 |  | 100 | 0 | 0 | 0 | 32 |  |  |  | -0.00447 |  |  |  | T126
246976 | 05MDL-3G C | W1 | 0.69 | 205 | Gen |  | 77 | 0 | 1 |  | 102 | 0 | 0 | 0 | 32.64 |  |  |  | -0.00447 |  |  |  | T126
246979 | 05MDL-4G C | W1 | 0.6 | 205 | Gen |  | 77 | 0 | 1 |  | 100 | 0 | 0 | 0 | 32 |  |  |  | -0.00447 |  |  |  | T127
246991 | 05WLD G1 C | W1 | 0.69 | 205 | Gen |  | 77 | 0 | 1 |  | 97.6 | 0 | 0 | 0 | 31.23 |  |  |  | -0.00447 |  |  |  | U3-002
247255 | 05WLD G2 C | W1 | 0.69 | 205 | Gen |  | 77 | 0 | 1 |  | 200 | 0 | 0 | 0 | 64 |  |  |  | -0.00447 |  |  |  | U3-002
247556 | 05MDL-5G | W1 | 0.69 | 205 | Gen |  | 77 | 0 | 1 |  | 100 | 0 | 0 | 0 | 32 |  |  |  | -0.00447 |  |  |  | T127
253394 | AE2-221_GEN | S1 | 0.63 | 209 | Gen |  | 86 | 0 | 1 |  | 150 | 0 | 0 | 0 | 81 |  |  |  | -0.00447 |  |  |  | AE2-221
253398 | AE2-221_GEN2 | S1 | 0.63 | 209 | Gen |  | 86 | 0 | 1 |  | 150 | 0 | 0 | 0 | 81 |  |  |  | -0.00447 |  |  |  | AE2-221
253406 | AD2-031_GEN | S1 | 0.55 | 209 | Gen |  | 83 | 0 | 1 |  | 50.69 | 0 | 0 | 0 | 26.86 |  |  |  | -0.00447 |  |  |  | AD2-031
270180 | AB1-006 W1 | W1 | 0.65 | 205 | Gen |  | 77 | 0 | 1 |  | 200.4 | 0 | 0 | 0 | 64.13 |  |  |  | -0.00447 |  |  |  | AB1-006
270209 | AC1-174 C | 1 | 0.39 | 205 | Gen |  | 83 | 0 | 1 |  | 100 | 0 | 0 | 0 | 53 |  |  |  | -0.00447 |  |  |  | AC1-174
270210 | AC1-175 C | 1 | 0.39 | 205 | Gen |  | 83 | 0 | 1 |  | 100 | 0 | 0 | 0 | 53 |  |  |  | -0.00447 |  |  |  | AC1-175
270222 | AC2-111 C | 1 | 0.39 | 205 | Gen |  | 86 | 0 | 1 |  | 81.51 | 0 | 0 | 0 | 44.01 |  |  |  | -0.00446 |  |  |  | AC2-111
270239 | V3-007_GEN1 | W1 | 0.65 | 205 | Gen |  | 77 | 0 | 1 |  | 48.1 | 0 | 0 | 0 | 15.39 |  |  |  | -0.00447 |  |  |  | V3-007
270240 | V3-007_GEN2 | W2 | 0.72 | 205 | Gen |  | 77 | 0 | 1 |  | 156.6 | 0 | 0 | 0 | 50.11 |  |  |  | -0.00447 |  |  |  | V3-007
274886 | PILOTHILLGEN | W1 | 0.69 | 222 | Gen |  | 77 | 0 | 1 |  | 154.7 | 0 | 0 | 0 | 49.5 |  |  |  | -0.00447 |  |  |  | S36
274887 | PILOTHILLGEN | W1 | 0.69 | 222 | Gen |  | 77 | 0 | 1 |  | 22.2 | 0 | 0 | 0 | 7.1 |  |  |  | -0.00447 |  |  |  | S36
274888 | KELLY CRK;1U | W1 | 0.69 | 222 | Gen |  | 77 | 0 | 1 |  | 175 | 0 | 0 | 0 | 56 |  |  |  | -0.00447
276772 | AC2-154 GEN | 1 | 0.6 | 222 | Gen |  | 86 | 0 | 1 |  | 49.98 | 0 | 0 | 0 | 26.99 |  |  |  | -0.00447 |  |  |  | AC2-154
276776 | AD2-060 GEN | 1 | 0.6 | 222 | Gen |  | 86 | 0 | 1 |  | 20.2 | 0 | 0 | 0 | 10.91 |  |  |  | -0.00447 |  |  |  | AD2-060
276167 | Z1-106 E2 | BA | 34.5 | 222 | Gen | New | 88 | 0 | 1 |  | 10 | 0 | -10 | 0 | 0 |  |  |  | -0.00445 |  |  |  | Z1-106
276168 | Z1-106 E1 | BA | 34.5 | 222 | Gen | New | 88 | 0 | 1 |  | 10 | 0 | -10 | 0 | 0 |  |  |  | -0.00445 |  |  |  | Z1-106
243859 | 05FR-11G C | W1 | 0.6 | 205 | Gen |  | 77 | 0 | 1 |  | 104 | 0 | 0 | 0 | 33.28 |  |  |  | -0.00446 |  |  |  | Q01/Q03
243862 | 05FR-12G C | W1 | 0.6 | 205 | Gen |  | 77 | 0 | 1 |  | 97.35 | 0 | 0 | 0 | 31.15 |  |  |  | -0.00446 |  |  |  | Q01/Q03
243864 | 05FR-21G C | W1 | 0.6 | 205 | Gen |  | 77 | 0 | 1 |  | 103.95 | 0 | 0 | 0 | 33.26 |  |  |  | -0.00446 |  |  |  | Q01/Q03
243866 | 05FR-22G C | W1 | 0.69 | 205 | Gen |  | 77 | 0 | 1 |  | 98.52 | 0 | 0 | 0 | 31.53 |  |  |  | -0.00446 |  |  |  | Q01/Q03
243870 | 05FR-3G C | W1 | 0.69 | 205 | Gen |  | 77 | 0 | 1 |  | 199.5 | 0 | 0 | 0 | 63.84 |  |  |  | -0.00446 |  |  |  | Q01/Q03
243873 | 05FR-4G C | W1 | 0.69 | 205 | Gen |  | 77 | 0 | 1 |  | 154.1 | 0 | 0 | 0 | 49.31 |  |  |  | -0.00446 |  |  |  | Q01/Q03
253313 | AC1-085 A_C | 1 | 0.6 | 209 | Gen |  | 86 | 0 | 1 |  | 200 | 0 | 0 | 0 | 108 |  |  |  | -0.00446 |  |  |  | AC1-085
253316 | AC1-085 B_C | 1 | 0.6 | 209 | Gen |  | 86 | 0 | 1 |  | 200 | 0 | 0 | 0 | 108 |  |  |  | -0.00446 |  |  |  | AC1-085
270356 | AE2-297 GEN | S1 | 0.55 | 205 | Gen |  | 86 | 0 | 1 |  | 154.03 | 0 | 0 | 0 | 83.18 |  |  |  | -0.00445 |  |  |  | AE2-297
274847 | GR RIDGE ;BU | W1 | 0.57 | 222 | Gen |  | 77 | 0 | 1 |  | 147.4 | 0 | 0 | 0 | 47.17 |  |  |  | -0.00446
274861 | TOP CROP ;1U | W1 | 0.69 | 222 | Gen |  | 77 | 0 | 1 |  | 150 | 0 | 0 | 0 | 48 |  |  |  | -0.00445
274862 | TOP CROP ;2U | W2 | 0.69 | 222 | Gen |  | 77 | 0 | 1 |  | 150 | 0 | 0 | 0 | 48 |  |  |  | -0.00445
274871 | GR RIDGE ;2U | W2 | 0.57 | 222 | Gen |  | 77 | 0 | 1 |  | 162.6 | 0 | 0 | 0 | 52.03 |  |  |  | -0.00446
276691 | AA1-018 GEN1 | W1 | 0.65 | 222 | Gen |  | 77 | 0 | 1 |  | 13.8 | 0 | 0 | 0 | 4.42 |  |  |  | -0.00445 |  |  |  | AA1-018
276694 | AA1-018 GEN2 | W2 | 0.65 | 222 | Gen |  | 77 | 0 | 1 |  | 136.8 | 0 | 0 | 0 | 43.78 |  |  |  | -0.00445 |  |  |  | AA1-018
252519 | AF1-045_GEN | B1 | 0.6 | 212 | Gen | New | 88 | 0.05 | 1 |  | 52.2 | 0 | -52.2 | 0 | 0 |  |  |  | -0.00444 |  |  |  | AF1-045
276170 | Z1-108 | B1 | 34.5 | 222 | Gen | New | 88 | 0 | 1 |  | 20 | 0 | -20 | 0 | 0 |  |  |  | -0.00445 |  |  |  | Z1-108
276778 | AA2-123 E | 1 | 34.5 | 222 | Gen | New | 88 | 0 | 1 |  | 20 | 0 | -20 | 0 | 0 |  |  |  | -0.00444 |  |  |  | AA2-123
251832 | 08HLCRTG | 1 | 0.38 | 212 | Gen |  | 86 | 0 | 1 |  | 200 | 0 | 0 | 0 | 108 |  |  |  | -0.00444
252510 | AF1-249 C | S1 | 138 | 212 | Gen |  | 86 | 0 | 1 |  | 19.92 | 0 | 0 | 0 | 10.76 |  |  |  | -0.00444 |  |  |  | AF1-249
252516 | AE2-318_GEN | S1 | 0.6 | 212 | Gen |  | 86 | 0 | 1 |  | 100 | 0 | 0 | 0 | 54 |  |  |  | -0.00444 |  |  |  | AE2-318
274863 | CAYUGA RI;1U | W1 | 0.69 | 222 | Gen |  | 77 | 0 | 1 |  | 150 | 0 | 0 | 0 | 48 |  |  |  | -0.00444
274864 | CAYUGA RI;2U | W2 | 0.69 | 222 | Gen |  | 77 | 0 | 1 |  | 150 | 0 | 0 | 0 | 48 |  |  |  | -0.00444
274872 | LEE DEKAL;1U | W1 | 0.57 | 222 | Gen |  | 77 | 0 | 1 |  | 240 | 0 | 0 | 0 | 76.8 |  |  |  | -0.00444 |  |  |  | Q57
274879 | MINONK ;1U | W1 | 0.69 | 222 | Gen |  | 77 | 0 | 1 |  | 200 | 0 | 0 | 0 | 64 |  |  |  | -0.00444
276678 | AD1-016 GEN | S1 | 138 | 222 | Gen | New | 83 | 0 | 1 |  | 20 | 0 | 0 | 0 | 0 |  |  |  | -0.00444 |  |  |  | AD1-016
251828 | 08CLESP1 | 1 | 34.5 | 212 | Gen | New | 88 | 0 | 1 |  | 10 | 0 | -10 | 0 | 0 |  |  |  | -0.00443
251827 | 08WLYESP | 1 | 34.5 | 212 | Gen | New | 88 | 0 | 1 |  | 6 | 0 | -6 | 0 | 0 |  |  |  | -0.00443
252507 | AC2-088 C | 1 | 0.57 | 212 | Gen |  | 83 | 0 | 1 |  | 70 | 0 | 0 | 0 | 37.1 |  |  |  | -0.00443 |  |  |  | AC2-088
252509 | AD1-136 GEN | S1 | 0.57 | 212 | Gen | New | 83 | 0 | 1 |  | 10 | 0 | 0 | 0 | 0 |  |  |  | -0.00443 |  |  |  | AC2-088
274850 | MENDOTA H;RU | W | 0.69 | 222 | Gen |  | 77 | 0 | 1 |  | 76.13 | 0 | 0 | 0 | 24.36 |  |  |  | -0.00444
274855 | GSG-6 ;RU | W | 0.69 | 222 | Gen |  | 77 | 0 | 1 |  | 80 | 0 | 0 | 0 | 25.6 |  |  |  | -0.00444
274856 | ECOGROVE ;U1 | W1 | 12 | 222 | Gen |  | 77 | 0 | 1 |  | 100 | 0 | 0 | 0 | 32 |  |  |  | -0.00443
276602 | WESTBROOK C | W1 | 138 | 222 | Gen |  | 77 | 0 | 1 |  | 54 | 0 | 0 | 0 | 17.28 |  |  |  | -0.00444
276611 | AD2-172 C | S1 | 138 | 222 | Gen |  | 86 | 0 | 1 |  | 50 | 0 | 0 | 0 | 27 |  |  |  | -0.00443 |  |  |  | AD2-172
276612 | AE2-035 C | S1 | 0.6 | 222 | Gen |  | 86 | 0 | 1 |  | 50 | 0 | 0 | 0 | 27 |  |  |  | -0.00443 |  |  |  | AE2-035
276679 | AD1-129 GEN | S1 | 34.5 | 222 | Gen | New | 86 | 0 | 1 |  | 12.5 | 0 | 0 | 0 | 0 |  |  |  | -0.00444 |  |  |  | AD1-129
926823 | AC1-168 GEN | 1 | 12 | 222 | Gen |  | 77 | 0 | 1 |  | 78.75 | 0 | 0 | 0 | 25.2 |  |  |  | -0.00444 |  |  |  | AC1-168
937001 | AD2-134 C | 1 | 138 | 222 | Gen | New | 77 | 0 | 1 |  | 105.9 | 0 | 0 | 0 | 0 |  |  |  | -0.00444 |  |  |  | AD2-134
250164 | 08BKJDB1 | 1 | 138 | 212 | Gen | New | 88 | 0 | 1 |  | 2 | 0 | -2 | 0 | 0 |  |  |  | -0.00443
250165 | 08BKJDB2 | 1 | 138 | 212 | Gen | New | 88 | 0 | 1 |  | 2 | 0 | -2 | 0 | 0 |  |  |  | -0.00443
276626 | AG1-044 E | E | 34.5 | 222 | Gen | New | 88 | 0 | 1 |  | 0.56 | 0 | -0.56 | 0 | 0 |  |  |  | -0.00442 |  |  |  | AG1-044
270309 | AB2-085 GEN | S1 | 0.38 | 205 | Gen | New | 86 | 0 | 1 |  | 80 | 0 | 0 | 0 | 0 |  |  |  | -0.00442 |  |  |  | AB2-085
270367 | AC2-061_GEN | S1 | 0.6 | 205 | Gen |  | 83 | 0 | 1 |  | 120.65 | 0 | 0 | 0 | 63.95 |  |  |  | -0.00443 |  |  |  | AC2-061
274848 | CAMPGROVE;RU | W | 0.57 | 222 | Gen |  | 77 | 0 | 1 |  | 150 | 0 | 0 | 0 | 48 |  |  |  | -0.00442
274849 | CRESCENT ;1U | W1 | 0.6 | 222 | Gen |  | 77 | 0 | 1 |  | 54.45 | 0 | 0 | 0 | 17.42 |  |  |  | -0.00443
274851 | PROVIDENC;RU | W3 | 0.69 | 222 | Gen |  | 77 | 0 | 1 |  | 74 | 0 | 0 | 0 | 23.68 |  |  |  | -0.00443
274853 | TWINGROVE;U1 | W1 | 0.69 | 222 | Gen |  | 77 | 0 | 1 |  | 198 | 0 | 0 | 0 | 63.36 |  |  |  | -0.00442
274854 | TWINGROVE;U2 | W2 | 0.69 | 222 | Gen |  | 77 | 0 | 1 |  | 198 | 0 | 0 | 0 | 63.36 |  |  |  | -0.00442
274857 | BIG SKY ;U1 | W1 | 0.69 | 222 | Gen |  | 77 | 0 | 1 |  | 120 | 0 | 0 | 0 | 38.4 |  |  |  | -0.00443
274858 | BIG SKY ;U2 | W2 | 0.69 | 222 | Gen |  | 77 | 0 | 1 |  | 120 | 0 | 0 | 0 | 38.4 |  |  |  | -0.00443
274877 | BISHOP HL;1U | W1 | 0.69 | 222 | Gen |  | 77 | 0 | 1 |  | 100 | 0 | 0 | 0 | 32 |  |  |  | -0.00442
274878 | BISHOP HL;2U | W2 | 0.69 | 222 | Gen |  | 77 | 0 | 1 |  | 100 | 0 | 0 | 0 | 32 |  |  |  | -0.00442
276157 | O29GEN1 | W1 | 0.69 | 222 | Gen |  | 77 | 0 | 1 |  | 112.88 | 0 | 0 | 0 | 36.12 |  |  |  | -0.00442 |  |  |  | O29
276158 | O29GEN2 | W1 | 0.69 | 222 | Gen |  | 77 | 0 | 1 |  | 112.88 | 0 | 0 | 0 | 36.12 |  |  |  | -0.00442 |  |  |  | O29
276603 | SUBLETTE C | W1 | 138 | 222 | Gen |  | 77 | 0 | 1 |  | 26 | 0 | 0 | 0 | 8.32 |  |  |  | -0.00443
276645 | AC1-214 C1 | W1 | 0.69 | 222 | Gen |  | 77 | 0 | 1 |  | 39.7 | 0 | 0 | 0 | 12.7 |  |  |  | -0.00443 |  |  |  | AC1-214
276646 | AC1-214 C2 | W1 | 0.69 | 222 | Gen |  | 77 | 0 | 1 |  | 39.7 | 0 | 0 | 0 | 12.7 |  |  |  | -0.00443 |  |  |  | AC1-214
276655 | AB2-047 C1 | W1 | 0.69 | 222 | Gen |  | 77 | 0 | 1 |  | 125 | 0 | 0 | 0 | 40 |  |  |  | -0.00443 |  |  |  | AB2-047
276656 | AB2-047 C2 | W1 | 0.69 | 222 | Gen |  | 77 | 0 | 1 |  | 125 | 0 | 0 | 0 | 40 |  |  |  | -0.00443 |  |  |  | AB2-047
276708 | O09 GEN2 | 1 | 0.69 | 222 | Gen |  | 77 | 0 | 1 |  | 106 | 0 | 0 | 0 | 21.24 |  |  |  | -0.00442 |  |  |  | O09
276726 | Z2-087_GEN | W1 | 0.65 | 222 | Gen |  | 77 | 0 | 1 |  | 205.2 | 0 | 0 | 0 | 65.66 |  |  |  | -0.00443 |  |  |  | Z2-087
276741 | O09 GEN1 | 1 | 0.69 | 222 | Gen |  | 77 | 0 | 1 |  | 106 | 0 | 0 | 0 | 20.64 |  |  |  | -0.00442 |  |  |  | O09
276780 | AC1-033 GEN | W1 | 0.69 | 222 | Gen |  | 77 | 0 | 1 |  | 100.8 | 0 | 0 | 0 | 32.26 |  |  |  | -0.00442 |  |  |  | AC1-033
270186 | AC1-089 C | S1 | 0.39 | 205 | Gen |  | 83 | 0 | 1 |  | 150 | 0 | 0 | 0 | 79.5 |  |  |  | -0.00442 |  |  |  | AC1-089
241966 | AE1-183 GEN | S1 | 0.6 | 202 | Gen | New | 86 | 0 | 1 |  | 20 | 0 | 0 | 0 | 0 |  |  |  | -0.0044 |  |  |  | AE1-183
241997 | AF1-093 GEN | S1 | 69 | 202 | Gen | New | 86 | 0 | 1 |  | 20 | 0 | 0 | 0 | 0 |  |  |  | -0.0044 |  |  |  | AF1-093
276174 | W4-005 GEN2 | W1 | 0.69 | 222 | Gen |  | 77 | 0 | 1 |  | 96.8 | 0 | 0 | 0 | 30.98 |  |  |  | -0.00441 |  |  |  | W4-005
276615 | AF2-317 | W1 | 0.69 | 222 | Gen |  | 77 | 0 | 1 |  | 65 | 0 | 0 | 0 | 20.8 |  |  |  | -0.0044 |  |  |  | AF2-317
276621 | X2-022 GEN | W1 | 0.69 | 222 | Gen |  | 77 | 0 | 1 |  | 185 | 0 | 0 | 0 | 59.2 |  |  |  | -0.0044 |  |  |  | X2-022
276668 | AB2-070 GEN1 | W1 | 0.69 | 222 | Gen |  | 77 | 0 | 1 |  | 200 | 0 | 0 | 0 | 64 |  |  |  | -0.00441 |  |  |  | AB2-070
276686 | W4-005 GEN3 | W1 | 0.69 | 222 | Gen |  | 77 | 0 | 1 |  | 105.6 | 0 | 0 | 0 | 33.79 |  |  |  | -0.00441 |  |  |  | W4-005
276763 | AC1-053 GEN1 | 1 | 0.69 | 222 | Gen |  | 77 | 0 | 1 |  | 100 | 0 | 0 | 0 | 32 |  |  |  | -0.0044 |  |  |  | AC1-053
276764 | AC1-053 GEN2 | 1 | 0.69 | 222 | Gen |  | 77 | 0 | 1 |  | 100 | 0 | 0 | 0 | 32 |  |  |  | -0.0044 |  |  |  | AC1-053
276785 | W4-005 GEN1 | W1 | 0.69 | 222 | Gen |  | 77 | 0 | 1 |  | 103.4 | 0 | 0 | 0 | 33.09 |  |  |  | -0.00441 |  |  |  | W4-005
339216 | AC1-074 C | 1 | 0.6 | 320 | Gen |  | 86 | 0 | 1 |  | 93.3 | 0 | 0 | 0 | 50.38 |  |  |  | -0.00436 |  |  |  | AC1-074
339218 | AC2-075 C | S1 | 0.6 | 320 | Gen |  | 86 | 0 | 1 |  | 20.7 | 0 | 0 | 0 | 11.18 |  |  |  | -0.00436 |  |  |  | AC2-075
339221 | AD2-048_GEN | S1 | 0.55 | 320 | Gen |  | 86 | 0 | 1 |  | 70.75 | 0 | 0 | 0 | 38.21 |  |  |  | -0.00436 |  |  |  | AD2-048
270329 | AC1-082 GEN1 | S1 | 0.69 | 205 | Gen | New | 86 | 0 | 1 |  | 15.75 | 0 | 0 | 0 | 0 |  |  |  | -0.00433 |  |  |  | AC1-082
270330 | AC1-082 GEN2 | S1 | 0.69 | 205 | Gen | New | 86 | 0 | 1 |  | 18.9 | 0 | 0 | 0 | 0 |  |  |  | -0.00433 |  |  |  | AC1-082
270331 | AC1-082 GEN3 | S1 | 0.69 | 205 | Gen | New | 86 | 0 | 1 |  | 15.75 | 0 | 0 | 0 | 0 |  |  |  | -0.00433 |  |  |  | AC1-082
339200 | AD2-072_GEN | S1 | 0.6 | 320 | Gen | New | 86 | 0 | 1 |  | 95 | 0 | 0 | 0 | 0 |  |  |  | -0.0043 |  |  |  | AD2-072
339211 | AE2-254 GEN | 1 | 0.66 | 320 | Gen |  | 86 | 0 | 1 |  | 50 | 0 | 0 | 0 | 27 |  |  |  | -0.00427 |  |  |  | AE2-254
270192 | AB1-055 E | 1 | 138 | 205 | Gen | New | 88 | 0 | 1 |  | 2 | 0 | -2 | 0 | 0 |  |  |  | -0.00422 |  |  |  | AB1-055
339206 | AE1-143 C | B1 | 0.64 | 320 | Gen | New | 88 | 0.05 | 1 |  | 96 | 0 | 0 | 0 | 0 |  |  |  | -0.00422 |  |  |  | AE1-143 |  | MFO
339206 | AE1-143 C | S1 | 0.64 | 320 | Gen |  | 86 | 0 | 1 |  | 96 | 0 | 0 | 0 | 52.43 |  |  |  | -0.00422 |  |  |  | AE1-143 |  | MFO
339241 | AF1-083 GEN | B1 | 0.6 | 320 | Gen | New | 88 | 0 | 1 |  | 26 | 0 | 0 | 0 | 0 |  |  |  | -0.00421 |  |  |  | AF1-083 |  | MFO
339241 | AF1-083 GEN | S1 | 0.6 | 320 | Gen |  | 86 | 0 | 1 |  | 55.6 | 0 | 0 | 0 | 30.02 |  |  |  | -0.00421 |  |  |  | AF1-083 |  | MFO
339236 | AF1-050_GEN | B1 | 0.66 | 320 | Gen | New | 88 | 0 | 1 |  | 30 | 0 | 0 | 0 | 0 |  |  |  | -0.0042 |  |  |  | AF1-050 |  | MFO
339236 | AF1-050_GEN | S1 | 0.66 | 320 | Gen |  | 86 | 0 | 1 |  | 60.5 | 0 | 0 | 0 | 32.67 |  |  |  | -0.0042 |  |  |  | AF1-050 |  | MFO
339231 | AF1-038_GEN | B1 | 0.66 | 320 | Gen | New | 88 | 0 | 1 |  | 30 | 0 | 0 | 0 | 0 |  |  |  | -0.00419 |  |  |  | AF1-038 |  | MFO
339231 | AF1-038_GEN | S1 | 0.66 | 320 | Gen |  | 86 | 0 | 1 |  | 60 | 0 | 0 | 0 | 32.4 |  |  |  | -0.00419 |  |  |  | AF1-038 |  | MFO
243758 | 05MIDDLECR | B1 | 46 | 205 | Gen | New | 88 | 0 | 1 |  | 2 | 0 | -2 | 0 | 0 |  |  |  | -0.00414
270399 | AC1-101 GEN | S1 | 0.64 | 205 | Gen |  | 83 | 0 | 1 |  | 50 | 0 | 0 | 0 | 26.5 |  |  |  | -0.00412 |  |  |  | AC1-101
270400 | AC1-102 GEN | 1 | 0.64 | 205 | Gen |  | 83 | 0 | 1 |  | 50 | 0 | 0 | 0 | 26.5 |  |  |  | -0.00412 |  |  |  | AC1-102
241986 | AG1-251 GEN | S1 | 69 | 202 | Gen |  | 86 | 0 | 1 |  | 3.88 | 0 | 0 | 0 | 2.09 |  |  |  | -0.00395 |  |  |  | AG1-251
270346 | AE1-212 GEN | S1 | 0.63 | 205 | Gen |  | 86 | 0 | 1 |  | 90 | 0 | 0 | 0 | 48.6 |  |  |  | -0.0039 |  |  |  | AE1-212
270167 | AD2-205 E | 1 | 69 | 205 | Gen | New | 88 | 0 | 1 |  | 4 | 0 | -4 | 0 | 0 |  |  |  | -0.0038 |  |  |  | AD2-205
270214 | AC2-123 C | 1 | 0.42 | 205 | Gen |  | 86 | 0 | 1 |  | 75 | 0 | 0 | 0 | 40.5 |  |  |  | -0.0038 |  |  |  | AC2-123
238115 | M24_BAT | W1 | 0.35 | 201 | Gen | New | 88 | 0 | 1 |  | 32 | 0 | -32 | 0 | 0 |  |  |  | -0.00361
235780 | M24_1 | W1 | 0.57 | 201 | Gen |  | 77 | 0 | 1 |  | 100.5 | 0 | 0 | 0 | 32.16 |  |  |  | -0.00361 |  |  |  | M24
237033 | AB1-150 GEN1 | W1 | 0.69 | 201 | Gen |  | 77 | 0 | 1 |  | 55.6 | 0 | 0 | 0 | 17.79 |  |  |  | -0.00361 |  |  |  | AB1-150
238114 | M24_2 | W1 | 0.57 | 201 | Gen |  | 77 | 0 | 1 |  | 54 | 0 | 0 | 0 | 17.28 |  |  |  | -0.00361 |  |  |  | M24
270336 | AE1-100 GEN | S1 | 0.55 | 205 | Gen |  | 86 | 0 | 1 |  | 66.75 | 0 | 0 | 0 | 36.05 |  |  |  | -0.00355 |  |  |  | AE1-100
270173 | AC1-122 C | 1 | 0.6 | 205 | Gen |  | 86 | 0 | 1 |  | 75.9 | 0 | 0 | 0 | 40.99 |  |  |  | -0.00345 |  |  |  | AC1-122
244012 | 05PINNACLE | 1 | 4 | 205 | Gen | New | 83 | 0 | 1 |  | 11 | 0 | 0 | 0 | 0 |  |  |  | -0.00342
270197 | AC1-083 C | 1 | 0.39 | 205 | Gen |  | 83 | 0 | 1 |  | 120 | 0 | 0 | 0 | 63.6 |  |  |  | -0.00341 |  |  |  | AC1-083
316197 | AC1-042 C | 1 | 0.39 | 345 | Gen |  | 84 | 0 | 1 |  | 42 | 0 | 0 | 0 | 24.78 |  |  |  | -0.00338 |  |  |  | AC1-042
316217 | AC1-145 C | 1 | 0.6 | 345 | Gen |  | 87 | 0 | 1 |  | 50 | 0 | 0 | 0 | 29 |  |  |  | -0.00338 |  |  |  | AC1-145
945081 | AF1-173 | 1 | 69 | 345 | Gen | New | 84 | 0 | 1 |  | 13.95 | 0 | 0 | 0 | 0 |  |  |  | -0.00338 |  |  |  | AF1-173
238122 | AG1-246 GEN | S1 | 25 | 201 | Gen |  | 86 | 0 | 1 |  | 7.5 | 0 | 0 | 0 | 4.05 |  |  |  | 0.00333 |  |  |  | AG1-246
316123 | AC1-075 C | 1 | 0.63 | 345 | Gen |  | 87 | 0 | 1 |  | 80 | 0 | 0 | 0 | 46.4 |  |  |  | -0.00318 |  |  |  | AC1-075 and AC1-080
316283 | AC2-100 C | S1 | 0.57 | 345 | Gen |  | 87 | 0 | 1 |  | 62 | 0 | 0 | 0 | 35.96 |  |  |  | -0.00318 |  |  |  | AC2-100
316222 | AC1-221 GEN | 1 | 0.6 | 345 | Gen | New | 87 | 0 | 1 |  | 65.8 | 0 | 0 | 0 | 0 |  |  |  | -0.00316 |  |  |  | AC1-221
316003 | AC1-222 GEN | S1 | 0.6 | 345 | Gen | New | 87 | 0 | 1 |  | 64.7 | 0 | 0 | 0 | 0 |  |  |  | -0.00306 |  |  |  | AC1-222
316248 | AF1-058 C | 1 | 115 | 345 | Gen |  | 87 | 0 | 1 |  | 20 | 0 | 0 | 0 | 11.6 |  |  |  | -0.00302 |  |  |  | AF1-058
316049 | AB1-081 GEN | 1 | 0.63 | 345 | Gen |  | 87 | 0 | 1 |  | 82.8 | 0 | 0 | 0 | 48.02 |  |  |  | -0.003 |  |  |  | AB1-081
316118 | AC1-105 C | 1 | 0.57 | 345 | Gen |  | 87 | 0 | 1 |  | 51.45 | 0 | 0 | 0 | 29.84 |  |  |  | -0.003 |  |  |  | AC1-105
316263 | AC1-034 C | 1 | 0.55 | 345 | Gen |  | 87 | 0 | 1 |  | 75 | 0 | 0 | 0 | 43.5 |  |  |  | -0.003 |  |  |  | AC1-034
316359 | AB2-059 C OP | 1 | 0.63 | 345 | Gen |  | 87 | 0 | 1 |  | 100 | 0 | 0 | 0 | 58 |  |  |  | -0.003 |  |  |  | AB2-059
316319 | Z2-044 C | S1 | 115 | 345 | Gen |  | 87 | 0 | 1 |  | 12 | 0 | 0 | 0 | 6.96 |  |  |  | -0.00297 |  |  |  | Z2-044
315601 | 1CONETOE2SOL | SA | 0.69 | 345 | Gen |  | 87 | 0 | 1 |  | 98.4 | 0 | 0 | 0 | 57.07 |  |  |  | -0.00297 |  |  |  | Z2-088
316494 | AC1-189 GEN | S1 | 0.38 | 345 | Gen | New | 87 | 0 | 1 |  | 80 | 0 | 0 | 0 | 0 |  |  |  | -0.00296 |  |  |  | AC1-189
316327 | AA2-057 C | S1 | 0.63 | 345 | Gen |  | 87 | 0 | 1 |  | 74.9 | 0 | 0 | 0 | 43.44 |  |  |  | -0.00295 |  |  |  | AA2-057
316005 | AA1-067 C | S1 | 230 | 345 | Gen |  | 87 | 0 | 1 |  | 15 | 0 | 0 | 0 | 8.7 |  |  |  | -0.00294 |  |  |  | AA1-067
316210 | AC1-098 GEN | 1 | 0.6 | 345 | Gen |  | 87 | 0 | 1 |  | 60 | 0 | 0 | 0 | 34.8 |  |  |  | -0.0029 |  |  |  | AC1-098
316212 | AC1-099_GEN | 1 | 0.6 | 345 | Gen |  | 87 | 0 | 1 |  | 20 | 0 | 0 | 0 | 11.6 |  |  |  | -0.0029 |  |  |  | AC1-099
316237 | AB2-079 C | 1 | 115 | 345 | Gen |  | 87 | 0 | 1 |  | 20 | 0 | 0 | 0 | 11.6 |  |  |  | -0.0029 |  |  |  | AB2-079
316238 | AB2-078 C | 1 | 115 | 345 | Gen |  | 87 | 0 | 1 |  | 20 | 0 | 0 | 0 | 11.6 |  |  |  | -0.0029 |  |  |  | AB2-078
316239 | AB2-077 C | 1 | 115 | 345 | Gen |  | 87 | 0 | 1 |  | 20 | 0 | 0 | 0 | 11.6 |  |  |  | -0.0029 |  |  |  | AB2-077
316274 | AC1-208 GEN | 1 | 0.38 | 345 | Gen |  | 87 | 0 | 1 |  | 80 | 0 | 0 | 0 | 46.4 |  |  |  | -0.00291 |  |  |  | AC1-208
316489 | AC2-084 GEN | S1 | 0.6 | 345 | Gen |  | 84 | 0 | 1 |  | 61.25 | 0 | 0 | 0 | 36.14 |  |  |  | -0.0029 |  |  |  | AC2-084
313527 | AB2-043 C | 1 | 0.55 | 345 | Gen |  | 87 | 0 | 1 |  | 49.9 | 0 | 0 | 0 | 28.94 |  |  |  | -0.0029 |  |  |  | AB2-043
316129 | AC1-054 C | 1 | 0.38 | 345 | Gen |  | 87 | 0 | 1 |  | 65 | 0 | 0 | 0 | 37.7 |  |  |  | -0.00289 |  |  |  | AC1-054
316131 | AB2-060 C | S1 | 0.63 | 345 | Gen |  | 87 | 0 | 1 |  | 80.08 | 0 | 0 | 0 | 46.45 |  |  |  | -0.0029 |  |  |  | AB2-060
315616 | AA1-038_C | W1 | 0.69 | 345 | Gen |  | 78 | 0 | 1 |  | 78.2 | 0 | 0 | 0 | 25.02 |  |  |  | -0.00288 |  |  |  | AA1-038
316034 | AC1-036 C | 1 | 115 | 345 | Gen |  | 87 | 0 | 1 |  | 17.9 | 0 | 0 | 0 | 10.38 |  |  |  | -0.00287 |  |  |  | AC1-036
316174 | AB2-169_C | S1 | 0.63 | 345 | Gen |  | 87 | 0 | 1 |  | 74 | 0 | 0 | 0 | 42.92 |  |  |  | -0.00286 |  |  |  | AB2-169
315687 | AD1-152 GEN | S1 | 0.6 | 345 | Gen |  | 87 | 0 | 1 |  | 80 | 0 | 0 | 0 | 46.4 |  |  |  | -0.00285 |  |  |  | AD1-152
316317 | KELFORD C | S1 | 115 | 345 | Gen |  | 87 | 0 | 1 |  | 20.2 | 0 | 0 | 0 | 11.72 |  |  |  | -0.00285
316478 | AD1-087 GEN | S1 | 0.66 | 345 | Gen |  | 87 | 0 | 1 |  | 64.2 | 0 | 0 | 0 | 37.24 |  |  |  | -0.00285 |  |  |  | AD1-087
316486 | AD2-202 GEN | S1 | 0.66 | 345 | Gen |  | 87 | 0 | 1 |  | 18.8 | 0 | 0 | 0 | 10.9 |  |  |  | -0.00285 |  |  |  | AD2-202
315606 | AA2-053 GEN | S1 | 0.63 | 345 | Gen |  | 87 | 0 | 1 |  | 77.3 | 0 | 0 | 0 | 44.83 |  |  |  | -0.00285 |  |  |  | AA2-053
315652 | AC1-086 GEN | S1 | 0.38 | 345 | Gen |  | 87 | 0 | 1 |  | 180 | 0 | 0 | 0 | 104.4 |  |  |  | -0.00285 |  |  |  | AC1-086
316011 | AB1-132 C OP | 1 | 230 | 345 | Gen |  | 87 | 0 | 1 |  | 120 | 0 | 0 | 0 | 69.6 |  |  |  | -0.00285 |  |  |  | AB1-132
316190 | AA2-174 GEN | S1 | 0.63 | 345 | Gen |  | 87 | 0 | 1 |  | 5 | 0 | 0 | 0 | 2.9 |  |  |  | -0.00285 |  |  |  | AA2-053
313506 | AB1-173 C OP | 1 | 115 | 345 | Gen |  | 87 | 0 | 1 |  | 59.6 | 0 | 0 | 0 | 34.57 |  |  |  | -0.00283 |  |  |  | AB1-173
315657 | AE1-056 GEN | S1 | 0.55 | 345 | Gen | New | 87 | 0 | 1 |  | 60.56 | 0 | 0 | 0 | 0 |  |  |  | -0.00284 |  |  |  | AE1-056
315693 | AD1-088 GEN | S1 | 0.7 | 345 | Gen |  | 87 | 0 | 1 |  | 113 | 0 | 0 | 0 | 65.54 |  |  |  | -0.00283 |  |  |  | AD1-088
316181 | AB2-040 GEN | 1 | 0.6 | 345 | Gen |  | 84 | 0 | 1 |  | 81.51 | 0 | 0 | 0 | 48.09 |  |  |  | -0.00283 |  |  |  | AB2-040
315607 | 3AA1-063SOLA | SA | 115 | 345 | Gen |  | 87 | 0 | 1 |  | 74.8 | 0 | 0 | 0 | 43.38 |  |  |  | -0.00283 |  |  |  | AA1-063
316087 | AB2-174 C | 1 | 0.4 | 345 | Gen |  | 84 | 0 | 1 |  | 80 | 0 | 0 | 0 | 47.2 |  |  |  | -0.00283 |  |  |  | AB2-174
316140 | AB2-099 | 1 | 115 | 345 | Gen | New | 87 | 0 | 1 |  | 5 | 0 | 0 | 0 | 0 |  |  |  | -0.00282 |  |  |  | AB2-099
316463 | AE2-346 GEN | S1 | 115 | 345 | Gen |  | 87 | 0 | 1 |  | 12 | 0 | 0 | 0 | 6.96 |  |  |  | -0.00282 |  |  |  | AE2-346
315602 | 1HOLLOMANSOL | SA | 0.69 | 345 | Gen |  | 87 | 0 | 1 |  | 91 | 0 | 0 | 0 | 52.78 |  |  |  | -0.00282
316065 | AD1-022 GEN | S1 | 0.55 | 345 | Gen |  | 87 | 0 | 1 |  | 81 | 0 | 0 | 0 | 46.98 |  |  |  | -0.0028 |  |  |  | AD1-022
316318 | V4-068 C | S1 | 115 | 345 | Gen |  | 87 | 0 | 1 |  | 4.67 | 0 | 0 | 0 | 2.71 |  |  |  | -0.0028 |  |  |  | V4-068
316023 | AB2-100 C2 | S2 | 0.55 | 345 | Gen |  | 87 | 0 | 1 |  | 50 | 0 | 0 | 0 | 29 |  |  |  | -0.00279 |  |  |  | AB2-100
316365 | AB2-100 C1 | S1 | 0.55 | 345 | Gen |  | 87 | 0 | 1 |  | 50 | 0 | 0 | 0 | 29 |  |  |  | -0.00279 |  |  |  | AB2-100
315608 | 3AA2-088SOLA | SA | 115 | 345 | Gen |  | 87 | 0 | 1 |  | 100 | 0 | 0 | 0 | 58 |  |  |  | -0.00278 |  |  |  | AA2-088
315614 | AA2-178 C | 1 | 0.69 | 345 | Gen |  | 87 | 0 | 1 |  | 80 | 0 | 0 | 0 | 46.4 |  |  |  | -0.00276 |  |  |  | AA2-178
316322 | AB2-045 C | S1 | 230 | 345 | Gen |  | 87 | 0 | 1 |  | 17.73 | 0 | 0 | 0 | 10.28 |  |  |  | -0.00275 |  |  |  | AB2-045
314541 | 3WATKINS | A | 115 | 345 | Gen | New | 84 | 0 | 1 |  | 4 | 0 | 0 | 0 | 0 |  |  |  | -0.00274
316299 | AC2-112 C | S1 | 0.6 | 345 | Gen |  | 87 | 0 | 1 |  | 150 | 0 | 0 | 0 | 87 |  |  |  | -0.00274 |  |  |  | AC2-112
316300 | AF2-400 C | S1 | 115 | 345 | Gen |  | 84 | 0 | 1 |  | 7.14 | 0 | 0 | 0 | 4.21 |  |  |  | -0.00273 |  |  |  | AF2-400
316334 | AE1-084 C | 1 | 0.63 | 345 | Gen | New | 87 | 0 | 1 |  | 83 | 0 | 0 | 0 | 0 |  |  |  | -0.00274 |  |  |  | AE1-084
237046 | AF1-021 C | 1 | 25 | 201 | Gen |  | 86 | 0 | 1 |  | 14 | 0 | 0 | 0 | 7.56 |  |  |  | 0.00272 |  |  |  | AF1-021
315611 | 6Z1-036WIND | WA | 230 | 345 | Gen |  | 78 | 0 | 1 |  | 300.3 | 0 | 0 | 0 | 96.1 |  |  |  | -0.00271 |  |  |  | Z1-036
316315 | AB2-025 C | S1 | 230 | 345 | Gen |  | 87 | 0 | 1 |  | 19.85 | 0 | 0 | 0 | 11.51 |  |  |  | -0.0027 |  |  |  | AB2-025
316035 | AC1-116 C | 1 | 230 | 345 | Gen |  | 84 | 0 | 1 |  | 12.5 | 0 | 0 | 0 | 7.38 |  |  |  | -0.00268 |  |  |  | AC1-116
316431 | W1029_GEN1 | 1 | 0.69 | 345 | Gen |  | 78 | 0 | 1 |  | 69.33 | 0 | 0 | 0 | 22.19 |  |  |  | -0.00268 |  |  |  | W1-029
316433 | W1029_GEN2 | 2 | 0.69 | 345 | Gen |  | 78 | 0 | 1 |  | 69.33 | 0 | 0 | 0 | 22.19 |  |  |  | -0.00268 |  |  |  | W1-029
316435 | W1029_GEN3 | 3 | 0.69 | 345 | Gen |  | 78 | 0 | 1 |  | 69.33 | 0 | 0 | 0 | 22.19 |  |  |  | -0.00268 |  |  |  | W1-029
316321 | Z2-027 C | S1 | 230 | 345 | Gen |  | 87 | 0 | 1 |  | 20 | 0 | 0 | 0 | 11.6 |  |  |  | -0.00267 |  |  |  | Z2-027
316499 | AE2-029_GEN | S1 | 0.6 | 345 | Gen |  | 87 | 0 | 1 |  | 50.5 | 0 | 0 | 0 | 29.29 |  |  |  | -0.00267 |  |  |  | AE2-029
313526 | AB2-022 C | 1 | 230 | 345 | Gen |  | 87 | 0 | 1 |  | 20 | 0 | 0 | 0 | 11.6 |  |  |  | -0.00267 |  |  |  | AB2-022
316320 | Y1-086 C | S1 | 230 | 345 | Gen |  | 84 | 0 | 1 |  | 20 | 0 | 0 | 0 | 11.8 |  |  |  | -0.00267 |  |  |  | Y1-086
316093 | AE2-104_GEN | S1 | 0.39 | 345 | Gen |  | 84 | 0 | 1 |  | 49.8 | 0 | 0 | 0 | 29.38 |  |  |  | -0.00266 |  |  |  | AE2-104
316246 | AF1-032 C | 1 | 230 | 345 | Gen |  | 87 | 0 | 1 |  | 15 | 0 | 0 | 0 | 8.7 |  |  |  | -0.00265 |  |  |  | AF1-032
316305 | AF2-043 C | S1 | 230 | 345 | Gen |  | 87 | 0 | 1 |  | 20 | 0 | 0 | 0 | 11.6 |  |  |  | -0.00265 |  |  |  | AF2-043
316017 | AA1-139 ULT1 | S1 | 0.69 | 345 | Gen |  | 87 | 0 | 1 |  | 60 | 0 | 0 | 0 | 34.8 |  |  |  | -0.00265 |  |  |  | AA1-139
316018 | AA1-139 ULT2 | S2 | 0.69 | 345 | Gen |  | 87 | 0 | 1 |  | 60 | 0 | 0 | 0 | 34.8 |  |  |  | -0.00265 |  |  |  | AA1-139
316311 | AC2-079 GEN | S1 | 0.64 | 345 | Gen | New | 84 | 0 | 1 |  | 85 | 0 | 0 | 0 | 0 |  |  |  | -0.00265 |  |  |  | AC2-079
316339 | AD2-160 C | 1 | 0.63 | 345 | Gen |  | 87 | 0 | 1 |  | 50 | 0 | 0 | 0 | 29 |  |  |  | -0.00265 |  |  |  | AD2-160
316349 | AD2-085 GEN | 1 | 0.39 | 345 | Gen |  | 84 | 0 | 1 |  | 51 | 0 | 0 | 0 | 30.09 |  |  |  | -0.00265 |  |  |  | AD2-085
316388 | AE2-253 GEN | 1 | 0.63 | 345 | Gen |  | 87 | 0 | 1 |  | 100 | 0 | 0 | 0 | 58 |  |  |  | -0.00265 |  |  |  | AE2-253
316416 | AF2-057 | B1 | 115 | 345 | Gen | New | 88 | 0 | 1 |  | 20 | 0 | -20 | 0 | 0 |  |  |  | -0.00263 |  |  |  | AF2-057
314295 | 6BIRDNECK | WA | 230 | 345 | Gen |  | 81 | 0 | 1 |  | 12 | 0 | 0 | 0 | 5.88 |  |  |  | -0.00264
316036 | AC1-147 C | S1 | 115 | 345 | Gen |  | 87 | 0 | 1 |  | 20 | 0 | 0 | 0 | 11.6 |  |  |  | -0.00263 |  |  |  | AC1-147
316072 | AD1-144 C | 1 | 230 | 345 | Gen |  | 87 | 0 | 1 |  | 15 | 0 | 0 | 0 | 8.7 |  |  |  | -0.00264 |  |  |  | AD1-144
316152 | AE1-098 C | 1 | 115 | 345 | Gen |  | 87 | 0 | 1 |  | 15.7 | 0 | 0 | 0 | 9.11 |  |  |  | -0.00263 |  |  |  | AE1-098
316154 | AE1-099 C | 1 | 115 | 345 | Gen |  | 87 | 0 | 1 |  | 15.7 | 0 | 0 | 0 | 9.11 |  |  |  | -0.00263 |  |  |  | AE1-099
316185 | AD1-033 C | S1 | 0.6 | 345 | Gen |  | 87 | 0 | 1 |  | 70 | 0 | 0 | 0 | 40.6 |  |  |  | -0.00264 |  |  |  | AD1-033
316316 | AC1-027 C | S1 | 115 | 345 | Gen |  | 87 | 0 | 1 |  | 17.2 | 0 | 0 | 0 | 9.98 |  |  |  | -0.00264 |  |  |  | AC1-027
316375 | AC2-012 C | S1 | 0.6 | 345 | Gen |  | 84 | 0 | 1 |  | 150 | 0 | 0 | 0 | 88.5 |  |  |  | -0.00263 |  |  |  | AC2-012
316083 | AB2-161 C | 1 | 0.55 | 345 | Gen |  | 84 | 0 | 1 |  | 50 | 0 | 0 | 0 | 29.5 |  |  |  | -0.00263 |  |  |  | AB2-161
316336 | AC2-165 C | 1 | 230 | 345 | Gen | New | 87 | 0 | 1 |  | 99.9 | 0 | 0 | 0 | 0 |  |  |  | -0.00262 |  |  |  | AC2-165
316381 | AD1-082 C | 1 | 0.55 | 345 | Gen |  | 87 | 0 | 1 |  | 68 | 0 | 0 | 0 | 39.44 |  |  |  | -0.00263 |  |  |  | AD1-082
316236 | AE1-162 C | 1 | 230 | 345 | Gen |  | 87 | 0 | 1 |  | 20 | 0 | 0 | 0 | 11.6 |  |  |  | -0.00261 |  |  |  | AE1-162
316294 | AC1-161 C | S1 | 0.44 | 345 | Gen |  | 87 | 0 | 1 |  | 240 | 0 | 0 | 0 | 139.2 |  |  |  | -0.00262 |  |  |  | AC1-161
316405 | AF2-144 C | B1 | 230 | 345 | Gen | New | 88 | 0 | 1 |  | 11 | 0 | -11 | 0 | 0 |  |  |  | -0.0026 |  |  |  | AF2-144 |  | MFO
316405 | AF2-144 C | S1 | 230 | 345 | Gen |  | 87 | 0 | 1 |  | 17 | 0 | 0 | 0 | 9.86 |  |  |  | -0.0026 |  |  |  | AF2-144 |  | MFO
316247 | AF1-033 C | 1 | 230 | 345 | Gen |  | 87 | 0 | 1 |  | 20 | 0 | 0 | 0 | 11.6 |  |  |  | -0.0026 |  |  |  | AF1-033
316258 | AE1-075 C | S1 | 230 | 345 | Gen |  | 87 | 0 | 1 |  | 18 | 0 | 0 | 0 | 10.44 |  |  |  | -0.0026 |  |  |  | AE1-075
316313 | AB2-026 C | S1 | 230 | 345 | Gen |  | 87 | 0 | 1 |  | 20 | 0 | 0 | 0 | 11.6 |  |  |  | -0.0026 |  |  |  | AB2-026
315697 | AD1-025 GEN | S1 | 0.6 | 345 | Gen |  | 87 | 0 | 1 |  | 153.41 | 0 | 0 | 0 | 88.98 |  |  |  | -0.00259 |  |  |  | AD1-025
316033 | AB2-134 GEN | S1 | 0.63 | 345 | Gen |  | 87 | 0 | 1 |  | 142.4 | 0 | 0 | 0 | 82.59 |  |  |  | -0.00259 |  |  |  | AB2-134
316108 | AB2-160 GEN | 1 | 0.55 | 345 | Gen | New | 84 | 0 | 1 |  | 80 | 0 | 0 | 0 | 0 |  |  |  | -0.00258 |  |  |  | AB2-160
316132 | AB2-190 C | S1 | 0.63 | 345 | Gen |  | 87 | 0 | 1 |  | 160 | 0 | 0 | 0 | 92.8 |  |  |  | -0.00259 |  |  |  | AB2-190
316369 | AC1-216 C | S1 | 34.5 | 345 | Gen |  | 87 | 0 | 1 |  | 97.9 | 0 | 0 | 0 | 56.78 |  |  |  | -0.00259 |  |  |  | AC1-216
315671 | AE2-027_GEN | 1 | 0.69 | 345 | Gen |  | 87 | 0 | 1 |  | 122.26 | 0 | 0 | 0 | 70.91 |  |  |  | -0.00258 |  |  |  | AE2-027
316240 | AF1-291 C | 1 | 230 | 345 | Gen |  | 87 | 0 | 1 |  | 20 | 0 | 0 | 0 | 11.6 |  |  |  | -0.00257 |  |  |  | AF1-291
316301 | AE2-228 C | S1 | 230 | 345 | Gen |  | 87 | 0 | 1 |  | 25 | 0 | 0 | 0 | 14.5 |  |  |  | -0.00258 |  |  |  | AE2-228
237028 | AC1-073 C | W1 | 138 | 201 | Gen |  | 77 | 0 | 1 |  | 16.3 | 0 | 0 | 0 | 5.22 |  |  |  | -0.00256 |  |  |  | AC1-073
237092 | AD1-085_C | 1 | 0.6 | 201 | Gen |  | 86 | 0 | 1 |  | 32.29 | 0 | 0 | 0 | 17.44 |  |  |  | -0.00257 |  |  |  | AD1-085
237511 | 01LEADS_P59 | W1 | 0.69 | 201 | Gen |  | 77 | 0 | 1 |  | 97.6 | 0 | 0 | 0 | 31.23 |  |  |  | -0.00256 |  |  |  | P59
316159 | AE1-175 C | 1 | 230 | 345 | Gen |  | 87 | 0 | 1 |  | 19.9 | 0 | 0 | 0 | 11.54 |  |  |  | -0.00256 |  |  |  | AE1-175
316382 | AG1-145 C | 1 | 230 | 345 | Gen |  | 87 | 0 | 1 |  | 20 | 0 | 0 | 0 | 11.6 |  |  |  | -0.00256 |  |  |  | AG1-145
316303 | AF2-085 | B1 | 230 | 345 | Gen | New | 88 | 0 | 1 |  | 20 | 0 | -20 | 0 | 0 |  |  |  | -0.00253 |  |  |  | AF2-085
315662 | AE1-191 GEN | S1 | 0.6 | 345 | Gen |  | 87 | 0 | 1 |  | 80 | 0 | 0 | 0 | 46.4 |  |  |  | -0.00252 |  |  |  | AE1-191
315666 | AE1-190 GEN | S1 | 0.6 | 345 | Gen |  | 87 | 0 | 1 |  | 20 | 0 | 0 | 0 | 11.6 |  |  |  | -0.00252 |  |  |  | AE1-190
316059 | AD1-063 C | 1 | 230 | 345 | Gen |  | 87 | 0 | 1 |  | 15 | 0 | 0 | 0 | 8.7 |  |  |  | -0.00252 |  |  |  | AD1-063
316156 | AD2-030 C | 1 | 115 | 345 | Gen |  | 87 | 0 | 1 |  | 19.8 | 0 | 0 | 0 | 11.48 |  |  |  | -0.00252 |  |  |  | AD2-030
316169 | AC1-164 GEN | 1 | 0.44 | 345 | Gen |  | 87 | 0 | 1 |  | 325.4 | 0 | 0 | 0 | 188.73 |  |  |  | -0.00252 |  |  |  | AC1-164
316201 | AC1-065 C | 1 | 0.39 | 345 | Gen |  | 87 | 0 | 1 |  | 149.9 | 0 | 0 | 0 | 86.94 |  |  |  | -0.00252 |  |  |  | AC1-065
316233 | AE1-074 C | S1 | 230 | 345 | Gen |  | 87 | 0 | 1 |  | 20 | 0 | 0 | 0 | 11.6 |  |  |  | -0.00253 |  |  |  | AE1-074
316280 | AD1-041 GEN | 1 | 0.55 | 345 | Gen |  | 87 | 0 | 1 |  | 50 | 0 | 0 | 0 | 29 |  |  |  | -0.00252 |  |  |  | AD1-041
316304 | AE2-227 C | S1 | 230 | 345 | Gen |  | 87 | 0 | 1 |  | 25 | 0 | 0 | 0 | 14.5 |  |  |  | -0.00253 |  |  |  | AE2-227
316314 | AB2-024 C | S1 | 230 | 345 | Gen |  | 87 | 0 | 1 |  | 16.2 | 0 | 0 | 0 | 9.4 |  |  |  | -0.00252 |  |  |  | AB2-024
316075 | AC2-137 C | 1 | 230 | 345 | Gen |  | 87 | 0 | 1 |  | 20.1 | 0 | 0 | 0 | 11.66 |  |  |  | -0.00252 |  |  |  | AC2-137
316004 | AC1-112 C | S1 | 230 | 345 | Gen |  | 87 | 0 | 1 |  | 17 | 0 | 0 | 0 | 9.86 |  |  |  | -0.0025 |  |  |  | AC1-112
316312 | AB1-027 C | S1 | 230 | 345 | Gen |  | 87 | 0 | 1 |  | 25 | 0 | 0 | 0 | 14.5 |  |  |  | -0.0025 |  |  |  | AB1-027
316484 | AD2-074 GEN | S1 | 0.39 | 345 | Gen |  | 84 | 0 | 1 |  | 87.8 | 0 | 0 | 0 | 51.8 |  |  |  | -0.00249 |  |  |  | AD2-074
316487 | AF1-042 GEN | S1 | 0.39 | 345 | Gen |  | 84 | 0 | 1 |  | 47 | 0 | 0 | 0 | 27.73 |  |  |  | -0.00249 |  |  |  | AF1-042
316404 | AE1-155 C | 1 | 0.63 | 345 | Gen |  | 87 | 0 | 1 |  | 127 | 0 | 0 | 0 | 73.66 |  |  |  | -0.00249 |  |  |  | AE1-155
200945 | 26CT_V3-030 | W1 | 0.69 | 226 | Gen |  | 76 | 0 | 1 |  | 33.5 | 0 | 0 | 0 | 9.72 |  |  |  | 0.00248 |  |  |  | V3-030
316077 | AC2-138 C | 1 | 115 | 345 | Gen |  | 87 | 0 | 1 |  | 14.4 | 0 | 0 | 0 | 8.35 |  |  |  | -0.00247 |  |  |  | AC2-138
316417 | AG1-388 C | S1 | 230 | 345 | Gen |  | 87 | 0 | 1 |  | 20 | 0 | 0 | 0 | 11.6 |  |  |  | -0.00248 |  |  |  | AG1-388
316473 | AC1-191 GEN | S1 | 0.38 | 345 | Gen | New | 87 | 0 | 1 |  | 80 | 0 | 0 | 0 | 0 |  |  |  | -0.00248 |  |  |  | AC1-191
235838 | 01GRNGAP | W1 | 0.69 | 201 | Gen |  | 77 | 0 | 1 |  | 300 | 0 | 0 | 0 | 96 |  |  |  | -0.00245
316337 | AD2-073 C | 1 | 230 | 345 | Gen |  | 87 | 0 | 1 |  | 19.92 | 0 | 0 | 0 | 11.55 |  |  |  | -0.00245 |  |  |  | AD2-073
316223 | AC1-118 C | S1 | 230 | 345 | Gen |  | 87 | 0 | 1 |  | 20 | 0 | 0 | 0 | 11.6 |  |  |  | -0.00243 |  |  |  | AC1-118
237066 | AD1-083 GEN1 | S1 | 0.6 | 201 | Gen | New | 86 | 0 | 1 |  | 102.4 | 0 | 0 | 0 | 0 |  |  |  | -0.00242 |  |  |  | AD1-083
316468 | AD1-105 GEN | 1 | 0.69 | 345 | Gen |  | 87 | 0 | 1 |  | 77.76 | 0 | 0 | 0 | 45.1 |  |  |  | -0.00242 |  |  |  | AD1-105
316095 | T157 G97 | W1 | 0.69 | 345 | Gen |  | 78 | 0 | 1 |  | 51.25 | 0 | 0 | 0 | 16.4 |  |  |  | -0.00241 |  |  |  | T157
316097 | T157 G90 | W1 | 0.69 | 345 | Gen |  | 78 | 0 | 1 |  | 51.25 | 0 | 0 | 0 | 16.4 |  |  |  | -0.00241 |  |  |  | T157
237050 | AF1-155 C | 1 | 46 | 201 | Gen | New | 86 | 0 | 1 |  | 20 | 0 | 0 | 0 | 0 |  |  |  | 0.00239 |  |  |  | AF1-155
316427 | AG1-213 C | B1 | 115 | 345 | Gen | New | 88 | 0 | 1 |  | 10 | 0 | -10 | 0 | 0 |  |  |  | -0.00236 |  |  |  | AG1-213
315673 | AE1-157 C O1 | 1 | 230 | 345 | Gen |  | 87 | 0 | 1 |  | 120 | 0 | 0 | 0 | 69.6 |  |  |  | -0.00234 |  |  |  | AE1-157
316192 | AB2-158 C | 1 | 230 | 345 | Gen |  | 87 | 0 | 1 |  | 98.2 | 0 | 0 | 0 | 56.96 |  |  |  | -0.0023 |  |  |  | AB2-158
316044 | AC1-158 C1 | S1 | 0.6 | 345 | Gen |  | 87 | 0 | 1 |  | 250 | 0 | 0 | 0 | 145 |  |  |  | -0.00226 |  |  |  | AC1-158
316045 | AC1-158 C2 | S1 | 0.6 | 345 | Gen |  | 87 | 0 | 1 |  | 250 | 0 | 0 | 0 | 145 |  |  |  | -0.00226 |  |  |  | AC1-158
316447 | AC1-158 HLD | S1 | 0.6 | 345 | Gen |  | 87 | 0 | 1 |  | 171.89 | 0 | 0 | 0 | 99.7 |  |  |  | -0.00226 |  |  |  | AC1-158
316450 | AC1-158 RIC | S4 | 0.6 | 345 | Gen |  | 87 | 0 | 1 |  | 21.48 | 0 | 0 | 0 | 12.46 |  |  |  | -0.00226 |  |  |  | AC1-158
237061 | AD1-155 C | S1 | 0.6 | 201 | Gen |  | 86 | 0 | 1 |  | 75 | 0 | 0 | 0 | 40.5 |  |  |  | -0.00225 |  |  |  | AD1-155
316164 | AC1-076_C | 1 | 0.6 | 345 | Gen |  | 87 | 0 | 1 |  | 63.22 | 0 | 0 | 0 | 36.67 |  |  |  | -0.00225 |  |  |  | AC1-076
315683 | AE1-153 C | S1 | 0.63 | 345 | Gen |  | 87 | 0 | 1 |  | 149 | 0 | 0 | 0 | 86.42 |  |  |  | -0.00225 |  |  |  | AE1-153
316170 | AC1-121 GEN2 | S1 | 0.6 | 345 | Gen | New | 87 | 0 | 1 |  | 20 | 0 | 0 | 0 | 0 |  |  |  | -0.00224 |  |  |  | AC1-121
316254 | AC1-120 GEN1 | 1 | 0.6 | 345 | Gen | New | 87 | 0 | 1 |  | 60 | 0 | 0 | 0 | 0 |  |  |  | -0.00224 |  |  |  | AC1-120
315651 | AD1-115 GEN | S1 | 115 | 345 | Gen | New | 84 | 0 | 1 |  | 50 | 0 | 0 | 0 | 0 |  |  |  | -0.00224 |  |  |  | AD1-115
316257 | AC1-043 C | 1 | 115 | 345 | Gen | New | 84 | 0 | 1 |  | 100 | 0 | 0 | 0 | 0 |  |  |  | -0.00224 |  |  |  | AC1-043
316267 | AC1-143 C | 1 | 0.38 | 345 | Gen |  | 87 | 0 | 1 |  | 60 | 0 | 0 | 0 | 34.8 |  |  |  | -0.00222 |  |  |  | AC1-143
235464 | 01DTGZ2-030 | 1 | 138 | 201 | Gen |  | 83 | 0 | 1 |  | 10 | 0 | 0 | 0 | 5.3 |  |  |  | -0.00221 |  |  |  | Z2-030
237077 | AC2-174 C | S1 | 138 | 201 | Gen |  | 83 | 0 | 1 |  | 10 | 0 | 0 | 0 | 5.3 |  |  |  | -0.00221 |  |  |  | AC2-174
316006 | AB2-029 C | S1 | 230 | 345 | Gen |  | 84 | 0 | 1 |  | 19.8 | 0 | 0 | 0 | 11.68 |  |  |  | -0.00222 |  |  |  | AB2-029
316029 | AE1-044 GEN | S1 | 0.63 | 345 | Gen | New | 87 | 0 | 1 |  | 200 | 0 | 0 | 0 | 0 |  |  |  | -0.00221 |  |  |  | AE1-044
238147 | AE2-230_GEN1 | S1 | 0.69 | 201 | Gen |  | 86 | 0 | 1 |  | 35 | 0 | 0 | 0 | 18.9 |  |  |  | -0.00218 |  |  |  | AE2-230
238148 | AE2-230_GEN2 | S2 | 0.69 | 201 | Gen |  | 86 | 0 | 1 |  | 35 | 0 | 0 | 0 | 18.9 |  |  |  | -0.00218 |  |  |  | AE2-230
238149 | AF1-291A_GEN | S1 | 0.69 | 201 | Gen |  | 86 | 0 | 1 |  | 10 | 0 | 0 | 0 | 5.4 |  |  |  | -0.00218 |  |  |  | AE2-230
238152 | AF2-075_GEN | S1 | 0.69 | 201 | Gen |  | 86 | 0 | 1 |  | 50 | 0 | 0 | 0 | 27 |  |  |  | -0.00218 |  |  |  | AE2-230
200925 | 26R32 | W1 | 34.5 | 226 | Gen |  | 76 | 0 | 1 |  | 75 | 0 | 0 | 0 | 21.75 |  |  |  | 0.00212 |  |  |  | R32
200888 | 26HIGHLAND | W1 | 34.5 | 226 | Gen |  | 76 | 0 | 1 |  | 65 | 0 | 0 | 0 | 18.85 |  |  |  | 0.00212
200846 | 26FORWARD | W1 | 34.5 | 226 | Gen |  | 76 | 0 | 1 |  | 29.4 | 0 | 0 | 0 | 8.53 |  |  |  | 0.00206
203940 | AF1-140 C | 1 | 23 | 226 | Gen | New | 85 | 0 | 1 |  | 16.3 | 0 | 0 | 0 | 0 |  |  |  | 0.00205 |  |  |  | AF1-140
316411 | AF1-147_GEN1 | S1 | 0.63 | 345 | Gen |  | 87 | 0 | 1 |  | 52.28 | 0 | 0 | 0 | 30.32 |  |  |  | -0.00204 |  |  |  | AF1-147
316415 | AF1-147_GEN2 | S2 | 0.63 | 345 | Gen |  | 87 | 0 | 1 |  | 52.28 | 0 | 0 | 0 | 30.32 |  |  |  | -0.00204 |  |  |  | AF1-147
200915 | 26CHSTN_FL | W1 | 34.5 | 226 | Gen |  | 76 | 0 | 1 |  | 38 | 0 | 0 | 0 | 11.02 |  |  |  | 0.00199
235072 | AD2-158 GEN | S1 | 0.55 | 201 | Gen | New | 86 | 0 | 1 |  | 79.22 | 0 | 0 | 0 | 0 |  |  |  | -0.00199 |  |  |  | AD2-158
203953 | AE2-249 C | 1 | 23 | 226 | Gen | New | 85 | 0 | 1 |  | 16.6 | 0 | 0 | 0 | 0 |  |  |  | 0.00199 |  |  |  | AE2-249
203942 | AF2-270 E | E | 23 | 226 | Gen | New | 82 | 0 | 1 |  | 3.72 | 0 | 0 | 0 | 0 |  |  |  | 0.00199 |  |  |  | AF2-270
235625 | 01BACKB | W1 | 34.5 | 201 | Gen |  | 77 | 0 | 1 |  | 66 | 0 | 0 | 0 | 21.12 |  |  |  | -0.00185
200889 | 26STNY CRK | W1 | 34.5 | 226 | Gen |  | 76 | 0 | 1 |  | 52.5 | 0 | 0 | 0 | 15.23 |  |  |  | 0.00183
203993 | AD2-133_GEN1 | 1 | 0.69 | 226 | Gen |  | 76 | 0 | 1 |  | 87.6 | 0 | 0 | 0 | 25.4 |  |  |  | 0.00182 |  |  |  | AD1-133
200905 | 26Q36 | W1 | 0.69 | 226 | Gen |  | 76 | 0 | 1 |  | 50 | 0 | 0 | 0 | 14.5 |  |  |  | 0.00182 |  |  |  | Q36
203946 | AE2-131 C | S1 | 34.5 | 226 | Gen | New | 85 | 0 | 1 |  | 20 | 0 | 0 | 0 | 0 |  |  |  | 0.0018 |  |  |  | AE2-131
203952 | AE2-129 C | 1 | 34.5 | 226 | Gen |  | 85 | 0 | 1 |  | 20 | 0 | 0 | 0 | 11.2 |  |  |  | 0.0018 |  |  |  | AE2-129
237512 | 01ROTHROCK | W1 | 34.5 | 201 | Gen |  | 77 | 0 | 1 |  | 50 | 0 | 0 | 0 | 16 |  |  |  | -0.0018
226931 | AG1-317 C | B1 | 69 | 233 | Gen | New | 88 | 0 | 1 |  | 1 | 0 | -1 | 0 | 0 |  |  |  | -0.00179 |  |  |  | AG1-317
226921 | AE1-013 C | 1 | 69 | 233 | Gen |  | 82 | 0 | 1 |  | 0.9 | 0 | 0 | 0 | 0.47 |  |  |  | -0.00179 |  |  |  | AE1-013
226929 | AD2-058 C | 1 | 69 | 233 | Gen |  | 82 | 0 | 1 |  | 5.6 | 0 | 0 | 0 | 2.91 |  |  |  | -0.00179 |  |  |  | AD2-058
226930 | AD2-199 C | 1 | 69 | 233 | Gen |  | 82 | 0 | 1 |  | 3 | 0 | 0 | 0 | 1.56 |  |  |  | -0.00179 |  |  |  | AD2-199
238141 | AE2-333 GEN1 | S1 | 0.69 | 201 | Gen |  | 86 | 0 | 1 |  | 50 | 0 | 0 | 0 | 27 |  |  |  | -0.00178 |  |  |  | AE2-333
238142 | AE2-333 GEN2 | S2 | 0.69 | 201 | Gen |  | 86 | 0 | 1 |  | 50 | 0 | 0 | 0 | 27 |  |  |  | -0.00178 |  |  |  | AE2-333
238108 | AE1-109 C1 | S1 | 0.55 | 201 | Gen |  | 83 | 0 | 1 |  | 6.67 | 0 | 0 | 0 | 3.54 |  |  |  | -0.00177 |  |  |  | AE1-109
238109 | AE1-109 C2 | S2 | 0.55 | 201 | Gen |  | 83 | 0 | 1 |  | 6.67 | 0 | 0 | 0 | 3.54 |  |  |  | -0.00177 |  |  |  | AE1-109
238110 | AE1-109 C3 | S3 | 0.55 | 201 | Gen |  | 83 | 0 | 1 |  | 6.67 | 0 | 0 | 0 | 3.54 |  |  |  | -0.00177 |  |  |  | AE1-109
235048 | AD1-125 C1 | 1 | 0.69 | 201 | Gen |  | 77 | 0 | 1 |  | 40 | 0 | 0 | 0 | 12.8 |  |  |  | -0.00173 |  |  |  | AD1-125
235049 | AD1-125 C2 | 1 | 0.69 | 201 | Gen |  | 77 | 0 | 1 |  | 40 | 0 | 0 | 0 | 12.8 |  |  |  | -0.00173 |  |  |  | AD1-125
226936 | AF1-003_GEN1 | S1 | 0.55 | 238 | Gen |  | 82 | 0 | 1 |  | 10 | 0 | 0 | 0 | 5.2 |  |  |  | -0.00172 |  |  |  | AF1-003
226937 | AF1-003_GEN2 | S2 | 0.55 | 238 | Gen |  | 82 | 0 | 1 |  | 10 | 0 | 0 | 0 | 5.2 |  |  |  | -0.00172 |  |  |  | AF1-003
226943 | AF1-005_GEN | S1 | 0.55 | 238 | Gen |  | 82 | 0 | 1 |  | 20 | 0 | 0 | 0 | 10.4 |  |  |  | -0.00172 |  |  |  | AF1-005
227287 | AC2-120 C | 1 | 0.55 | 238 | Gen |  | 82 | 0 | 1 |  | 30 | 0 | 0 | 0 | 15.6 |  |  |  | -0.00172 |  |  |  | AC2-120
237779 | 01MDS_W4-102 | S1 | 34.5 | 201 | Gen |  | 83 | 0 | 1 |  | 20 | 0 | 0 | 0 | 10.6 |  |  |  | -0.0017 |  |  |  | W4-102
238112 | AG1-095 C | S1 | 34.5 | 201 | Gen |  | 86 | 0 | 1 |  | 16 | 0 | 0 | 0 | 8.64 |  |  |  | -0.00171 |  |  |  | AG1-095
203954 | AE2-126 C | 1 | 34.5 | 226 | Gen |  | 85 | 0 | 1 |  | 20 | 0 | 0 | 0 | 11.2 |  |  |  | 0.0017 |  |  |  | AE2-126
203941 | AF2-087 C | S1 | 46 | 226 | Gen | New | 82 | 0 | 1 |  | 7.25 | 0 | 0 | 0 | 0 |  |  |  | 0.0017 |  |  |  | AF2-087
200834 | 26SW_E13_K22 | W1 | 23 | 226 | Gen |  | 76 | 0 | 1 |  | 9 | 0 | 0 | 0 | 2.61 |  |  |  | 0.0017 |  |  |  | K22
226910 | AB2-157 C | 1 | 69 | 233 | Gen |  | 82 | 0 | 1 |  | 2.5 | 0 | 0 | 0 | 1.3 |  |  |  | -0.0017 |  |  |  | AB2-157
235020 | AA1-095 C | S1 | 34.5 | 201 | Gen |  | 86 | 0 | 1 |  | 6.23 | 0 | 0 | 0 | 3.36 |  |  |  | -0.0017 |  |  |  | AA1-095
235004 | AA1-092 C | S1 | 34.5 | 201 | Gen |  | 86 | 0 | 1 |  | 12 | 0 | 0 | 0 | 6.48 |  |  |  | -0.00167 |  |  |  | AA1-092
235025 | AB2-097 E | S1 | 34.5 | 201 | Gen | New | 83 | 0 | 1 |  | 10 | 0 | 0 | 0 | 0 |  |  |  | -0.00167 |  |  |  | AB2-097
237034 | AC2-136 C | S1 | 138 | 201 | Gen | New | 83 | 0 | 1 |  | 11.8 | 0 | 0 | 0 | 0 |  |  |  | -0.00165 |  |  |  | AC2-136
237798 | 01AA1-109 C | S1 | 34.5 | 201 | Gen |  | 83 | 0 | 1 |  | 9 | 0 | 0 | 0 | 4.77 |  |  |  | -0.00162 |  |  |  | Z2-030
237507 | 01CROSSCHOOL | W1 | 34.5 | 201 | Gen |  | 77 | 0 | 1 |  | 85 | 0 | 0 | 0 | 27.2 |  |  |  | -0.0016
237778 | 01MSM_W1-116 | S1 | 34.5 | 201 | Gen |  | 83 | 0 | 1 |  | 14.02 | 0 | 0 | 0 | 7.43 |  |  |  | -0.0016 |  |  |  | W1-116
237080 | AD1-060 C | S1 | 0.41 | 201 | Gen |  | 86 | 0 | 1 |  | 19.4 | 0 | 0 | 0 | 10.48 |  |  |  | -0.00159 |  |  |  | AD1-060
235054 | AD2-180 C | 1 | 0.72 | 201 | Gen |  | 77 | 0 | 1 |  | 111.83 | 0 | 0 | 0 | 35.79 |  |  |  | -0.00159 |  |  |  | AD2-180
203961 | AE2-224 C | S1 | 0.6 | 226 | Gen |  | 85 | 0 | 1 |  | 100 | 0 | 0 | 0 | 56 |  |  |  | 0.00157 |  |  |  | AE2-224
237006 | AB1-125_C | S | 0.6 | 201 | Gen |  | 83 | 0 | 1 |  | 15 | 0 | 0 | 0 | 7.95 |  |  |  | -0.00156 |  |  |  | AB1-125
237025 | AB1-124 C | S1 | 34.5 | 201 | Gen |  | 83 | 0 | 1 |  | 20 | 0 | 0 | 0 | 10.6 |  |  |  | -0.00156 |  |  |  | AB1-124
237030 | AB1-096 C | S1 | 34.5 | 201 | Gen |  | 83 | 0 | 1 |  | 9.9 | 0 | 0 | 0 | 5.25 |  |  |  | -0.00157 |  |  |  | AB1-096
237038 | AE2-054 C | 1 | 34.5 | 201 | Gen |  | 86 | 0 | 1 |  | 20 | 0 | 0 | 0 | 10.8 |  |  |  | -0.00156 |  |  |  | AE2-054
235526 | 01WR_AA1-100 | 1 | 138 | 201 | Gen | New | 88 | 0 | 1 |  | 11 | 0 | -11 | 0 | 0 |  |  |  | -0.00156 |  |  |  | AA1-100
235067 | AD1-061 C | 1 | 0.41 | 201 | Gen |  | 83 | 0 | 1 |  | 21 | 0 | 0 | 0 | 11.13 |  |  |  | -0.00156 |  |  |  | AD1-061
235854 | 01KL_K28_T16 | W1 | 0.69 | 201 | Gen |  | 77 | 0 | 1 |  | 99.9 | 0 | 0 | 0 | 31.97 |  |  |  | -0.00154 |  |  |  | K28
237085 | AD2-009_C | 1 | 0.6 | 201 | Gen |  | 86 | 0 | 1 |  | 70 | 0 | 0 | 0 | 37.8 |  |  |  | -0.00154 |  |  |  | AD2-009
238120 | AE2-309 GEN | B1 | 34.5 | 201 | Gen | New | 88 | 0 | 1 |  | 11.9 | 0 | -11.9 | 0 | 0 |  |  |  | -0.00152 |  |  |  | AE2-309 |  | MFO
235531 | U2-073 GEN | 1 | 34.5 | 201 | Gen |  | 77 | 0 | 1 |  | 138.04 | 0 | 0 | 0 | 44.17 |  |  |  | -0.00152 |  |  |  | U2-073
237037 | AE1-188 C | 1 | 34.5 | 201 | Gen |  | 86 | 0 | 1 |  | 31.9 | 0 | 0 | 0 | 17.23 |  |  |  | -0.00152 |  |  |  | AE1-188
238120 | AE2-309 GEN | S1 | 34.5 | 201 | Gen |  | 83 | 0 | 1 |  | 19.8 | 0 | 0 | 0 | 10.49 |  |  |  | -0.00152 |  |  |  | AE2-309 |  | MFO
200886 | 26ARWF_N39 | W1 | 0.69 | 226 | Gen |  | 76 | 0 | 1 |  | 80 | 0 | 0 | 0 | 23.2 |  |  |  | 0.00151 |  |  |  | N39
203034 | 26NA_O38_P22 | W1 | 0.69 | 226 | Gen |  | 76 | 0 | 1 |  | 65.1 | 0 | 0 | 0 | 18.88 |  |  |  | 0.00151 |  |  |  | P22
223403 | AG1-063 GEN | 1 | 34.5 | 232 | Gen | New | 88 | 0 | 1 |  | 2.5 | 0 | -2.5 | 0 | 0 |  |  |  | -0.00151 |  |  |  | AG1-063
238101 | AF2-275 E | B1 | 34.5 | 201 | Gen | New | 88 | 0 | 1 |  | 1.5 | 0 | -1.5 | 0 | 0 |  |  |  | -0.0015 |  |  |  | AF2-275 |  | MFO
235043 | AF1-166 GEN | S1 | 34.5 | 201 | Gen | New | 86 | 0 | 1 |  | 16 | 0 | 0 | 0 | 0 |  |  |  | -0.0015 |  |  |  | AF1-166
235062 | AE1-101 C1 | 1 | 0.6 | 201 | Gen |  | 86 | 0 | 1 |  | 75 | 0 | 0 | 0 | 40.5 |  |  |  | -0.00151 |  |  |  | AE1-101
235063 | AE1-101 C2 | 1 | 0.48 | 201 | Gen |  | 86 | 0 | 1 |  | 75 | 0 | 0 | 0 | 40.5 |  |  |  | -0.00151 |  |  |  | AE1-101
235073 | AF1-209 C O1 | S1 | 34.5 | 201 | Gen | New | 86 | 0 | 1 |  | 15.9 | 0 | 0 | 0 | 0 |  |  |  | -0.0015 |  |  |  | AF1-209
237001 | AB1-127 C | 1 | 34.5 | 201 | Gen |  | 86 | 0 | 1 |  | 25.8 | 0 | 0 | 0 | 13.93 |  |  |  | -0.0015 |  |  |  | AB1-127
237002 | AB1-128 C | S1 | 34.5 | 201 | Gen |  | 86 | 0 | 1 |  | 25.8 | 0 | 0 | 0 | 13.93 |  |  |  | -0.0015 |  |  |  | AB1-12
238101 | AF2-275 E | E | 34.5 | 201 | Gen | New | 83 | 0 | 1 |  | 3 | 0 | 0 | 0 | 0 |  |  |  | -0.0015 |  |  |  | AF2-275 |  | MFO
238117 | U2-030 | W1 | 0.66 | 201 | Gen |  | 77 | 0 | 1 |  | 40 | 0 | 0 | 0 | 12.8 |  |  |  | -0.0015 |  |  |  | U2-030
238118 | U2-030_1 | W1 | 0.66 | 201 | Gen |  | 77 | 0 | 1 |  | 20 | 0 | 0 | 0 | 6.4 |  |  |  | -0.0015 |  |  |  | U2-030
203944 | AF2-271 E | E | 46 | 226 | Gen | New | 82 | 0 | 1 |  | 3 | 0 | 0 | 0 | 0 |  |  |  | 0.00148 |  |  |  | AF2-271
238126 | S14_GEN_1 | W1 | 0.69 | 201 | Gen |  | 77 | 0 | 1 |  | 35 | 0 | 0 | 0 | 11.2 |  |  |  | -0.00145 |  |  |  | S14
238127 | S14_GEN_2 | W2 | 0.69 | 201 | Gen |  | 77 | 0 | 1 |  | 35 | 0 | 0 | 0 | 11.2 |  |  |  | -0.00145 |  |  |  | S14
203939 | AE1-160 C | 1 | 34.5 | 226 | Gen |  | 85 | 0 | 1 |  | 20 | 0 | 0 | 0 | 11.2 |  |  |  | 0.00143 |  |  |  | AE1-160
203987 | AE2-118 C | S1 | 46 | 226 | Gen |  | 85 | 0 | 1 |  | 20 | 0 | 0 | 0 | 11.2 |  |  |  | 0.00137 |  |  |  | AE2-118
203947 | AF1-006 C | 1 | 34.5 | 226 | Gen |  | 85 | 0 | 1 |  | 20 | 0 | 0 | 0 | 11.2 |  |  |  | -0.00137 |  |  |  | AF1-006
238103 | AF2-293 E | B1 | 46 | 201 | Gen | New | 88 | 0 | 1 |  | 1.5 | 0 | -1.5 | 0 | 0 |  |  |  | 0.00131 |  |  |  | AF2-293 |  | MFO
238103 | AF2-293 E | 1 | 46 | 201 | Gen | New | 83 | 0 | 1 |  | 1.17 | 0 | 0 | 0 | 0 |  |  |  | 0.00131 |  |  |  | AF2-293 |  | MFO
236828 | 01GRAYMONT | 1 | 46 | 201 | Gen | New | 83 | 0 | 1 |  | 4 | 0 | 0 | 0 | 0 |  |  |  | 0.0013
235056 | AG1-142 C | S1 | 69 | 201 | Gen |  | 86 | 0 | 1 |  | 2.5 | 0 | 0 | 0 | 1.35 |  |  |  | 0.0013 |  |  |  | AG1-142
200894 | LAURHILL-G | W1 | 34.5 | 226 | Gen | New | 79 | 0 | 1 |  | 70 | 0 | 0 | 0 | 0 |  |  |  | 0.00128
238104 | AF2-426 E | B1 | 138 | 201 | Gen | New | 88 | 0 | 1 |  | 1.5 | 0 | -1.5 | 0 | 0 |  |  |  | 0.00128 |  |  |  | AF2-426 |  | MFO
238104 | AF2-426 E | E | 138 | 201 | Gen | New | 83 | 0 | 1 |  | 1.17 | 0 | 0 | 0 | 0 |  |  |  | 0.00128 |  |  |  | AF2-426 |  | MFO
203349 | 26Z1-069 C | 1 | 115 | 226 | Gen |  | 76 | 0 | 1 |  | 90 | 0 | 0 | 0 | 26.1 |  |  |  | 0.00127 |  |  |  | Z1-069
235003 | AC1-025 E | 1 | 46 | 201 | Gen | New | 88 | 0 | 1 |  | 1.5 | 0 | -1.5 | 0 | 0 |  |  |  | 0.00126 |  |  |  | AC1-025
237041 | AE2-055 C | 1 | 46 | 201 | Gen |  | 86 | 0 | 1 |  | 20 | 0 | 0 | 0 | 10.8 |  |  |  | 0.00125 |  |  |  | AE2-055
200890 | 26BF_G21_K23 | W1 | 0.6 | 226 | Gen |  | 76 | 0 | 1 |  | 46.8 | 0 | 0 | 0 | 13.57 |  |  |  | 0.00117 |  |  |  | G21
200891 | 26CSLMN_L13 | W1 | 0.57 | 226 | Gen |  | 76 | 0 | 1 |  | 37.9 | 0 | 0 | 0 | 10.99 |  |  |  | 0.00117
200892 | 26LOOKOUT | W1 | 24.9 | 226 | Gen |  | 76 | 0 | 1 |  | 36.9 | 0 | 0 | 0 | 10.7 |  |  |  | 0.00117
203915 | 26BF_Z2-108 | 1 | 0.45 | 226 | Gen | New | 88 | 0 | 1 |  | 18 | 0 | -18 | 0 | 0 |  |  |  | 0.00117 |  |  |  | Z2-108
200835 | 26ARN_Z1-066 | 1 | 25 | 226 | Gen | New | 88 | 0 | 1 |  | 6 | 0 | -6 | 0 | 0 |  |  |  | 0.00117 |  |  |  | Z1-065
200887 | 26ARMNA MT | W1 | 0.69 | 226 | Gen |  | 76 | 0 | 1 |  | 100.5 | 0 | 0 | 0 | 29.15 |  |  |  | 0.00114
238100 | AF2-274 E | B1 | 138 | 201 | Gen | New | 88 | 0 | 1 |  | 1.5 | 0 | -1.5 | 0 | 0 |  |  |  | -0.00113 |  |  |  | AF2-274 |  | MFO
237027 | AG1-315 C | S1 | 138 | 201 | Gen |  | 58 | 0 | 1 |  | 2 | 0 | 0 | 0 | 1.06 |  |  |  | -0.00113 |  |  |  | AG1-315
238100 | AF2-274 E | E | 138 | 201 | Gen | New | 83 | 0 | 1 |  | 3.72 | 0 | 0 | 0 | 0 |  |  |  | -0.00113 |  |  |  | AF2-274 |  | MFO
203951 | AF2-265 C | 1 | 34.5 | 226 | Gen |  | 85 | 0 | 1 |  | 15 | 0 | 0 | 0 | 8.4 |  |  |  | 0.00111 |  |  |  | AF2-265
223401 | AF1-299 C | S1 | 34.5 | 232 | Gen |  | 85 | 0 | 1 |  | 17 | 0 | 0 | 0 | 9.52 |  |  |  | -0.0011 |  |  |  | AF1-299
223402 | AF1-300 C | S1 | 34.5 | 232 | Gen |  | 85 | 0 | 1 |  | 17 | 0 | 0 | 0 | 9.52 |  |  |  | -0.0011 |  |  |  | AF1-300
203948 | AG1-140 C | 1 | 34.5 | 226 | Gen |  | 85 | 0 | 1 |  | 2.62 | 0 | 0 | 0 | 1.47 |  |  |  | -0.00108 |  |  |  | AG1-140
203963 | AG1-253 C | S1 | 34.5 | 226 | Gen |  | 85 | 0 | 1 |  | 4 | 0 | 0 | 0 | 2.24 |  |  |  | -0.00108 |  |  |  | AG1-253
223204 | AA2-072 GEN | S1 | 34.5 | 232 | Gen | New | 82 | 0 | 1 |  | 1.1 | 0 | 0 | 0 | 0 |  |  |  | -0.00104 |  |  |  | AA2-072
237039 | AF1-001 C | 1 | 34.5 | 201 | Gen | New | 83 | 0 | 1 |  | 13.75 | 0 | 0 | 0 | 0 |  |  |  | -0.00101 |  |  |  | AF1-001
203982 | AD2-062_GEN | S1 | 0.6 | 226 | Gen |  | 85 | 0 | 1 |  | 82.15 | 0 | 0 | 0 | 46 |  |  |  | -0.00098 |  |  |  | AD2-062
203950 | AF1-217 C | 1 | 34.5 | 226 | Gen | New | 85 | 0 | 1 |  | 20 | 0 | 0 | 0 | 0 |  |  |  | -0.00093 |  |  |  | AF1-217
203962 | AF1-287 C | S1 | 34.5 | 226 | Gen |  | 85 | 0 | 1 |  | 20 | 0 | 0 | 0 | 11.2 |  |  |  | -0.00093 |  |  |  | AF1-287
205907 | AC1-048 GEN | 1 | 0.39 | 227 | Gen |  | 82 | 0 | 1 |  | 75 | 0 | 0 | 0 | 39 |  |  |  | -0.00093 |  |  |  | AC1-048
208254 | AF2-280 E | E | 12.5 | 229 | Gen | New | 82 | 0 | 1 |  | 3 | 0 | 0 | 0 | 0 |  |  |  | -0.00077 |  |  |  | AF2-280
208856 | AE1-226 GEN | S1 | 69 | 229 | Gen | New | 85 | 0 | 1 |  | 19.8 | 0 | 0 | 0 | 0 |  |  |  | -0.00077 |  |  |  | AE1-226
208923 | BUSO V4-027 | 1 | 12.47 | 229 | Gen |  | 85 | 0 | 1 |  | 5 | 0 | 0 | 0 | 2.8 |  |  |  | -0.00077 |  |  |  | V4-027
200917 | 26MTNTP_P28 | W1 | 0.69 | 226 | Gen |  | 76 | 0 | 1 |  | 150 | 0 | 0 | 0 | 43.5 |  |  |  | 0.00071 |  |  |  | P28
203905 | 26W1-045 C | S1 | 23 | 226 | Gen |  | 85 | 0 | 1 |  | 17.4 | 0 | 0 | 0 | 9.74 |  |  |  | -0.00067 |  |  |  | W1-045
208527 | AF2-279 E | E | 12.5 | 229 | Gen | New | 82 | 0 | 1 |  | 3 | 0 | 0 | 0 | 0 |  |  |  | -0.00065 |  |  |  | AF2-279
208835 | TUHI V3-051 | W1 | 12.47 | 229 | Gen |  | 76 | 0 | 1 |  | 3.2 | 0 | 0 | 0 | 0.93 |  |  |  | -0.00065 |  |  |  | V3-051
208835 | TUHI V3-051 | W2 | 12.47 | 229 | Gen |  | 76 | 0 | 1 |  | 1.6 | 0 | 0 | 0 | 0.46 |  |  |  | -0.00065 |  |  |  | V3-051
205922 | AF2-268 E | E | 115 | 227 | Gen | New | 82 | 0 | 1 |  | 2 | 0 | 0 | 0 | 0 |  |  |  | -0.00061 |  |  |  | AF2-268
205916 | AD1-020 GEN | 1 | 0.6 | 227 | Gen |  | 85 | 0 | 1 |  | 100 | 0 | 0 | 0 | 56 |  |  |  | -0.00061 |  |  |  | AD1-020
205917 | AD1-020 ES | 1 | 0.55 | 227 | Gen | New | 85 | 0 | 1 |  | 21.5 | 0 | 0 | 0 | 0 |  |  |  | -0.00061 |  |  |  | AD1-020
202652 | 26RGH_Y1-033 | W1 | 0.69 | 226 | Gen |  | 76 | 0 | 1 |  | 39.02 | 0 | 0 | 0 | 11.32 |  |  |  | 0.00052 |  |  |  | Y1-033
203955 | AF1-039 C O1 | 1 | 115 | 226 | Gen |  | 85 | 0 | 1 |  | 15 | 0 | 0 | 0 | 8.4 |  |  |  | 0.00052 |  |  |  | AF1-039
205932 | AD2-116_C | 1 | 0.55 | 227 | Gen |  | 85 | 0 | 1 |  | 20 | 0 | 0 | 0 | 11.2 |  |  |  | -0.00049 |  |  |  | AD2-116
205943 | AE1-185 C | S1 | 69 | 227 | Gen |  | 85 | 0 | 1 |  | 20 | 0 | 0 | 0 | 11.2 |  |  |  | -0.00049 |  |  |  | AE1-185
205956 | AE1-196_GEN | S1 | 0.55 | 227 | Gen |  | 85 | 0 | 1 |  | 20.17 | 0 | 0 | 0 | 11.3 |  |  |  | -0.00049 |  |  |  | AE1-196
203980 | AG1-197 GEN | S1 | 34.5 | 226 | Gen |  | 85 | 0 | 1 |  | 15 | 0 | 0 | 0 | 8.4 |  |  |  | -0.00049 |  |  |  | AG1-197
205930 | AF2-099 C | S1 | 115 | 227 | Gen | New | 85 | 0 | 1 |  | 3 | 0 | 0 | 0 | 0 |  |  |  | -0.00049 |  |  |  | AF2-099
205931 | AF2-100 C | S1 | 115 | 227 | Gen | New | 85 | 0 | 1 |  | 3 | 0 | 0 | 0 | 0 |  |  |  | -0.00049 |  |  |  | AF2-100
216407 | AF1-137 C | 1 | 35 | 230 | Gen |  | 85 | 0 | 1 |  | 9.8 | 0 | 0 | 0 | 5.49 |  |  |  | -0.00048 |  |  |  | AF1-137
216408 | AF1-174 C | S1 | 35 | 230 | Gen |  | 85 | 0 | 1 |  | 20 | 0 | 0 | 0 | 11.2 |  |  |  | -0.00048 |  |  |  | AF1-174
233915 | AB1-141 C | 1 | 0.55 | 235 | Gen |  | 85 | 0 | 1 |  | 19.8 | 0 | 0 | 0 | 11.09 |  |  |  | -0.00047 |  |  |  | AB1-141
233918 | AB1-142 C | S1 | 0.55 | 235 | Gen |  | 85 | 0 | 1 |  | 19.8 | 0 | 0 | 0 | 11.09 |  |  |  | -0.00047 |  |  |  | AB1-142
233930 | AB2-032 GEN | S1 | 0.6 | 235 | Gen |  | 85 | 0 | 1 |  | 20 | 0 | 0 | 0 | 11.2 |  |  |  | -0.00047 |  |  |  | AB2-032
233933 | AB2-153 GEN | S1 | 0.6 | 235 | Gen |  | 82 | 0 | 1 |  | 20 | 0 | 0 | 0 | 10.4 |  |  |  | -0.00047 |  |  |  | AB2-153
233935 | AB2-179 C | S1 | 0.38 | 235 | Gen |  | 85 | 0 | 1 |  | 50 | 0 | 0 | 0 | 28 |  |  |  | -0.00047 |  |  |  | AB2-179
233982 | AB2-133 C | S1 | 0.6 | 235 | Gen |  | 85 | 0 | 1 |  | 57.04 | 0 | 0 | 0 | 31.94 |  |  |  | -0.00047 |  |  |  | AB2-133
233961 | AE1-087 GEN | 1 | 0.63 | 235 | Gen | New | 88 | 0 | 1 |  | 20 | 0 | -20 | 0 | 0 |  |  |  | -0.00047 |  |  |  | AE1-087
234011 | AF2-249 BAT | B1 | 69 | 235 | Gen | New | 88 | 0 | 1 |  | 3 | 0 | -3 | 0 | 0 |  |  |  | -0.00047 |  |  |  | AF2-249
233985 | AG1-318 E | B1 | 12.47 | 235 | Gen | New | 88 | 0 | 1 |  | 1 | 0 | -1 | 0 | 0 |  |  |  | -0.00047 |  |  |  | AG1-318
205921 | AF2-151 C | S1 | 115 | 227 | Gen | New | 85 | 0 | 1 |  | 3 | 0 | 0 | 0 | 0 |  |  |  | -0.00047 |  |  |  | AF2-151
232404 | W1-003 C | 1 | 138 | 235 | Gen |  | 85 | 0 | 1 |  | 25.76 | 0 | 0 | 0 | 14.43 |  |  |  | -0.00047 |  |  |  | W1-003
232406 | W1-004 C | 1 | 138 | 235 | Gen |  | 85 | 0 | 1 |  | 25.76 | 0 | 0 | 0 | 14.43 |  |  |  | -0.00047 |  |  |  | W1-004
232408 | W1-005 C | 1 | 138 | 235 | Gen |  | 85 | 0 | 1 |  | 25.76 | 0 | 0 | 0 | 14.43 |  |  |  | -0.00047 |  |  |  | W1-005
232410 | W1-006 C | 1 | 138 | 235 | Gen |  | 85 | 0 | 1 |  | 25.76 | 0 | 0 | 0 | 14.43 |  |  |  | -0.00047 |  |  |  | W1-006
232412 | X1-032 E | 1 | 138 | 235 | Gen | New | 82 | 0 | 1 |  | 4 | 0 | 0 | 0 | 0 |  |  |  | -0.00047 |  |  |  | X1-032
232417 | X3-008 C | 1 | 69 | 235 | Gen |  | 82 | 0 | 1 |  | 20 | 0 | 0 | 0 | 10.4 |  |  |  | -0.00047 |  |  |  | X3-008
232422 | X3-066 C | 1 | 12.47 | 235 | Gen |  | 82 | 0 | 1 |  | 6.8 | 0 | 0 | 0 | 3.54 |  |  |  | -0.00047 |  |  |  | X3-066
232424 | Y1-079 C | 1 | 24.94 | 235 | Gen |  | 82 | 0 | 1 |  | 10 | 0 | 0 | 0 | 5.2 |  |  |  | -0.00047 |  |  |  | Y1-079
232426 | Y1-080 FULL | 1 | 69 | 235 | Gen |  | 82 | 0 | 1 |  | 3.38 | 0 | 0 | 0 | 1.76 |  |  |  | -0.00047 |  |  |  | Y1-080
232428 | Y3-058 C | 1 | 69 | 235 | Gen |  | 85 | 0 | 1 |  | 18.2 | 0 | 0 | 0 | 10.19 |  |  |  | -0.00047 |  |  |  | Y3-058
232432 | Z2-076 C | S1 | 24.94 | 235 | Gen |  | 85 | 0 | 1 |  | 6 | 0 | 0 | 0 | 3.36 |  |  |  | -0.00047 |  |  |  | Z2-076
232434 | Z2-077 C | S1 | 24.94 | 235 | Gen |  | 85 | 0 | 1 |  | 6 | 0 | 0 | 0 | 3.36 |  |  |  | -0.00047 |  |  |  | Z2-077
232436 | AB1-176 C | 1 | 69 | 235 | Gen |  | 82 | 0 | 1 |  | 9 | 0 | 0 | 0 | 4.68 |  |  |  | -0.00047 |  |  |  | AB1-176
233901 | CHERRYDALE C | S1 | 69 | 235 | Gen |  | 82 | 0 | 1 |  | 20 | 0 | 0 | 0 | 10.4 |  |  |  | -0.00047
233906 | AB1-056 C | W1 | 0.69 | 235 | Gen |  | 76 | 0 | 1 |  | 247.8 | 0 | 0 | 0 | 71.86 |  |  |  | -0.00047 |  |  |  | AB1-056
233923 | AA1-102 C | 1 | 0.55 | 235 | Gen |  | 82 | 0 | 1 |  | 151.5 | 0 | 0 | 0 | 78.78 |  |  |  | -0.00047 |  |  |  | AA1-102
233939 | AC1-091 C | S1 | 138 | 235 | Gen |  | 82 | 0 | 1 |  | 19.8 | 0 | 0 | 0 | 10.3 |  |  |  | -0.00046 |  |  |  | AC1-091
233940 | AF2-379 C | S1 | 69 | 235 | Gen |  | 82 | 0 | 1 |  | 3.9 | 0 | 0 | 0 | 2.03 |  |  |  | -0.00047 |  |  |  | AF2-379
233944 | AB2-135 C | 1 | 69 | 235 | Gen |  | 85 | 0 | 1 |  | 64 | 0 | 0 | 0 | 35.84 |  |  |  | -0.00047 |  |  |  | AB2-135
233946 | AB2-136 C | 1 | 69 | 235 | Gen |  | 85 | 0 | 1 |  | 51.1 | 0 | 0 | 0 | 28.62 |  |  |  | -0.00047 |  |  |  | AB2-136
233950 | AC2-186 C | 1 | 0.55 | 235 | Gen |  | 82 | 0 | 1 |  | 10 | 0 | 0 | 0 | 5.2 |  |  |  | -0.00047 |  |  |  | AC2-186
233952 | AC2-187 C | 1 | 0.55 | 235 | Gen |  | 82 | 0 | 1 |  | 20 | 0 | 0 | 0 | 10.4 |  |  |  | -0.00047 |  |  |  | AC2-187
233954 | AC2-188 C | 1 | 0.55 | 235 | Gen |  | 82 | 0 | 1 |  | 20 | 0 | 0 | 0 | 10.4 |  |  |  | -0.00047 |  |  |  | AC2-188
233955 | AB2-172 C | S1 | 0.55 | 235 | Gen |  | 85 | 0 | 1 |  | 50.4 | 0 | 0 | 0 | 28.22 |  |  |  | -0.00047 |  |  |  | AB2-172
233964 | AF2-378 C | S1 | 12.47 | 235 | Gen |  | 82 | 0 | 1 |  | 2.65 | 0 | 0 | 0 | 1.38 |  |  |  | -0.00047 |  |  |  | AF2-378
233968 | AD2-076_C | 1 | 0.39 | 235 | Gen |  | 82 | 0 | 1 |  | 49 | 0 | 0 | 0 | 25.48 |  |  |  | -0.00047 |  |  |  | AD2-076
233970 | AC1-092 C | S1 | 138 | 235 | Gen |  | 82 | 0 | 1 |  | 19.8 | 0 | 0 | 0 | 10.3 |  |  |  | -0.00046 |  |  |  | AC1-092
233971 | AC1-093 C | S1 | 138 | 235 | Gen |  | 82 | 0 | 1 |  | 18.8 | 0 | 0 | 0 | 9.78 |  |  |  | -0.00046 |  |  |  | AC1-093
233972 | AC1-094 C | S1 | 138 | 235 | Gen |  | 82 | 0 | 1 |  | 15.9 | 0 | 0 | 0 | 8.27 |  |  |  | -0.00046 |  |  |  | AC1-094
233973 | AC2-185 C | S1 | 138 | 235 | Gen |  | 82 | 0 | 1 |  | 40 | 0 | 0 | 0 | 20.8 |  |  |  | -0.00046 |  |  |  | AC2-185
233984 | AB2-036 GEN | S1 | 0.38 | 235 | Gen | New | 82 | 0 | 1 |  | 92 | 0 | 0 | 0 | 0 |  |  |  | -0.00047 |  |  |  | AB2-036
233987 | AB2-037 GEN | S1 | 0.38 | 235 | Gen |  | 82 | 0 | 1 |  | 212.5 | 0 | 0 | 0 | 110.5 |  |  |  | -0.00047 |  |  |  | AB2-037
233989 | AG1-360 E | S1 | 138 | 235 | Gen | New | 82 | 0 | 1 |  | 8.75 | 0 | 0 | 0 | 0 |  |  |  | -0.00047 |  |  |  | AG1-360
233994 | AC2-023 GEN | S1 | 0.6 | 235 | Gen |  | 85 | 0 | 1 |  | 46.8 | 0 | 0 | 0 | 26.21 |  |  |  | -0.00047 |  |  |  | AC2-023
234012 | AE2-112_GEN | S1 | 0.39 | 235 | Gen |  | 82 | 0 | 1 |  | 17 | 0 | 0 | 0 | 8.84 |  |  |  | -0.00047 |  |  |  | AE2-112
234014 | AF1-036_GEN | S1 | 0.39 | 235 | Gen |  | 82 | 0 | 1 |  | 20 | 0 | 0 | 0 | 10.4 |  |  |  | -0.00047 |  |  |  | AF1-036
234015 | AF2-250 GEN | S1 | 69 | 235 | Gen |  | 85 | 0 | 1 |  | 1.95 | 0 | 0 | 0 | 1.09 |  |  |  | -0.00047 |  |  |  | AF2-250
234020 | AE2-093_GEN | S1 | 0.39 | 235 | Gen |  | 82 | 0 | 1 |  | 45.98 | 0 | 0 | 0 | 23.91 |  |  |  | -0.00047 |  |  |  | AE2-093
234021 | AF1-015_GEN | S2 | 0.39 | 235 | Gen |  | 82 | 0 | 1 |  | 16.72 | 0 | 0 | 0 | 8.69 |  |  |  | -0.00047 |  |  |  | AF1-015
233990 | AG1-397 GEN | S1 | 69 | 235 | Gen |  | 82 | 0 | 1 |  | 9.97 | 0 | 0 | 0 | 5.18 |  |  |  | -0.00047 |  |  |  | AG1-397 |  | MFO
233990 | AG1-397 GEN | B1 | 69 | 235 | Gen | New | 88 | 0 | 1 |  | 3 | 0 | 0 | 0 | 0 |  |  |  | -0.00047 |  |  |  | AG1-397 |  | MFO
205951 | AE1-129 C | S1 | 0.63 | 227 | Gen |  | 85 | 0 | 1 |  | 79.6 | 0 | 0 | 0 | 44.58 |  |  |  | -0.00045 |  |  |  | AE1-129
203975 | AE1-071-GEN | S1 | 0.6 | 226 | Gen |  | 85 | 0 | 1 |  | 100.1 | 0 | 0 | 0 | 56.06 |  |  |  | -0.00044 |  |  |  | AE1-071
237000 | AF2-398 C | S1 | 138 | 201 | Gen |  | 86 | 0 | 1 |  | 3 | 0 | 0 | 0 | 1.62 |  |  |  | 0.00043 |  |  |  | AF2-398
205920 | AF2-101 C | S1 | 115 | 227 | Gen | New | 85 | 0 | 1 |  | 3 | 0 | 0 | 0 | 0 |  |  |  | -0.00041 |  |  |  | AF2-101
228260 | V4-054C | 1 | 12.9 | 234 | Gen |  | 82 | 0 | 1 |  | 10 | 0 | 0 | 0 | 5.2 |  |  |  | -0.00041 |  |  |  | V4-054C
228261 | V4-054E | 1 | 12.9 | 234 | Gen | New | 82 | 0 | 1 |  | 6.2 | 0 | 0 | 0 | 0 |  |  |  | -0.00041 |  |  |  | V4-054E
228351 | V2-046C | 1 | 12.9 | 234 | Gen |  | 82 | 0 | 1 |  | 20.7 | 0 | 0 | 0 | 10.76 |  |  |  | -0.00041 |  |  |  | V2-046
228711 | V2-041C | 1 | 13.2 | 234 | Gen |  | 85 | 0 | 1 |  | 4 | 0 | 0 | 0 | 2.24 |  |  |  | -0.00041 |  |  |  | V2-041C
228712 | V2-041E | 1 | 13.2 | 234 | Gen | New | 85 | 0 | 1 |  | 2.48 | 0 | 0 | 0 | 0 |  |  |  | -0.00041 |  |  |  | V2-041
230430 | AE1-229 GEN | S1 | 0.63 | 234 | Gen |  | 85 | 0 | 1 |  | 151.2 | 0 | 0 | 0 | 84.67 |  |  |  | -0.00041 |  |  |  | AE1-229
230452 | AE1-240_GEN | 1 | 0.63 | 234 | Gen |  | 85 | 0 | 1 |  | 50.4 | 0 | 0 | 0 | 28.22 |  |  |  | -0.00041 |  |  |  | AE1-240
230447 | AE1-061 GEN | 1 | 12.9 | 234 | Gen | New | 88 | 0 | 1 |  | 5.5 | 0 | -5.5 | 0 | 0 |  |  |  | -0.00041 |  |  |  | AE1-061
219240 | MANTUACREK E | BA | 26.4 | 231 | Gen | New | 88 | 0 | 1 |  | 2 | 0 | -2 | 0 | 0 |  |  |  | -0.0004
219726 | BAT.STORG E | BA | 13.2 | 231 | Gen | New | 88 | 0 | 1 |  | 1 | 0 | -1 | 0 | 0 |  |  |  | -0.0004
219137 | THOSOLAR C | 1 | 13.2 | 231 | Gen |  | 82 | 0 | 1 |  | 8.67 | 0 | 0 | 0 | 4.51 |  |  |  | -0.00041
219258 | KINSLEYDEP C | 1 | 13.2 | 231 | Gen |  | 82 | 0 | 1 |  | 5.76 | 0 | 0 | 0 | 2.99 |  |  |  | -0.0004
219623 | KINSLEYBEA C | 1 | 13.2 | 231 | Gen |  | 82 | 0 | 1 |  | 5.11 | 0 | 0 | 0 | 2.66 |  |  |  | -0.0004
219766 | PARADISE C | 1 | 26.4 | 231 | Gen |  | 82 | 0 | 1 |  | 5.1 | 0 | 0 | 0 | 2.65 |  |  |  | -0.0004
219904 | AC1-010 C | S1 | 26.4 | 231 | Gen |  | 82 | 0 | 1 |  | 6 | 0 | 0 | 0 | 3.12 |  |  |  | -0.0004 |  |  |  | AC1-010
219912 | AD2-042 C | 1 | 26.4 | 231 | Gen |  | 82 | 0 | 1 |  | 13.2 | 0 | 0 | 0 | 6.86 |  |  |  | -0.0004 |  |  |  | AD2-042
219914 | AD2-027 C | 1 | 26.4 | 231 | Gen |  | 82 | 0 | 1 |  | 10 | 0 | 0 | 0 | 5.2 |  |  |  | -0.0004 |  |  |  | AD2-027
219917 | AB1-063 E | E | 13.2 | 231 | Gen | New | 82 | 0 | 1 |  | 0.4 | 0 | 0 | 0 | 0 |  |  |  | -0.0004 |  |  |  | AB1-063
219921 | AF1-264 | 1 | 13.2 | 231 | Gen |  | 82 | 0 | 1 |  | 4.3 | 0 | 0 | 0 | 2.24 |  |  |  | -0.0004 |  |  |  | AF1-264
227841 | ONTRIO 4 | W1 | 12.9 | 234 | Gen | New | 76 | 0 | 1 |  | 7.5 | 0 | 0 | 0 | 0 |  |  |  | -0.0004
227927 | V4-067C | 1 | 12.9 | 234 | Gen |  | 82 | 0 | 1 |  | 2.6 | 0 | 0 | 0 | 1.35 |  |  |  | -0.0004 |  |  |  | V4-067
228720 | V2-035C | 1 | 12.9 | 234 | Gen |  | 82 | 0 | 1 |  | 2 | 0 | 0 | 0 | 1.04 |  |  |  | -0.00041 |  |  |  | V2-035
228728 | W1-130C | 1 | 12.9 | 234 | Gen |  | 82 | 0 | 1 |  | 8.9 | 0 | 0 | 0 | 4.63 |  |  |  | -0.00041 |  |  |  | W1-130
228729 | W2-030 C | 1 | 12.9 | 234 | Gen |  | 82 | 0 | 1 |  | 9.65 | 0 | 0 | 0 | 5.02 |  |  |  | -0.0004 |  |  |  | W2-030
228754 | AB1-001 C | S1 | 12.9 | 234 | Gen |  | 82 | 0 | 1 |  | 2.3 | 0 | 0 | 0 | 1.2 |  |  |  | -0.0004 |  |  |  | AB1-001
230407 | AD2-065_C | 1 | 12.9 | 234 | Gen |  | 82 | 0 | 1 |  | 4.11 | 0 | 0 | 0 | 2.14 |  |  |  | -0.00041 |  |  |  | AD2-065
230409 | AE1-218 C | 1 | 12.9 | 234 | Gen |  | 82 | 0 | 1 |  | 2 | 0 | 0 | 0 | 1.04 |  |  |  | -0.00041 |  |  |  | AE1-218
230414 | AF1-041 E | 1 | 69 | 234 | Gen | New | 82 | 0 | 1 |  | 2.4 | 0 | 0 | 0 | 0 |  |  |  | -0.0004 |  |  |  | AF1-041
230415 | AB2-049 C | S1 | 69 | 234 | Gen |  | 82 | 0 | 1 |  | 7.34 | 0 | 0 | 0 | 3.82 |  |  |  | -0.00041 |  |  |  | AB2-049
230422 | AE1-104_GEN1 | 1 | 3.1 | 234 | Gen |  | 79 | 0 | 1 |  | 216 | 0 | 0 | 0 | 99.36 |  |  |  | -0.00041 |  |  |  | AE1-104
230425 | AE1-104_GEN2 | 1 | 3.1 | 234 | Gen |  | 79 | 0 | 1 |  | 216 | 0 | 0 | 0 | 99.36 |  |  |  | -0.00041 |  |  |  | AE1-104
230433 | AD2-135 GEN | S1 | 69 | 234 | Gen |  | 82 | 0 | 1 |  | 1.62 | 0 | 0 | 0 | 0.84 |  |  |  | -0.00041 |  |  |  | AD2-135
230434 | AG1-499 GEN | S1 | 12.9 | 234 | Gen |  | 85 | 0 | 1 |  | 10 | 0 | 0 | 0 | 5.6 |  |  |  | -0.00041 |  |  |  | AG1-499
230446 | AE2-334_GEN | S1 | 0.6 | 234 | Gen |  | 85 | 0 | 1 |  | 44 | 0 | 0 | 0 | 24.64 |  |  |  | -0.00041 |  |  |  | AE2-334
940361 | AE2-020 | 1 | 230 | 234 | Gen |  | 79 | 0 | 1 |  | 604.8 | 0 | 0 | 0 | 278.21 |  |  |  | -0.0004 |  |  |  | AE2-020
940371 | AE2-021 | 1 | 230 | 234 | Gen |  | 79 | 0 | 1 |  | 604.8 | 0 | 0 | 0 | 278.21 |  |  |  | -0.0004 |  |  |  | AE2-021
940381 | AE2-022 | 1 | 230 | 234 | Gen |  | 79 | 0 | 1 |  | 300 | 0 | 0 | 0 | 138 |  |  |  | -0.0004 |  |  |  | AE2-022
218660 | EHAMPSOLAR C | 1 | 13.2 | 231 | Gen |  | 82 | 0 | 1 |  | 2.9 | 0 | 0 | 0 | 1.51 |  |  |  | -0.0004
219236 | SOUTHERNHQ C | 1 | 13.2 | 231 | Gen |  | 82 | 0 | 1 |  | 0.93 | 0 | 0 | 0 | 0.48 |  |  |  | -0.0004
219272 | CLEANLIGHT C | 1 | 13.2 | 231 | Gen |  | 82 | 0 | 1 |  | 2.8 | 0 | 0 | 0 | 1.46 |  |  |  | -0.0004
219287 | REEVESEAST C | 1 | 13.2 | 231 | Gen |  | 82 | 0 | 1 |  | 11 | 0 | 0 | 0 | 5.72 |  |  |  | -0.00039
219291 | REEVESSOUT C | 1 | 13.2 | 231 | Gen |  | 82 | 0 | 1 |  | 1 | 0 | 0 | 0 | 0.52 |  |  |  | -0.0004
219615 | MILLCREEK C | 1 | 13.2 | 231 | Gen |  | 82 | 0 | 1 |  | 3.5 | 0 | 0 | 0 | 1.82 |  |  |  | -0.00039
219686 | LUMSOLAR_N C | 1 | 13.2 | 231 | Gen |  | 82 | 0 | 1 |  | 3.4 | 0 | 0 | 0 | 1.77 |  |  |  | -0.00039
219688 | LUMSOLAR_S C | 1 | 13.2 | 231 | Gen |  | 82 | 0 | 1 |  | 3.4 | 0 | 0 | 0 | 1.77 |  |  |  | -0.00039
219906 | AC1-017 C | S1 | 13.2 | 231 | Gen |  | 82 | 0 | 1 |  | 3.71 | 0 | 0 | 0 | 1.93 |  |  |  | -0.00039 |  |  |  | AC1-017
219907 | AC1-030 C | S1 | 13 | 231 | Gen |  | 82 | 0 | 1 |  | 2.5 | 0 | 0 | 0 | 1.3 |  |  |  | -0.0004 |  |  |  | AC1-030
219927 | AG1-080 C O1 | S1 | 69 | 231 | Gen |  | 82 | 0 | 1 |  | 19.9 | 0 | 0 | 0 | 10.35 |  |  |  | -0.0004 |  |  |  | AG1-080
219924 | AG1-130 C | B1 | 26.4 | 231 | Gen | New | 88 | 0 | 1 |  | 5 | 0 | -5 | 0 | 0 |  |  |  | -0.00039 |  |  |  | AG1-130
208862 | AG1-362 C | S1 | 12.47 | 229 | Gen |  | 85 | 0 | 1 |  | 5 | 0 | 0 | 0 | 2.8 |  |  |  | -0.00039 |  |  |  | AG1-362
214067 | T20SOLAR | 1 | 0.48 | 230 | Gen |  | 82 | 0 | 1 |  | 3.3 | 0 | 0 | 0 | 1.72 |  |  |  | -0.00038 |  |  |  | T20
219304 | NAMERICA C | 1 | 26.4 | 231 | Gen |  | 82 | 0 | 1 |  | 7.9 | 0 | 0 | 0 | 4.11 |  |  |  | -0.00039
219348 | LDSOLAR C | 1 | 26.4 | 231 | Gen |  | 82 | 0 | 1 |  | 10 | 0 | 0 | 0 | 5.2 |  |  |  | -0.00039
219607 | WPEMNERT C | 1 | 26.4 | 231 | Gen |  | 82 | 0 | 1 |  | 7 | 0 | 0 | 0 | 3.64 |  |  |  | -0.00039
219610 | FLORENCE C | 1 | 26.4 | 231 | Gen |  | 82 | 0 | 1 |  | 16.1 | 0 | 0 | 0 | 8.37 |  |  |  | -0.00039
207150 | 28HAN_X4-015 | S1 | 34.5 | 228 | Gen |  | 82 | 0 | 1 |  | 5 | 0 | 0 | 0 | 2.6 |  |  |  | -0.00037 |  |  |  | X4-015
207160 | 28EGP_W2-019 | S1 | 34.5 | 228 | Gen |  | 82 | 0 | 1 |  | 6 | 0 | 0 | 0 | 3.12 |  |  |  | -0.00037 |  |  |  | W2-019
207164 | 28NHV_W2-082 | S1 | 34.5 | 228 | Gen |  | 82 | 0 | 1 |  | 17 | 0 | 0 | 0 | 8.84 |  |  |  | -0.00037 |  |  |  | W2-082
207207 | 28JCB_W1-129 | S1 | 34.5 | 228 | Gen |  | 82 | 0 | 1 |  | 5 | 0 | 0 | 0 | 2.6 |  |  |  | -0.00037 |  |  |  | W1-129
207208 | 28JCB_W4-025 | S1 | 34.5 | 228 | Gen |  | 82 | 0 | 1 |  | 7 | 0 | 0 | 0 | 3.64 |  |  |  | -0.00037 |  |  |  | W4-025
207400 | 28PL_AA1-060 | BA | 34.5 | 228 | Gen | New | 88 | 0 | 1 |  | 20 | 0 | -20 | 0 | 0 |  |  |  | -0.00037 |  |  |  | AA1-060
207149 | 28UPF_X1-085 | S1 | 34.5 | 228 | Gen |  | 82 | 0 | 1 |  | 5 | 0 | 0 | 0 | 2.6 |  |  |  | -0.00036 |  |  |  | X1-085
207157 | 28PEM_W1-119 | S1 | 34.5 | 228 | Gen |  | 82 | 0 | 1 |  | 8.8 | 0 | 0 | 0 | 4.58 |  |  |  | -0.00037 |  |  |  | W1-119
207158 | 28PEM_W1-120 | S1 | 34.5 | 228 | Gen |  | 82 | 0 | 1 |  | 8.8 | 0 | 0 | 0 | 4.58 |  |  |  | -0.00037 |  |  |  | W1-120
207171 | 28DIX_Z2-102 | S1 | 34.5 | 228 | Gen |  | 82 | 0 | 1 |  | 13 | 0 | 0 | 0 | 6.76 |  |  |  | -0.00037 |  |  |  | Z2-102
207445 | AB1-138 C | S | 0.38 | 228 | Gen |  | 82 | 0 | 1 |  | 9.6 | 0 | 0 | 0 | 4.99 |  |  |  | -0.00036 |  |  |  | AB1-138
207450 | AB1-163 E | E | 34.5 | 228 | Gen | New | 82 | 0 | 1 |  | 5 | 0 | 0 | 0 | 0 |  |  |  | -0.00036 |  |  |  | AB1-163
207459 | AE1-142 C | 1 | 34.5 | 228 | Gen |  | 82 | 0 | 1 |  | 20 | 0 | 0 | 0 | 10.4 |  |  |  | -0.00036 |  |  |  | AE1-142
207487 | AE2-000G4 | W4 | 3.1 | 228 | Gen |  | 79 | 0 | 1 |  | 204 | 0 | 0 | 0 | 93.84 |  |  |  | -0.00037 |  |  |  | AE2-000
207497 | AE2-000G2 | W2 | 3.1 | 228 | Gen |  | 79 | 0 | 1 |  | 204 | 0 | 0 | 0 | 93.84 |  |  |  | -0.00037 |  |  |  | AE2-000
207500 | AE2-000G1 | W1 | 3.1 | 228 | Gen |  | 79 | 0 | 1 |  | 204 | 0 | 0 | 0 | 93.84 |  |  |  | -0.00037 |  |  |  | AE2-000
207507 | AE2-000G3 | W3 | 3.1 | 228 | Gen |  | 79 | 0 | 1 |  | 204 | 0 | 0 | 0 | 93.84 |  |  |  | -0.00037 |  |  |  | AE2-000
219114 | HARTZY_C | 1 | 13.2 | 231 | Gen |  | 82 | 0 | 1 |  | 7.57 | 0 | 0 | 0 | 3.94 |  |  |  | -0.00037
219727 | YARDVSOLFA C | 1 | 13.2 | 231 | Gen |  | 82 | 0 | 1 |  | 8.67 | 0 | 0 | 0 | 4.51 |  |  |  | -0.00036
207451 | AA2-048 E | BA | 34.5 | 228 | Gen | New | 88 | 0 | 1 |  | 7 | 0 | -7 | 0 | 0 |  |  |  | -0.00035 |  |  |  | AA2-048
205925 | AF2-428 E | E | 69 | 227 | Gen | New | 82 | 0 | 1 |  | 3 | 0 | 0 | 0 | 0 |  |  |  | -0.00035 |  |  |  | AF2-428
206416 | 28MLH_W1-032 | S1 | 230 | 228 | Gen |  | 82 | 0 | 1 |  | 3 | 0 | 0 | 0 | 1.56 |  |  |  | -0.00035 |  |  |  | W1-032
207145 | 28FRN_Y2-051 | S1 | 34.5 | 228 | Gen |  | 82 | 0 | 1 |  | 5 | 0 | 0 | 0 | 2.6 |  |  |  | -0.00035 |  |  |  | Y2-051
207148 | 28MDF_W3-079 | S1 | 34.5 | 228 | Gen |  | 82 | 0 | 1 |  | 8 | 0 | 0 | 0 | 4.16 |  |  |  | -0.00035 |  |  |  | W3-079
219276 | PARKLANDSO C | 1 | 26.4 | 231 | Gen |  | 82 | 0 | 1 |  | 7.84 | 0 | 0 | 0 | 4.08 |  |  |  | -0.00036
219620 | RIDERU C | 1 | 13.2 | 231 | Gen |  | 82 | 0 | 1 |  | 0.7 | 0 | 0 | 0 | 0.37 |  |  |  | -0.00036
219680 | HOPEWELLV C | 1 | 13.2 | 231 | Gen |  | 82 | 0 | 1 |  | 1.7 | 0 | 0 | 0 | 0.88 |  |  |  | -0.00035
219817 | TRENTONSOL C | 1 | 13.2 | 231 | Gen |  | 82 | 0 | 1 |  | 8.67 | 0 | 0 | 0 | 4.51 |  |  |  | -0.00036
219918 | AC2-009 C | S1 | 13.2 | 231 | Gen |  | 82 | 0 | 1 |  | 0.59 | 0 | 0 | 0 | 0.31 |  |  |  | -0.00035 |  |  |  | AC2-009
207419 | AB2-139 E | 1 | 34.5 | 228 | Gen | New | 88 | 0 | 1 |  | 0.21 | 0 | -0.21 | 0 | 0 |  |  |  | -0.00035 |  |  |  | AB2-139
205923 | AF2-272 E | E | 69 | 227 | Gen | New | 82 | 0 | 1 |  | 3 | 0 | 0 | 0 | 0 |  |  |  | -0.00035 |  |  |  | AF2-272
205924 | AF2-281 E | E | 69 | 227 | Gen | New | 82 | 0 | 1 |  | 3 | 0 | 0 | 0 | 0 |  |  |  | -0.00035 |  |  |  | AF2-281
205926 | AF2-429 E | E | 34.5 | 227 | Gen | New | 82 | 0 | 1 |  | 3.72 | 0 | 0 | 0 | 0 |  |  |  | -0.00035 |  |  |  | AF2-429
205927 | AF2-430 E | E | 69 | 227 | Gen | New | 82 | 0 | 1 |  | 3 | 0 | 0 | 0 | 0 |  |  |  | -0.00035 |  |  |  | AF2-430
205928 | AF2-431 E | E | 69 | 227 | Gen | New | 82 | 0 | 1 |  | 1.17 | 0 | 0 | 0 | 0 |  |  |  | -0.00034 |  |  |  | AF2-431
205941 | AD2-115 C | 1 | 0.55 | 227 | Gen |  | 85 | 0 | 1 |  | 20 | 0 | 0 | 0 | 11.2 |  |  |  | -0.00034 |  |  |  | AD2-115
207143 | 28BYD_X4-031 | E | 34.5 | 228 | Gen |  | 82 | 0 | 1 |  | 2 | 0 | 0 | 0 | 1.04 |  |  |  | -0.00035 |  |  |  | X4-031
207144 | 28HOW_X1-037 | S1 | 34.5 | 228 | Gen |  | 82 | 0 | 1 |  | 14.74 | 0 | 0 | 0 | 7.66 |  |  |  | -0.00035 |  |  |  | X1-037
207152 | 28NPK_W1-113 | S1 | 34.5 | 228 | Gen |  | 82 | 0 | 1 |  | 7.8 | 0 | 0 | 0 | 4.06 |  |  |  | -0.00035 |  |  |  | W1-113
207162 | 28APLW2-078 | S1 | 34.5 | 228 | Gen |  | 82 | 0 | 1 |  | 8.7 | 0 | 0 | 0 | 4.52 |  |  |  | -0.00035 |  |  |  | W1-113
207204 | 28HOL_W1-112 | S1 | 34.5 | 228 | Gen |  | 82 | 0 | 1 |  | 3.65 | 0 | 0 | 0 | 1.9 |  |  |  | -0.00034 |  |  |  | W1-112
207205 | 28MAN_W1-024 | S1 | 34.5 | 228 | Gen |  | 82 | 0 | 1 |  | 3.8 | 0 | 0 | 0 | 1.98 |  |  |  | -0.00035 |  |  |  | W1-024
207206 | 28TIN_W1-124 | S1 | 34.5 | 228 | Gen |  | 82 | 0 | 1 |  | 16.9 | 0 | 0 | 0 | 8.79 |  |  |  | -0.00035 |  |  |  | W1-124
207420 | 28HF_AC1-207 | S1 | 34.5 | 228 | Gen |  | 82 | 0 | 1 |  | 13.1 | 0 | 0 | 0 | 6.81 |  |  |  | -0.00035 |  |  |  | AC1-207
207464 | AA2-184 E | 1 | 34.5 | 228 | Gen |  | 82 | 0 | 1 |  | 20 | 0 | 0 | 0 | 10.4 |  |  |  | -0.00035 |  |  |  | AA2-184
210323 | AF2-286 E | E | 13.8 | 229 | Gen | New | 82 | 0 | 1 |  | 3 | 0 | 0 | 0 | 0 |  |  |  | -0.00035 |  |  |  | AF2-286
217197 | RE CRAN C | 1 | 13 | 231 | Gen |  | 82 | 0 | 1 |  | 5 | 0 | 0 | 0 | 2.6 |  |  |  | -0.00034
218438 | BLK ROCK C | 1 | 13 | 231 | Gen |  | 82 | 0 | 1 |  | 2.36 | 0 | 0 | 0 | 1.23 |  |  |  | -0.00034
219612 | MATRIX C | 1 | 13.2 | 231 | Gen |  | 82 | 0 | 1 |  | 2.85 | 0 | 0 | 0 | 1.48 |  |  |  | -0.00034
219879 | V2-009 C4 | 1 | 13.2 | 231 | Gen |  | 82 | 0 | 1 |  | 4.03 | 0 | 0 | 0 | 2.1 |  |  |  | -0.00035 |  |  |  | V2-009
219880 | V2-009 C3 | 1 | 13.2 | 231 | Gen |  | 82 | 0 | 1 |  | 4.03 | 0 | 0 | 0 | 2.1 |  |  |  | -0.00035 |  |  |  | V2-009
219882 | V2-009 C2 | 1 | 13.2 | 231 | Gen |  | 82 | 0 | 1 |  | 4.03 | 0 | 0 | 0 | 2.1 |  |  |  | -0.00034 |  |  |  | V2-009
219884 | V2-009 C1 | 1 | 13.2 | 231 | Gen |  | 82 | 0 | 1 |  | 4.03 | 0 | 0 | 0 | 2.1 |  |  |  | -0.00034 |  |  |  | V2-009
219922 | AF2-168 E | 1 | 69 | 231 | Gen | New | 82 | 0 | 1 |  | 0.9 | 0 | 0 | 0 | 0 |  |  |  | -0.00035 |  |  |  | AF2-168
967451 | AG2-055 | 1 | 500 | 225 | Gen | New | 79 | 0 | 1 |  | 1148 | 0 | 0 | 0 | 0 |  |  |  | -0.00034 |  |  |  | AG2-055
7 | G-007 |  |  |  | LTF | [5 empty] | 105 | 0 | 0 | 0 |  |  |  |  | 0.0003
219916 | AD2-025 E | 1 | 13.2 | 231 | Gen | New | 88 | 0 | 1 |  | 2 | 0 | -2 | 0 | 0 |  |  |  | -0.00033 |  |  |  | AD2-025
206755 | 28CPH_W2-050 | S1 | 34.5 | 228 | Gen | New | 82 | 0 | 1 |  | 8 | 0 | 0 | 0 | 0 |  |  |  | -0.00033 |  |  |  | W2-050
207169 | 28W4-060COL | S1 | 34.5 | 228 | Gen |  | 82 | 0 | 1 |  | 10 | 0 | 0 | 0 | 5.2 |  |  |  | -0.00034 |  |  |  | W4-06
217198 | V3-058 E | 1 | 26.4 | 231 | Gen | New | 82 | 0 | 1 |  | 2 | 0 | 0 | 0 | 0 |  |  |  | -0.00034 |  |  |  | V3-058
217199 | V3-059 E | 1 | 26.4 | 231 | Gen | New | 82 | 0 | 1 |  | 2 | 0 | 0 | 0 | 0 |  |  |  | -0.00034 |  |  |  | V3-059
218526 | CNTRALGAS2 C | 1 | 13.2 | 231 | Gen |  | 82 | 0 | 1 |  | 8.67 | 0 | 0 | 0 | 4.51 |  |  |  | -0.00033
219903 | AB2-057 C | S1 | 26 | 231 | Gen |  | 82 | 0 | 1 |  | 10 | 0 | 0 | 0 | 5.2 |  |  |  | -0.00034 |  |  |  | AB2-057
207474 | AD2-213 E O1 | B1 | 34.5 | 228 | Gen | New | 88 | 0 | 1 |  | 20 | 0 | -20 | 0 | 0 |  |  |  | -0.00032 |  |  |  | AD2-213
219920 | AE1-041 EBAT | BA | 26.4 | 231 | Gen | New | 88 | 0 | 1 |  | 0.5 | 0 | -0.5 | 0 | 0 |  |  |  | -0.00033 |  |  |  | AE1-041
206736 | 28F1S_V4-069 | S1 | 34.5 | 228 | Gen |  | 82 | 0 | 1 |  | 3 | 0 | 0 | 0 | 1.56 |  |  |  | -0.00032 |  |  |  | V4-069
206737 | 28F2S_V4-070 | S1 | 34.5 | 228 | Gen |  | 82 | 0 | 1 |  | 3 | 0 | 0 | 0 | 1.56 |  |  |  | -0.00032 |  |  |  | V4-070
206738 | 28FLE_V3-070 | S1 | 34.5 | 228 | Gen |  | 82 | 0 | 1 |  | 8 | 0 | 0 | 0 | 4.16 |  |  |  | -0.00033 |  |  |  | V3-070
206744 | 28PIT_W1-132 | S1 | 34.5 | 228 | Gen | New | 82 | 0 | 1 |  | 2 | 0 | 0 | 0 | 0 |  |  |  | -0.00032 |  |  |  | W1-132
206754 | 28EAM_W2-061 | S1 | 34.5 | 228 | Gen |  | 82 | 0 | 1 |  | 2.76 | 0 | 0 | 0 | 1.43 |  |  |  | -0.00032 |  |  |  | W2-061
206761 | 28MHD_W3-029 | S1 | 34.5 | 228 | Gen |  | 82 | 0 | 1 |  | 13.7 | 0 | 0 | 0 | 7.12 |  |  |  | -0.00032 |  |  |  | W3-029
206764 | 28JCR_X2-075 | S1 | 34.5 | 228 | Gen |  | 82 | 0 | 1 |  | 6 | 0 | 0 | 0 | 3.12 |  |  |  | -0.00032 |  |  |  | X2-075
207482 | AE1-156 | S1 | 34.5 | 228 | Gen |  | 82 | 0 | 1 |  | 17.6 | 0 | 0 | 0 | 9.15 |  |  |  | -0.00032 |  |  |  | AE1-156
207483 | W3-003 E | E | 34.5 | 228 | Gen | New | 82 | 0 | 1 |  | 10 | 0 | 0 | 0 | 0 |  |  |  | -0.00032 |  |  |  | W3-003
211089 | AF2-277 E | E | 12.5 | 229 | Gen | New | 82 | 0 | 1 |  | 2 | 0 | 0 | 0 | 0 |  |  |  | -0.00032 |  |  |  | AF2-277
217213 | AMBOY SO C | S1 | 13.2 | 231 | Gen |  | 82 | 0 | 1 |  | 2.3 | 0 | 0 | 0 | 1.2 |  |  |  | -0.00033
218428 | ETC SOLAR C | 1 | 13.2 | 231 | Gen |  | 82 | 0 | 1 |  | 0.57 | 0 | 0 | 0 | 0.29 |  |  |  | -0.00033
218440 | SUMMTASSOC C | 1 | 13 | 231 | Gen |  | 82 | 0 | 1 |  | 2 | 0 | 0 | 0 | 1.04 |  |  |  | -0.00033
218524 | CNTRALGAS1 C | 1 | 13.2 | 231 | Gen |  | 82 | 0 | 1 |  | 8.67 | 0 | 0 | 0 | 4.51 |  |  |  | -0.00033
219249 | CENTRALDIV C | 1 | 13.2 | 231 | Gen |  | 82 | 0 | 1 |  | 0.76 | 0 | 0 | 0 | 0.4 |  |  |  | -0.00033
219908 | AB1-139 C | S1 | 26.4 | 231 | Gen |  | 82 | 0 | 1 |  | 6.6 | 0 | 0 | 0 | 3.43 |  |  |  | -0.00033 |  |  |  | AB1-139
219919 | AE1-041 C | S1 | 26.4 | 231 | Gen |  | 82 | 0 | 1 |  | 1.1 | 0 | 0 | 0 | 0.57 |  |  |  | -0.00033 |  |  |  | AE1-041
206718 | 28STAW2-080 | S1 | 34.5 | 228 | Gen |  | 82 | 0 | 1 |  | 2 | 0 | 0 | 0 | 1.04 |  |  |  | -0.00032 |  |  |  | 28STAW2
206745 | 28F3S_W2-016 | S1 | 34.5 | 228 | Gen |  | 82 | 0 | 1 |  | 15 | 0 | 0 | 0 | 7.8 |  |  |  | -0.00032 |  |  |  | W2-016
217081 | WEATEXAS C | 1 | 13.2 | 231 | Gen |  | 82 | 0 | 1 |  | 1.4 | 0 | 0 | 0 | 0.73 |  |  |  | -0.00031
217202 | FBANKSOLAR C | 1 | 13.2 | 231 | Gen |  | 82 | 0 | 1 |  | 1.01 | 0 | 0 | 0 | 0.53 |  |  |  | -0.00031
217209 | CENTRL HS C | 1 | 13.8 | 231 | Gen |  | 82 | 0 | 1 |  | 0.8 | 0 | 0 | 0 | 0.42 |  |  |  | -0.00031
217211 | CAMDEN ST C | 1 | 13.8 | 231 | Gen |  | 82 | 0 | 1 |  | 0.43 | 0 | 0 | 0 | 0.22 |  |  |  | -0.00031
218449 | LINSOLAR C | 1 | 26.4 | 231 | Gen |  | 82 | 0 | 1 |  | 8.67 | 0 | 0 | 0 | 4.51 |  |  |  | -0.00032
26 | O66 |  |  |  | LTF | [5 empty] | 673 | 0 | 0 | 0 |  |  |  |  | 0.0003
207458 | AD2-210 E | E | 34.5 | 228 | Gen | New | 88 | 0 | 1 |  | 2 | 0 | -2 | 0 | 0 |  |  |  | -0.0003 |  |  |  | AD2-210
206767 | 28BRNX1-095 | S1 | 34.5 | 228 | Gen |  | 82 | 0 | 1 |  | 3 | 0 | 0 | 0 | 1.56 |  |  |  | -0.0003 |  |  |  | X1-095
217169 | METRODIV C | 1 | 13.2 | 231 | Gen |  | 82 | 0 | 1 |  | 1.86 | 0 | 0 | 0 | 0.97 |  |  |  | -0.00031
217194 | REDH C | 1 | 13 | 231 | Gen |  | 82 | 0 | 1 |  | 5 | 0 | 0 | 0 | 2.6 |  |  |  | -0.00031
217201 | HACKENSOLA C | 1 | 26.4 | 231 | Gen |  | 82 | 0 | 1 |  | 1 | 0 | 0 | 0 | 0.52 |  |  |  | -0.00031
217204 | WCALDSOLAR C | 1 | 13.2 | 231 | Gen |  | 82 | 0 | 1 |  | 1 | 0 | 0 | 0 | 0.52 |  |  |  | -0.00031
217206 | BARNGR HS C | 1 | 26.4 | 231 | Gen |  | 82 | 0 | 1 |  | 0.55 | 0 | 0 | 0 | 0.28 |  |  |  | -0.00031
217208 | PARK ELE C | 1 | 13.2 | 231 | Gen |  | 82 | 0 | 1 |  | 0.43 | 0 | 0 | 0 | 0.22 |  |  |  | -0.00031
219910 | AD1-054 E | S1 | 13.2 | 231 | Gen | New | 82 | 0 | 1 |  | 1.5 | 0 | 0 | 0 | 0 |  |  |  | -0.00031 |  |  |  | AD1-054
206743 | 28GAR_V4-001 | S1 | 34.5 | 228 | Gen |  | 82 | 0 | 1 |  | 2.76 | 0 | 0 | 0 | 1.43 |  |  |  | -0.0003 |  |  |  | V4-001
207402 | 28AA2-082 E | E | 34.5 | 228 | Gen | New | 88 | 0 | 1 |  | 20 | 0 | -20 | 0 | 0 |  |  |  | -0.00028 |  |  |  | AA2-082
207413 | 28AA2-061 E | 1 | 34.5 | 228 | Gen | New | 88 | 0 | 1 |  | 8 | 0 | -8 | 0 | 0 |  |  |  | -0.00028 |  |  |  | AA2-061
207412 | 28AA2-060 E | BA | 34.5 | 228 | Gen | New | 88 | 0 | 1 |  | 6 | 0 | -6 | 0 | 0 |  |  |  | -0.00028 |  |  |  | AA2-060
206345 | 28N27_Y2-018 | S1 | 13.8 | 228 | Gen |  | 85 | 0 | 1 |  | 3.8 | 0 | 0 | 0 | 2.13 |  |  |  | -0.00028 |  |  |  | Y2-018
206679 | 28M&M S721 | 1 | 34.5 | 228 | Gen | New | 82 | 0 | 1 |  | 10.3 | 0 | 0 | 0 | 0 |  |  |  | -0.00028
206746 | 28WNG_W3-110 | S1 | 34.5 | 228 | Gen |  | 82 | 0 | 1 |  | 7.5 | 0 | 0 | 0 | 3.9 |  |  |  | -0.00029 |  |  |  | W3-110
206748 | 28DL_W4-046 | S1 | 34.5 | 228 | Gen |  | 82 | 0 | 1 |  | 8.6 | 0 | 0 | 0 | 4.47 |  |  |  | -0.00028 |  |  |  | W4-046
206749 | 28WA_W3-044 | S1 | 34.5 | 228 | Gen |  | 82 | 0 | 1 |  | 20 | 0 | 0 | 0 | 10.4 |  |  |  | -0.00029 |  |  |  | W3-044
206757 | 28RH_W2-091 | S1 | 34.5 | 228 | Gen |  | 82 | 0 | 1 |  | 8 | 0 | 0 | 0 | 4.16 |  |  |  | -0.00028 |  |  |  | W2-091
206759 | 28HOL_W4-097 | S1 | 34.5 | 228 | Gen |  | 82 | 0 | 1 |  | 3.2 | 0 | 0 | 0 | 1.66 |  |  |  | -0.00029 |  |  |  | W4-097
206762 | 28FRD_X1-012 | S1 | 34.5 | 228 | Gen |  | 82 | 0 | 1 |  | 10 | 0 | 0 | 0 | 5.2 |  |  |  | -0.00028 |  |  |  | X1-012
206763 | 28BVR_Y1-020 | S1 | 34.5 | 228 | Gen |  | 82 | 0 | 1 |  | 3.72 | 0 | 0 | 0 | 1.93 |  |  |  | -0.00029 |  |  |  | Y1-020
207408 | W3-077 C | S1 | 34.5 | 228 | Gen |  | 82 | 0 | 1 |  | 12.5 | 0 | 0 | 0 | 6.5 |  |  |  | -0.00028 |  |  |  | W3-077
207432 | AC2-175 E | 1 | 34.5 | 228 | Gen | New | 82 | 0 | 1 |  | 1.6 | 0 | 0 | 0 | 0 |  |  |  | -0.00029 |  |  |  | AC2-175
207437 | AD2-070 C | 1 | 34.5 | 228 | Gen |  | 82 | 0 | 1 |  | 7.8 | 0 | 0 | 0 | 4.06 |  |  |  | -0.00028 |  |  |  | AD2-070
207439 | AE1-081 C | 1 | 34.5 | 228 | Gen |  | 82 | 0 | 1 |  | 2.3 | 0 | 0 | 0 | 1.2 |  |  |  | -0.00029 |  |  |  | AE1-081
207462 | AF1-133 C | 1 | 34.5 | 228 | Gen |  | 85 | 0 | 1 |  | 20 | 0 | 0 | 0 | 11.2 |  |  |  | -0.00028 |  |  |  | AF1-133
207471 | AF2-354 C | 1 | 34.5 | 228 | Gen | New | 82 | 0 | 1 |  | 11 | 0 | 0 | 0 | 0 |  |  |  | -0.00029 |  |  |  | AF2-354
207472 | AE2-028 C | 1 | 34.5 | 228 | Gen |  | 82 | 0 | 1 |  | 0.75 | 0 | 0 | 0 | 0.39 |  |  |  | -0.00028 |  |  |  | AE2-028
207484 | AF2-139 C O1 | S1 | 34.5 | 228 | Gen |  | 82 | 0 | 1 |  | 8.8 | 0 | 0 | 0 | 4.58 |  |  |  | -0.00028 |  |  |  | AF2-139
207510 | AF2-138 C | S1 | 34.5 | 228 | Gen |  | 82 | 0 | 1 |  | 19.8 | 0 | 0 | 0 | 10.3 |  |  |  | -0.00029 |  |  |  | AF2-138
207511 | W3-106 GEN | S1 | 34.5 | 228 | Gen | New | 82 | 0 | 1 |  | 10.5 | 0 | 0 | 0 | 0 |  |  |  | -0.00029 |  |  |  | W3-106
207477 | AE1-060 E | E | 34.5 | 228 | Gen | New | 88 | 0 | 1 |  | 19.8 | 0 | -19.8 | 0 | 0 |  |  |  | -0.00027 |  |  |  | AE1-060
206719 | 28W4-073 | S1 | 34.5 | 228 | Gen |  | 82 | 0 | 1 |  | 13.54 | 0 | 0 | 0 | 7.04 |  |  |  | -0.00028 |  |  |  | 28W4-07
206741 | 28FR_U2-059 | S1 | 34.5 | 228 | Gen |  | 82 | 0 | 1 |  | 2.04 | 0 | 0 | 0 | 1.06 |  |  |  | -0.00028 |  |  |  | U2-059
206751 | 28HRM_W1-127 | S1 | 34.5 | 228 | Gen |  | 82 | 0 | 1 |  | 3.04 | 0 | 0 | 0 | 1.58 |  |  |  | -0.00028 |  |  |  | W1-127
206758 | 28AU_W4-064 | S1 | 34.5 | 228 | Gen |  | 82 | 0 | 1 |  | 3 | 0 | 0 | 0 | 1.56 |  |  |  | -0.00028 |  |  |  | W4-064
210947 | AG1-498 C | S1 | 12.5 | 229 | Gen |  | 82 | 0 | 1 |  | 8.8 | 0 | 0 | 0 | 4.58 |  |  |  | -0.00026 |  |  |  | AG1-498
211066 | AD1-143 C1 | B1 | 69 | 229 | Gen | New | 88 | 0 | 1 |  | 10 | 0 | -10 | 0 | 0 |  |  |  | -0.00024 |  |  |  | AD1-143
209945 | AF2-278 E | E | 12.5 | 229 | Gen | New | 82 | 0 | 1 |  | 3 | 0 | 0 | 0 | 0 |  |  |  | -0.00024 |  |  |  | AF2-278
211065 | PASP 1_2 C | 1 | 13.8 | 229 | Gen |  | 82 | 0 | 1 |  | 10 | 0 | 0 | 0 | 5.2 |  |  |  | -0.00024
211065 | PASP 1_2 C | S2 | 13.8 | 229 | Gen |  | 82 | 0 | 1 |  | 10 | 0 | 0 | 0 | 5.2 |  |  |  | -0.00024
211066 | AD1-143 C1 | 1 | 69 | 229 | Gen | New | 76 | 0 | 1 |  | 40 | 0 | 0 | 0 | 0 |  |  |  | -0.00024 |  |  |  | AD1-143
211067 | AD1-143 C2 | 2 | 69 | 229 | Gen | New | 76 | 0 | 1 |  | 40 | 0 | 0 | 0 | 0 |  |  |  | -0.00024 |  |  |  | AD1-143
237048 | AF1-022 C | 1 | 25 | 201 | Gen |  | 86 | 0 | 1 |  | 14 | 0 | 0 | 0 | 7.56 |  |  |  | -0.0002 |  |  |  | AF1-022
203979 | AG1-198 GEN | S1 | 34.5 | 226 | Gen |  | 85 | 0 | 1 |  | 12 | 0 | 0 | 0 | 6.72 |  |  |  | -0.00019 |  |  |  | AG1-198
211375 | BEAC | 1 | 69 | 229 | Gen | New | 88 | 0 | 1 |  | 20 | 0 | -20 | 0 | 0 |  |  |  | -0.00018 |  |  |  | W1-111
238102 | AF2-292 E | B1 | 138 | 201 | Gen | New | 88 | 0 | 1 |  | 1.5 | 0 | -1.5 | 0 | 0 |  |  |  | 0.00018 |  |  |  | AF2-292 |  | MFO
238102 | AF2-292 E | E | 138 | 201 | Gen | New | 83 | 0 | 1 |  | 1.17 | 0 | 0 | 0 | 0 |  |  |  | 0.00018 |  |  |  | AF2-292 |  | MFO
209063 | AE2-046 GEN | S1 | 0.55 | 229 | Gen | New | 82 | 0 | 1 |  | 50 | 0 | 0 | 0 | 0 |  |  |  | -0.00018 |  |  |  | AE2-046
209027 | LOR2_Q27 | W1 | 0.69 | 229 | Gen |  | 76 | 0 | 1 |  | 100 | 0 | 0 | 0 | 29 |  |  |  | -0.00016 |  |  |  | Q27
212266 | LOR1 | W1 | 0.69 | 229 | Gen |  | 76 | 0 | 1 |  | 3.4 | 0 | 0 | 0 | 0.99 |  |  |  | -0.00016 |  |  |  | N14
209093 | AE2-110 GEN | S1 | 0.55 | 229 | Gen |  | 82 | 0 | 1 |  | 20 | 0 | 0 | 0 | 10.4 |  |  |  | -0.00015 |  |  |  | AE2-110
211938 | AF2-285 E | E | 12.5 | 229 | Gen | New | 82 | 0 | 1 |  | 3 | 0 | 0 | 0 | 0 |  |  |  | -0.00015 |  |  |  | AF2-285
212451 | AF2-427 E | E | 12.5 | 229 | Gen | New | 82 | 0 | 1 |  | 3 | 0 | 0 | 0 | 0 |  |  |  | -0.00014 |  |  |  | AF2-427
212464 | AF2-289 E | E | 12.5 | 229 | Gen | New | 82 | 0 | 1 |  | 3 | 0 | 0 | 0 | 0 |  |  |  | -0.00014 |  |  |  | AF2-289
212495 | AF2-284 E | E | 12.5 | 229 | Gen | New | 82 | 0 | 1 |  | 2 | 0 | 0 | 0 | 0 |  |  |  | -0.00014 |  |  |  | AF2-284
209054 | AE2-059 GEN | S1 | 0.55 | 229 | Gen |  | 85 | 0 | 1 |  | 20 | 0 | 0 | 0 | 11.2 |  |  |  | -0.00014 |  |  |  | AE2-059
209059 | AE2-084 GEN | S1 | 0.55 | 229 | Gen | New | 82 | 0 | 1 |  | 20 | 0 | 0 | 0 | 0 |  |  |  | -0.00014 |  |  |  | AE2-084
209071 | AE2-133 GEN | S1 | 0.55 | 229 | Gen |  | 85 | 0 | 1 |  | 20 | 0 | 0 | 0 | 11.2 |  |  |  | -0.00013 |  |  |  | AE2-133
209089 | AE1-225 GEN | S1 | 69 | 229 | Gen |  | 82 | 0 | 1 |  | 19.8 | 0 | 0 | 0 | 10.3 |  |  |  | -0.00013 |  |  |  | AE1-225
209097 | AE2-111_GEN | S1 | 0.55 | 229 | Gen |  | 82 | 0 | 1 |  | 20 | 0 | 0 | 0 | 10.4 |  |  |  | -0.00013 |  |  |  | AE2-111
212455 | AF2-290 E | E | 12.5 | 229 | Gen | New | 82 | 0 | 1 |  | 2 | 0 | 0 | 0 | 0 |  |  |  | -0.00014 |  |  |  | AF2-290
212507 | AE2-042_GEN | S1 | 0.6 | 229 | Gen |  | 85 | 0 | 1 |  | 70 | 0 | 0 | 0 | 39.2 |  |  |  | -0.00014 |  |  |  | AE2-042
237505 | 01ELLIOTTS | W1 | 34.5 | 201 | Gen |  | 77 | 0 | 1 |  | 50.4 | 0 | 0 | 0 | 16.13 |  |  |  | 0.00013
211913 | AB1-182 E | 1 | 69 | 229 | Gen | New | 88 | 0 | 1 |  | 20 | 0 | -20 | 0 | 0 |  |  |  | -0.00013 |  |  |  | AB1-182
208972 | BECR L18 | W1 | 0.69 | 229 | Gen |  | 76 | 0 | 1 |  | 26 | 0 | 0 | 0 | 7.54 |  |  |  | -0.00013 |  |  |  | L18
209029 | WAYM IPP | W1 | 0.57 | 229 | Gen |  | 76 | 0 | 1 |  | 70 | 0 | 0 | 0 | 20.3 |  |  |  | -9e-05 |  |  |  | D05
211490 | AF2-282 E | E | 12.5 | 229 | Gen | New | 82 | 0 | 1 |  | 3 | 0 | 0 | 0 | 0 |  |  |  | -9e-05 |  |  |  | AF2-282
211554 | AF2-283 E | E | 12.5 | 229 | Gen | New | 82 | 0 | 1 |  | 2 | 0 | 0 | 0 | 0 |  |  |  | -9e-05 |  |  |  | AF2-283
209067 | AE2-060 GEN | S1 | 0.55 | 229 | Gen |  | 85 | 0 | 1 |  | 20 | 0 | 0 | 0 | 11.2 |  |  |  | -3e-05 |  |  |  | AE2-060
209937 | AF2-287 E | E | 12.5 | 229 | Gen | New | 82 | 0 | 1 |  | 3 | 0 | 0 | 0 | 0 |  |  |  | -3e-05 |  |  |  | AF2-287
209972 | AF2-288 E | E | 12.5 | 229 | Gen | New | 82 | 0 | 1 |  | 3 | 0 | 0 | 0 | 0 |  |  |  | -3e-05 |  |  |  | AF2-288
9 | NY |  |  |  | LTF | [5 empty] | 55.3 | 0 | 0 | 0 |  |  |  |  | -0.0001
8 | VTF |  |  |  | LTF | [5 empty] | 645 | 0 | 0 | 0 |  |  |  |  | -0.0003
6 | G-007A |  |  |  | LTF | [5 empty] | 239.8 | 0 | 0 | 0 |  |  |  |  | -0.0003
14 | CPLE |  |  |  | LTF | [5 empty] | 94.5 | 0 | 0 | 0 |  |  |  |  | -0.0033
5 | CBM South 2 |  |  |  | LTF | [5 empty] | 1356 | 0 | 0 | 0 |  |  |  |  | -0.0036
16 | TVA |  |  |  | LTF | [5 empty] | 87.5 | 0 | 0 | 0 |  |  |  |  | -0.004
23 | LAGN |  |  |  | LTF | [5 empty] | 175 | 0 | 0 | 0 |  |  |  |  | -0.0041
4 | CBM South 1 |  |  |  | LTF | [5 empty] | 0 | 0 | 0 | 0 |  |  |  |  | -0.0041
3 | CBM West 2 |  |  |  | LTF | [5 empty] | 605 | 0 | 0 | 0 |  |  |  |  | -0.0042
20 | MEC |  |  |  | LTF | [5 empty] | 158.9 | 0 | 0 | 0 |  |  |  |  | -0.0043
24 | SIGE |  |  |  | LTF | [5 empty] | 19.6 | 0 | 0 | 0 |  |  |  |  | -0.0043
10 | LGEE |  |  |  | LTF | [5 empty] | 59.5 | 0 | 0 | 0 |  |  |  |  | -0.0043
12 | WEC |  |  |  | LTF | [5 empty] | 32.9 | 0 | 0 | 0 |  |  |  |  | -0.0044
2 | CBM West 1 |  |  |  | LTF | [5 empty] | 1447 | 0 | 0 | 0 |  |  |  |  | -0.0045

## GDDetail_2023W1-GD-LL905
****** PJM Generator Deliverability Detailed Report ****** PJM [TARA Ver 2302.2.0.3 PJMGD 2022 Reform RC2 64-bit - Mon Jul 17 16:29:40 2023]
FG Index [All Queue] | 905 | FG ID | 204 | Monitored Facility:235283 01WYCOFJ 138 254064 15CHESWK 138 1 / Contingency:AP_P7-1_WP-138-AA2-161_1_SRT-A[Tower]
Rating | Final DC %LD | Final AC %LD | DC¦AC | Base FG Flow | 50/50 MW | Regular Adder MW | SW Harmer | SW Helper | LTF Impact | DC Final Flow | AC Final Flow | Transfer Cap | 50¦50 Dispatch | Regular Adder Dispatch | SW Harmer Dispatch | SW Helper Dispatch | Ext Regular Adder Dispatch | Ext SW Harmer Dispatch
248 | 101.26 | 100.67 | AC | 246.72 | 0 | 0 | 0 | 0 | 4.39 | 251.11 | 249.7 | 860.3 | 0 | 0 | 0 | 0 | 0 | 0
Bus#¦LTF# | Gen¦LTF Name | Gen ID | Volt | Area | Category | PJT Status | Gen Class | EEFORD | Com.Prob | CIR | MWP Cap | MWP Energy | MWN Cap | MWN Energy | PGen | PNew | Ramping Factor | Flag | Dfax | Impact | FRMP | Cum Avai | Group ID | Study Unit? | MFO Limited?
22 | BlueGrass |  |  |  | LTF | [5 empty] | 173.3 | 0 | 0 | 0 |  | 173.3 | 1 | CLTF | 0.00435 | 0.7542 | 0.7542
18 | TRIMBLE |  |  |  | LTF | [5 empty] | 55.7 | 0 | 0 | 0 |  | 55.7 | 1 | CLTF | 0.00436 | 0.2425 | 0.2425
11 | Gibson |  |  |  | LTF | [5 empty] | 54.6 | 0 | 0 | 0 |  | 54.6 | 1 | CLTF | 0.00435 | 0.2375 | 0.2375
25 | MDU |  |  |  | LTF | [5 empty] | 0 | 0 | 0 | 0 |  | 0 | 1 | CLTF | 0.00436 | 0 | 0
17 | PRAIRIE |  |  |  | LTF | [5 empty] | 131.3 | 0 | 0 | 0 |  | 131.3 | 1 | CLTF | 0.00428 | 0.5621 | 0.5621
19 | CALDErWOOD |  |  |  | LTF | [5 empty] | 49.7 | 0 | 0 | 0 |  | 49.7 | 1 | CLTF | 0.00391 | 0.1942 | 0.1942
21 | CHEOAH |  |  |  | LTF | [5 empty] | 50 | 0 | 0 | 0 |  | 50 | 1 | CLTF | 0.0039 | 0.195 | 0.195
15 | CATAWBA |  |  |  | LTF | [5 empty] | 35 | 0 | 0 | 0 |  | 35 | 1 | CLTF | 0.00356 | 0.1245 | 0.1245
13 | HAMLET |  |  |  | LTF | [5 empty] | 57.8 | 0 | 0 | 0 |  | 57.8 | 1 | CLTF | 0.0034 | 0.1962 | 0.1962
1 | CBM North |  |  |  | LTF | [5 empty] | 93 | 0 | 0 | 0 |  | 93 | 1 | LTF/CBM | 0.00014 | 0.0135 | 0.0135
27 | MISO WIND |  |  |  | LTF | [5 empty] | 16783.3 | 0 | 0 | 0 |  | 16783.3 | 1 | CLTF | 0.00011 | 1.8722 | 1.8722
238105 | AF2-314 GEN | S1 | 25 | 201 | Gen |  | 86 | 0 | 1 |  | 10 | 0 | 0 | 0 | 5.4 |  |  |  | 0.01655 |  |  |  | AF2-314
254310 | AG1-086 GEN | B1 | 138 | 215 | Gen | New | 88 | 0 | 1 |  | 5.63 | 0 | 0 | 0 | 0 |  |  |  | -0.01297 |  |  |  | AG1-086 |  | MFO
254310 | AG1-086 GEN | S1 | 138 | 215 | Gen |  | 86 | 0 | 1 |  | 17.5 | 0 | 0 | 0 | 9.45 |  |  |  | -0.01297 |  |  |  | AG1-086 |  | MFO
254303 | AC2-168C | 1 | 23 | 215 | Gen |  | 83 | 0 | 1 |  | 20 | 0 | 0 | 0 | 10.6 |  |  |  | -0.01272 |  |  |  | AC2-168
254304 | AE2-114 C | 1 | 138 | 215 | Gen |  | 86 | 0 | 1 |  | 17.1 | 0 | 0 | 0 | 9.23 |  |  |  | -0.01216 |  |  |  | AE2-114
254305 | AE2-115 C | 1 | 138 | 215 | Gen |  | 86 | 0 | 1 |  | 17.1 | 0 | 0 | 0 | 9.23 |  |  |  | -0.01216 |  |  |  | AE2-115
235055 | AG1-141 C | S1 | 138 | 201 | Gen | New | 86 | 0 | 1 |  | 5 | 0 | 0 | 0 | 0 |  |  |  | 0.00992 |  |  |  | AG1-141
237043 | AE2-125 C | 1 | 25 | 201 | Gen |  | 86 | 0 | 1 |  | 13.8 | 0 | 0 | 0 | 7.45 |  |  |  | 0.00974 |  |  |  | AE2-125
237052 | AF1-210 C | 1 | 25 | 201 | Gen | New | 86 | 0 | 1 |  | 16 | 0 | 0 | 0 | 0 |  |  |  | 0.00659 |  |  |  | AF1-210
270322 | AE2-290 GEN | S1 | 0.6 | 205 | Gen |  | 86 | 0 | 1 |  | 101.32 | 0 | 0 | 0 | 54.71 |  |  |  | -0.00598 |  |  |  | AE2-290
241916 | 02Z1-035 | W1 | 69 | 202 | Gen |  | 77 | 0 | 1 |  | 18 | 0 | 0 | 0 | 5.76 |  |  |  | -0.00595 |  |  |  | Z1-035
270387 | AD2-014 GEN | S1 | 0.6 | 205 | Gen |  | 83 | 0 | 1 |  | 54 | 0 | 0 | 0 | 28.62 |  |  |  | -0.00586 |  |  |  | AD2-014
241801 | AE1-079 GEN | B1 | 69 | 202 | Gen | New | 88 | 0 | 1 |  | 4 | 0 | -4 | 0 | 0 |  |  |  | -0.00585 |  |  |  | AE1-079 |  | MFO
241985 | AE1-237 GEN | B1 | 69 | 202 | Gen | New | 88 | 0 | 1 |  | 4 | 0 | -4 | 0 | 0 |  |  |  | -0.00584 |  |  |  | AE1-237 |  | MFO
241982 | AE2-343 S C | B1 | 69 | 202 | Gen | New | 88 | 0 | 1 |  | 4 | 0 | -4 | 0 | 0 |  |  |  | -0.00584 |  |  |  | AE2-343 |  | MFO
241801 | AE1-079 GEN | S1 | 69 | 202 | Gen |  | 86 | 0 | 1 |  | 19.9 | 0 | 0 | 0 | 10.75 |  |  |  | -0.00585 |  |  |  | AE1-079 |  | MFO
241985 | AE1-237 GEN | S1 | 69 | 202 | Gen |  | 86 | 0 | 1 |  | 19.9 | 0 | 0 | 0 | 10.75 |  |  |  | -0.00584 |  |  |  | AE1-237 |  | MFO
241982 | AE2-343 S C | S1 | 69 | 202 | Gen |  | 86 | 0 | 1 |  | 17.9 | 0 | 0 | 0 | 9.67 |  |  |  | -0.00584 |  |  |  | AE2-343 |  | MFO
241967 | AE2-285 GEN | S1 | 69 | 202 | Gen |  | 86 | 0 | 1 |  | 50 | 0 | 0 | 0 | 27 |  |  |  | -0.00584 |  |  |  | AE2-285
238124 | AG1-029 G1 | S1 | 25 | 201 | Gen |  | 83 | 0 | 1 |  | 15 | 0 | 0 | 0 | 7.95 |  |  |  | -0.00561 |  |  |  | AG1-029
238125 | AG1-029 G2 | S2 | 25 | 201 | Gen |  | 83 | 0 | 1 |  | 15 | 0 | 0 | 0 | 7.95 |  |  |  | -0.00561 |  |  |  | AG1-029
241885 | AC2-103 C1 | W1 | 0.69 | 202 | Gen |  | 77 | 0 | 1 |  | 148.83 | 0 | 0 | 0 | 47.63 |  |  |  | -0.00547 |  |  |  | AC2-103
241886 | AC2-103 C2 | W2 | 0.69 | 202 | Gen |  | 77 | 0 | 1 |  | 148.83 | 0 | 0 | 0 | 47.63 |  |  |  | -0.00547 |  |  |  | AC2-103
236523 | 01WDPWR_K20 | W1 | 25 | 201 | Gen |  | 77 | 0 | 1 |  | 15 | 0 | 0 | 0 | 4.8 |  |  |  | 0.00527 |  |  |  | K20
235058 | AG1-386 C | B1 | 25 | 201 | Gen | New | 88 | 0 | 1 |  | 8.57 | 0 | -8.57 | 0 | 0 |  |  |  | -0.00511 |  |  |  | AG1-386 |  | MFO
235058 | AG1-386 C | S1 | 25 | 201 | Gen |  | 83 | 0 | 1 |  | 20 | 0 | 0 | 0 | 10.8 |  |  |  | -0.00511 |  |  |  | AG1-386 |  | MFO
240997 | 02BG10 | S1 | 69 | 202 | Gen | New | 83 | 0 | 1 |  | 20 | 0 | 0 | 0 | 0 |  |  |  | -0.00509 |  |  |  | G10
241996 | AE2-282_GEN | S1 | 0.64 | 202 | Gen |  | 86 | 0 | 1 |  | 68.67 | 0 | 0 | 0 | 37.08 |  |  |  | -0.00501 |  |  |  | AE2-282
270361 | AD1-070 GEN | S1 | 0.69 | 205 | Gen |  | 83 | 0 | 1 |  | 205 | 0 | 0 | 0 | 108.65 |  |  |  | -0.00499 |  |  |  | AD1-070
247522 | U1-059 C | W1 | 69 | 205 | Gen |  | 77 | 0 | 1 |  | 53.1 | 0 | 0 | 0 | 16.99 |  |  |  | -0.00488 |  |  |  | U1-059
247555 | W1-056 C | W1 | 69 | 205 | Gen |  | 77 | 0 | 1 |  | 66.7 | 0 | 0 | 0 | 21.34 |  |  |  | -0.00488 |  |  |  | W1-056
241960 | AC2-195 C | S1 | 0.42 | 202 | Gen |  | 86 | 0 | 1 |  | 99.96 | 0 | 0 | 0 | 53.98 |  |  |  | -0.00486 |  |  |  | AC2-195
270377 | AD1-106 GEN | S1 | 0.55 | 205 | Gen |  | 83 | 0 | 1 |  | 61.75 | 0 | 0 | 0 | 32.73 |  |  |  | -0.00486 |  |  |  | AD1-106
270297 | AD1-101 C | S1 | 0.39 | 205 | Gen |  | 83 | 0 | 1 |  | 50 | 0 | 0 | 0 | 26.5 |  |  |  | -0.00471 |  |  |  | AD1-101
247549 | V3-028 C | S1 | 345 | 205 | Gen |  | 86 | 0 | 1 |  | 150 | 0 | 0 | 0 | 81 |  |  |  | -0.00468 |  |  |  | V3-028
270317 | AD1-130_GEN | S1 | 0.63 | 205 | Gen |  | 86 | 0 | 1 |  | 170 | 0 | 0 | 0 | 91.8 |  |  |  | -0.00468 |  |  |  | V3-028
246936 | 05BLCK-1 C | W1 | 0.69 | 205 | Gen |  | 77 | 0 | 1 |  | 116 | 0 | 0 | 0 | 37.12 |  |  |  | -0.00466 |  |  |  | R60
246937 | 05BLCK-2 C | W1 | 0.69 | 205 | Gen |  | 77 | 0 | 1 |  | 116 | 0 | 0 | 0 | 37.12 |  |  |  | -0.00466 |  |  |  | R60
246938 | 05BLCK-3 C | W1 | 0.69 | 205 | Gen |  | 77 | 0 | 1 |  | 118 | 0 | 0 | 0 | 37.76 |  |  |  | -0.00466 |  |  |  | R60
270223 | U2-072_GEN1 | W1 | 0.69 | 205 | Gen |  | 77 | 0 | 1 |  | 50 | 0 | 0 | 0 | 16 |  |  |  | -0.00467 |  |  |  | U2-072
270224 | U2-072_GEN2 | W2 | 0.69 | 205 | Gen |  | 77 | 0 | 1 |  | 50 | 0 | 0 | 0 | 16 |  |  |  | -0.00467 |  |  |  | U2-072
270227 | U2-072_GEN3 | W3 | 0.69 | 205 | Gen |  | 77 | 0 | 1 |  | 50 | 0 | 0 | 0 | 16 |  |  |  | -0.00467 |  |  |  | U2-072
270228 | U2-072_GEN4 | W4 | 0.69 | 205 | Gen |  | 77 | 0 | 1 |  | 50 | 0 | 0 | 0 | 16 |  |  |  | -0.00467 |  |  |  | U2-072
270231 | U2-072_GEN5 | W5 | 0.69 | 205 | Gen |  | 77 | 0 | 1 |  | 50 | 0 | 0 | 0 | 16 |  |  |  | -0.00467 |  |  |  | U2-072
270391 | AE2-306 GEN | S1 | 0.63 | 205 | Gen |  | 86 | 0 | 1 |  | 30 | 0 | 0 | 0 | 16.2 |  |  |  | -0.00467 |  |  |  | AE2-306
270404 | AC1-167 GEN | S1 | 0.36 | 205 | Gen |  | 86 | 0 | 1 |  | 49.98 | 0 | 0 | 0 | 26.99 |  |  |  | -0.00467 |  |  |  | AC1-167
247965 | Y1-063 E | E | 34.5 | 205 | Gen | New | 88 | 0 | 1 |  | 4 | 0 | -4 | 0 | 0 |  |  |  | -0.00465 |  |  |  | Y1-063
270258 | AD1-119 C | S1 | 0.39 | 205 | Gen |  | 83 | 0 | 1 |  | 49.96 | 0 | 0 | 0 | 26.48 |  |  |  | -0.00465 |  |  |  | AD1-119
247607 | V1-011 GEN | W1 | 0.69 | 205 | Gen |  | 77 | 0 | 1 |  | 100 | 0 | 0 | 0 | 32 |  |  |  | -0.00465 |  |  |  | V1-011
253369 | AE2-303_GEN | S1 | 0.64 | 209 | Gen |  | 86 | 0 | 1 |  | 49.9 | 0 | 0 | 0 | 26.95 |  |  |  | -0.00462 |  |  |  | AE2-303
270284 | AF1-227 C1 | S1 | 0.6 | 205 | Gen |  | 86 | 0 | 1 |  | 112.25 | 0 | 0 | 0 | 60.61 |  |  |  | -0.00462 |  |  |  | AF1-227
270286 | AF1-227 C2 | S1 | 0.6 | 205 | Gen |  | 86 | 0 | 1 |  | 152.55 | 0 | 0 | 0 | 82.38 |  |  |  | -0.00462 |  |  |  | AF1-227
270287 | AF1-227 C3 | S1 | 0.63 | 205 | Gen |  | 86 | 0 | 1 |  | 106.38 | 0 | 0 | 0 | 57.45 |  |  |  | -0.00462 |  |  |  | AF1-227
246953 | 05TIMB G C | W1 | 0.69 | 205 | Gen |  | 77 | 0 | 1 |  | 149.4 | 0 | 0 | 0 | 47.81 |  |  |  | -0.00462 |  |  |  | R49
241973 | AD2-163_C1 | 1 | 0.6 | 202 | Gen |  | 86 | 0 | 1 |  | 90 | 0 | 0 | 0 | 48.6 |  |  |  | -0.0046 |  |  |  | AD2-163
241974 | AD2-163_C2 | 1 | 0.6 | 202 | Gen |  | 86 | 0 | 1 |  | 90 | 0 | 0 | 0 | 48.6 |  |  |  | -0.0046 |  |  |  | AD2-163
247521 | TR3_G114 | W1 | 0.69 | 205 | Gen |  | 77 | 0 | 1 |  | 99.6 | 0 | 0 | 0 | 31.87 |  |  |  | -0.0046
270191 | TR4_S_V150 | W1 | 0.72 | 205 | Gen |  | 77 | 0 | 1 |  | 75.9 | 0 | 0 | 0 | 24.29 |  |  |  | -0.0046
270246 | TR3_N_V150 | W3 | 0.72 | 205 | Gen |  | 77 | 0 | 1 |  | 25.2 | 0 | 0 | 0 | 8.06 |  |  |  | -0.0046 |  |  |  | V150
270247 | TR3_N_V136 | W2 | 0.65 | 205 | Gen |  | 77 | 0 | 1 |  | 25.2 | 0 | 0 | 0 | 8.06 |  |  |  | -0.0046 |  |  |  | V136
241955 | AC1-078 C | 1 | 0.6 | 202 | Gen |  | 83 | 0 | 1 |  | 196 | 0 | 0 | 0 | 103.88 |  |  |  | -0.0046 |  |  |  | AC1-078
241992 | AE2-217_GEN | S1 | 0.63 | 202 | Gen | New | 86 | 0 | 1 |  | 181.2 | 0 | 0 | 0 | 0 |  |  |  | -0.00459 |  |  |  | AE2-217
253378 | AE2-206_GEN | S1 | 0.39 | 209 | Gen |  | 83 | 0 | 1 |  | 146.3 | 0 | 0 | 0 | 77.54 |  |  |  | -0.0046 |  |  |  | AE2-206
253383 | AE2-342_GEN | S1 | 0.6 | 209 | Gen |  | 86 | 0 | 1 |  | 40 | 0 | 0 | 0 | 21.6 |  |  |  | -0.0046 |  |  |  | AE2-342
270349 | AD2-093_GEN | S1 | 0.63 | 205 | Gen |  | 86 | 0 | 1 |  | 226.5 | 0 | 0 | 0 | 122.31 |  |  |  | -0.00459 |  |  |  | AD2-093
244412 | 05WTRV SLR | S1 | 138 | 205 | Gen |  | 83 | 0 | 1 |  | 4.6 | 0 | 0 | 0 | 2.44 |  |  |  | -0.00457
247643 | Z2-116 C | 1C | 138 | 205 | Gen |  | 83 | 0 | 1 |  | 2.6 | 0 | 0 | 0 | 1.38 |  |  |  | -0.00455 |  |  |  | Z2-116
253388 | AE2-218 GEN | S1 | 0.63 | 209 | Gen | New | 86 | 0 | 1 |  | 178.18 | 0 | 0 | 0 | 0 |  |  |  | -0.00455 |  |  |  | AE2-218
270216 | AD2-079_C O | S1 | 0.63 | 205 | Gen |  | 86 | 0 | 1 |  | 20 | 0 | 0 | 0 | 10.8 |  |  |  | -0.00455 |  |  |  | AD2-079
241972 | AD1-140 GEN | 1 | 0.57 | 202 | Gen | New | 83 | 0 | 1 |  | 175 | 0 | 0 | 0 | 0 |  |  |  | -0.00454 |  |  |  | AD1-140
253325 | AC1-069 C | 1 | 0.36 | 209 | Gen |  | 86 | 0 | 1 |  | 49.9 | 0 | 0 | 0 | 26.95 |  |  |  | -0.00453 |  |  |  | AC1-069
253333 | AC1-068 C | 1 | 0.36 | 209 | Gen |  | 86 | 0 | 1 |  | 49.9 | 0 | 0 | 0 | 26.95 |  |  |  | -0.00453 |  |  |  | AC1-068
253338 | AC1-165 C | 1 | 0.36 | 209 | Gen |  | 86 | 0 | 1 |  | 49.9 | 0 | 0 | 0 | 26.95 |  |  |  | -0.00453 |  |  |  | AC1-165
253343 | AC1-166 C | 1 | 0.36 | 209 | Gen |  | 86 | 0 | 1 |  | 49.9 | 0 | 0 | 0 | 26.95 |  |  |  | -0.00453 |  |  |  | AC1-166
253420 | AE2-319_GEN | S1 | 0.6 | 209 | Gen |  | 86 | 0 | 1 |  | 100 | 0 | 0 | 0 | 54 |  |  |  | -0.00453 |  |  |  | AE2-319
244415 | 05OLIV SLR | S1 | 138 | 205 | Gen |  | 83 | 0 | 1 |  | 5 | 0 | 0 | 0 | 2.65 |  |  |  | -0.00453
270269 | AC2-059 C | S1 | 0.63 | 205 | Gen |  | 86 | 0 | 1 |  | 146.2 | 0 | 0 | 0 | 78.95 |  |  |  | -0.00452 |  |  |  | AC2-059
270273 | AD2-016 C | S1 | 0.63 | 205 | Gen |  | 86 | 0 | 1 |  | 274 | 0 | 0 | 0 | 147.96 |  |  |  | -0.00452 |  |  |  | AD2-016
270291 | AC1-194 C | S1 | 0.55 | 205 | Gen |  | 83 | 0 | 1 |  | 125 | 0 | 0 | 0 | 66.25 |  |  |  | -0.00451 |  |  |  | AC1-194
270201 | AC2-176 GEN | W1 | 0.69 | 205 | Gen |  | 77 | 0 | 1 |  | 130 | 0 | 0 | 0 | 41.6 |  |  |  | -0.0045 |  |  |  | AC2-176
270263 | AC1-001 C | 1 | 0.38 | 205 | Gen |  | 86 | 0 | 1 |  | 49.9 | 0 | 0 | 0 | 26.95 |  |  |  | -0.0045 |  |  |  | AC1-001
247536 | 05BLUFF P WF | W1 | 138 | 205 | Gen |  | 77 | 0 | 1 |  | 120 | 0 | 0 | 0 | 38.4 |  |  |  | -0.0045 |  |  |  | S71
253303 | V4-073 C | S1 | 69 | 209 | Gen |  | 83 | 0 | 1 |  | 2.05 | 0 | 0 | 0 | 1.09 |  |  |  | -0.0045 |  |  |  | V4-073
253349 | AC2-067 C | S1 | 0.38 | 209 | Gen |  | 83 | 0 | 1 |  | 57.5 | 0 | 0 | 0 | 30.48 |  |  |  | -0.0045 |  |  |  | AC2-067
253400 | AC2-068 GEN | S1 | 0.38 | 209 | Gen |  | 83 | 0 | 1 |  | 20.9 | 0 | 0 | 0 | 11.08 |  |  |  | -0.0045 |  |  |  | AC2-068
253415 | AE1-040 GEN | S1 | 0.6 | 209 | Gen |  | 86 | 0 | 1 |  | 48.64 | 0 | 0 | 0 | 26.27 |  |  |  | -0.00449 |  |  |  | AE1-040
270340 | AC2-060 GEN | S1 | 0.55 | 205 | Gen |  | 86 | 0 | 1 |  | 123.65 | 0 | 0 | 0 | 66.77 |  |  |  | -0.00449 |  |  |  | AC2-060
247642 | Z2-115 C | S1 | 12 | 205 | Gen |  | 83 | 0 | 1 |  | 2.5 | 0 | 0 | 0 | 1.33 |  |  |  | -0.00447 |  |  |  | Z2-115
270383 | AD1-128 GEN | S1 | 0.39 | 205 | Gen |  | 83 | 0 | 1 |  | 150 | 0 | 0 | 0 | 79.5 |  |  |  | -0.00447 |  |  |  | AD1-128
276164 | X3-005 C | 1 | 13.2 | 222 | Gen |  | 86 | 0 | 1 |  | 9 | 0 | 0 | 0 | 4.86 |  |  |  | -0.00447 |  |  |  | X3-005
276169 | Z1-107 E | BA | 34.5 | 222 | Gen | New | 88 | 0 | 1 |  | 20 | 0 | -20 | 0 | 0 |  |  |  | -0.00446 |  |  |  | Z1-107
276675 | AE2-062 E | 1 | 138 | 222 | Gen | New | 88 | 0 | 1 |  | 1 | 0 | -1 | 0 | 0 |  |  |  | -0.00446 |  |  |  | AE2-062
243795 | 05HDWTR1G C | W1 | 0.69 | 205 | Gen |  | 77 | 0 | 1 |  | 200 | 0 | 0 | 0 | 64 |  |  |  | -0.00447 |  |  |  | U2-090
246909 | 05MDL-1G C | W1 | 0.6 | 205 | Gen |  | 77 | 0 | 1 |  | 202 | 0 | 0 | 0 | 64.64 |  |  |  | -0.00447 |  |  |  | S06
246910 | 05MDL-2G C | W1 | 12 | 205 | Gen |  | 77 | 0 | 1 |  | 100 | 0 | 0 | 0 | 32 |  |  |  | -0.00447 |  |  |  | T126
246976 | 05MDL-3G C | W1 | 0.69 | 205 | Gen |  | 77 | 0 | 1 |  | 102 | 0 | 0 | 0 | 32.64 |  |  |  | -0.00447 |  |  |  | T126
246979 | 05MDL-4G C | W1 | 0.6 | 205 | Gen |  | 77 | 0 | 1 |  | 100 | 0 | 0 | 0 | 32 |  |  |  | -0.00447 |  |  |  | T127
246991 | 05WLD G1 C | W1 | 0.69 | 205 | Gen |  | 77 | 0 | 1 |  | 97.6 | 0 | 0 | 0 | 31.23 |  |  |  | -0.00447 |  |  |  | U3-002
247255 | 05WLD G2 C | W1 | 0.69 | 205 | Gen |  | 77 | 0 | 1 |  | 200 | 0 | 0 | 0 | 64 |  |  |  | -0.00447 |  |  |  | U3-002
247556 | 05MDL-5G | W1 | 0.69 | 205 | Gen |  | 77 | 0 | 1 |  | 100 | 0 | 0 | 0 | 32 |  |  |  | -0.00447 |  |  |  | T127
253394 | AE2-221_GEN | S1 | 0.63 | 209 | Gen |  | 86 | 0 | 1 |  | 150 | 0 | 0 | 0 | 81 |  |  |  | -0.00447 |  |  |  | AE2-221
253398 | AE2-221_GEN2 | S1 | 0.63 | 209 | Gen |  | 86 | 0 | 1 |  | 150 | 0 | 0 | 0 | 81 |  |  |  | -0.00447 |  |  |  | AE2-221
253406 | AD2-031_GEN | S1 | 0.55 | 209 | Gen |  | 83 | 0 | 1 |  | 50.69 | 0 | 0 | 0 | 26.86 |  |  |  | -0.00447 |  |  |  | AD2-031
270180 | AB1-006 W1 | W1 | 0.65 | 205 | Gen |  | 77 | 0 | 1 |  | 200.4 | 0 | 0 | 0 | 64.13 |  |  |  | -0.00447 |  |  |  | AB1-006
270209 | AC1-174 C | 1 | 0.39 | 205 | Gen |  | 83 | 0 | 1 |  | 100 | 0 | 0 | 0 | 53 |  |  |  | -0.00447 |  |  |  | AC1-174
270210 | AC1-175 C | 1 | 0.39 | 205 | Gen |  | 83 | 0 | 1 |  | 100 | 0 | 0 | 0 | 53 |  |  |  | -0.00447 |  |  |  | AC1-175
270222 | AC2-111 C | 1 | 0.39 | 205 | Gen |  | 86 | 0 | 1 |  | 81.51 | 0 | 0 | 0 | 44.01 |  |  |  | -0.00446 |  |  |  | AC2-111
270239 | V3-007_GEN1 | W1 | 0.65 | 205 | Gen |  | 77 | 0 | 1 |  | 48.1 | 0 | 0 | 0 | 15.39 |  |  |  | -0.00447 |  |  |  | V3-007
270240 | V3-007_GEN2 | W2 | 0.72 | 205 | Gen |  | 77 | 0 | 1 |  | 156.6 | 0 | 0 | 0 | 50.11 |  |  |  | -0.00447 |  |  |  | V3-007
274886 | PILOTHILLGEN | W1 | 0.69 | 222 | Gen |  | 77 | 0 | 1 |  | 154.7 | 0 | 0 | 0 | 49.5 |  |  |  | -0.00447 |  |  |  | S36
274887 | PILOTHILLGEN | W1 | 0.69 | 222 | Gen |  | 77 | 0 | 1 |  | 22.2 | 0 | 0 | 0 | 7.1 |  |  |  | -0.00447 |  |  |  | S36
274888 | KELLY CRK;1U | W1 | 0.69 | 222 | Gen |  | 77 | 0 | 1 |  | 175 | 0 | 0 | 0 | 56 |  |  |  | -0.00447
276772 | AC2-154 GEN | 1 | 0.6 | 222 | Gen |  | 86 | 0 | 1 |  | 49.98 | 0 | 0 | 0 | 26.99 |  |  |  | -0.00447 |  |  |  | AC2-154
276776 | AD2-060 GEN | 1 | 0.6 | 222 | Gen |  | 86 | 0 | 1 |  | 20.2 | 0 | 0 | 0 | 10.91 |  |  |  | -0.00447 |  |  |  | AD2-060
276167 | Z1-106 E2 | BA | 34.5 | 222 | Gen | New | 88 | 0 | 1 |  | 10 | 0 | -10 | 0 | 0 |  |  |  | -0.00445 |  |  |  | Z1-106
276168 | Z1-106 E1 | BA | 34.5 | 222 | Gen | New | 88 | 0 | 1 |  | 10 | 0 | -10 | 0 | 0 |  |  |  | -0.00445 |  |  |  | Z1-106
243859 | 05FR-11G C | W1 | 0.6 | 205 | Gen |  | 77 | 0 | 1 |  | 104 | 0 | 0 | 0 | 33.28 |  |  |  | -0.00446 |  |  |  | Q01/Q03
243862 | 05FR-12G C | W1 | 0.6 | 205 | Gen |  | 77 | 0 | 1 |  | 97.35 | 0 | 0 | 0 | 31.15 |  |  |  | -0.00446 |  |  |  | Q01/Q03
243864 | 05FR-21G C | W1 | 0.6 | 205 | Gen |  | 77 | 0 | 1 |  | 103.95 | 0 | 0 | 0 | 33.26 |  |  |  | -0.00446 |  |  |  | Q01/Q03
243866 | 05FR-22G C | W1 | 0.69 | 205 | Gen |  | 77 | 0 | 1 |  | 98.52 | 0 | 0 | 0 | 31.53 |  |  |  | -0.00446 |  |  |  | Q01/Q03
243870 | 05FR-3G C | W1 | 0.69 | 205 | Gen |  | 77 | 0 | 1 |  | 199.5 | 0 | 0 | 0 | 63.84 |  |  |  | -0.00446 |  |  |  | Q01/Q03
243873 | 05FR-4G C | W1 | 0.69 | 205 | Gen |  | 77 | 0 | 1 |  | 154.1 | 0 | 0 | 0 | 49.31 |  |  |  | -0.00446 |  |  |  | Q01/Q03
253313 | AC1-085 A_C | 1 | 0.6 | 209 | Gen |  | 86 | 0 | 1 |  | 200 | 0 | 0 | 0 | 108 |  |  |  | -0.00446 |  |  |  | AC1-085
253316 | AC1-085 B_C | 1 | 0.6 | 209 | Gen |  | 86 | 0 | 1 |  | 200 | 0 | 0 | 0 | 108 |  |  |  | -0.00446 |  |  |  | AC1-085
270356 | AE2-297 GEN | S1 | 0.55 | 205 | Gen |  | 86 | 0 | 1 |  | 154.03 | 0 | 0 | 0 | 83.18 |  |  |  | -0.00445 |  |  |  | AE2-297
274847 | GR RIDGE ;BU | W1 | 0.57 | 222 | Gen |  | 77 | 0 | 1 |  | 147.4 | 0 | 0 | 0 | 47.17 |  |  |  | -0.00446
274861 | TOP CROP ;1U | W1 | 0.69 | 222 | Gen |  | 77 | 0 | 1 |  | 150 | 0 | 0 | 0 | 48 |  |  |  | -0.00445
274862 | TOP CROP ;2U | W2 | 0.69 | 222 | Gen |  | 77 | 0 | 1 |  | 150 | 0 | 0 | 0 | 48 |  |  |  | -0.00445
274871 | GR RIDGE ;2U | W2 | 0.57 | 222 | Gen |  | 77 | 0 | 1 |  | 162.6 | 0 | 0 | 0 | 52.03 |  |  |  | -0.00446
276691 | AA1-018 GEN1 | W1 | 0.65 | 222 | Gen |  | 77 | 0 | 1 |  | 13.8 | 0 | 0 | 0 | 4.42 |  |  |  | -0.00445 |  |  |  | AA1-018
276694 | AA1-018 GEN2 | W2 | 0.65 | 222 | Gen |  | 77 | 0 | 1 |  | 136.8 | 0 | 0 | 0 | 43.78 |  |  |  | -0.00445 |  |  |  | AA1-018
252519 | AF1-045_GEN | B1 | 0.6 | 212 | Gen | New | 88 | 0.05 | 1 |  | 52.2 | 0 | -52.2 | 0 | 0 |  |  |  | -0.00444 |  |  |  | AF1-045
276170 | Z1-108 | B1 | 34.5 | 222 | Gen | New | 88 | 0 | 1 |  | 20 | 0 | -20 | 0 | 0 |  |  |  | -0.00445 |  |  |  | Z1-108
276778 | AA2-123 E | 1 | 34.5 | 222 | Gen | New | 88 | 0 | 1 |  | 20 | 0 | -20 | 0 | 0 |  |  |  | -0.00444 |  |  |  | AA2-123
251832 | 08HLCRTG | 1 | 0.38 | 212 | Gen |  | 86 | 0 | 1 |  | 200 | 0 | 0 | 0 | 108 |  |  |  | -0.00444
252510 | AF1-249 C | S1 | 138 | 212 | Gen |  | 86 | 0 | 1 |  | 19.92 | 0 | 0 | 0 | 10.76 |  |  |  | -0.00444 |  |  |  | AF1-249
252516 | AE2-318_GEN | S1 | 0.6 | 212 | Gen |  | 86 | 0 | 1 |  | 100 | 0 | 0 | 0 | 54 |  |  |  | -0.00444 |  |  |  | AE2-318
274863 | CAYUGA RI;1U | W1 | 0.69 | 222 | Gen |  | 77 | 0 | 1 |  | 150 | 0 | 0 | 0 | 48 |  |  |  | -0.00444
274864 | CAYUGA RI;2U | W2 | 0.69 | 222 | Gen |  | 77 | 0 | 1 |  | 150 | 0 | 0 | 0 | 48 |  |  |  | -0.00444
274872 | LEE DEKAL;1U | W1 | 0.57 | 222 | Gen |  | 77 | 0 | 1 |  | 240 | 0 | 0 | 0 | 76.8 |  |  |  | -0.00444 |  |  |  | Q57
274879 | MINONK ;1U | W1 | 0.69 | 222 | Gen |  | 77 | 0 | 1 |  | 200 | 0 | 0 | 0 | 64 |  |  |  | -0.00444
276678 | AD1-016 GEN | S1 | 138 | 222 | Gen | New | 83 | 0 | 1 |  | 20 | 0 | 0 | 0 | 0 |  |  |  | -0.00444 |  |  |  | AD1-016
251828 | 08CLESP1 | 1 | 34.5 | 212 | Gen | New | 88 | 0 | 1 |  | 10 | 0 | -10 | 0 | 0 |  |  |  | -0.00443
251827 | 08WLYESP | 1 | 34.5 | 212 | Gen | New | 88 | 0 | 1 |  | 6 | 0 | -6 | 0 | 0 |  |  |  | -0.00443
252507 | AC2-088 C | 1 | 0.57 | 212 | Gen |  | 83 | 0 | 1 |  | 70 | 0 | 0 | 0 | 37.1 |  |  |  | -0.00443 |  |  |  | AC2-088
252509 | AD1-136 GEN | S1 | 0.57 | 212 | Gen | New | 83 | 0 | 1 |  | 10 | 0 | 0 | 0 | 0 |  |  |  | -0.00443 |  |  |  | AC2-088
274850 | MENDOTA H;RU | W | 0.69 | 222 | Gen |  | 77 | 0 | 1 |  | 76.13 | 0 | 0 | 0 | 24.36 |  |  |  | -0.00444
274855 | GSG-6 ;RU | W | 0.69 | 222 | Gen |  | 77 | 0 | 1 |  | 80 | 0 | 0 | 0 | 25.6 |  |  |  | -0.00444
274856 | ECOGROVE ;U1 | W1 | 12 | 222 | Gen |  | 77 | 0 | 1 |  | 100 | 0 | 0 | 0 | 32 |  |  |  | -0.00443
276602 | WESTBROOK C | W1 | 138 | 222 | Gen |  | 77 | 0 | 1 |  | 54 | 0 | 0 | 0 | 17.28 |  |  |  | -0.00444
276611 | AD2-172 C | S1 | 138 | 222 | Gen |  | 86 | 0 | 1 |  | 50 | 0 | 0 | 0 | 27 |  |  |  | -0.00443 |  |  |  | AD2-172
276612 | AE2-035 C | S1 | 0.6 | 222 | Gen |  | 86 | 0 | 1 |  | 50 | 0 | 0 | 0 | 27 |  |  |  | -0.00443 |  |  |  | AE2-035
276679 | AD1-129 GEN | S1 | 34.5 | 222 | Gen | New | 86 | 0 | 1 |  | 12.5 | 0 | 0 | 0 | 0 |  |  |  | -0.00444 |  |  |  | AD1-129
926823 | AC1-168 GEN | 1 | 12 | 222 | Gen |  | 77 | 0 | 1 |  | 78.75 | 0 | 0 | 0 | 25.2 |  |  |  | -0.00444 |  |  |  | AC1-168
937001 | AD2-134 C | 1 | 138 | 222 | Gen | New | 77 | 0 | 1 |  | 105.9 | 0 | 0 | 0 | 0 |  |  |  | -0.00444 |  |  |  | AD2-134
250164 | 08BKJDB1 | 1 | 138 | 212 | Gen | New | 88 | 0 | 1 |  | 2 | 0 | -2 | 0 | 0 |  |  |  | -0.00443
250165 | 08BKJDB2 | 1 | 138 | 212 | Gen | New | 88 | 0 | 1 |  | 2 | 0 | -2 | 0 | 0 |  |  |  | -0.00443
276626 | AG1-044 E | E | 34.5 | 222 | Gen | New | 88 | 0 | 1 |  | 0.56 | 0 | -0.56 | 0 | 0 |  |  |  | -0.00442 |  |  |  | AG1-044
270309 | AB2-085 GEN | S1 | 0.38 | 205 | Gen | New | 86 | 0 | 1 |  | 80 | 0 | 0 | 0 | 0 |  |  |  | -0.00442 |  |  |  | AB2-085
270367 | AC2-061_GEN | S1 | 0.6 | 205 | Gen |  | 83 | 0 | 1 |  | 120.65 | 0 | 0 | 0 | 63.95 |  |  |  | -0.00443 |  |  |  | AC2-061
274848 | CAMPGROVE;RU | W | 0.57 | 222 | Gen |  | 77 | 0 | 1 |  | 150 | 0 | 0 | 0 | 48 |  |  |  | -0.00442
274849 | CRESCENT ;1U | W1 | 0.6 | 222 | Gen |  | 77 | 0 | 1 |  | 54.45 | 0 | 0 | 0 | 17.42 |  |  |  | -0.00443
274851 | PROVIDENC;RU | W3 | 0.69 | 222 | Gen |  | 77 | 0 | 1 |  | 74 | 0 | 0 | 0 | 23.68 |  |  |  | -0.00443
274853 | TWINGROVE;U1 | W1 | 0.69 | 222 | Gen |  | 77 | 0 | 1 |  | 198 | 0 | 0 | 0 | 63.36 |  |  |  | -0.00442
274854 | TWINGROVE;U2 | W2 | 0.69 | 222 | Gen |  | 77 | 0 | 1 |  | 198 | 0 | 0 | 0 | 63.36 |  |  |  | -0.00442
274857 | BIG SKY ;U1 | W1 | 0.69 | 222 | Gen |  | 77 | 0 | 1 |  | 120 | 0 | 0 | 0 | 38.4 |  |  |  | -0.00443
274858 | BIG SKY ;U2 | W2 | 0.69 | 222 | Gen |  | 77 | 0 | 1 |  | 120 | 0 | 0 | 0 | 38.4 |  |  |  | -0.00443
274877 | BISHOP HL;1U | W1 | 0.69 | 222 | Gen |  | 77 | 0 | 1 |  | 100 | 0 | 0 | 0 | 32 |  |  |  | -0.00442
274878 | BISHOP HL;2U | W2 | 0.69 | 222 | Gen |  | 77 | 0 | 1 |  | 100 | 0 | 0 | 0 | 32 |  |  |  | -0.00442
276157 | O29GEN1 | W1 | 0.69 | 222 | Gen |  | 77 | 0 | 1 |  | 112.88 | 0 | 0 | 0 | 36.12 |  |  |  | -0.00442 |  |  |  | O29
276158 | O29GEN2 | W1 | 0.69 | 222 | Gen |  | 77 | 0 | 1 |  | 112.88 | 0 | 0 | 0 | 36.12 |  |  |  | -0.00442 |  |  |  | O29
276603 | SUBLETTE C | W1 | 138 | 222 | Gen |  | 77 | 0 | 1 |  | 26 | 0 | 0 | 0 | 8.32 |  |  |  | -0.00443
276645 | AC1-214 C1 | W1 | 0.69 | 222 | Gen |  | 77 | 0 | 1 |  | 39.7 | 0 | 0 | 0 | 12.7 |  |  |  | -0.00443 |  |  |  | AC1-214
276646 | AC1-214 C2 | W1 | 0.69 | 222 | Gen |  | 77 | 0 | 1 |  | 39.7 | 0 | 0 | 0 | 12.7 |  |  |  | -0.00443 |  |  |  | AC1-214
276655 | AB2-047 C1 | W1 | 0.69 | 222 | Gen |  | 77 | 0 | 1 |  | 125 | 0 | 0 | 0 | 40 |  |  |  | -0.00443 |  |  |  | AB2-047
276656 | AB2-047 C2 | W1 | 0.69 | 222 | Gen |  | 77 | 0 | 1 |  | 125 | 0 | 0 | 0 | 40 |  |  |  | -0.00443 |  |  |  | AB2-047
276708 | O09 GEN2 | 1 | 0.69 | 222 | Gen |  | 77 | 0 | 1 |  | 106 | 0 | 0 | 0 | 21.24 |  |  |  | -0.00442 |  |  |  | O09
276726 | Z2-087_GEN | W1 | 0.65 | 222 | Gen |  | 77 | 0 | 1 |  | 205.2 | 0 | 0 | 0 | 65.66 |  |  |  | -0.00443 |  |  |  | Z2-087
276741 | O09 GEN1 | 1 | 0.69 | 222 | Gen |  | 77 | 0 | 1 |  | 106 | 0 | 0 | 0 | 20.64 |  |  |  | -0.00442 |  |  |  | O09
276780 | AC1-033 GEN | W1 | 0.69 | 222 | Gen |  | 77 | 0 | 1 |  | 100.8 | 0 | 0 | 0 | 32.26 |  |  |  | -0.00442 |  |  |  | AC1-033
270186 | AC1-089 C | S1 | 0.39 | 205 | Gen |  | 83 | 0 | 1 |  | 150 | 0 | 0 | 0 | 79.5 |  |  |  | -0.00442 |  |  |  | AC1-089
241966 | AE1-183 GEN | S1 | 0.6 | 202 | Gen | New | 86 | 0 | 1 |  | 20 | 0 | 0 | 0 | 0 |  |  |  | -0.0044 |  |  |  | AE1-183
241997 | AF1-093 GEN | S1 | 69 | 202 | Gen | New | 86 | 0 | 1 |  | 20 | 0 | 0 | 0 | 0 |  |  |  | -0.0044 |  |  |  | AF1-093
276174 | W4-005 GEN2 | W1 | 0.69 | 222 | Gen |  | 77 | 0 | 1 |  | 96.8 | 0 | 0 | 0 | 30.98 |  |  |  | -0.00441 |  |  |  | W4-005
276615 | AF2-317 | W1 | 0.69 | 222 | Gen |  | 77 | 0 | 1 |  | 65 | 0 | 0 | 0 | 20.8 |  |  |  | -0.0044 |  |  |  | AF2-317
276621 | X2-022 GEN | W1 | 0.69 | 222 | Gen |  | 77 | 0 | 1 |  | 185 | 0 | 0 | 0 | 59.2 |  |  |  | -0.0044 |  |  |  | X2-022
276668 | AB2-070 GEN1 | W1 | 0.69 | 222 | Gen |  | 77 | 0 | 1 |  | 200 | 0 | 0 | 0 | 64 |  |  |  | -0.00441 |  |  |  | AB2-070
276686 | W4-005 GEN3 | W1 | 0.69 | 222 | Gen |  | 77 | 0 | 1 |  | 105.6 | 0 | 0 | 0 | 33.79 |  |  |  | -0.00441 |  |  |  | W4-005
276763 | AC1-053 GEN1 | 1 | 0.69 | 222 | Gen |  | 77 | 0 | 1 |  | 100 | 0 | 0 | 0 | 32 |  |  |  | -0.0044 |  |  |  | AC1-053
276764 | AC1-053 GEN2 | 1 | 0.69 | 222 | Gen |  | 77 | 0 | 1 |  | 100 | 0 | 0 | 0 | 32 |  |  |  | -0.0044 |  |  |  | AC1-053
276785 | W4-005 GEN1 | W1 | 0.69 | 222 | Gen |  | 77 | 0 | 1 |  | 103.4 | 0 | 0 | 0 | 33.09 |  |  |  | -0.00441 |  |  |  | W4-005
339216 | AC1-074 C | 1 | 0.6 | 320 | Gen |  | 86 | 0 | 1 |  | 93.3 | 0 | 0 | 0 | 50.38 |  |  |  | -0.00436 |  |  |  | AC1-074
339218 | AC2-075 C | S1 | 0.6 | 320 | Gen |  | 86 | 0 | 1 |  | 20.7 | 0 | 0 | 0 | 11.18 |  |  |  | -0.00436 |  |  |  | AC2-075
339221 | AD2-048_GEN | S1 | 0.55 | 320 | Gen |  | 86 | 0 | 1 |  | 70.75 | 0 | 0 | 0 | 38.21 |  |  |  | -0.00436 |  |  |  | AD2-048
270329 | AC1-082 GEN1 | S1 | 0.69 | 205 | Gen | New | 86 | 0 | 1 |  | 15.75 | 0 | 0 | 0 | 0 |  |  |  | -0.00433 |  |  |  | AC1-082
270330 | AC1-082 GEN2 | S1 | 0.69 | 205 | Gen | New | 86 | 0 | 1 |  | 18.9 | 0 | 0 | 0 | 0 |  |  |  | -0.00433 |  |  |  | AC1-082
270331 | AC1-082 GEN3 | S1 | 0.69 | 205 | Gen | New | 86 | 0 | 1 |  | 15.75 | 0 | 0 | 0 | 0 |  |  |  | -0.00433 |  |  |  | AC1-082
339200 | AD2-072_GEN | S1 | 0.6 | 320 | Gen | New | 86 | 0 | 1 |  | 95 | 0 | 0 | 0 | 0 |  |  |  | -0.0043 |  |  |  | AD2-072
339211 | AE2-254 GEN | 1 | 0.66 | 320 | Gen |  | 86 | 0 | 1 |  | 50 | 0 | 0 | 0 | 27 |  |  |  | -0.00427 |  |  |  | AE2-254
270192 | AB1-055 E | 1 | 138 | 205 | Gen | New | 88 | 0 | 1 |  | 2 | 0 | -2 | 0 | 0 |  |  |  | -0.00422 |  |  |  | AB1-055
339206 | AE1-143 C | B1 | 0.64 | 320 | Gen | New | 88 | 0.05 | 1 |  | 96 | 0 | 0 | 0 | 0 |  |  |  | -0.00422 |  |  |  | AE1-143 |  | MFO
339206 | AE1-143 C | S1 | 0.64 | 320 | Gen |  | 86 | 0 | 1 |  | 96 | 0 | 0 | 0 | 52.43 |  |  |  | -0.00422 |  |  |  | AE1-143 |  | MFO
339241 | AF1-083 GEN | B1 | 0.6 | 320 | Gen | New | 88 | 0 | 1 |  | 26 | 0 | 0 | 0 | 0 |  |  |  | -0.00421 |  |  |  | AF1-083 |  | MFO
339241 | AF1-083 GEN | S1 | 0.6 | 320 | Gen |  | 86 | 0 | 1 |  | 55.6 | 0 | 0 | 0 | 30.02 |  |  |  | -0.00421 |  |  |  | AF1-083 |  | MFO
339236 | AF1-050_GEN | B1 | 0.66 | 320 | Gen | New | 88 | 0 | 1 |  | 30 | 0 | 0 | 0 | 0 |  |  |  | -0.0042 |  |  |  | AF1-050 |  | MFO
339236 | AF1-050_GEN | S1 | 0.66 | 320 | Gen |  | 86 | 0 | 1 |  | 60.5 | 0 | 0 | 0 | 32.67 |  |  |  | -0.0042 |  |  |  | AF1-050 |  | MFO
339231 | AF1-038_GEN | B1 | 0.66 | 320 | Gen | New | 88 | 0 | 1 |  | 30 | 0 | 0 | 0 | 0 |  |  |  | -0.00419 |  |  |  | AF1-038 |  | MFO
339231 | AF1-038_GEN | S1 | 0.66 | 320 | Gen |  | 86 | 0 | 1 |  | 60 | 0 | 0 | 0 | 32.4 |  |  |  | -0.00419 |  |  |  | AF1-038 |  | MFO
243758 | 05MIDDLECR | B1 | 46 | 205 | Gen | New | 88 | 0 | 1 |  | 2 | 0 | -2 | 0 | 0 |  |  |  | -0.00414
270399 | AC1-101 GEN | S1 | 0.64 | 205 | Gen |  | 83 | 0 | 1 |  | 50 | 0 | 0 | 0 | 26.5 |  |  |  | -0.00412 |  |  |  | AC1-101
270400 | AC1-102 GEN | 1 | 0.64 | 205 | Gen |  | 83 | 0 | 1 |  | 50 | 0 | 0 | 0 | 26.5 |  |  |  | -0.00412 |  |  |  | AC1-102
241986 | AG1-251 GEN | S1 | 69 | 202 | Gen |  | 86 | 0 | 1 |  | 3.88 | 0 | 0 | 0 | 2.09 |  |  |  | -0.00395 |  |  |  | AG1-251
270346 | AE1-212 GEN | S1 | 0.63 | 205 | Gen |  | 86 | 0 | 1 |  | 90 | 0 | 0 | 0 | 48.6 |  |  |  | -0.0039 |  |  |  | AE1-212
270167 | AD2-205 E | 1 | 69 | 205 | Gen | New | 88 | 0 | 1 |  | 4 | 0 | -4 | 0 | 0 |  |  |  | -0.0038 |  |  |  | AD2-205
270214 | AC2-123 C | 1 | 0.42 | 205 | Gen |  | 86 | 0 | 1 |  | 75 | 0 | 0 | 0 | 40.5 |  |  |  | -0.0038 |  |  |  | AC2-123
238115 | M24_BAT | W1 | 0.35 | 201 | Gen | New | 88 | 0 | 1 |  | 32 | 0 | -32 | 0 | 0 |  |  |  | -0.00361
235780 | M24_1 | W1 | 0.57 | 201 | Gen |  | 77 | 0 | 1 |  | 100.5 | 0 | 0 | 0 | 32.16 |  |  |  | -0.00361 |  |  |  | M24
237033 | AB1-150 GEN1 | W1 | 0.69 | 201 | Gen |  | 77 | 0 | 1 |  | 55.6 | 0 | 0 | 0 | 17.79 |  |  |  | -0.00361 |  |  |  | AB1-150
238114 | M24_2 | W1 | 0.57 | 201 | Gen |  | 77 | 0 | 1 |  | 54 | 0 | 0 | 0 | 17.28 |  |  |  | -0.00361 |  |  |  | M24
270336 | AE1-100 GEN | S1 | 0.55 | 205 | Gen |  | 86 | 0 | 1 |  | 66.75 | 0 | 0 | 0 | 36.05 |  |  |  | -0.00355 |  |  |  | AE1-100
270173 | AC1-122 C | 1 | 0.6 | 205 | Gen |  | 86 | 0 | 1 |  | 75.9 | 0 | 0 | 0 | 40.99 |  |  |  | -0.00345 |  |  |  | AC1-122
244012 | 05PINNACLE | 1 | 4 | 205 | Gen | New | 83 | 0 | 1 |  | 11 | 0 | 0 | 0 | 0 |  |  |  | -0.00342
270197 | AC1-083 C | 1 | 0.39 | 205 | Gen |  | 83 | 0 | 1 |  | 120 | 0 | 0 | 0 | 63.6 |  |  |  | -0.00341 |  |  |  | AC1-083
316197 | AC1-042 C | 1 | 0.39 | 345 | Gen |  | 84 | 0 | 1 |  | 42 | 0 | 0 | 0 | 24.78 |  |  |  | -0.00338 |  |  |  | AC1-042
316217 | AC1-145 C | 1 | 0.6 | 345 | Gen |  | 87 | 0 | 1 |  | 50 | 0 | 0 | 0 | 29 |  |  |  | -0.00338 |  |  |  | AC1-145
945081 | AF1-173 | 1 | 69 | 345 | Gen | New | 84 | 0 | 1 |  | 13.95 | 0 | 0 | 0 | 0 |  |  |  | -0.00338 |  |  |  | AF1-173
238122 | AG1-246 GEN | S1 | 25 | 201 | Gen |  | 86 | 0 | 1 |  | 7.5 | 0 | 0 | 0 | 4.05 |  |  |  | 0.00333 |  |  |  | AG1-246
316123 | AC1-075 C | 1 | 0.63 | 345 | Gen |  | 87 | 0 | 1 |  | 80 | 0 | 0 | 0 | 46.4 |  |  |  | -0.00318 |  |  |  | AC1-075 and AC1-080
316283 | AC2-100 C | S1 | 0.57 | 345 | Gen |  | 87 | 0 | 1 |  | 62 | 0 | 0 | 0 | 35.96 |  |  |  | -0.00318 |  |  |  | AC2-100
316222 | AC1-221 GEN | 1 | 0.6 | 345 | Gen | New | 87 | 0 | 1 |  | 65.8 | 0 | 0 | 0 | 0 |  |  |  | -0.00316 |  |  |  | AC1-221
316003 | AC1-222 GEN | S1 | 0.6 | 345 | Gen | New | 87 | 0 | 1 |  | 64.7 | 0 | 0 | 0 | 0 |  |  |  | -0.00306 |  |  |  | AC1-222
316248 | AF1-058 C | 1 | 115 | 345 | Gen |  | 87 | 0 | 1 |  | 20 | 0 | 0 | 0 | 11.6 |  |  |  | -0.00302 |  |  |  | AF1-058
316049 | AB1-081 GEN | 1 | 0.63 | 345 | Gen |  | 87 | 0 | 1 |  | 82.8 | 0 | 0 | 0 | 48.02 |  |  |  | -0.003 |  |  |  | AB1-081
316118 | AC1-105 C | 1 | 0.57 | 345 | Gen |  | 87 | 0 | 1 |  | 51.45 | 0 | 0 | 0 | 29.84 |  |  |  | -0.003 |  |  |  | AC1-105
316263 | AC1-034 C | 1 | 0.55 | 345 | Gen |  | 87 | 0 | 1 |  | 75 | 0 | 0 | 0 | 43.5 |  |  |  | -0.003 |  |  |  | AC1-034
316359 | AB2-059 C OP | 1 | 0.63 | 345 | Gen |  | 87 | 0 | 1 |  | 100 | 0 | 0 | 0 | 58 |  |  |  | -0.003 |  |  |  | AB2-059
316319 | Z2-044 C | S1 | 115 | 345 | Gen |  | 87 | 0 | 1 |  | 12 | 0 | 0 | 0 | 6.96 |  |  |  | -0.00297 |  |  |  | Z2-044
315601 | 1CONETOE2SOL | SA | 0.69 | 345 | Gen |  | 87 | 0 | 1 |  | 98.4 | 0 | 0 | 0 | 57.07 |  |  |  | -0.00297 |  |  |  | Z2-088
316494 | AC1-189 GEN | S1 | 0.38 | 345 | Gen | New | 87 | 0 | 1 |  | 80 | 0 | 0 | 0 | 0 |  |  |  | -0.00296 |  |  |  | AC1-189
316327 | AA2-057 C | S1 | 0.63 | 345 | Gen |  | 87 | 0 | 1 |  | 74.9 | 0 | 0 | 0 | 43.44 |  |  |  | -0.00295 |  |  |  | AA2-057
316005 | AA1-067 C | S1 | 230 | 345 | Gen |  | 87 | 0 | 1 |  | 15 | 0 | 0 | 0 | 8.7 |  |  |  | -0.00294 |  |  |  | AA1-067
316210 | AC1-098 GEN | 1 | 0.6 | 345 | Gen |  | 87 | 0 | 1 |  | 60 | 0 | 0 | 0 | 34.8 |  |  |  | -0.0029 |  |  |  | AC1-098
316212 | AC1-099_GEN | 1 | 0.6 | 345 | Gen |  | 87 | 0 | 1 |  | 20 | 0 | 0 | 0 | 11.6 |  |  |  | -0.0029 |  |  |  | AC1-099
316237 | AB2-079 C | 1 | 115 | 345 | Gen |  | 87 | 0 | 1 |  | 20 | 0 | 0 | 0 | 11.6 |  |  |  | -0.0029 |  |  |  | AB2-079
316238 | AB2-078 C | 1 | 115 | 345 | Gen |  | 87 | 0 | 1 |  | 20 | 0 | 0 | 0 | 11.6 |  |  |  | -0.0029 |  |  |  | AB2-078
316239 | AB2-077 C | 1 | 115 | 345 | Gen |  | 87 | 0 | 1 |  | 20 | 0 | 0 | 0 | 11.6 |  |  |  | -0.0029 |  |  |  | AB2-077
316274 | AC1-208 GEN | 1 | 0.38 | 345 | Gen |  | 87 | 0 | 1 |  | 80 | 0 | 0 | 0 | 46.4 |  |  |  | -0.00291 |  |  |  | AC1-208
316489 | AC2-084 GEN | S1 | 0.6 | 345 | Gen |  | 84 | 0 | 1 |  | 61.25 | 0 | 0 | 0 | 36.14 |  |  |  | -0.0029 |  |  |  | AC2-084
313527 | AB2-043 C | 1 | 0.55 | 345 | Gen |  | 87 | 0 | 1 |  | 49.9 | 0 | 0 | 0 | 28.94 |  |  |  | -0.0029 |  |  |  | AB2-043
316129 | AC1-054 C | 1 | 0.38 | 345 | Gen |  | 87 | 0 | 1 |  | 65 | 0 | 0 | 0 | 37.7 |  |  |  | -0.00289 |  |  |  | AC1-054
316131 | AB2-060 C | S1 | 0.63 | 345 | Gen |  | 87 | 0 | 1 |  | 80.08 | 0 | 0 | 0 | 46.45 |  |  |  | -0.0029 |  |  |  | AB2-060
315616 | AA1-038_C | W1 | 0.69 | 345 | Gen |  | 78 | 0 | 1 |  | 78.2 | 0 | 0 | 0 | 25.02 |  |  |  | -0.00288 |  |  |  | AA1-038
316034 | AC1-036 C | 1 | 115 | 345 | Gen |  | 87 | 0 | 1 |  | 17.9 | 0 | 0 | 0 | 10.38 |  |  |  | -0.00287 |  |  |  | AC1-036
316174 | AB2-169_C | S1 | 0.63 | 345 | Gen |  | 87 | 0 | 1 |  | 74 | 0 | 0 | 0 | 42.92 |  |  |  | -0.00286 |  |  |  | AB2-169
315687 | AD1-152 GEN | S1 | 0.6 | 345 | Gen |  | 87 | 0 | 1 |  | 80 | 0 | 0 | 0 | 46.4 |  |  |  | -0.00285 |  |  |  | AD1-152
316317 | KELFORD C | S1 | 115 | 345 | Gen |  | 87 | 0 | 1 |  | 20.2 | 0 | 0 | 0 | 11.72 |  |  |  | -0.00285
316478 | AD1-087 GEN | S1 | 0.66 | 345 | Gen |  | 87 | 0 | 1 |  | 64.2 | 0 | 0 | 0 | 37.24 |  |  |  | -0.00285 |  |  |  | AD1-087
316486 | AD2-202 GEN | S1 | 0.66 | 345 | Gen |  | 87 | 0 | 1 |  | 18.8 | 0 | 0 | 0 | 10.9 |  |  |  | -0.00285 |  |  |  | AD2-202
315606 | AA2-053 GEN | S1 | 0.63 | 345 | Gen |  | 87 | 0 | 1 |  | 77.3 | 0 | 0 | 0 | 44.83 |  |  |  | -0.00285 |  |  |  | AA2-053
315652 | AC1-086 GEN | S1 | 0.38 | 345 | Gen |  | 87 | 0 | 1 |  | 180 | 0 | 0 | 0 | 104.4 |  |  |  | -0.00285 |  |  |  | AC1-086
316011 | AB1-132 C OP | 1 | 230 | 345 | Gen |  | 87 | 0 | 1 |  | 120 | 0 | 0 | 0 | 69.6 |  |  |  | -0.00285 |  |  |  | AB1-132
316190 | AA2-174 GEN | S1 | 0.63 | 345 | Gen |  | 87 | 0 | 1 |  | 5 | 0 | 0 | 0 | 2.9 |  |  |  | -0.00285 |  |  |  | AA2-053
313506 | AB1-173 C OP | 1 | 115 | 345 | Gen |  | 87 | 0 | 1 |  | 59.6 | 0 | 0 | 0 | 34.57 |  |  |  | -0.00283 |  |  |  | AB1-173
315657 | AE1-056 GEN | S1 | 0.55 | 345 | Gen | New | 87 | 0 | 1 |  | 60.56 | 0 | 0 | 0 | 0 |  |  |  | -0.00284 |  |  |  | AE1-056
315693 | AD1-088 GEN | S1 | 0.7 | 345 | Gen |  | 87 | 0 | 1 |  | 113 | 0 | 0 | 0 | 65.54 |  |  |  | -0.00283 |  |  |  | AD1-088
316181 | AB2-040 GEN | 1 | 0.6 | 345 | Gen |  | 84 | 0 | 1 |  | 81.51 | 0 | 0 | 0 | 48.09 |  |  |  | -0.00283 |  |  |  | AB2-040
315607 | 3AA1-063SOLA | SA | 115 | 345 | Gen |  | 87 | 0 | 1 |  | 74.8 | 0 | 0 | 0 | 43.38 |  |  |  | -0.00283 |  |  |  | AA1-063
316087 | AB2-174 C | 1 | 0.4 | 345 | Gen |  | 84 | 0 | 1 |  | 80 | 0 | 0 | 0 | 47.2 |  |  |  | -0.00283 |  |  |  | AB2-174
316140 | AB2-099 | 1 | 115 | 345 | Gen | New | 87 | 0 | 1 |  | 5 | 0 | 0 | 0 | 0 |  |  |  | -0.00282 |  |  |  | AB2-099
316463 | AE2-346 GEN | S1 | 115 | 345 | Gen |  | 87 | 0 | 1 |  | 12 | 0 | 0 | 0 | 6.96 |  |  |  | -0.00282 |  |  |  | AE2-346
315602 | 1HOLLOMANSOL | SA | 0.69 | 345 | Gen |  | 87 | 0 | 1 |  | 91 | 0 | 0 | 0 | 52.78 |  |  |  | -0.00282
316065 | AD1-022 GEN | S1 | 0.55 | 345 | Gen |  | 87 | 0 | 1 |  | 81 | 0 | 0 | 0 | 46.98 |  |  |  | -0.0028 |  |  |  | AD1-022
316318 | V4-068 C | S1 | 115 | 345 | Gen |  | 87 | 0 | 1 |  | 4.67 | 0 | 0 | 0 | 2.71 |  |  |  | -0.0028 |  |  |  | V4-068
316023 | AB2-100 C2 | S2 | 0.55 | 345 | Gen |  | 87 | 0 | 1 |  | 50 | 0 | 0 | 0 | 29 |  |  |  | -0.00279 |  |  |  | AB2-100
316365 | AB2-100 C1 | S1 | 0.55 | 345 | Gen |  | 87 | 0 | 1 |  | 50 | 0 | 0 | 0 | 29 |  |  |  | -0.00279 |  |  |  | AB2-100
315608 | 3AA2-088SOLA | SA | 115 | 345 | Gen |  | 87 | 0 | 1 |  | 100 | 0 | 0 | 0 | 58 |  |  |  | -0.00278 |  |  |  | AA2-088
315614 | AA2-178 C | 1 | 0.69 | 345 | Gen |  | 87 | 0 | 1 |  | 80 | 0 | 0 | 0 | 46.4 |  |  |  | -0.00276 |  |  |  | AA2-178
316322 | AB2-045 C | S1 | 230 | 345 | Gen |  | 87 | 0 | 1 |  | 17.73 | 0 | 0 | 0 | 10.28 |  |  |  | -0.00275 |  |  |  | AB2-045
314541 | 3WATKINS | A | 115 | 345 | Gen | New | 84 | 0 | 1 |  | 4 | 0 | 0 | 0 | 0 |  |  |  | -0.00274
316299 | AC2-112 C | S1 | 0.6 | 345 | Gen |  | 87 | 0 | 1 |  | 150 | 0 | 0 | 0 | 87 |  |  |  | -0.00274 |  |  |  | AC2-112
316300 | AF2-400 C | S1 | 115 | 345 | Gen |  | 84 | 0 | 1 |  | 7.14 | 0 | 0 | 0 | 4.21 |  |  |  | -0.00273 |  |  |  | AF2-400
316334 | AE1-084 C | 1 | 0.63 | 345 | Gen | New | 87 | 0 | 1 |  | 83 | 0 | 0 | 0 | 0 |  |  |  | -0.00274 |  |  |  | AE1-084
237046 | AF1-021 C | 1 | 25 | 201 | Gen |  | 86 | 0 | 1 |  | 14 | 0 | 0 | 0 | 7.56 |  |  |  | 0.00272 |  |  |  | AF1-021
315611 | 6Z1-036WIND | WA | 230 | 345 | Gen |  | 78 | 0 | 1 |  | 300.3 | 0 | 0 | 0 | 96.1 |  |  |  | -0.00271 |  |  |  | Z1-036
316315 | AB2-025 C | S1 | 230 | 345 | Gen |  | 87 | 0 | 1 |  | 19.85 | 0 | 0 | 0 | 11.51 |  |  |  | -0.0027 |  |  |  | AB2-025
316035 | AC1-116 C | 1 | 230 | 345 | Gen |  | 84 | 0 | 1 |  | 12.5 | 0 | 0 | 0 | 7.38 |  |  |  | -0.00268 |  |  |  | AC1-116
316431 | W1029_GEN1 | 1 | 0.69 | 345 | Gen |  | 78 | 0 | 1 |  | 69.33 | 0 | 0 | 0 | 22.19 |  |  |  | -0.00268 |  |  |  | W1-029
316433 | W1029_GEN2 | 2 | 0.69 | 345 | Gen |  | 78 | 0 | 1 |  | 69.33 | 0 | 0 | 0 | 22.19 |  |  |  | -0.00268 |  |  |  | W1-029
316435 | W1029_GEN3 | 3 | 0.69 | 345 | Gen |  | 78 | 0 | 1 |  | 69.33 | 0 | 0 | 0 | 22.19 |  |  |  | -0.00268 |  |  |  | W1-029
316321 | Z2-027 C | S1 | 230 | 345 | Gen |  | 87 | 0 | 1 |  | 20 | 0 | 0 | 0 | 11.6 |  |  |  | -0.00267 |  |  |  | Z2-027
316499 | AE2-029_GEN | S1 | 0.6 | 345 | Gen |  | 87 | 0 | 1 |  | 50.5 | 0 | 0 | 0 | 29.29 |  |  |  | -0.00267 |  |  |  | AE2-029
313526 | AB2-022 C | 1 | 230 | 345 | Gen |  | 87 | 0 | 1 |  | 20 | 0 | 0 | 0 | 11.6 |  |  |  | -0.00267 |  |  |  | AB2-022
316320 | Y1-086 C | S1 | 230 | 345 | Gen |  | 84 | 0 | 1 |  | 20 | 0 | 0 | 0 | 11.8 |  |  |  | -0.00267 |  |  |  | Y1-086
316093 | AE2-104_GEN | S1 | 0.39 | 345 | Gen |  | 84 | 0 | 1 |  | 49.8 | 0 | 0 | 0 | 29.38 |  |  |  | -0.00266 |  |  |  | AE2-104
316246 | AF1-032 C | 1 | 230 | 345 | Gen |  | 87 | 0 | 1 |  | 15 | 0 | 0 | 0 | 8.7 |  |  |  | -0.00265 |  |  |  | AF1-032
316305 | AF2-043 C | S1 | 230 | 345 | Gen |  | 87 | 0 | 1 |  | 20 | 0 | 0 | 0 | 11.6 |  |  |  | -0.00265 |  |  |  | AF2-043
316017 | AA1-139 ULT1 | S1 | 0.69 | 345 | Gen |  | 87 | 0 | 1 |  | 60 | 0 | 0 | 0 | 34.8 |  |  |  | -0.00265 |  |  |  | AA1-139
316018 | AA1-139 ULT2 | S2 | 0.69 | 345 | Gen |  | 87 | 0 | 1 |  | 60 | 0 | 0 | 0 | 34.8 |  |  |  | -0.00265 |  |  |  | AA1-139
316311 | AC2-079 GEN | S1 | 0.64 | 345 | Gen | New | 84 | 0 | 1 |  | 85 | 0 | 0 | 0 | 0 |  |  |  | -0.00265 |  |  |  | AC2-079
316339 | AD2-160 C | 1 | 0.63 | 345 | Gen |  | 87 | 0 | 1 |  | 50 | 0 | 0 | 0 | 29 |  |  |  | -0.00265 |  |  |  | AD2-160
316349 | AD2-085 GEN | 1 | 0.39 | 345 | Gen |  | 84 | 0 | 1 |  | 51 | 0 | 0 | 0 | 30.09 |  |  |  | -0.00265 |  |  |  | AD2-085
316388 | AE2-253 GEN | 1 | 0.63 | 345 | Gen |  | 87 | 0 | 1 |  | 100 | 0 | 0 | 0 | 58 |  |  |  | -0.00265 |  |  |  | AE2-253
316416 | AF2-057 | B1 | 115 | 345 | Gen | New | 88 | 0 | 1 |  | 20 | 0 | -20 | 0 | 0 |  |  |  | -0.00263 |  |  |  | AF2-057
314295 | 6BIRDNECK | WA | 230 | 345 | Gen |  | 81 | 0 | 1 |  | 12 | 0 | 0 | 0 | 5.88 |  |  |  | -0.00264
316036 | AC1-147 C | S1 | 115 | 345 | Gen |  | 87 | 0 | 1 |  | 20 | 0 | 0 | 0 | 11.6 |  |  |  | -0.00263 |  |  |  | AC1-147
316072 | AD1-144 C | 1 | 230 | 345 | Gen |  | 87 | 0 | 1 |  | 15 | 0 | 0 | 0 | 8.7 |  |  |  | -0.00264 |  |  |  | AD1-144
316152 | AE1-098 C | 1 | 115 | 345 | Gen |  | 87 | 0 | 1 |  | 15.7 | 0 | 0 | 0 | 9.11 |  |  |  | -0.00263 |  |  |  | AE1-098
316154 | AE1-099 C | 1 | 115 | 345 | Gen |  | 87 | 0 | 1 |  | 15.7 | 0 | 0 | 0 | 9.11 |  |  |  | -0.00263 |  |  |  | AE1-099
316185 | AD1-033 C | S1 | 0.6 | 345 | Gen |  | 87 | 0 | 1 |  | 70 | 0 | 0 | 0 | 40.6 |  |  |  | -0.00264 |  |  |  | AD1-033
316316 | AC1-027 C | S1 | 115 | 345 | Gen |  | 87 | 0 | 1 |  | 17.2 | 0 | 0 | 0 | 9.98 |  |  |  | -0.00264 |  |  |  | AC1-027
316375 | AC2-012 C | S1 | 0.6 | 345 | Gen |  | 84 | 0 | 1 |  | 150 | 0 | 0 | 0 | 88.5 |  |  |  | -0.00263 |  |  |  | AC2-012
316083 | AB2-161 C | 1 | 0.55 | 345 | Gen |  | 84 | 0 | 1 |  | 50 | 0 | 0 | 0 | 29.5 |  |  |  | -0.00263 |  |  |  | AB2-161
316336 | AC2-165 C | 1 | 230 | 345 | Gen | New | 87 | 0 | 1 |  | 99.9 | 0 | 0 | 0 | 0 |  |  |  | -0.00262 |  |  |  | AC2-165
316381 | AD1-082 C | 1 | 0.55 | 345 | Gen |  | 87 | 0 | 1 |  | 68 | 0 | 0 | 0 | 39.44 |  |  |  | -0.00263 |  |  |  | AD1-082
316236 | AE1-162 C | 1 | 230 | 345 | Gen |  | 87 | 0 | 1 |  | 20 | 0 | 0 | 0 | 11.6 |  |  |  | -0.00261 |  |  |  | AE1-162
316294 | AC1-161 C | S1 | 0.44 | 345 | Gen |  | 87 | 0 | 1 |  | 240 | 0 | 0 | 0 | 139.2 |  |  |  | -0.00262 |  |  |  | AC1-161
316405 | AF2-144 C | B1 | 230 | 345 | Gen | New | 88 | 0 | 1 |  | 11 | 0 | -11 | 0 | 0 |  |  |  | -0.0026 |  |  |  | AF2-144 |  | MFO
316405 | AF2-144 C | S1 | 230 | 345 | Gen |  | 87 | 0 | 1 |  | 17 | 0 | 0 | 0 | 9.86 |  |  |  | -0.0026 |  |  |  | AF2-144 |  | MFO
316247 | AF1-033 C | 1 | 230 | 345 | Gen |  | 87 | 0 | 1 |  | 20 | 0 | 0 | 0 | 11.6 |  |  |  | -0.0026 |  |  |  | AF1-033
316258 | AE1-075 C | S1 | 230 | 345 | Gen |  | 87 | 0 | 1 |  | 18 | 0 | 0 | 0 | 10.44 |  |  |  | -0.0026 |  |  |  | AE1-075
316313 | AB2-026 C | S1 | 230 | 345 | Gen |  | 87 | 0 | 1 |  | 20 | 0 | 0 | 0 | 11.6 |  |  |  | -0.0026 |  |  |  | AB2-026
315697 | AD1-025 GEN | S1 | 0.6 | 345 | Gen |  | 87 | 0 | 1 |  | 153.41 | 0 | 0 | 0 | 88.98 |  |  |  | -0.00259 |  |  |  | AD1-025
316033 | AB2-134 GEN | S1 | 0.63 | 345 | Gen |  | 87 | 0 | 1 |  | 142.4 | 0 | 0 | 0 | 82.59 |  |  |  | -0.00259 |  |  |  | AB2-134
316108 | AB2-160 GEN | 1 | 0.55 | 345 | Gen | New | 84 | 0 | 1 |  | 80 | 0 | 0 | 0 | 0 |  |  |  | -0.00258 |  |  |  | AB2-160
316132 | AB2-190 C | S1 | 0.63 | 345 | Gen |  | 87 | 0 | 1 |  | 160 | 0 | 0 | 0 | 92.8 |  |  |  | -0.00259 |  |  |  | AB2-190
316369 | AC1-216 C | S1 | 34.5 | 345 | Gen |  | 87 | 0 | 1 |  | 97.9 | 0 | 0 | 0 | 56.78 |  |  |  | -0.00259 |  |  |  | AC1-216
315671 | AE2-027_GEN | 1 | 0.69 | 345 | Gen |  | 87 | 0 | 1 |  | 122.26 | 0 | 0 | 0 | 70.91 |  |  |  | -0.00258 |  |  |  | AE2-027
316240 | AF1-291 C | 1 | 230 | 345 | Gen |  | 87 | 0 | 1 |  | 20 | 0 | 0 | 0 | 11.6 |  |  |  | -0.00257 |  |  |  | AF1-291
316301 | AE2-228 C | S1 | 230 | 345 | Gen |  | 87 | 0 | 1 |  | 25 | 0 | 0 | 0 | 14.5 |  |  |  | -0.00258 |  |  |  | AE2-228
237028 | AC1-073 C | W1 | 138 | 201 | Gen |  | 77 | 0 | 1 |  | 16.3 | 0 | 0 | 0 | 5.22 |  |  |  | -0.00256 |  |  |  | AC1-073
237092 | AD1-085_C | 1 | 0.6 | 201 | Gen |  | 86 | 0 | 1 |  | 32.29 | 0 | 0 | 0 | 17.44 |  |  |  | -0.00257 |  |  |  | AD1-085
237511 | 01LEADS_P59 | W1 | 0.69 | 201 | Gen |  | 77 | 0 | 1 |  | 97.6 | 0 | 0 | 0 | 31.23 |  |  |  | -0.00256 |  |  |  | P59
316159 | AE1-175 C | 1 | 230 | 345 | Gen |  | 87 | 0 | 1 |  | 19.9 | 0 | 0 | 0 | 11.54 |  |  |  | -0.00256 |  |  |  | AE1-175
316382 | AG1-145 C | 1 | 230 | 345 | Gen |  | 87 | 0 | 1 |  | 20 | 0 | 0 | 0 | 11.6 |  |  |  | -0.00256 |  |  |  | AG1-145
316303 | AF2-085 | B1 | 230 | 345 | Gen | New | 88 | 0 | 1 |  | 20 | 0 | -20 | 0 | 0 |  |  |  | -0.00253 |  |  |  | AF2-085
315662 | AE1-191 GEN | S1 | 0.6 | 345 | Gen |  | 87 | 0 | 1 |  | 80 | 0 | 0 | 0 | 46.4 |  |  |  | -0.00252 |  |  |  | AE1-191
315666 | AE1-190 GEN | S1 | 0.6 | 345 | Gen |  | 87 | 0 | 1 |  | 20 | 0 | 0 | 0 | 11.6 |  |  |  | -0.00252 |  |  |  | AE1-190
316059 | AD1-063 C | 1 | 230 | 345 | Gen |  | 87 | 0 | 1 |  | 15 | 0 | 0 | 0 | 8.7 |  |  |  | -0.00252 |  |  |  | AD1-063
316156 | AD2-030 C | 1 | 115 | 345 | Gen |  | 87 | 0 | 1 |  | 19.8 | 0 | 0 | 0 | 11.48 |  |  |  | -0.00252 |  |  |  | AD2-030
316169 | AC1-164 GEN | 1 | 0.44 | 345 | Gen |  | 87 | 0 | 1 |  | 325.4 | 0 | 0 | 0 | 188.73 |  |  |  | -0.00252 |  |  |  | AC1-164
316201 | AC1-065 C | 1 | 0.39 | 345 | Gen |  | 87 | 0 | 1 |  | 149.9 | 0 | 0 | 0 | 86.94 |  |  |  | -0.00252 |  |  |  | AC1-065
316233 | AE1-074 C | S1 | 230 | 345 | Gen |  | 87 | 0 | 1 |  | 20 | 0 | 0 | 0 | 11.6 |  |  |  | -0.00253 |  |  |  | AE1-074
316280 | AD1-041 GEN | 1 | 0.55 | 345 | Gen |  | 87 | 0 | 1 |  | 50 | 0 | 0 | 0 | 29 |  |  |  | -0.00252 |  |  |  | AD1-041
316304 | AE2-227 C | S1 | 230 | 345 | Gen |  | 87 | 0 | 1 |  | 25 | 0 | 0 | 0 | 14.5 |  |  |  | -0.00253 |  |  |  | AE2-227
316314 | AB2-024 C | S1 | 230 | 345 | Gen |  | 87 | 0 | 1 |  | 16.2 | 0 | 0 | 0 | 9.4 |  |  |  | -0.00252 |  |  |  | AB2-024
316075 | AC2-137 C | 1 | 230 | 345 | Gen |  | 87 | 0 | 1 |  | 20.1 | 0 | 0 | 0 | 11.66 |  |  |  | -0.00252 |  |  |  | AC2-137
316004 | AC1-112 C | S1 | 230 | 345 | Gen |  | 87 | 0 | 1 |  | 17 | 0 | 0 | 0 | 9.86 |  |  |  | -0.0025 |  |  |  | AC1-112
316312 | AB1-027 C | S1 | 230 | 345 | Gen |  | 87 | 0 | 1 |  | 25 | 0 | 0 | 0 | 14.5 |  |  |  | -0.0025 |  |  |  | AB1-027
316484 | AD2-074 GEN | S1 | 0.39 | 345 | Gen |  | 84 | 0 | 1 |  | 87.8 | 0 | 0 | 0 | 51.8 |  |  |  | -0.00249 |  |  |  | AD2-074
316487 | AF1-042 GEN | S1 | 0.39 | 345 | Gen |  | 84 | 0 | 1 |  | 47 | 0 | 0 | 0 | 27.73 |  |  |  | -0.00249 |  |  |  | AF1-042
316404 | AE1-155 C | 1 | 0.63 | 345 | Gen |  | 87 | 0 | 1 |  | 127 | 0 | 0 | 0 | 73.66 |  |  |  | -0.00249 |  |  |  | AE1-155
200945 | 26CT_V3-030 | W1 | 0.69 | 226 | Gen |  | 76 | 0 | 1 |  | 33.5 | 0 | 0 | 0 | 9.72 |  |  |  | 0.00248 |  |  |  | V3-030
316077 | AC2-138 C | 1 | 115 | 345 | Gen |  | 87 | 0 | 1 |  | 14.4 | 0 | 0 | 0 | 8.35 |  |  |  | -0.00247 |  |  |  | AC2-138
316417 | AG1-388 C | S1 | 230 | 345 | Gen |  | 87 | 0 | 1 |  | 20 | 0 | 0 | 0 | 11.6 |  |  |  | -0.00248 |  |  |  | AG1-388
316473 | AC1-191 GEN | S1 | 0.38 | 345 | Gen | New | 87 | 0 | 1 |  | 80 | 0 | 0 | 0 | 0 |  |  |  | -0.00248 |  |  |  | AC1-191
235838 | 01GRNGAP | W1 | 0.69 | 201 | Gen |  | 77 | 0 | 1 |  | 300 | 0 | 0 | 0 | 96 |  |  |  | -0.00245
316337 | AD2-073 C | 1 | 230 | 345 | Gen |  | 87 | 0 | 1 |  | 19.92 | 0 | 0 | 0 | 11.55 |  |  |  | -0.00245 |  |  |  | AD2-073
316223 | AC1-118 C | S1 | 230 | 345 | Gen |  | 87 | 0 | 1 |  | 20 | 0 | 0 | 0 | 11.6 |  |  |  | -0.00243 |  |  |  | AC1-118
237066 | AD1-083 GEN1 | S1 | 0.6 | 201 | Gen | New | 86 | 0 | 1 |  | 102.4 | 0 | 0 | 0 | 0 |  |  |  | -0.00242 |  |  |  | AD1-083
316468 | AD1-105 GEN | 1 | 0.69 | 345 | Gen |  | 87 | 0 | 1 |  | 77.76 | 0 | 0 | 0 | 45.1 |  |  |  | -0.00242 |  |  |  | AD1-105
316095 | T157 G97 | W1 | 0.69 | 345 | Gen |  | 78 | 0 | 1 |  | 51.25 | 0 | 0 | 0 | 16.4 |  |  |  | -0.00241 |  |  |  | T157
316097 | T157 G90 | W1 | 0.69 | 345 | Gen |  | 78 | 0 | 1 |  | 51.25 | 0 | 0 | 0 | 16.4 |  |  |  | -0.00241 |  |  |  | T157
237050 | AF1-155 C | 1 | 46 | 201 | Gen | New | 86 | 0 | 1 |  | 20 | 0 | 0 | 0 | 0 |  |  |  | 0.00239 |  |  |  | AF1-155
316427 | AG1-213 C | B1 | 115 | 345 | Gen | New | 88 | 0 | 1 |  | 10 | 0 | -10 | 0 | 0 |  |  |  | -0.00236 |  |  |  | AG1-213
315673 | AE1-157 C O1 | 1 | 230 | 345 | Gen |  | 87 | 0 | 1 |  | 120 | 0 | 0 | 0 | 69.6 |  |  |  | -0.00234 |  |  |  | AE1-157
316192 | AB2-158 C | 1 | 230 | 345 | Gen |  | 87 | 0 | 1 |  | 98.2 | 0 | 0 | 0 | 56.96 |  |  |  | -0.0023 |  |  |  | AB2-158
316044 | AC1-158 C1 | S1 | 0.6 | 345 | Gen |  | 87 | 0 | 1 |  | 250 | 0 | 0 | 0 | 145 |  |  |  | -0.00226 |  |  |  | AC1-158
316045 | AC1-158 C2 | S1 | 0.6 | 345 | Gen |  | 87 | 0 | 1 |  | 250 | 0 | 0 | 0 | 145 |  |  |  | -0.00226 |  |  |  | AC1-158
316447 | AC1-158 HLD | S1 | 0.6 | 345 | Gen |  | 87 | 0 | 1 |  | 171.89 | 0 | 0 | 0 | 99.7 |  |  |  | -0.00226 |  |  |  | AC1-158
316450 | AC1-158 RIC | S4 | 0.6 | 345 | Gen |  | 87 | 0 | 1 |  | 21.48 | 0 | 0 | 0 | 12.46 |  |  |  | -0.00226 |  |  |  | AC1-158
237061 | AD1-155 C | S1 | 0.6 | 201 | Gen |  | 86 | 0 | 1 |  | 75 | 0 | 0 | 0 | 40.5 |  |  |  | -0.00225 |  |  |  | AD1-155
316164 | AC1-076_C | 1 | 0.6 | 345 | Gen |  | 87 | 0 | 1 |  | 63.22 | 0 | 0 | 0 | 36.67 |  |  |  | -0.00225 |  |  |  | AC1-076
315683 | AE1-153 C | S1 | 0.63 | 345 | Gen |  | 87 | 0 | 1 |  | 149 | 0 | 0 | 0 | 86.42 |  |  |  | -0.00225 |  |  |  | AE1-153
316170 | AC1-121 GEN2 | S1 | 0.6 | 345 | Gen | New | 87 | 0 | 1 |  | 20 | 0 | 0 | 0 | 0 |  |  |  | -0.00224 |  |  |  | AC1-121
316254 | AC1-120 GEN1 | 1 | 0.6 | 345 | Gen | New | 87 | 0 | 1 |  | 60 | 0 | 0 | 0 | 0 |  |  |  | -0.00224 |  |  |  | AC1-120
315651 | AD1-115 GEN | S1 | 115 | 345 | Gen | New | 84 | 0 | 1 |  | 50 | 0 | 0 | 0 | 0 |  |  |  | -0.00224 |  |  |  | AD1-115
316257 | AC1-043 C | 1 | 115 | 345 | Gen | New | 84 | 0 | 1 |  | 100 | 0 | 0 | 0 | 0 |  |  |  | -0.00224 |  |  |  | AC1-043
316267 | AC1-143 C | 1 | 0.38 | 345 | Gen |  | 87 | 0 | 1 |  | 60 | 0 | 0 | 0 | 34.8 |  |  |  | -0.00222 |  |  |  | AC1-143
235464 | 01DTGZ2-030 | 1 | 138 | 201 | Gen |  | 83 | 0 | 1 |  | 10 | 0 | 0 | 0 | 5.3 |  |  |  | -0.00221 |  |  |  | Z2-030
237077 | AC2-174 C | S1 | 138 | 201 | Gen |  | 83 | 0 | 1 |  | 10 | 0 | 0 | 0 | 5.3 |  |  |  | -0.00221 |  |  |  | AC2-174
316006 | AB2-029 C | S1 | 230 | 345 | Gen |  | 84 | 0 | 1 |  | 19.8 | 0 | 0 | 0 | 11.68 |  |  |  | -0.00222 |  |  |  | AB2-029
316029 | AE1-044 GEN | S1 | 0.63 | 345 | Gen | New | 87 | 0 | 1 |  | 200 | 0 | 0 | 0 | 0 |  |  |  | -0.00221 |  |  |  | AE1-044
238147 | AE2-230_GEN1 | S1 | 0.69 | 201 | Gen |  | 86 | 0 | 1 |  | 35 | 0 | 0 | 0 | 18.9 |  |  |  | -0.00218 |  |  |  | AE2-230
238148 | AE2-230_GEN2 | S2 | 0.69 | 201 | Gen |  | 86 | 0 | 1 |  | 35 | 0 | 0 | 0 | 18.9 |  |  |  | -0.00218 |  |  |  | AE2-230
238149 | AF1-291A_GEN | S1 | 0.69 | 201 | Gen |  | 86 | 0 | 1 |  | 10 | 0 | 0 | 0 | 5.4 |  |  |  | -0.00218 |  |  |  | AE2-230
238152 | AF2-075_GEN | S1 | 0.69 | 201 | Gen |  | 86 | 0 | 1 |  | 50 | 0 | 0 | 0 | 27 |  |  |  | -0.00218 |  |  |  | AE2-230
200925 | 26R32 | W1 | 34.5 | 226 | Gen |  | 76 | 0 | 1 |  | 75 | 0 | 0 | 0 | 21.75 |  |  |  | 0.00212 |  |  |  | R32
200888 | 26HIGHLAND | W1 | 34.5 | 226 | Gen |  | 76 | 0 | 1 |  | 65 | 0 | 0 | 0 | 18.85 |  |  |  | 0.00212
200846 | 26FORWARD | W1 | 34.5 | 226 | Gen |  | 76 | 0 | 1 |  | 29.4 | 0 | 0 | 0 | 8.53 |  |  |  | 0.00206
203940 | AF1-140 C | 1 | 23 | 226 | Gen | New | 85 | 0 | 1 |  | 16.3 | 0 | 0 | 0 | 0 |  |  |  | 0.00205 |  |  |  | AF1-140
316411 | AF1-147_GEN1 | S1 | 0.63 | 345 | Gen |  | 87 | 0 | 1 |  | 52.28 | 0 | 0 | 0 | 30.32 |  |  |  | -0.00204 |  |  |  | AF1-147
316415 | AF1-147_GEN2 | S2 | 0.63 | 345 | Gen |  | 87 | 0 | 1 |  | 52.28 | 0 | 0 | 0 | 30.32 |  |  |  | -0.00204 |  |  |  | AF1-147
200915 | 26CHSTN_FL | W1 | 34.5 | 226 | Gen |  | 76 | 0 | 1 |  | 38 | 0 | 0 | 0 | 11.02 |  |  |  | 0.00199
235072 | AD2-158 GEN | S1 | 0.55 | 201 | Gen | New | 86 | 0 | 1 |  | 79.22 | 0 | 0 | 0 | 0 |  |  |  | -0.00199 |  |  |  | AD2-158
203953 | AE2-249 C | 1 | 23 | 226 | Gen | New | 85 | 0 | 1 |  | 16.6 | 0 | 0 | 0 | 0 |  |  |  | 0.00199 |  |  |  | AE2-249
203942 | AF2-270 E | E | 23 | 226 | Gen | New | 82 | 0 | 1 |  | 3.72 | 0 | 0 | 0 | 0 |  |  |  | 0.00199 |  |  |  | AF2-270
235625 | 01BACKB | W1 | 34.5 | 201 | Gen |  | 77 | 0 | 1 |  | 66 | 0 | 0 | 0 | 21.12 |  |  |  | -0.00185
200889 | 26STNY CRK | W1 | 34.5 | 226 | Gen |  | 76 | 0 | 1 |  | 52.5 | 0 | 0 | 0 | 15.23 |  |  |  | 0.00183
203993 | AD2-133_GEN1 | 1 | 0.69 | 226 | Gen |  | 76 | 0 | 1 |  | 87.6 | 0 | 0 | 0 | 25.4 |  |  |  | 0.00182 |  |  |  | AD1-133
200905 | 26Q36 | W1 | 0.69 | 226 | Gen |  | 76 | 0 | 1 |  | 50 | 0 | 0 | 0 | 14.5 |  |  |  | 0.00182 |  |  |  | Q36
203946 | AE2-131 C | S1 | 34.5 | 226 | Gen | New | 85 | 0 | 1 |  | 20 | 0 | 0 | 0 | 0 |  |  |  | 0.0018 |  |  |  | AE2-131
203952 | AE2-129 C | 1 | 34.5 | 226 | Gen |  | 85 | 0 | 1 |  | 20 | 0 | 0 | 0 | 11.2 |  |  |  | 0.0018 |  |  |  | AE2-129
237512 | 01ROTHROCK | W1 | 34.5 | 201 | Gen |  | 77 | 0 | 1 |  | 50 | 0 | 0 | 0 | 16 |  |  |  | -0.0018
226931 | AG1-317 C | B1 | 69 | 233 | Gen | New | 88 | 0 | 1 |  | 1 | 0 | -1 | 0 | 0 |  |  |  | -0.00179 |  |  |  | AG1-317
226921 | AE1-013 C | 1 | 69 | 233 | Gen |  | 82 | 0 | 1 |  | 0.9 | 0 | 0 | 0 | 0.47 |  |  |  | -0.00179 |  |  |  | AE1-013
226929 | AD2-058 C | 1 | 69 | 233 | Gen |  | 82 | 0 | 1 |  | 5.6 | 0 | 0 | 0 | 2.91 |  |  |  | -0.00179 |  |  |  | AD2-058
226930 | AD2-199 C | 1 | 69 | 233 | Gen |  | 82 | 0 | 1 |  | 3 | 0 | 0 | 0 | 1.56 |  |  |  | -0.00179 |  |  |  | AD2-199
238141 | AE2-333 GEN1 | S1 | 0.69 | 201 | Gen |  | 86 | 0 | 1 |  | 50 | 0 | 0 | 0 | 27 |  |  |  | -0.00178 |  |  |  | AE2-333
238142 | AE2-333 GEN2 | S2 | 0.69 | 201 | Gen |  | 86 | 0 | 1 |  | 50 | 0 | 0 | 0 | 27 |  |  |  | -0.00178 |  |  |  | AE2-333
238108 | AE1-109 C1 | S1 | 0.55 | 201 | Gen |  | 83 | 0 | 1 |  | 6.67 | 0 | 0 | 0 | 3.54 |  |  |  | -0.00177 |  |  |  | AE1-109
238109 | AE1-109 C2 | S2 | 0.55 | 201 | Gen |  | 83 | 0 | 1 |  | 6.67 | 0 | 0 | 0 | 3.54 |  |  |  | -0.00177 |  |  |  | AE1-109
238110 | AE1-109 C3 | S3 | 0.55 | 201 | Gen |  | 83 | 0 | 1 |  | 6.67 | 0 | 0 | 0 | 3.54 |  |  |  | -0.00177 |  |  |  | AE1-109
235048 | AD1-125 C1 | 1 | 0.69 | 201 | Gen |  | 77 | 0 | 1 |  | 40 | 0 | 0 | 0 | 12.8 |  |  |  | -0.00173 |  |  |  | AD1-125
235049 | AD1-125 C2 | 1 | 0.69 | 201 | Gen |  | 77 | 0 | 1 |  | 40 | 0 | 0 | 0 | 12.8 |  |  |  | -0.00173 |  |  |  | AD1-125
226936 | AF1-003_GEN1 | S1 | 0.55 | 238 | Gen |  | 82 | 0 | 1 |  | 10 | 0 | 0 | 0 | 5.2 |  |  |  | -0.00172 |  |  |  | AF1-003
226937 | AF1-003_GEN2 | S2 | 0.55 | 238 | Gen |  | 82 | 0 | 1 |  | 10 | 0 | 0 | 0 | 5.2 |  |  |  | -0.00172 |  |  |  | AF1-003
226943 | AF1-005_GEN | S1 | 0.55 | 238 | Gen |  | 82 | 0 | 1 |  | 20 | 0 | 0 | 0 | 10.4 |  |  |  | -0.00172 |  |  |  | AF1-005
227287 | AC2-120 C | 1 | 0.55 | 238 | Gen |  | 82 | 0 | 1 |  | 30 | 0 | 0 | 0 | 15.6 |  |  |  | -0.00172 |  |  |  | AC2-120
237779 | 01MDS_W4-102 | S1 | 34.5 | 201 | Gen |  | 83 | 0 | 1 |  | 20 | 0 | 0 | 0 | 10.6 |  |  |  | -0.0017 |  |  |  | W4-102
238112 | AG1-095 C | S1 | 34.5 | 201 | Gen |  | 86 | 0 | 1 |  | 16 | 0 | 0 | 0 | 8.64 |  |  |  | -0.00171 |  |  |  | AG1-095
203954 | AE2-126 C | 1 | 34.5 | 226 | Gen |  | 85 | 0 | 1 |  | 20 | 0 | 0 | 0 | 11.2 |  |  |  | 0.0017 |  |  |  | AE2-126
203941 | AF2-087 C | S1 | 46 | 226 | Gen | New | 82 | 0 | 1 |  | 7.25 | 0 | 0 | 0 | 0 |  |  |  | 0.0017 |  |  |  | AF2-087
200834 | 26SW_E13_K22 | W1 | 23 | 226 | Gen |  | 76 | 0 | 1 |  | 9 | 0 | 0 | 0 | 2.61 |  |  |  | 0.0017 |  |  |  | K22
226910 | AB2-157 C | 1 | 69 | 233 | Gen |  | 82 | 0 | 1 |  | 2.5 | 0 | 0 | 0 | 1.3 |  |  |  | -0.0017 |  |  |  | AB2-157
235020 | AA1-095 C | S1 | 34.5 | 201 | Gen |  | 86 | 0 | 1 |  | 6.23 | 0 | 0 | 0 | 3.36 |  |  |  | -0.0017 |  |  |  | AA1-095
235004 | AA1-092 C | S1 | 34.5 | 201 | Gen |  | 86 | 0 | 1 |  | 12 | 0 | 0 | 0 | 6.48 |  |  |  | -0.00167 |  |  |  | AA1-092
235025 | AB2-097 E | S1 | 34.5 | 201 | Gen | New | 83 | 0 | 1 |  | 10 | 0 | 0 | 0 | 0 |  |  |  | -0.00167 |  |  |  | AB2-097
237034 | AC2-136 C | S1 | 138 | 201 | Gen | New | 83 | 0 | 1 |  | 11.8 | 0 | 0 | 0 | 0 |  |  |  | -0.00165 |  |  |  | AC2-136
237798 | 01AA1-109 C | S1 | 34.5 | 201 | Gen |  | 83 | 0 | 1 |  | 9 | 0 | 0 | 0 | 4.77 |  |  |  | -0.00162 |  |  |  | Z2-030
237507 | 01CROSSCHOOL | W1 | 34.5 | 201 | Gen |  | 77 | 0 | 1 |  | 85 | 0 | 0 | 0 | 27.2 |  |  |  | -0.0016
237778 | 01MSM_W1-116 | S1 | 34.5 | 201 | Gen |  | 83 | 0 | 1 |  | 14.02 | 0 | 0 | 0 | 7.43 |  |  |  | -0.0016 |  |  |  | W1-116
237080 | AD1-060 C | S1 | 0.41 | 201 | Gen |  | 86 | 0 | 1 |  | 19.4 | 0 | 0 | 0 | 10.48 |  |  |  | -0.00159 |  |  |  | AD1-060
235054 | AD2-180 C | 1 | 0.72 | 201 | Gen |  | 77 | 0 | 1 |  | 111.83 | 0 | 0 | 0 | 35.79 |  |  |  | -0.00159 |  |  |  | AD2-180
203961 | AE2-224 C | S1 | 0.6 | 226 | Gen |  | 85 | 0 | 1 |  | 100 | 0 | 0 | 0 | 56 |  |  |  | 0.00157 |  |  |  | AE2-224
237006 | AB1-125_C | S | 0.6 | 201 | Gen |  | 83 | 0 | 1 |  | 15 | 0 | 0 | 0 | 7.95 |  |  |  | -0.00156 |  |  |  | AB1-125
237025 | AB1-124 C | S1 | 34.5 | 201 | Gen |  | 83 | 0 | 1 |  | 20 | 0 | 0 | 0 | 10.6 |  |  |  | -0.00156 |  |  |  | AB1-124
237030 | AB1-096 C | S1 | 34.5 | 201 | Gen |  | 83 | 0 | 1 |  | 9.9 | 0 | 0 | 0 | 5.25 |  |  |  | -0.00157 |  |  |  | AB1-096
237038 | AE2-054 C | 1 | 34.5 | 201 | Gen |  | 86 | 0 | 1 |  | 20 | 0 | 0 | 0 | 10.8 |  |  |  | -0.00156 |  |  |  | AE2-054
235526 | 01WR_AA1-100 | 1 | 138 | 201 | Gen | New | 88 | 0 | 1 |  | 11 | 0 | -11 | 0 | 0 |  |  |  | -0.00156 |  |  |  | AA1-100
235067 | AD1-061 C | 1 | 0.41 | 201 | Gen |  | 83 | 0 | 1 |  | 21 | 0 | 0 | 0 | 11.13 |  |  |  | -0.00156 |  |  |  | AD1-061
235854 | 01KL_K28_T16 | W1 | 0.69 | 201 | Gen |  | 77 | 0 | 1 |  | 99.9 | 0 | 0 | 0 | 31.97 |  |  |  | -0.00154 |  |  |  | K28
237085 | AD2-009_C | 1 | 0.6 | 201 | Gen |  | 86 | 0 | 1 |  | 70 | 0 | 0 | 0 | 37.8 |  |  |  | -0.00154 |  |  |  | AD2-009
238120 | AE2-309 GEN | B1 | 34.5 | 201 | Gen | New | 88 | 0 | 1 |  | 11.9 | 0 | -11.9 | 0 | 0 |  |  |  | -0.00152 |  |  |  | AE2-309 |  | MFO
235531 | U2-073 GEN | 1 | 34.5 | 201 | Gen |  | 77 | 0 | 1 |  | 138.04 | 0 | 0 | 0 | 44.17 |  |  |  | -0.00152 |  |  |  | U2-073
237037 | AE1-188 C | 1 | 34.5 | 201 | Gen |  | 86 | 0 | 1 |  | 31.9 | 0 | 0 | 0 | 17.23 |  |  |  | -0.00152 |  |  |  | AE1-188
238120 | AE2-309 GEN | S1 | 34.5 | 201 | Gen |  | 83 | 0 | 1 |  | 19.8 | 0 | 0 | 0 | 10.49 |  |  |  | -0.00152 |  |  |  | AE2-309 |  | MFO
200886 | 26ARWF_N39 | W1 | 0.69 | 226 | Gen |  | 76 | 0 | 1 |  | 80 | 0 | 0 | 0 | 23.2 |  |  |  | 0.00151 |  |  |  | N39
203034 | 26NA_O38_P22 | W1 | 0.69 | 226 | Gen |  | 76 | 0 | 1 |  | 65.1 | 0 | 0 | 0 | 18.88 |  |  |  | 0.00151 |  |  |  | P22
223403 | AG1-063 GEN | 1 | 34.5 | 232 | Gen | New | 88 | 0 | 1 |  | 2.5 | 0 | -2.5 | 0 | 0 |  |  |  | -0.00151 |  |  |  | AG1-063
238101 | AF2-275 E | B1 | 34.5 | 201 | Gen | New | 88 | 0 | 1 |  | 1.5 | 0 | -1.5 | 0 | 0 |  |  |  | -0.0015 |  |  |  | AF2-275 |  | MFO
235043 | AF1-166 GEN | S1 | 34.5 | 201 | Gen | New | 86 | 0 | 1 |  | 16 | 0 | 0 | 0 | 0 |  |  |  | -0.0015 |  |  |  | AF1-166
235062 | AE1-101 C1 | 1 | 0.6 | 201 | Gen |  | 86 | 0 | 1 |  | 75 | 0 | 0 | 0 | 40.5 |  |  |  | -0.00151 |  |  |  | AE1-101
235063 | AE1-101 C2 | 1 | 0.48 | 201 | Gen |  | 86 | 0 | 1 |  | 75 | 0 | 0 | 0 | 40.5 |  |  |  | -0.00151 |  |  |  | AE1-101
235073 | AF1-209 C O1 | S1 | 34.5 | 201 | Gen | New | 86 | 0 | 1 |  | 15.9 | 0 | 0 | 0 | 0 |  |  |  | -0.0015 |  |  |  | AF1-209
237001 | AB1-127 C | 1 | 34.5 | 201 | Gen |  | 86 | 0 | 1 |  | 25.8 | 0 | 0 | 0 | 13.93 |  |  |  | -0.0015 |  |  |  | AB1-127
237002 | AB1-128 C | S1 | 34.5 | 201 | Gen |  | 86 | 0 | 1 |  | 25.8 | 0 | 0 | 0 | 13.93 |  |  |  | -0.0015 |  |  |  | AB1-12
238101 | AF2-275 E | E | 34.5 | 201 | Gen | New | 83 | 0 | 1 |  | 3 | 0 | 0 | 0 | 0 |  |  |  | -0.0015 |  |  |  | AF2-275 |  | MFO
238117 | U2-030 | W1 | 0.66 | 201 | Gen |  | 77 | 0 | 1 |  | 40 | 0 | 0 | 0 | 12.8 |  |  |  | -0.0015 |  |  |  | U2-030
238118 | U2-030_1 | W1 | 0.66 | 201 | Gen |  | 77 | 0 | 1 |  | 20 | 0 | 0 | 0 | 6.4 |  |  |  | -0.0015 |  |  |  | U2-030
203944 | AF2-271 E | E | 46 | 226 | Gen | New | 82 | 0 | 1 |  | 3 | 0 | 0 | 0 | 0 |  |  |  | 0.00148 |  |  |  | AF2-271
238126 | S14_GEN_1 | W1 | 0.69 | 201 | Gen |  | 77 | 0 | 1 |  | 35 | 0 | 0 | 0 | 11.2 |  |  |  | -0.00145 |  |  |  | S14
238127 | S14_GEN_2 | W2 | 0.69 | 201 | Gen |  | 77 | 0 | 1 |  | 35 | 0 | 0 | 0 | 11.2 |  |  |  | -0.00145 |  |  |  | S14
203939 | AE1-160 C | 1 | 34.5 | 226 | Gen |  | 85 | 0 | 1 |  | 20 | 0 | 0 | 0 | 11.2 |  |  |  | 0.00143 |  |  |  | AE1-160
203987 | AE2-118 C | S1 | 46 | 226 | Gen |  | 85 | 0 | 1 |  | 20 | 0 | 0 | 0 | 11.2 |  |  |  | 0.00137 |  |  |  | AE2-118
203947 | AF1-006 C | 1 | 34.5 | 226 | Gen |  | 85 | 0 | 1 |  | 20 | 0 | 0 | 0 | 11.2 |  |  |  | -0.00137 |  |  |  | AF1-006
238103 | AF2-293 E | B1 | 46 | 201 | Gen | New | 88 | 0 | 1 |  | 1.5 | 0 | -1.5 | 0 | 0 |  |  |  | 0.00131 |  |  |  | AF2-293 |  | MFO
238103 | AF2-293 E | 1 | 46 | 201 | Gen | New | 83 | 0 | 1 |  | 1.17 | 0 | 0 | 0 | 0 |  |  |  | 0.00131 |  |  |  | AF2-293 |  | MFO
236828 | 01GRAYMONT | 1 | 46 | 201 | Gen | New | 83 | 0 | 1 |  | 4 | 0 | 0 | 0 | 0 |  |  |  | 0.0013
235056 | AG1-142 C | S1 | 69 | 201 | Gen |  | 86 | 0 | 1 |  | 2.5 | 0 | 0 | 0 | 1.35 |  |  |  | 0.0013 |  |  |  | AG1-142
200894 | LAURHILL-G | W1 | 34.5 | 226 | Gen | New | 79 | 0 | 1 |  | 70 | 0 | 0 | 0 | 0 |  |  |  | 0.00128
238104 | AF2-426 E | B1 | 138 | 201 | Gen | New | 88 | 0 | 1 |  | 1.5 | 0 | -1.5 | 0 | 0 |  |  |  | 0.00128 |  |  |  | AF2-426 |  | MFO
238104 | AF2-426 E | E | 138 | 201 | Gen | New | 83 | 0 | 1 |  | 1.17 | 0 | 0 | 0 | 0 |  |  |  | 0.00128 |  |  |  | AF2-426 |  | MFO
203349 | 26Z1-069 C | 1 | 115 | 226 | Gen |  | 76 | 0 | 1 |  | 90 | 0 | 0 | 0 | 26.1 |  |  |  | 0.00127 |  |  |  | Z1-069
235003 | AC1-025 E | 1 | 46 | 201 | Gen | New | 88 | 0 | 1 |  | 1.5 | 0 | -1.5 | 0 | 0 |  |  |  | 0.00126 |  |  |  | AC1-025
237041 | AE2-055 C | 1 | 46 | 201 | Gen |  | 86 | 0 | 1 |  | 20 | 0 | 0 | 0 | 10.8 |  |  |  | 0.00125 |  |  |  | AE2-055
200890 | 26BF_G21_K23 | W1 | 0.6 | 226 | Gen |  | 76 | 0 | 1 |  | 46.8 | 0 | 0 | 0 | 13.57 |  |  |  | 0.00117 |  |  |  | G21
200891 | 26CSLMN_L13 | W1 | 0.57 | 226 | Gen |  | 76 | 0 | 1 |  | 37.9 | 0 | 0 | 0 | 10.99 |  |  |  | 0.00117
200892 | 26LOOKOUT | W1 | 24.9 | 226 | Gen |  | 76 | 0 | 1 |  | 36.9 | 0 | 0 | 0 | 10.7 |  |  |  | 0.00117
203915 | 26BF_Z2-108 | 1 | 0.45 | 226 | Gen | New | 88 | 0 | 1 |  | 18 | 0 | -18 | 0 | 0 |  |  |  | 0.00117 |  |  |  | Z2-108
200835 | 26ARN_Z1-066 | 1 | 25 | 226 | Gen | New | 88 | 0 | 1 |  | 6 | 0 | -6 | 0 | 0 |  |  |  | 0.00117 |  |  |  | Z1-065
200887 | 26ARMNA MT | W1 | 0.69 | 226 | Gen |  | 76 | 0 | 1 |  | 100.5 | 0 | 0 | 0 | 29.15 |  |  |  | 0.00114
238100 | AF2-274 E | B1 | 138 | 201 | Gen | New | 88 | 0 | 1 |  | 1.5 | 0 | -1.5 | 0 | 0 |  |  |  | -0.00113 |  |  |  | AF2-274 |  | MFO
237027 | AG1-315 C | S1 | 138 | 201 | Gen |  | 58 | 0 | 1 |  | 2 | 0 | 0 | 0 | 1.06 |  |  |  | -0.00113 |  |  |  | AG1-315
238100 | AF2-274 E | E | 138 | 201 | Gen | New | 83 | 0 | 1 |  | 3.72 | 0 | 0 | 0 | 0 |  |  |  | -0.00113 |  |  |  | AF2-274 |  | MFO
203951 | AF2-265 C | 1 | 34.5 | 226 | Gen |  | 85 | 0 | 1 |  | 15 | 0 | 0 | 0 | 8.4 |  |  |  | 0.00111 |  |  |  | AF2-265
223401 | AF1-299 C | S1 | 34.5 | 232 | Gen |  | 85 | 0 | 1 |  | 17 | 0 | 0 | 0 | 9.52 |  |  |  | -0.0011 |  |  |  | AF1-299
223402 | AF1-300 C | S1 | 34.5 | 232 | Gen |  | 85 | 0 | 1 |  | 17 | 0 | 0 | 0 | 9.52 |  |  |  | -0.0011 |  |  |  | AF1-300
203948 | AG1-140 C | 1 | 34.5 | 226 | Gen |  | 85 | 0 | 1 |  | 2.62 | 0 | 0 | 0 | 1.47 |  |  |  | -0.00108 |  |  |  | AG1-140
203963 | AG1-253 C | S1 | 34.5 | 226 | Gen |  | 85 | 0 | 1 |  | 4 | 0 | 0 | 0 | 2.24 |  |  |  | -0.00108 |  |  |  | AG1-253
223204 | AA2-072 GEN | S1 | 34.5 | 232 | Gen | New | 82 | 0 | 1 |  | 1.1 | 0 | 0 | 0 | 0 |  |  |  | -0.00104 |  |  |  | AA2-072
237039 | AF1-001 C | 1 | 34.5 | 201 | Gen | New | 83 | 0 | 1 |  | 13.75 | 0 | 0 | 0 | 0 |  |  |  | -0.00101 |  |  |  | AF1-001
203982 | AD2-062_GEN | S1 | 0.6 | 226 | Gen |  | 85 | 0 | 1 |  | 82.15 | 0 | 0 | 0 | 46 |  |  |  | -0.00098 |  |  |  | AD2-062
203950 | AF1-217 C | 1 | 34.5 | 226 | Gen | New | 85 | 0 | 1 |  | 20 | 0 | 0 | 0 | 0 |  |  |  | -0.00093 |  |  |  | AF1-217
203962 | AF1-287 C | S1 | 34.5 | 226 | Gen |  | 85 | 0 | 1 |  | 20 | 0 | 0 | 0 | 11.2 |  |  |  | -0.00093 |  |  |  | AF1-287
205907 | AC1-048 GEN | 1 | 0.39 | 227 | Gen |  | 82 | 0 | 1 |  | 75 | 0 | 0 | 0 | 39 |  |  |  | -0.00093 |  |  |  | AC1-048
208254 | AF2-280 E | E | 12.5 | 229 | Gen | New | 82 | 0 | 1 |  | 3 | 0 | 0 | 0 | 0 |  |  |  | -0.00077 |  |  |  | AF2-280
208856 | AE1-226 GEN | S1 | 69 | 229 | Gen | New | 85 | 0 | 1 |  | 19.8 | 0 | 0 | 0 | 0 |  |  |  | -0.00077 |  |  |  | AE1-226
208923 | BUSO V4-027 | 1 | 12.47 | 229 | Gen |  | 85 | 0 | 1 |  | 5 | 0 | 0 | 0 | 2.8 |  |  |  | -0.00077 |  |  |  | V4-027
200917 | 26MTNTP_P28 | W1 | 0.69 | 226 | Gen |  | 76 | 0 | 1 |  | 150 | 0 | 0 | 0 | 43.5 |  |  |  | 0.00071 |  |  |  | P28
203905 | 26W1-045 C | S1 | 23 | 226 | Gen |  | 85 | 0 | 1 |  | 17.4 | 0 | 0 | 0 | 9.74 |  |  |  | -0.00067 |  |  |  | W1-045
208527 | AF2-279 E | E | 12.5 | 229 | Gen | New | 82 | 0 | 1 |  | 3 | 0 | 0 | 0 | 0 |  |  |  | -0.00065 |  |  |  | AF2-279
208835 | TUHI V3-051 | W1 | 12.47 | 229 | Gen |  | 76 | 0 | 1 |  | 3.2 | 0 | 0 | 0 | 0.93 |  |  |  | -0.00065 |  |  |  | V3-051
208835 | TUHI V3-051 | W2 | 12.47 | 229 | Gen |  | 76 | 0 | 1 |  | 1.6 | 0 | 0 | 0 | 0.46 |  |  |  | -0.00065 |  |  |  | V3-051
205922 | AF2-268 E | E | 115 | 227 | Gen | New | 82 | 0 | 1 |  | 2 | 0 | 0 | 0 | 0 |  |  |  | -0.00061 |  |  |  | AF2-268
205916 | AD1-020 GEN | 1 | 0.6 | 227 | Gen |  | 85 | 0 | 1 |  | 100 | 0 | 0 | 0 | 56 |  |  |  | -0.00061 |  |  |  | AD1-020
205917 | AD1-020 ES | 1 | 0.55 | 227 | Gen | New | 85 | 0 | 1 |  | 21.5 | 0 | 0 | 0 | 0 |  |  |  | -0.00061 |  |  |  | AD1-020
202652 | 26RGH_Y1-033 | W1 | 0.69 | 226 | Gen |  | 76 | 0 | 1 |  | 39.02 | 0 | 0 | 0 | 11.32 |  |  |  | 0.00052 |  |  |  | Y1-033
203955 | AF1-039 C O1 | 1 | 115 | 226 | Gen |  | 85 | 0 | 1 |  | 15 | 0 | 0 | 0 | 8.4 |  |  |  | 0.00052 |  |  |  | AF1-039
205932 | AD2-116_C | 1 | 0.55 | 227 | Gen |  | 85 | 0 | 1 |  | 20 | 0 | 0 | 0 | 11.2 |  |  |  | -0.00049 |  |  |  | AD2-116
205943 | AE1-185 C | S1 | 69 | 227 | Gen |  | 85 | 0 | 1 |  | 20 | 0 | 0 | 0 | 11.2 |  |  |  | -0.00049 |  |  |  | AE1-185
205956 | AE1-196_GEN | S1 | 0.55 | 227 | Gen |  | 85 | 0 | 1 |  | 20.17 | 0 | 0 | 0 | 11.3 |  |  |  | -0.00049 |  |  |  | AE1-196
203980 | AG1-197 GEN | S1 | 34.5 | 226 | Gen |  | 85 | 0 | 1 |  | 15 | 0 | 0 | 0 | 8.4 |  |  |  | -0.00049 |  |  |  | AG1-197
205930 | AF2-099 C | S1 | 115 | 227 | Gen | New | 85 | 0 | 1 |  | 3 | 0 | 0 | 0 | 0 |  |  |  | -0.00049 |  |  |  | AF2-099
205931 | AF2-100 C | S1 | 115 | 227 | Gen | New | 85 | 0 | 1 |  | 3 | 0 | 0 | 0 | 0 |  |  |  | -0.00049 |  |  |  | AF2-100
216407 | AF1-137 C | 1 | 35 | 230 | Gen |  | 85 | 0 | 1 |  | 9.8 | 0 | 0 | 0 | 5.49 |  |  |  | -0.00048 |  |  |  | AF1-137
216408 | AF1-174 C | S1 | 35 | 230 | Gen |  | 85 | 0 | 1 |  | 20 | 0 | 0 | 0 | 11.2 |  |  |  | -0.00048 |  |  |  | AF1-174
233915 | AB1-141 C | 1 | 0.55 | 235 | Gen |  | 85 | 0 | 1 |  | 19.8 | 0 | 0 | 0 | 11.09 |  |  |  | -0.00047 |  |  |  | AB1-141
233918 | AB1-142 C | S1 | 0.55 | 235 | Gen |  | 85 | 0 | 1 |  | 19.8 | 0 | 0 | 0 | 11.09 |  |  |  | -0.00047 |  |  |  | AB1-142
233930 | AB2-032 GEN | S1 | 0.6 | 235 | Gen |  | 85 | 0 | 1 |  | 20 | 0 | 0 | 0 | 11.2 |  |  |  | -0.00047 |  |  |  | AB2-032
233933 | AB2-153 GEN | S1 | 0.6 | 235 | Gen |  | 82 | 0 | 1 |  | 20 | 0 | 0 | 0 | 10.4 |  |  |  | -0.00047 |  |  |  | AB2-153
233935 | AB2-179 C | S1 | 0.38 | 235 | Gen |  | 85 | 0 | 1 |  | 50 | 0 | 0 | 0 | 28 |  |  |  | -0.00047 |  |  |  | AB2-179
233982 | AB2-133 C | S1 | 0.6 | 235 | Gen |  | 85 | 0 | 1 |  | 57.04 | 0 | 0 | 0 | 31.94 |  |  |  | -0.00047 |  |  |  | AB2-133
233961 | AE1-087 GEN | 1 | 0.63 | 235 | Gen | New | 88 | 0 | 1 |  | 20 | 0 | -20 | 0 | 0 |  |  |  | -0.00047 |  |  |  | AE1-087
234011 | AF2-249 BAT | B1 | 69 | 235 | Gen | New | 88 | 0 | 1 |  | 3 | 0 | -3 | 0 | 0 |  |  |  | -0.00047 |  |  |  | AF2-249
233985 | AG1-318 E | B1 | 12.47 | 235 | Gen | New | 88 | 0 | 1 |  | 1 | 0 | -1 | 0 | 0 |  |  |  | -0.00047 |  |  |  | AG1-318
205921 | AF2-151 C | S1 | 115 | 227 | Gen | New | 85 | 0 | 1 |  | 3 | 0 | 0 | 0 | 0 |  |  |  | -0.00047 |  |  |  | AF2-151
232404 | W1-003 C | 1 | 138 | 235 | Gen |  | 85 | 0 | 1 |  | 25.76 | 0 | 0 | 0 | 14.43 |  |  |  | -0.00047 |  |  |  | W1-003
232406 | W1-004 C | 1 | 138 | 235 | Gen |  | 85 | 0 | 1 |  | 25.76 | 0 | 0 | 0 | 14.43 |  |  |  | -0.00047 |  |  |  | W1-004
232408 | W1-005 C | 1 | 138 | 235 | Gen |  | 85 | 0 | 1 |  | 25.76 | 0 | 0 | 0 | 14.43 |  |  |  | -0.00047 |  |  |  | W1-005
232410 | W1-006 C | 1 | 138 | 235 | Gen |  | 85 | 0 | 1 |  | 25.76 | 0 | 0 | 0 | 14.43 |  |  |  | -0.00047 |  |  |  | W1-006
232412 | X1-032 E | 1 | 138 | 235 | Gen | New | 82 | 0 | 1 |  | 4 | 0 | 0 | 0 | 0 |  |  |  | -0.00047 |  |  |  | X1-032
232417 | X3-008 C | 1 | 69 | 235 | Gen |  | 82 | 0 | 1 |  | 20 | 0 | 0 | 0 | 10.4 |  |  |  | -0.00047 |  |  |  | X3-008
232422 | X3-066 C | 1 | 12.47 | 235 | Gen |  | 82 | 0 | 1 |  | 6.8 | 0 | 0 | 0 | 3.54 |  |  |  | -0.00047 |  |  |  | X3-066
232424 | Y1-079 C | 1 | 24.94 | 235 | Gen |  | 82 | 0 | 1 |  | 10 | 0 | 0 | 0 | 5.2 |  |  |  | -0.00047 |  |  |  | Y1-079
232426 | Y1-080 FULL | 1 | 69 | 235 | Gen |  | 82 | 0 | 1 |  | 3.38 | 0 | 0 | 0 | 1.76 |  |  |  | -0.00047 |  |  |  | Y1-080
232428 | Y3-058 C | 1 | 69 | 235 | Gen |  | 85 | 0 | 1 |  | 18.2 | 0 | 0 | 0 | 10.19 |  |  |  | -0.00047 |  |  |  | Y3-058
232432 | Z2-076 C | S1 | 24.94 | 235 | Gen |  | 85 | 0 | 1 |  | 6 | 0 | 0 | 0 | 3.36 |  |  |  | -0.00047 |  |  |  | Z2-076
232434 | Z2-077 C | S1 | 24.94 | 235 | Gen |  | 85 | 0 | 1 |  | 6 | 0 | 0 | 0 | 3.36 |  |  |  | -0.00047 |  |  |  | Z2-077
232436 | AB1-176 C | 1 | 69 | 235 | Gen |  | 82 | 0 | 1 |  | 9 | 0 | 0 | 0 | 4.68 |  |  |  | -0.00047 |  |  |  | AB1-176
233901 | CHERRYDALE C | S1 | 69 | 235 | Gen |  | 82 | 0 | 1 |  | 20 | 0 | 0 | 0 | 10.4 |  |  |  | -0.00047
233906 | AB1-056 C | W1 | 0.69 | 235 | Gen |  | 76 | 0 | 1 |  | 247.8 | 0 | 0 | 0 | 71.86 |  |  |  | -0.00047 |  |  |  | AB1-056
233923 | AA1-102 C | 1 | 0.55 | 235 | Gen |  | 82 | 0 | 1 |  | 151.5 | 0 | 0 | 0 | 78.78 |  |  |  | -0.00047 |  |  |  | AA1-102
233939 | AC1-091 C | S1 | 138 | 235 | Gen |  | 82 | 0 | 1 |  | 19.8 | 0 | 0 | 0 | 10.3 |  |  |  | -0.00046 |  |  |  | AC1-091
233940 | AF2-379 C | S1 | 69 | 235 | Gen |  | 82 | 0 | 1 |  | 3.9 | 0 | 0 | 0 | 2.03 |  |  |  | -0.00047 |  |  |  | AF2-379
233944 | AB2-135 C | 1 | 69 | 235 | Gen |  | 85 | 0 | 1 |  | 64 | 0 | 0 | 0 | 35.84 |  |  |  | -0.00047 |  |  |  | AB2-135
233946 | AB2-136 C | 1 | 69 | 235 | Gen |  | 85 | 0 | 1 |  | 51.1 | 0 | 0 | 0 | 28.62 |  |  |  | -0.00047 |  |  |  | AB2-136
233950 | AC2-186 C | 1 | 0.55 | 235 | Gen |  | 82 | 0 | 1 |  | 10 | 0 | 0 | 0 | 5.2 |  |  |  | -0.00047 |  |  |  | AC2-186
233952 | AC2-187 C | 1 | 0.55 | 235 | Gen |  | 82 | 0 | 1 |  | 20 | 0 | 0 | 0 | 10.4 |  |  |  | -0.00047 |  |  |  | AC2-187
233954 | AC2-188 C | 1 | 0.55 | 235 | Gen |  | 82 | 0 | 1 |  | 20 | 0 | 0 | 0 | 10.4 |  |  |  | -0.00047 |  |  |  | AC2-188
233955 | AB2-172 C | S1 | 0.55 | 235 | Gen |  | 85 | 0 | 1 |  | 50.4 | 0 | 0 | 0 | 28.22 |  |  |  | -0.00047 |  |  |  | AB2-172
233964 | AF2-378 C | S1 | 12.47 | 235 | Gen |  | 82 | 0 | 1 |  | 2.65 | 0 | 0 | 0 | 1.38 |  |  |  | -0.00047 |  |  |  | AF2-378
233968 | AD2-076_C | 1 | 0.39 | 235 | Gen |  | 82 | 0 | 1 |  | 49 | 0 | 0 | 0 | 25.48 |  |  |  | -0.00047 |  |  |  | AD2-076
233970 | AC1-092 C | S1 | 138 | 235 | Gen |  | 82 | 0 | 1 |  | 19.8 | 0 | 0 | 0 | 10.3 |  |  |  | -0.00046 |  |  |  | AC1-092
233971 | AC1-093 C | S1 | 138 | 235 | Gen |  | 82 | 0 | 1 |  | 18.8 | 0 | 0 | 0 | 9.78 |  |  |  | -0.00046 |  |  |  | AC1-093
233972 | AC1-094 C | S1 | 138 | 235 | Gen |  | 82 | 0 | 1 |  | 15.9 | 0 | 0 | 0 | 8.27 |  |  |  | -0.00046 |  |  |  | AC1-094
233973 | AC2-185 C | S1 | 138 | 235 | Gen |  | 82 | 0 | 1 |  | 40 | 0 | 0 | 0 | 20.8 |  |  |  | -0.00046 |  |  |  | AC2-185
233984 | AB2-036 GEN | S1 | 0.38 | 235 | Gen | New | 82 | 0 | 1 |  | 92 | 0 | 0 | 0 | 0 |  |  |  | -0.00047 |  |  |  | AB2-036
233987 | AB2-037 GEN | S1 | 0.38 | 235 | Gen |  | 82 | 0 | 1 |  | 212.5 | 0 | 0 | 0 | 110.5 |  |  |  | -0.00047 |  |  |  | AB2-037
233989 | AG1-360 E | S1 | 138 | 235 | Gen | New | 82 | 0 | 1 |  | 8.75 | 0 | 0 | 0 | 0 |  |  |  | -0.00047 |  |  |  | AG1-360
233994 | AC2-023 GEN | S1 | 0.6 | 235 | Gen |  | 85 | 0 | 1 |  | 46.8 | 0 | 0 | 0 | 26.21 |  |  |  | -0.00047 |  |  |  | AC2-023
234012 | AE2-112_GEN | S1 | 0.39 | 235 | Gen |  | 82 | 0 | 1 |  | 17 | 0 | 0 | 0 | 8.84 |  |  |  | -0.00047 |  |  |  | AE2-112
234014 | AF1-036_GEN | S1 | 0.39 | 235 | Gen |  | 82 | 0 | 1 |  | 20 | 0 | 0 | 0 | 10.4 |  |  |  | -0.00047 |  |  |  | AF1-036
234015 | AF2-250 GEN | S1 | 69 | 235 | Gen |  | 85 | 0 | 1 |  | 1.95 | 0 | 0 | 0 | 1.09 |  |  |  | -0.00047 |  |  |  | AF2-250
234020 | AE2-093_GEN | S1 | 0.39 | 235 | Gen |  | 82 | 0 | 1 |  | 45.98 | 0 | 0 | 0 | 23.91 |  |  |  | -0.00047 |  |  |  | AE2-093
234021 | AF1-015_GEN | S2 | 0.39 | 235 | Gen |  | 82 | 0 | 1 |  | 16.72 | 0 | 0 | 0 | 8.69 |  |  |  | -0.00047 |  |  |  | AF1-015
233990 | AG1-397 GEN | S1 | 69 | 235 | Gen |  | 82 | 0 | 1 |  | 9.97 | 0 | 0 | 0 | 5.18 |  |  |  | -0.00047 |  |  |  | AG1-397 |  | MFO
233990 | AG1-397 GEN | B1 | 69 | 235 | Gen | New | 88 | 0 | 1 |  | 3 | 0 | 0 | 0 | 0 |  |  |  | -0.00047 |  |  |  | AG1-397 |  | MFO
205951 | AE1-129 C | S1 | 0.63 | 227 | Gen |  | 85 | 0 | 1 |  | 79.6 | 0 | 0 | 0 | 44.58 |  |  |  | -0.00045 |  |  |  | AE1-129
203975 | AE1-071-GEN | S1 | 0.6 | 226 | Gen |  | 85 | 0 | 1 |  | 100.1 | 0 | 0 | 0 | 56.06 |  |  |  | -0.00044 |  |  |  | AE1-071
237000 | AF2-398 C | S1 | 138 | 201 | Gen |  | 86 | 0 | 1 |  | 3 | 0 | 0 | 0 | 1.62 |  |  |  | 0.00043 |  |  |  | AF2-398
205920 | AF2-101 C | S1 | 115 | 227 | Gen | New | 85 | 0 | 1 |  | 3 | 0 | 0 | 0 | 0 |  |  |  | -0.00041 |  |  |  | AF2-101
228260 | V4-054C | 1 | 12.9 | 234 | Gen |  | 82 | 0 | 1 |  | 10 | 0 | 0 | 0 | 5.2 |  |  |  | -0.00041 |  |  |  | V4-054C
228261 | V4-054E | 1 | 12.9 | 234 | Gen | New | 82 | 0 | 1 |  | 6.2 | 0 | 0 | 0 | 0 |  |  |  | -0.00041 |  |  |  | V4-054E
228351 | V2-046C | 1 | 12.9 | 234 | Gen |  | 82 | 0 | 1 |  | 20.7 | 0 | 0 | 0 | 10.76 |  |  |  | -0.00041 |  |  |  | V2-046
228711 | V2-041C | 1 | 13.2 | 234 | Gen |  | 85 | 0 | 1 |  | 4 | 0 | 0 | 0 | 2.24 |  |  |  | -0.00041 |  |  |  | V2-041C
228712 | V2-041E | 1 | 13.2 | 234 | Gen | New | 85 | 0 | 1 |  | 2.48 | 0 | 0 | 0 | 0 |  |  |  | -0.00041 |  |  |  | V2-041
230430 | AE1-229 GEN | S1 | 0.63 | 234 | Gen |  | 85 | 0 | 1 |  | 151.2 | 0 | 0 | 0 | 84.67 |  |  |  | -0.00041 |  |  |  | AE1-229
230452 | AE1-240_GEN | 1 | 0.63 | 234 | Gen |  | 85 | 0 | 1 |  | 50.4 | 0 | 0 | 0 | 28.22 |  |  |  | -0.00041 |  |  |  | AE1-240
230447 | AE1-061 GEN | 1 | 12.9 | 234 | Gen | New | 88 | 0 | 1 |  | 5.5 | 0 | -5.5 | 0 | 0 |  |  |  | -0.00041 |  |  |  | AE1-061
219240 | MANTUACREK E | BA | 26.4 | 231 | Gen | New | 88 | 0 | 1 |  | 2 | 0 | -2 | 0 | 0 |  |  |  | -0.0004
219726 | BAT.STORG E | BA | 13.2 | 231 | Gen | New | 88 | 0 | 1 |  | 1 | 0 | -1 | 0 | 0 |  |  |  | -0.0004
219137 | THOSOLAR C | 1 | 13.2 | 231 | Gen |  | 82 | 0 | 1 |  | 8.67 | 0 | 0 | 0 | 4.51 |  |  |  | -0.00041
219258 | KINSLEYDEP C | 1 | 13.2 | 231 | Gen |  | 82 | 0 | 1 |  | 5.76 | 0 | 0 | 0 | 2.99 |  |  |  | -0.0004
219623 | KINSLEYBEA C | 1 | 13.2 | 231 | Gen |  | 82 | 0 | 1 |  | 5.11 | 0 | 0 | 0 | 2.66 |  |  |  | -0.0004
219766 | PARADISE C | 1 | 26.4 | 231 | Gen |  | 82 | 0 | 1 |  | 5.1 | 0 | 0 | 0 | 2.65 |  |  |  | -0.0004
219904 | AC1-010 C | S1 | 26.4 | 231 | Gen |  | 82 | 0 | 1 |  | 6 | 0 | 0 | 0 | 3.12 |  |  |  | -0.0004 |  |  |  | AC1-010
219912 | AD2-042 C | 1 | 26.4 | 231 | Gen |  | 82 | 0 | 1 |  | 13.2 | 0 | 0 | 0 | 6.86 |  |  |  | -0.0004 |  |  |  | AD2-042
219914 | AD2-027 C | 1 | 26.4 | 231 | Gen |  | 82 | 0 | 1 |  | 10 | 0 | 0 | 0 | 5.2 |  |  |  | -0.0004 |  |  |  | AD2-027
219917 | AB1-063 E | E | 13.2 | 231 | Gen | New | 82 | 0 | 1 |  | 0.4 | 0 | 0 | 0 | 0 |  |  |  | -0.0004 |  |  |  | AB1-063
219921 | AF1-264 | 1 | 13.2 | 231 | Gen |  | 82 | 0 | 1 |  | 4.3 | 0 | 0 | 0 | 2.24 |  |  |  | -0.0004 |  |  |  | AF1-264
227841 | ONTRIO 4 | W1 | 12.9 | 234 | Gen | New | 76 | 0 | 1 |  | 7.5 | 0 | 0 | 0 | 0 |  |  |  | -0.0004
227927 | V4-067C | 1 | 12.9 | 234 | Gen |  | 82 | 0 | 1 |  | 2.6 | 0 | 0 | 0 | 1.35 |  |  |  | -0.0004 |  |  |  | V4-067
228720 | V2-035C | 1 | 12.9 | 234 | Gen |  | 82 | 0 | 1 |  | 2 | 0 | 0 | 0 | 1.04 |  |  |  | -0.00041 |  |  |  | V2-035
228728 | W1-130C | 1 | 12.9 | 234 | Gen |  | 82 | 0 | 1 |  | 8.9 | 0 | 0 | 0 | 4.63 |  |  |  | -0.00041 |  |  |  | W1-130
228729 | W2-030 C | 1 | 12.9 | 234 | Gen |  | 82 | 0 | 1 |  | 9.65 | 0 | 0 | 0 | 5.02 |  |  |  | -0.0004 |  |  |  | W2-030
228754 | AB1-001 C | S1 | 12.9 | 234 | Gen |  | 82 | 0 | 1 |  | 2.3 | 0 | 0 | 0 | 1.2 |  |  |  | -0.0004 |  |  |  | AB1-001
230407 | AD2-065_C | 1 | 12.9 | 234 | Gen |  | 82 | 0 | 1 |  | 4.11 | 0 | 0 | 0 | 2.14 |  |  |  | -0.00041 |  |  |  | AD2-065
230409 | AE1-218 C | 1 | 12.9 | 234 | Gen |  | 82 | 0 | 1 |  | 2 | 0 | 0 | 0 | 1.04 |  |  |  | -0.00041 |  |  |  | AE1-218
230414 | AF1-041 E | 1 | 69 | 234 | Gen | New | 82 | 0 | 1 |  | 2.4 | 0 | 0 | 0 | 0 |  |  |  | -0.0004 |  |  |  | AF1-041
230415 | AB2-049 C | S1 | 69 | 234 | Gen |  | 82 | 0 | 1 |  | 7.34 | 0 | 0 | 0 | 3.82 |  |  |  | -0.00041 |  |  |  | AB2-049
230422 | AE1-104_GEN1 | 1 | 3.1 | 234 | Gen |  | 79 | 0 | 1 |  | 216 | 0 | 0 | 0 | 99.36 |  |  |  | -0.00041 |  |  |  | AE1-104
230425 | AE1-104_GEN2 | 1 | 3.1 | 234 | Gen |  | 79 | 0 | 1 |  | 216 | 0 | 0 | 0 | 99.36 |  |  |  | -0.00041 |  |  |  | AE1-104
230433 | AD2-135 GEN | S1 | 69 | 234 | Gen |  | 82 | 0 | 1 |  | 1.62 | 0 | 0 | 0 | 0.84 |  |  |  | -0.00041 |  |  |  | AD2-135
230434 | AG1-499 GEN | S1 | 12.9 | 234 | Gen |  | 85 | 0 | 1 |  | 10 | 0 | 0 | 0 | 5.6 |  |  |  | -0.00041 |  |  |  | AG1-499
230446 | AE2-334_GEN | S1 | 0.6 | 234 | Gen |  | 85 | 0 | 1 |  | 44 | 0 | 0 | 0 | 24.64 |  |  |  | -0.00041 |  |  |  | AE2-334
940361 | AE2-020 | 1 | 230 | 234 | Gen |  | 79 | 0 | 1 |  | 604.8 | 0 | 0 | 0 | 278.21 |  |  |  | -0.0004 |  |  |  | AE2-020
940371 | AE2-021 | 1 | 230 | 234 | Gen |  | 79 | 0 | 1 |  | 604.8 | 0 | 0 | 0 | 278.21 |  |  |  | -0.0004 |  |  |  | AE2-021
940381 | AE2-022 | 1 | 230 | 234 | Gen |  | 79 | 0 | 1 |  | 300 | 0 | 0 | 0 | 138 |  |  |  | -0.0004 |  |  |  | AE2-022
218660 | EHAMPSOLAR C | 1 | 13.2 | 231 | Gen |  | 82 | 0 | 1 |  | 2.9 | 0 | 0 | 0 | 1.51 |  |  |  | -0.0004
219236 | SOUTHERNHQ C | 1 | 13.2 | 231 | Gen |  | 82 | 0 | 1 |  | 0.93 | 0 | 0 | 0 | 0.48 |  |  |  | -0.0004
219272 | CLEANLIGHT C | 1 | 13.2 | 231 | Gen |  | 82 | 0 | 1 |  | 2.8 | 0 | 0 | 0 | 1.46 |  |  |  | -0.0004
219287 | REEVESEAST C | 1 | 13.2 | 231 | Gen |  | 82 | 0 | 1 |  | 11 | 0 | 0 | 0 | 5.72 |  |  |  | -0.00039
219291 | REEVESSOUT C | 1 | 13.2 | 231 | Gen |  | 82 | 0 | 1 |  | 1 | 0 | 0 | 0 | 0.52 |  |  |  | -0.0004
219615 | MILLCREEK C | 1 | 13.2 | 231 | Gen |  | 82 | 0 | 1 |  | 3.5 | 0 | 0 | 0 | 1.82 |  |  |  | -0.00039
219686 | LUMSOLAR_N C | 1 | 13.2 | 231 | Gen |  | 82 | 0 | 1 |  | 3.4 | 0 | 0 | 0 | 1.77 |  |  |  | -0.00039
219688 | LUMSOLAR_S C | 1 | 13.2 | 231 | Gen |  | 82 | 0 | 1 |  | 3.4 | 0 | 0 | 0 | 1.77 |  |  |  | -0.00039
219906 | AC1-017 C | S1 | 13.2 | 231 | Gen |  | 82 | 0 | 1 |  | 3.71 | 0 | 0 | 0 | 1.93 |  |  |  | -0.00039 |  |  |  | AC1-017
219907 | AC1-030 C | S1 | 13 | 231 | Gen |  | 82 | 0 | 1 |  | 2.5 | 0 | 0 | 0 | 1.3 |  |  |  | -0.0004 |  |  |  | AC1-030
219927 | AG1-080 C O1 | S1 | 69 | 231 | Gen |  | 82 | 0 | 1 |  | 19.9 | 0 | 0 | 0 | 10.35 |  |  |  | -0.0004 |  |  |  | AG1-080
219924 | AG1-130 C | B1 | 26.4 | 231 | Gen | New | 88 | 0 | 1 |  | 5 | 0 | -5 | 0 | 0 |  |  |  | -0.00039 |  |  |  | AG1-130
208862 | AG1-362 C | S1 | 12.47 | 229 | Gen |  | 85 | 0 | 1 |  | 5 | 0 | 0 | 0 | 2.8 |  |  |  | -0.00039 |  |  |  | AG1-362
214067 | T20SOLAR | 1 | 0.48 | 230 | Gen |  | 82 | 0 | 1 |  | 3.3 | 0 | 0 | 0 | 1.72 |  |  |  | -0.00038 |  |  |  | T20
219304 | NAMERICA C | 1 | 26.4 | 231 | Gen |  | 82 | 0 | 1 |  | 7.9 | 0 | 0 | 0 | 4.11 |  |  |  | -0.00039
219348 | LDSOLAR C | 1 | 26.4 | 231 | Gen |  | 82 | 0 | 1 |  | 10 | 0 | 0 | 0 | 5.2 |  |  |  | -0.00039
219607 | WPEMNERT C | 1 | 26.4 | 231 | Gen |  | 82 | 0 | 1 |  | 7 | 0 | 0 | 0 | 3.64 |  |  |  | -0.00039
219610 | FLORENCE C | 1 | 26.4 | 231 | Gen |  | 82 | 0 | 1 |  | 16.1 | 0 | 0 | 0 | 8.37 |  |  |  | -0.00039
207150 | 28HAN_X4-015 | S1 | 34.5 | 228 | Gen |  | 82 | 0 | 1 |  | 5 | 0 | 0 | 0 | 2.6 |  |  |  | -0.00037 |  |  |  | X4-015
207160 | 28EGP_W2-019 | S1 | 34.5 | 228 | Gen |  | 82 | 0 | 1 |  | 6 | 0 | 0 | 0 | 3.12 |  |  |  | -0.00037 |  |  |  | W2-019
207164 | 28NHV_W2-082 | S1 | 34.5 | 228 | Gen |  | 82 | 0 | 1 |  | 17 | 0 | 0 | 0 | 8.84 |  |  |  | -0.00037 |  |  |  | W2-082
207207 | 28JCB_W1-129 | S1 | 34.5 | 228 | Gen |  | 82 | 0 | 1 |  | 5 | 0 | 0 | 0 | 2.6 |  |  |  | -0.00037 |  |  |  | W1-129
207208 | 28JCB_W4-025 | S1 | 34.5 | 228 | Gen |  | 82 | 0 | 1 |  | 7 | 0 | 0 | 0 | 3.64 |  |  |  | -0.00037 |  |  |  | W4-025
207400 | 28PL_AA1-060 | BA | 34.5 | 228 | Gen | New | 88 | 0 | 1 |  | 20 | 0 | -20 | 0 | 0 |  |  |  | -0.00037 |  |  |  | AA1-060
207149 | 28UPF_X1-085 | S1 | 34.5 | 228 | Gen |  | 82 | 0 | 1 |  | 5 | 0 | 0 | 0 | 2.6 |  |  |  | -0.00036 |  |  |  | X1-085
207157 | 28PEM_W1-119 | S1 | 34.5 | 228 | Gen |  | 82 | 0 | 1 |  | 8.8 | 0 | 0 | 0 | 4.58 |  |  |  | -0.00037 |  |  |  | W1-119
207158 | 28PEM_W1-120 | S1 | 34.5 | 228 | Gen |  | 82 | 0 | 1 |  | 8.8 | 0 | 0 | 0 | 4.58 |  |  |  | -0.00037 |  |  |  | W1-120
207171 | 28DIX_Z2-102 | S1 | 34.5 | 228 | Gen |  | 82 | 0 | 1 |  | 13 | 0 | 0 | 0 | 6.76 |  |  |  | -0.00037 |  |  |  | Z2-102
207445 | AB1-138 C | S | 0.38 | 228 | Gen |  | 82 | 0 | 1 |  | 9.6 | 0 | 0 | 0 | 4.99 |  |  |  | -0.00036 |  |  |  | AB1-138
207450 | AB1-163 E | E | 34.5 | 228 | Gen | New | 82 | 0 | 1 |  | 5 | 0 | 0 | 0 | 0 |  |  |  | -0.00036 |  |  |  | AB1-163
207459 | AE1-142 C | 1 | 34.5 | 228 | Gen |  | 82 | 0 | 1 |  | 20 | 0 | 0 | 0 | 10.4 |  |  |  | -0.00036 |  |  |  | AE1-142
207487 | AE2-000G4 | W4 | 3.1 | 228 | Gen |  | 79 | 0 | 1 |  | 204 | 0 | 0 | 0 | 93.84 |  |  |  | -0.00037 |  |  |  | AE2-000
207497 | AE2-000G2 | W2 | 3.1 | 228 | Gen |  | 79 | 0 | 1 |  | 204 | 0 | 0 | 0 | 93.84 |  |  |  | -0.00037 |  |  |  | AE2-000
207500 | AE2-000G1 | W1 | 3.1 | 228 | Gen |  | 79 | 0 | 1 |  | 204 | 0 | 0 | 0 | 93.84 |  |  |  | -0.00037 |  |  |  | AE2-000
207507 | AE2-000G3 | W3 | 3.1 | 228 | Gen |  | 79 | 0 | 1 |  | 204 | 0 | 0 | 0 | 93.84 |  |  |  | -0.00037 |  |  |  | AE2-000
219114 | HARTZY_C | 1 | 13.2 | 231 | Gen |  | 82 | 0 | 1 |  | 7.57 | 0 | 0 | 0 | 3.94 |  |  |  | -0.00037
219727 | YARDVSOLFA C | 1 | 13.2 | 231 | Gen |  | 82 | 0 | 1 |  | 8.67 | 0 | 0 | 0 | 4.51 |  |  |  | -0.00036
207451 | AA2-048 E | BA | 34.5 | 228 | Gen | New | 88 | 0 | 1 |  | 7 | 0 | -7 | 0 | 0 |  |  |  | -0.00035 |  |  |  | AA2-048
205925 | AF2-428 E | E | 69 | 227 | Gen | New | 82 | 0 | 1 |  | 3 | 0 | 0 | 0 | 0 |  |  |  | -0.00035 |  |  |  | AF2-428
206416 | 28MLH_W1-032 | S1 | 230 | 228 | Gen |  | 82 | 0 | 1 |  | 3 | 0 | 0 | 0 | 1.56 |  |  |  | -0.00035 |  |  |  | W1-032
207145 | 28FRN_Y2-051 | S1 | 34.5 | 228 | Gen |  | 82 | 0 | 1 |  | 5 | 0 | 0 | 0 | 2.6 |  |  |  | -0.00035 |  |  |  | Y2-051
207148 | 28MDF_W3-079 | S1 | 34.5 | 228 | Gen |  | 82 | 0 | 1 |  | 8 | 0 | 0 | 0 | 4.16 |  |  |  | -0.00035 |  |  |  | W3-079
219276 | PARKLANDSO C | 1 | 26.4 | 231 | Gen |  | 82 | 0 | 1 |  | 7.84 | 0 | 0 | 0 | 4.08 |  |  |  | -0.00036
219620 | RIDERU C | 1 | 13.2 | 231 | Gen |  | 82 | 0 | 1 |  | 0.7 | 0 | 0 | 0 | 0.37 |  |  |  | -0.00036
219680 | HOPEWELLV C | 1 | 13.2 | 231 | Gen |  | 82 | 0 | 1 |  | 1.7 | 0 | 0 | 0 | 0.88 |  |  |  | -0.00035
219817 | TRENTONSOL C | 1 | 13.2 | 231 | Gen |  | 82 | 0 | 1 |  | 8.67 | 0 | 0 | 0 | 4.51 |  |  |  | -0.00036
219918 | AC2-009 C | S1 | 13.2 | 231 | Gen |  | 82 | 0 | 1 |  | 0.59 | 0 | 0 | 0 | 0.31 |  |  |  | -0.00035 |  |  |  | AC2-009
207419 | AB2-139 E | 1 | 34.5 | 228 | Gen | New | 88 | 0 | 1 |  | 0.21 | 0 | -0.21 | 0 | 0 |  |  |  | -0.00035 |  |  |  | AB2-139
205923 | AF2-272 E | E | 69 | 227 | Gen | New | 82 | 0 | 1 |  | 3 | 0 | 0 | 0 | 0 |  |  |  | -0.00035 |  |  |  | AF2-272
205924 | AF2-281 E | E | 69 | 227 | Gen | New | 82 | 0 | 1 |  | 3 | 0 | 0 | 0 | 0 |  |  |  | -0.00035 |  |  |  | AF2-281
205926 | AF2-429 E | E | 34.5 | 227 | Gen | New | 82 | 0 | 1 |  | 3.72 | 0 | 0 | 0 | 0 |  |  |  | -0.00035 |  |  |  | AF2-429
205927 | AF2-430 E | E | 69 | 227 | Gen | New | 82 | 0 | 1 |  | 3 | 0 | 0 | 0 | 0 |  |  |  | -0.00035 |  |  |  | AF2-430
205928 | AF2-431 E | E | 69 | 227 | Gen | New | 82 | 0 | 1 |  | 1.17 | 0 | 0 | 0 | 0 |  |  |  | -0.00034 |  |  |  | AF2-431
205941 | AD2-115 C | 1 | 0.55 | 227 | Gen |  | 85 | 0 | 1 |  | 20 | 0 | 0 | 0 | 11.2 |  |  |  | -0.00034 |  |  |  | AD2-115
207143 | 28BYD_X4-031 | E | 34.5 | 228 | Gen |  | 82 | 0 | 1 |  | 2 | 0 | 0 | 0 | 1.04 |  |  |  | -0.00035 |  |  |  | X4-031
207144 | 28HOW_X1-037 | S1 | 34.5 | 228 | Gen |  | 82 | 0 | 1 |  | 14.74 | 0 | 0 | 0 | 7.66 |  |  |  | -0.00035 |  |  |  | X1-037
207152 | 28NPK_W1-113 | S1 | 34.5 | 228 | Gen |  | 82 | 0 | 1 |  | 7.8 | 0 | 0 | 0 | 4.06 |  |  |  | -0.00035 |  |  |  | W1-113
207162 | 28APLW2-078 | S1 | 34.5 | 228 | Gen |  | 82 | 0 | 1 |  | 8.7 | 0 | 0 | 0 | 4.52 |  |  |  | -0.00035 |  |  |  | W1-113
207204 | 28HOL_W1-112 | S1 | 34.5 | 228 | Gen |  | 82 | 0 | 1 |  | 3.65 | 0 | 0 | 0 | 1.9 |  |  |  | -0.00034 |  |  |  | W1-112
207205 | 28MAN_W1-024 | S1 | 34.5 | 228 | Gen |  | 82 | 0 | 1 |  | 3.8 | 0 | 0 | 0 | 1.98 |  |  |  | -0.00035 |  |  |  | W1-024
207206 | 28TIN_W1-124 | S1 | 34.5 | 228 | Gen |  | 82 | 0 | 1 |  | 16.9 | 0 | 0 | 0 | 8.79 |  |  |  | -0.00035 |  |  |  | W1-124
207420 | 28HF_AC1-207 | S1 | 34.5 | 228 | Gen |  | 82 | 0 | 1 |  | 13.1 | 0 | 0 | 0 | 6.81 |  |  |  | -0.00035 |  |  |  | AC1-207
207464 | AA2-184 E | 1 | 34.5 | 228 | Gen |  | 82 | 0 | 1 |  | 20 | 0 | 0 | 0 | 10.4 |  |  |  | -0.00035 |  |  |  | AA2-184
210323 | AF2-286 E | E | 13.8 | 229 | Gen | New | 82 | 0 | 1 |  | 3 | 0 | 0 | 0 | 0 |  |  |  | -0.00035 |  |  |  | AF2-286
217197 | RE CRAN C | 1 | 13 | 231 | Gen |  | 82 | 0 | 1 |  | 5 | 0 | 0 | 0 | 2.6 |  |  |  | -0.00034
218438 | BLK ROCK C | 1 | 13 | 231 | Gen |  | 82 | 0 | 1 |  | 2.36 | 0 | 0 | 0 | 1.23 |  |  |  | -0.00034
219612 | MATRIX C | 1 | 13.2 | 231 | Gen |  | 82 | 0 | 1 |  | 2.85 | 0 | 0 | 0 | 1.48 |  |  |  | -0.00034
219879 | V2-009 C4 | 1 | 13.2 | 231 | Gen |  | 82 | 0 | 1 |  | 4.03 | 0 | 0 | 0 | 2.1 |  |  |  | -0.00035 |  |  |  | V2-009
219880 | V2-009 C3 | 1 | 13.2 | 231 | Gen |  | 82 | 0 | 1 |  | 4.03 | 0 | 0 | 0 | 2.1 |  |  |  | -0.00035 |  |  |  | V2-009
219882 | V2-009 C2 | 1 | 13.2 | 231 | Gen |  | 82 | 0 | 1 |  | 4.03 | 0 | 0 | 0 | 2.1 |  |  |  | -0.00034 |  |  |  | V2-009
219884 | V2-009 C1 | 1 | 13.2 | 231 | Gen |  | 82 | 0 | 1 |  | 4.03 | 0 | 0 | 0 | 2.1 |  |  |  | -0.00034 |  |  |  | V2-009
219922 | AF2-168 E | 1 | 69 | 231 | Gen | New | 82 | 0 | 1 |  | 0.9 | 0 | 0 | 0 | 0 |  |  |  | -0.00035 |  |  |  | AF2-168
967451 | AG2-055 | 1 | 500 | 225 | Gen | New | 79 | 0 | 1 |  | 1148 | 0 | 0 | 0 | 0 |  |  |  | -0.00034 |  |  |  | AG2-055
7 | G-007 |  |  |  | LTF | [5 empty] | 105 | 0 | 0 | 0 |  |  |  |  | 0.0003
219916 | AD2-025 E | 1 | 13.2 | 231 | Gen | New | 88 | 0 | 1 |  | 2 | 0 | -2 | 0 | 0 |  |  |  | -0.00033 |  |  |  | AD2-025
206755 | 28CPH_W2-050 | S1 | 34.5 | 228 | Gen | New | 82 | 0 | 1 |  | 8 | 0 | 0 | 0 | 0 |  |  |  | -0.00033 |  |  |  | W2-050
207169 | 28W4-060COL | S1 | 34.5 | 228 | Gen |  | 82 | 0 | 1 |  | 10 | 0 | 0 | 0 | 5.2 |  |  |  | -0.00034 |  |  |  | W4-06
217198 | V3-058 E | 1 | 26.4 | 231 | Gen | New | 82 | 0 | 1 |  | 2 | 0 | 0 | 0 | 0 |  |  |  | -0.00034 |  |  |  | V3-058
217199 | V3-059 E | 1 | 26.4 | 231 | Gen | New | 82 | 0 | 1 |  | 2 | 0 | 0 | 0 | 0 |  |  |  | -0.00034 |  |  |  | V3-059
218526 | CNTRALGAS2 C | 1 | 13.2 | 231 | Gen |  | 82 | 0 | 1 |  | 8.67 | 0 | 0 | 0 | 4.51 |  |  |  | -0.00033
219903 | AB2-057 C | S1 | 26 | 231 | Gen |  | 82 | 0 | 1 |  | 10 | 0 | 0 | 0 | 5.2 |  |  |  | -0.00034 |  |  |  | AB2-057
207474 | AD2-213 E O1 | B1 | 34.5 | 228 | Gen | New | 88 | 0 | 1 |  | 20 | 0 | -20 | 0 | 0 |  |  |  | -0.00032 |  |  |  | AD2-213
219920 | AE1-041 EBAT | BA | 26.4 | 231 | Gen | New | 88 | 0 | 1 |  | 0.5 | 0 | -0.5 | 0 | 0 |  |  |  | -0.00033 |  |  |  | AE1-041
206736 | 28F1S_V4-069 | S1 | 34.5 | 228 | Gen |  | 82 | 0 | 1 |  | 3 | 0 | 0 | 0 | 1.56 |  |  |  | -0.00032 |  |  |  | V4-069
206737 | 28F2S_V4-070 | S1 | 34.5 | 228 | Gen |  | 82 | 0 | 1 |  | 3 | 0 | 0 | 0 | 1.56 |  |  |  | -0.00032 |  |  |  | V4-070
206738 | 28FLE_V3-070 | S1 | 34.5 | 228 | Gen |  | 82 | 0 | 1 |  | 8 | 0 | 0 | 0 | 4.16 |  |  |  | -0.00033 |  |  |  | V3-070
206744 | 28PIT_W1-132 | S1 | 34.5 | 228 | Gen | New | 82 | 0 | 1 |  | 2 | 0 | 0 | 0 | 0 |  |  |  | -0.00032 |  |  |  | W1-132
206754 | 28EAM_W2-061 | S1 | 34.5 | 228 | Gen |  | 82 | 0 | 1 |  | 2.76 | 0 | 0 | 0 | 1.43 |  |  |  | -0.00032 |  |  |  | W2-061
206761 | 28MHD_W3-029 | S1 | 34.5 | 228 | Gen |  | 82 | 0 | 1 |  | 13.7 | 0 | 0 | 0 | 7.12 |  |  |  | -0.00032 |  |  |  | W3-029
206764 | 28JCR_X2-075 | S1 | 34.5 | 228 | Gen |  | 82 | 0 | 1 |  | 6 | 0 | 0 | 0 | 3.12 |  |  |  | -0.00032 |  |  |  | X2-075
207482 | AE1-156 | S1 | 34.5 | 228 | Gen |  | 82 | 0 | 1 |  | 17.6 | 0 | 0 | 0 | 9.15 |  |  |  | -0.00032 |  |  |  | AE1-156
207483 | W3-003 E | E | 34.5 | 228 | Gen | New | 82 | 0 | 1 |  | 10 | 0 | 0 | 0 | 0 |  |  |  | -0.00032 |  |  |  | W3-003
211089 | AF2-277 E | E | 12.5 | 229 | Gen | New | 82 | 0 | 1 |  | 2 | 0 | 0 | 0 | 0 |  |  |  | -0.00032 |  |  |  | AF2-277
217213 | AMBOY SO C | S1 | 13.2 | 231 | Gen |  | 82 | 0 | 1 |  | 2.3 | 0 | 0 | 0 | 1.2 |  |  |  | -0.00033
218428 | ETC SOLAR C | 1 | 13.2 | 231 | Gen |  | 82 | 0 | 1 |  | 0.57 | 0 | 0 | 0 | 0.29 |  |  |  | -0.00033
218440 | SUMMTASSOC C | 1 | 13 | 231 | Gen |  | 82 | 0 | 1 |  | 2 | 0 | 0 | 0 | 1.04 |  |  |  | -0.00033
218524 | CNTRALGAS1 C | 1 | 13.2 | 231 | Gen |  | 82 | 0 | 1 |  | 8.67 | 0 | 0 | 0 | 4.51 |  |  |  | -0.00033
219249 | CENTRALDIV C | 1 | 13.2 | 231 | Gen |  | 82 | 0 | 1 |  | 0.76 | 0 | 0 | 0 | 0.4 |  |  |  | -0.00033
219908 | AB1-139 C | S1 | 26.4 | 231 | Gen |  | 82 | 0 | 1 |  | 6.6 | 0 | 0 | 0 | 3.43 |  |  |  | -0.00033 |  |  |  | AB1-139
219919 | AE1-041 C | S1 | 26.4 | 231 | Gen |  | 82 | 0 | 1 |  | 1.1 | 0 | 0 | 0 | 0.57 |  |  |  | -0.00033 |  |  |  | AE1-041
206718 | 28STAW2-080 | S1 | 34.5 | 228 | Gen |  | 82 | 0 | 1 |  | 2 | 0 | 0 | 0 | 1.04 |  |  |  | -0.00032 |  |  |  | 28STAW2
206745 | 28F3S_W2-016 | S1 | 34.5 | 228 | Gen |  | 82 | 0 | 1 |  | 15 | 0 | 0 | 0 | 7.8 |  |  |  | -0.00032 |  |  |  | W2-016
217081 | WEATEXAS C | 1 | 13.2 | 231 | Gen |  | 82 | 0 | 1 |  | 1.4 | 0 | 0 | 0 | 0.73 |  |  |  | -0.00031
217202 | FBANKSOLAR C | 1 | 13.2 | 231 | Gen |  | 82 | 0 | 1 |  | 1.01 | 0 | 0 | 0 | 0.53 |  |  |  | -0.00031
217209 | CENTRL HS C | 1 | 13.8 | 231 | Gen |  | 82 | 0 | 1 |  | 0.8 | 0 | 0 | 0 | 0.42 |  |  |  | -0.00031
217211 | CAMDEN ST C | 1 | 13.8 | 231 | Gen |  | 82 | 0 | 1 |  | 0.43 | 0 | 0 | 0 | 0.22 |  |  |  | -0.00031
218449 | LINSOLAR C | 1 | 26.4 | 231 | Gen |  | 82 | 0 | 1 |  | 8.67 | 0 | 0 | 0 | 4.51 |  |  |  | -0.00032
26 | O66 |  |  |  | LTF | [5 empty] | 673 | 0 | 0 | 0 |  |  |  |  | 0.0003
207458 | AD2-210 E | E | 34.5 | 228 | Gen | New | 88 | 0 | 1 |  | 2 | 0 | -2 | 0 | 0 |  |  |  | -0.0003 |  |  |  | AD2-210
206767 | 28BRNX1-095 | S1 | 34.5 | 228 | Gen |  | 82 | 0 | 1 |  | 3 | 0 | 0 | 0 | 1.56 |  |  |  | -0.0003 |  |  |  | X1-095
217169 | METRODIV C | 1 | 13.2 | 231 | Gen |  | 82 | 0 | 1 |  | 1.86 | 0 | 0 | 0 | 0.97 |  |  |  | -0.00031
217194 | REDH C | 1 | 13 | 231 | Gen |  | 82 | 0 | 1 |  | 5 | 0 | 0 | 0 | 2.6 |  |  |  | -0.00031
217201 | HACKENSOLA C | 1 | 26.4 | 231 | Gen |  | 82 | 0 | 1 |  | 1 | 0 | 0 | 0 | 0.52 |  |  |  | -0.00031
217204 | WCALDSOLAR C | 1 | 13.2 | 231 | Gen |  | 82 | 0 | 1 |  | 1 | 0 | 0 | 0 | 0.52 |  |  |  | -0.00031
217206 | BARNGR HS C | 1 | 26.4 | 231 | Gen |  | 82 | 0 | 1 |  | 0.55 | 0 | 0 | 0 | 0.28 |  |  |  | -0.00031
217208 | PARK ELE C | 1 | 13.2 | 231 | Gen |  | 82 | 0 | 1 |  | 0.43 | 0 | 0 | 0 | 0.22 |  |  |  | -0.00031
219910 | AD1-054 E | S1 | 13.2 | 231 | Gen | New | 82 | 0 | 1 |  | 1.5 | 0 | 0 | 0 | 0 |  |  |  | -0.00031 |  |  |  | AD1-054
206743 | 28GAR_V4-001 | S1 | 34.5 | 228 | Gen |  | 82 | 0 | 1 |  | 2.76 | 0 | 0 | 0 | 1.43 |  |  |  | -0.0003 |  |  |  | V4-001
207402 | 28AA2-082 E | E | 34.5 | 228 | Gen | New | 88 | 0 | 1 |  | 20 | 0 | -20 | 0 | 0 |  |  |  | -0.00028 |  |  |  | AA2-082
207413 | 28AA2-061 E | 1 | 34.5 | 228 | Gen | New | 88 | 0 | 1 |  | 8 | 0 | -8 | 0 | 0 |  |  |  | -0.00028 |  |  |  | AA2-061
207412 | 28AA2-060 E | BA | 34.5 | 228 | Gen | New | 88 | 0 | 1 |  | 6 | 0 | -6 | 0 | 0 |  |  |  | -0.00028 |  |  |  | AA2-060
206345 | 28N27_Y2-018 | S1 | 13.8 | 228 | Gen |  | 85 | 0 | 1 |  | 3.8 | 0 | 0 | 0 | 2.13 |  |  |  | -0.00028 |  |  |  | Y2-018
206679 | 28M&M S721 | 1 | 34.5 | 228 | Gen | New | 82 | 0 | 1 |  | 10.3 | 0 | 0 | 0 | 0 |  |  |  | -0.00028
206746 | 28WNG_W3-110 | S1 | 34.5 | 228 | Gen |  | 82 | 0 | 1 |  | 7.5 | 0 | 0 | 0 | 3.9 |  |  |  | -0.00029 |  |  |  | W3-110
206748 | 28DL_W4-046 | S1 | 34.5 | 228 | Gen |  | 82 | 0 | 1 |  | 8.6 | 0 | 0 | 0 | 4.47 |  |  |  | -0.00028 |  |  |  | W4-046
206749 | 28WA_W3-044 | S1 | 34.5 | 228 | Gen |  | 82 | 0 | 1 |  | 20 | 0 | 0 | 0 | 10.4 |  |  |  | -0.00029 |  |  |  | W3-044
206757 | 28RH_W2-091 | S1 | 34.5 | 228 | Gen |  | 82 | 0 | 1 |  | 8 | 0 | 0 | 0 | 4.16 |  |  |  | -0.00028 |  |  |  | W2-091
206759 | 28HOL_W4-097 | S1 | 34.5 | 228 | Gen |  | 82 | 0 | 1 |  | 3.2 | 0 | 0 | 0 | 1.66 |  |  |  | -0.00029 |  |  |  | W4-097
206762 | 28FRD_X1-012 | S1 | 34.5 | 228 | Gen |  | 82 | 0 | 1 |  | 10 | 0 | 0 | 0 | 5.2 |  |  |  | -0.00028 |  |  |  | X1-012
206763 | 28BVR_Y1-020 | S1 | 34.5 | 228 | Gen |  | 82 | 0 | 1 |  | 3.72 | 0 | 0 | 0 | 1.93 |  |  |  | -0.00029 |  |  |  | Y1-020
207408 | W3-077 C | S1 | 34.5 | 228 | Gen |  | 82 | 0 | 1 |  | 12.5 | 0 | 0 | 0 | 6.5 |  |  |  | -0.00028 |  |  |  | W3-077
207432 | AC2-175 E | 1 | 34.5 | 228 | Gen | New | 82 | 0 | 1 |  | 1.6 | 0 | 0 | 0 | 0 |  |  |  | -0.00029 |  |  |  | AC2-175
207437 | AD2-070 C | 1 | 34.5 | 228 | Gen |  | 82 | 0 | 1 |  | 7.8 | 0 | 0 | 0 | 4.06 |  |  |  | -0.00028 |  |  |  | AD2-070
207439 | AE1-081 C | 1 | 34.5 | 228 | Gen |  | 82 | 0 | 1 |  | 2.3 | 0 | 0 | 0 | 1.2 |  |  |  | -0.00029 |  |  |  | AE1-081
207462 | AF1-133 C | 1 | 34.5 | 228 | Gen |  | 85 | 0 | 1 |  | 20 | 0 | 0 | 0 | 11.2 |  |  |  | -0.00028 |  |  |  | AF1-133
207471 | AF2-354 C | 1 | 34.5 | 228 | Gen | New | 82 | 0 | 1 |  | 11 | 0 | 0 | 0 | 0 |  |  |  | -0.00029 |  |  |  | AF2-354
207472 | AE2-028 C | 1 | 34.5 | 228 | Gen |  | 82 | 0 | 1 |  | 0.75 | 0 | 0 | 0 | 0.39 |  |  |  | -0.00028 |  |  |  | AE2-028
207484 | AF2-139 C O1 | S1 | 34.5 | 228 | Gen |  | 82 | 0 | 1 |  | 8.8 | 0 | 0 | 0 | 4.58 |  |  |  | -0.00028 |  |  |  | AF2-139
207510 | AF2-138 C | S1 | 34.5 | 228 | Gen |  | 82 | 0 | 1 |  | 19.8 | 0 | 0 | 0 | 10.3 |  |  |  | -0.00029 |  |  |  | AF2-138
207511 | W3-106 GEN | S1 | 34.5 | 228 | Gen | New | 82 | 0 | 1 |  | 10.5 | 0 | 0 | 0 | 0 |  |  |  | -0.00029 |  |  |  | W3-106
207477 | AE1-060 E | E | 34.5 | 228 | Gen | New | 88 | 0 | 1 |  | 19.8 | 0 | -19.8 | 0 | 0 |  |  |  | -0.00027 |  |  |  | AE1-060
206719 | 28W4-073 | S1 | 34.5 | 228 | Gen |  | 82 | 0 | 1 |  | 13.54 | 0 | 0 | 0 | 7.04 |  |  |  | -0.00028 |  |  |  | 28W4-07
206741 | 28FR_U2-059 | S1 | 34.5 | 228 | Gen |  | 82 | 0 | 1 |  | 2.04 | 0 | 0 | 0 | 1.06 |  |  |  | -0.00028 |  |  |  | U2-059
206751 | 28HRM_W1-127 | S1 | 34.5 | 228 | Gen |  | 82 | 0 | 1 |  | 3.04 | 0 | 0 | 0 | 1.58 |  |  |  | -0.00028 |  |  |  | W1-127
206758 | 28AU_W4-064 | S1 | 34.5 | 228 | Gen |  | 82 | 0 | 1 |  | 3 | 0 | 0 | 0 | 1.56 |  |  |  | -0.00028 |  |  |  | W4-064
210947 | AG1-498 C | S1 | 12.5 | 229 | Gen |  | 82 | 0 | 1 |  | 8.8 | 0 | 0 | 0 | 4.58 |  |  |  | -0.00026 |  |  |  | AG1-498
211066 | AD1-143 C1 | B1 | 69 | 229 | Gen | New | 88 | 0 | 1 |  | 10 | 0 | -10 | 0 | 0 |  |  |  | -0.00024 |  |  |  | AD1-143
209945 | AF2-278 E | E | 12.5 | 229 | Gen | New | 82 | 0 | 1 |  | 3 | 0 | 0 | 0 | 0 |  |  |  | -0.00024 |  |  |  | AF2-278
211065 | PASP 1_2 C | 1 | 13.8 | 229 | Gen |  | 82 | 0 | 1 |  | 10 | 0 | 0 | 0 | 5.2 |  |  |  | -0.00024
211065 | PASP 1_2 C | S2 | 13.8 | 229 | Gen |  | 82 | 0 | 1 |  | 10 | 0 | 0 | 0 | 5.2 |  |  |  | -0.00024
211066 | AD1-143 C1 | 1 | 69 | 229 | Gen | New | 76 | 0 | 1 |  | 40 | 0 | 0 | 0 | 0 |  |  |  | -0.00024 |  |  |  | AD1-143
211067 | AD1-143 C2 | 2 | 69 | 229 | Gen | New | 76 | 0 | 1 |  | 40 | 0 | 0 | 0 | 0 |  |  |  | -0.00024 |  |  |  | AD1-143
237048 | AF1-022 C | 1 | 25 | 201 | Gen |  | 86 | 0 | 1 |  | 14 | 0 | 0 | 0 | 7.56 |  |  |  | -0.0002 |  |  |  | AF1-022
203979 | AG1-198 GEN | S1 | 34.5 | 226 | Gen |  | 85 | 0 | 1 |  | 12 | 0 | 0 | 0 | 6.72 |  |  |  | -0.00019 |  |  |  | AG1-198
211375 | BEAC | 1 | 69 | 229 | Gen | New | 88 | 0 | 1 |  | 20 | 0 | -20 | 0 | 0 |  |  |  | -0.00018 |  |  |  | W1-111
238102 | AF2-292 E | B1 | 138 | 201 | Gen | New | 88 | 0 | 1 |  | 1.5 | 0 | -1.5 | 0 | 0 |  |  |  | 0.00018 |  |  |  | AF2-292 |  | MFO
238102 | AF2-292 E | E | 138 | 201 | Gen | New | 83 | 0 | 1 |  | 1.17 | 0 | 0 | 0 | 0 |  |  |  | 0.00018 |  |  |  | AF2-292 |  | MFO
209063 | AE2-046 GEN | S1 | 0.55 | 229 | Gen | New | 82 | 0 | 1 |  | 50 | 0 | 0 | 0 | 0 |  |  |  | -0.00018 |  |  |  | AE2-046
209027 | LOR2_Q27 | W1 | 0.69 | 229 | Gen |  | 76 | 0 | 1 |  | 100 | 0 | 0 | 0 | 29 |  |  |  | -0.00016 |  |  |  | Q27
212266 | LOR1 | W1 | 0.69 | 229 | Gen |  | 76 | 0 | 1 |  | 3.4 | 0 | 0 | 0 | 0.99 |  |  |  | -0.00016 |  |  |  | N14
209093 | AE2-110 GEN | S1 | 0.55 | 229 | Gen |  | 82 | 0 | 1 |  | 20 | 0 | 0 | 0 | 10.4 |  |  |  | -0.00015 |  |  |  | AE2-110
211938 | AF2-285 E | E | 12.5 | 229 | Gen | New | 82 | 0 | 1 |  | 3 | 0 | 0 | 0 | 0 |  |  |  | -0.00015 |  |  |  | AF2-285
212451 | AF2-427 E | E | 12.5 | 229 | Gen | New | 82 | 0 | 1 |  | 3 | 0 | 0 | 0 | 0 |  |  |  | -0.00014 |  |  |  | AF2-427
212464 | AF2-289 E | E | 12.5 | 229 | Gen | New | 82 | 0 | 1 |  | 3 | 0 | 0 | 0 | 0 |  |  |  | -0.00014 |  |  |  | AF2-289
212495 | AF2-284 E | E | 12.5 | 229 | Gen | New | 82 | 0 | 1 |  | 2 | 0 | 0 | 0 | 0 |  |  |  | -0.00014 |  |  |  | AF2-284
209054 | AE2-059 GEN | S1 | 0.55 | 229 | Gen |  | 85 | 0 | 1 |  | 20 | 0 | 0 | 0 | 11.2 |  |  |  | -0.00014 |  |  |  | AE2-059
209059 | AE2-084 GEN | S1 | 0.55 | 229 | Gen | New | 82 | 0 | 1 |  | 20 | 0 | 0 | 0 | 0 |  |  |  | -0.00014 |  |  |  | AE2-084
209071 | AE2-133 GEN | S1 | 0.55 | 229 | Gen |  | 85 | 0 | 1 |  | 20 | 0 | 0 | 0 | 11.2 |  |  |  | -0.00013 |  |  |  | AE2-133
209089 | AE1-225 GEN | S1 | 69 | 229 | Gen |  | 82 | 0 | 1 |  | 19.8 | 0 | 0 | 0 | 10.3 |  |  |  | -0.00013 |  |  |  | AE1-225
209097 | AE2-111_GEN | S1 | 0.55 | 229 | Gen |  | 82 | 0 | 1 |  | 20 | 0 | 0 | 0 | 10.4 |  |  |  | -0.00013 |  |  |  | AE2-111
212455 | AF2-290 E | E | 12.5 | 229 | Gen | New | 82 | 0 | 1 |  | 2 | 0 | 0 | 0 | 0 |  |  |  | -0.00014 |  |  |  | AF2-290
212507 | AE2-042_GEN | S1 | 0.6 | 229 | Gen |  | 85 | 0 | 1 |  | 70 | 0 | 0 | 0 | 39.2 |  |  |  | -0.00014 |  |  |  | AE2-042
237505 | 01ELLIOTTS | W1 | 34.5 | 201 | Gen |  | 77 | 0 | 1 |  | 50.4 | 0 | 0 | 0 | 16.13 |  |  |  | 0.00013
211913 | AB1-182 E | 1 | 69 | 229 | Gen | New | 88 | 0 | 1 |  | 20 | 0 | -20 | 0 | 0 |  |  |  | -0.00013 |  |  |  | AB1-182
208972 | BECR L18 | W1 | 0.69 | 229 | Gen |  | 76 | 0 | 1 |  | 26 | 0 | 0 | 0 | 7.54 |  |  |  | -0.00013 |  |  |  | L18
209029 | WAYM IPP | W1 | 0.57 | 229 | Gen |  | 76 | 0 | 1 |  | 70 | 0 | 0 | 0 | 20.3 |  |  |  | -9e-05 |  |  |  | D05
211490 | AF2-282 E | E | 12.5 | 229 | Gen | New | 82 | 0 | 1 |  | 3 | 0 | 0 | 0 | 0 |  |  |  | -9e-05 |  |  |  | AF2-282
211554 | AF2-283 E | E | 12.5 | 229 | Gen | New | 82 | 0 | 1 |  | 2 | 0 | 0 | 0 | 0 |  |  |  | -9e-05 |  |  |  | AF2-283
209067 | AE2-060 GEN | S1 | 0.55 | 229 | Gen |  | 85 | 0 | 1 |  | 20 | 0 | 0 | 0 | 11.2 |  |  |  | -3e-05 |  |  |  | AE2-060
209937 | AF2-287 E | E | 12.5 | 229 | Gen | New | 82 | 0 | 1 |  | 3 | 0 | 0 | 0 | 0 |  |  |  | -3e-05 |  |  |  | AF2-287
209972 | AF2-288 E | E | 12.5 | 229 | Gen | New | 82 | 0 | 1 |  | 3 | 0 | 0 | 0 | 0 |  |  |  | -3e-05 |  |  |  | AF2-288
9 | NY |  |  |  | LTF | [5 empty] | 55.3 | 0 | 0 | 0 |  |  |  |  | -0.0001
8 | VTF |  |  |  | LTF | [5 empty] | 645 | 0 | 0 | 0 |  |  |  |  | -0.0003
6 | G-007A |  |  |  | LTF | [5 empty] | 239.8 | 0 | 0 | 0 |  |  |  |  | -0.0003
14 | CPLE |  |  |  | LTF | [5 empty] | 94.5 | 0 | 0 | 0 |  |  |  |  | -0.0033
5 | CBM South 2 |  |  |  | LTF | [5 empty] | 1356 | 0 | 0 | 0 |  |  |  |  | -0.0036
16 | TVA |  |  |  | LTF | [5 empty] | 87.5 | 0 | 0 | 0 |  |  |  |  | -0.004
23 | LAGN |  |  |  | LTF | [5 empty] | 175 | 0 | 0 | 0 |  |  |  |  | -0.0041
4 | CBM South 1 |  |  |  | LTF | [5 empty] | 0 | 0 | 0 | 0 |  |  |  |  | -0.0041
3 | CBM West 2 |  |  |  | LTF | [5 empty] | 605 | 0 | 0 | 0 |  |  |  |  | -0.0042
20 | MEC |  |  |  | LTF | [5 empty] | 158.9 | 0 | 0 | 0 |  |  |  |  | -0.0043
24 | SIGE |  |  |  | LTF | [5 empty] | 19.6 | 0 | 0 | 0 |  |  |  |  | -0.0043
10 | LGEE |  |  |  | LTF | [5 empty] | 59.5 | 0 | 0 | 0 |  |  |  |  | -0.0043
12 | WEC |  |  |  | LTF | [5 empty] | 32.9 | 0 | 0 | 0 |  |  |  |  | -0.0044
2 | CBM West 1 |  |  |  | LTF | [5 empty] | 1447 | 0 | 0 | 0 |  |  |  |  | -0.0045