## Light Load GenDeliv
| Note | APS and Dominion zones as a whole are quarantined pending Window 3 outcome and are not included in above results
Related to 2022 Window 3, pending window outcome
2028 RTEP PJM Generation Deliverability Result (Light Load)
FG # | Fr Bus | Name | To Bus | Name | CKT | KVs | Areas | Rating | FN DC Flow | FN AC Flow | FN DC % | FN AC % | Cont Label | Cont Type | Conductor/Transformer Rating (MVA) | PJM Accepting Proposals | Reason For Exclusion | Comments
2023W1-GD-LL905 | 235283 | 01WYCOFJ | 254064 | 15CHESWK | 1 | 138 | 201/215 | 248 | 251.1 | 249.7 | 101.26 | 100.67 | AP_P7-1_WP-138-AA2-161_1_SRT-A | Tower | APS side: 288/355/405 (SN/SE/SLD); DLCO side: 220/248/267 (SN/SE/SLD) | YES
2023W1-GD-LL550 | 235283 | 01WYCOFJ | 254064 | 15CHESWK | 1 | 138 | 201/215 | 248 | 251.1 | 249.7 | 101.26 | 100.67 | AP_P2-3_WP-138-AA2-161-B5_SRT-A | Breaker | APS side: 288/355/405 (SN/SE/SLD); DLCO side: 220/248/267 (SN/SE/SLD) | YES
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 607 | 1196.4 | 1187.4 | 197.11 | 195.61 | PECO_P1-2_5012_SRT-A | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 607 | 1203 | 1187.4 | 198.19 | 195.61 | PECO_P1-2_5012_SRT-A | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 607 | 1191.9 | 1175.9 | 196.36 | 193.72 | PECO_P4_PEACH235_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 607 | 1185.4 | 1175.9 | 195.28 | 193.72 | PECO_P4_PEACH235_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 607 | 1191.4 | 1175.4 | 196.27 | 193.65 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 607 | 1184.8 | 1175.4 | 195.2 | 193.65 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 607 | 1180.7 | 1173.2 | 194.52 | 193.28 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 607 | 1187.3 | 1173.2 | 195.6 | 193.28 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 628 | 1181.4 | 1173.7 | 188.12 | 186.89 | PECO_P1-2_5012_SRT-A | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 628 | 1170.3 | 1162.2 | 186.36 | 185.07 | PECO_P4_PEACH235_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 628 | 1169.8 | 1161.7 | 186.27 | 184.99 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 628 | 1165.7 | 1159.5 | 185.62 | 184.64 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 628 | 1164.4 | 1159.3 | 185.41 | 184.61 | PECO_P1-2_5012_SRT-A | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 628 | 1153.3 | 1147.8 | 183.65 | 182.78 | PECO_P4_PEACH235_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 628 | 1152.8 | 1147.4 | 183.57 | 182.7 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 628 | 1148.7 | 1145.2 | 182.91 | 182.35 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 607 | 1102.6 | 1090.2 | 181.65 | 179.6 | PECO_P4_PEACH245_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 607 | 1109.2 | 1090.2 | 182.73 | 179.6 | PECO_P4_PEACH245_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 235463 | 01TANEY | 1 | 138 | 227/201 | 268 | 487.5 | 477.2 | 181.88 | 178.05 | PJM_500_BG_P4_5_CNSTN_J_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 235463 | 01TANEY | 1 | 138 | 227/201 | 268 | 487.5 | 477.2 | 181.88 | 178.05 | PJM_500_BG_P1_5011_SRT-A | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 235463 | 01TANEY | 1 | 138 | 227/201 | 268 | 487.3 | 477 | 181.83 | 177.99 | PEPCO_P4_PP40_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 628 | 1087.6 | 1076.4 | 173.19 | 171.4 | PECO_P4_PEACH245_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 628 | 1070.6 | 1061.9 | 170.48 | 169.09 | PECO_P4_PEACH245_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 205912 | AD1-020 TAP | 204544 | 27LINCOLN | 1 | 115 | 227 | 282 | 456.8 | 456 | 161.97 | 161.71 | PJM_500_BG_P1_5011_SRT-A | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 205912 | AD1-020 TAP | 204544 | 27LINCOLN | 1 | 115 | 227 | 282 | 456.8 | 456 | 161.97 | 161.71 | PJM_500_BG_P4_5_CNSTN_J_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 205912 | AD1-020 TAP | 204544 | 27LINCOLN | 1 | 115 | 227 | 282 | 456.6 | 455.9 | 161.93 | 161.66 | PEPCO_P4_PP40_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 2293 | 2246.6 | 160.57 | 157.33 | DVP_P1-2: LN 514_SRT-A | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 2293 | 2246.6 | 160.57 | 157.33 | AP_P1-2_PE-500-407T_SRT-SL | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 204538 | 27STRABAN | 1 | 115 | 227 | 313 | 486.5 | 489.5 | 155.43 | 156.39 | PJM_500_BG_P4_5_CNSTN_J_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 204538 | 27STRABAN | 1 | 115 | 227 | 313 | 486.5 | 489.5 | 155.43 | 156.39 | PJM_500_BG_P1_5011_SRT-A | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 204538 | 27STRABAN | 1 | 115 | 227 | 313 | 486.3 | 489.3 | 155.38 | 156.33 | PEPCO_P4_PP40_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 2253.1 | 2208.6 | 157.78 | 154.66 | DVP_P4-2: 51482_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 797 | 1264.5 | 1225.1 | 158.66 | 153.71 | PECO_P1-2_5012_SRT-A | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204538 | 27STRABAN | 204529 | 27GERMANTN | 1 | 115 | 227 | 313 | 475.8 | 480.9 | 152.03 | 153.66 | PJM_500_BG_P4_5_CNSTN_J_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204538 | 27STRABAN | 204529 | 27GERMANTN | 1 | 115 | 227 | 313 | 475.8 | 480.9 | 152.03 | 153.66 | PJM_500_BG_P1_5011_SRT-A | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204538 | 27STRABAN | 204529 | 27GERMANTN | 1 | 115 | 227 | 313 | 475.7 | 480.8 | 151.98 | 153.6 | PEPCO_P4_PP40_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 797 | 1254.6 | 1215.5 | 157.41 | 152.51 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 797 | 1254.4 | 1215.4 | 157.39 | 152.49 | PECO_P4_PEACH235_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 203981 | AD2-062_POI | 235188 | 01GREENE | 1 | 138 | 226/201 | 268 | 419.5 | 407.8 | 156.54 | 152.18 | PJM_500_BG_P1_5011_SRT-A | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 203981 | AD2-062_POI | 235188 | 01GREENE | 1 | 138 | 226/201 | 268 | 419.5 | 407.8 | 156.54 | 152.18 | PJM_500_BG_P4_5_CNSTN_J_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 797 | 1249 | 1212.5 | 156.71 | 152.13 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 203981 | AD2-062_POI | 235188 | 01GREENE | 1 | 138 | 226/201 | 268 | 419.3 | 407.6 | 156.47 | 152.11 | PEPCO_P4_PP40_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204539 | 27HUNTRSTN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 282 | 428.5 | 427 | 151.95 | 151.43 | PJM_500_BG_P1_5011_SRT-A | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204539 | 27HUNTRSTN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 282 | 428.5 | 427 | 151.95 | 151.43 | PJM_500_BG_P4_5_CNSTN_J_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204539 | 27HUNTRSTN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 282 | 428.4 | 426.9 | 151.9 | 151.37 | PEPCO_P4_PP40_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 2177.1 | 2132.6 | 152.46 | 149.34 | AP_P2-3_PE-500-019C_SRT-SL | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 235463 | 01TANEY | 1 | 138 | 227/201 | 221 | 331.9 | 329.7 | 150.18 | 149.21 | Base Case | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 235463 | 01TANEY | 1 | 138 | 227/201 | 268 | 413.2 | 395 | 154.16 | 147.38 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 235463 | 01TANEY | 1 | 138 | 227/201 | 268 | 412.7 | 394.7 | 153.99 | 147.29 | PECO_P1-2_5012_SRT-A | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 235463 | 01TANEY | 1 | 138 | 227/201 | 268 | 412.7 | 394.7 | 153.99 | 147.29 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 235463 | 01TANEY | 1 | 138 | 227/201 | 268 | 412.7 | 394.7 | 153.98 | 147.28 | PECO_P4_PEACH235_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200004 | CNASTONE | 1 | 500 | 225 | 3369 | 5137.9 | 4961.5 | 152.5 | 147.27 | Base Case | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223938 | DICKH230 | 223937 | DICK 230 | 1 | 230 | 233 | 680 | 1018 | 998.3 | 149.71 | 146.81 | PEPCO_P4_PP19_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204550 | 27ORRTANNA | 204544 | 27LINCOLN | 1 | 115 | 227 | 160 | 235.9 | 233.7 | 147.43 | 146.05 | ME_P1-2_ME-115-068_SRT-A | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 814 | 1227 | 1184.6 | 150.74 | 145.53 | PECO_P1-2_5012_SRT-A | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204550 | 27ORRTANNA | 204544 | 27LINCOLN | 1 | 115 | 227 | 160 | 233.4 | 231.2 | 145.88 | 144.47 | ME_P2-3_ME-115-013B_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204550 | 27ORRTANNA | 204544 | 27LINCOLN | 1 | 115 | 227 | 160 | 233.2 | 230.9 | 145.74 | 144.33 | ME_P2-3_ME-115-013A_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 797 | 1188.5 | 1150.3 | 149.12 | 144.32 | PECO_P4_PEACH245_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 814 | 1214.5 | 1172.7 | 149.2 | 144.06 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204529 | 27GERMANTN | 204530 | 27GERMANTN | 1 | 115/138 | 227 | 345 | 487.5 | 497 | 141.29 | 144.06 | PJM_500_BG_P1_5011_SRT-A | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204529 | 27GERMANTN | 204530 | 27GERMANTN | 1 | 115/138 | 227 | 345 | 487.5 | 497 | 141.29 | 144.06 | PJM_500_BG_P4_5_CNSTN_J_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 814 | 1214.3 | 1172.5 | 149.18 | 144.05 | PECO_P4_PEACH235_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204529 | 27GERMANTN | 204530 | 27GERMANTN | 1 | 115/138 | 227 | 345 | 487.3 | 496.8 | 141.25 | 144 | PEPCO_P4_PP40_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 203981 | AD2-062_POI | 235188 | 01GREENE | 1 | 138 | 226/201 | 268 | 403.6 | 384.8 | 150.58 | 143.59 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 203981 | AD2-062_POI | 235188 | 01GREENE | 1 | 138 | 226/201 | 268 | 403.1 | 384.5 | 150.4 | 143.49 | PECO_P1-2_5012_SRT-A | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 203981 | AD2-062_POI | 235188 | 01GREENE | 1 | 138 | 226/201 | 268 | 403.1 | 384.5 | 150.4 | 143.48 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 203981 | AD2-062_POI | 235188 | 01GREENE | 1 | 138 | 226/201 | 268 | 403 | 384.5 | 150.39 | 143.48 | PECO_P4_PEACH235_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 814 | 1202.1 | 1165.3 | 147.68 | 143.16 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204550 | 27ORRTANNA | 204544 | 27LINCOLN | 1 | 115 | 227 | 160 | 228.7 | 227.7 | 142.96 | 142.32 | ME_P2-3_ME-115-035A_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204550 | 27ORRTANNA | 204544 | 27LINCOLN | 1 | 115 | 227 | 160 | 226.3 | 225.2 | 141.41 | 140.75 | ME_P2-3_ME-115-035B_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200532 | 26ROXBURY | 203981 | AD2-062_POI | 1 | 138 | 226 | 268 | 386.5 | 374.2 | 144.21 | 139.62 | PJM_500_BG_P4_5_CNSTN_J_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200532 | 26ROXBURY | 203981 | AD2-062_POI | 1 | 138 | 226 | 268 | 386.5 | 374.2 | 144.21 | 139.62 | PJM_500_BG_P1_5011_SRT-A | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200532 | 26ROXBURY | 203981 | AD2-062_POI | 1 | 138 | 226 | 268 | 386.3 | 374 | 144.14 | 139.55 | PEPCO_P4_PP40_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 235463 | 01TANEY | 1 | 138 | 227/201 | 268 | 376.7 | 371.8 | 140.54 | 138.73 | PEPCO_P1_5055_SRT-A | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 235463 | 01TANEY | 1 | 138 | 227/201 | 268 | 376.7 | 371.8 | 140.54 | 138.73 | AP_P1-2_PE-500-406T_SRT-SL | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223938 | DICKH230 | 223937 | DICK 230 | 2 | 230 | 233 | 680 | 961.3 | 942.4 | 141.37 | 138.58 | PEPCO_P1_PP1_SRT-A | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223938 | DICKH230 | 223937 | DICK 230 | 1 | 230 | 233 | 680 | 961.3 | 942.4 | 141.37 | 138.58 | PEPCO_P1_PP2_SRT-A | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200065 | PCHBTM2S | 200064 | PCHBTM1S | Z1 | 500 | 225 | 3198 | 4608.6 | 4430.3 | 144.11 | 138.53 | PECO_P4_PEACH255_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200003 | BRIGHTON | 1 | 500 | 225 | 3099 | 4294 | 4268 | 138.56 | 137.72 | BG_P7_CNSTN_NWEST2_SRT-A | Tower |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 203981 | AD2-062_POI | 235188 | 01GREENE | 1 | 138 | 226/201 | 221 | 304.1 | 302.6 | 137.61 | 136.93 | Base Case | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200004 | CNASTONE | 1 | 500 | 225 | 3949 | 5588.5 | 5382.8 | 141.52 | 136.31 | PECO_P4_PEACH035_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200003 | BRIGHTON | 1 | 500 | 225 | 3099 | 4244.9 | 4220.5 | 136.98 | 136.19 | BG_P7_GRCTN_RAPHEL_SRT-A | Tower |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 235463 | 01TANEY | 1 | 138 | 227/201 | 268 | 367.3 | 364.5 | 137.07 | 136 | BG_P7_GRCTN_RAPHEL_SRT-A | Tower |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 235463 | 01TANEY | 1 | 138 | 227/201 | 268 | 367 | 364.2 | 136.95 | 135.89 | BG_P7_CNSTN_NWEST2_SRT-A | Tower |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 205912 | AD1-020 TAP | 204544 | 27LINCOLN | 1 | 115 | 227 | 232 | 318.6 | 314.3 | 137.34 | 135.46 | Base Case | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 814 | 1139.3 | 1099.2 | 139.97 | 135.03 | PECO_P4_PEACH245_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204550 | 27ORRTANNA | 204544 | 27LINCOLN | 1 | 115 | 227 | 160 | 219 | 215.8 | 136.89 | 134.89 | ME_P1-2_ME-115-067_SRT-A | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 235463 | 01TANEY | 1 | 138 | 227/201 | 268 | 363.3 | 360.9 | 135.57 | 134.65 | BG_P7_NEAST_RPHLRD_SRT-A | Tower |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200003 | BRIGHTON | 1 | 500 | 225 | 3099 | 4194.3 | 4170.8 | 135.34 | 134.59 | BG_P7_NEAST_RPHLRD_SRT-A | Tower |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 235463 | 01TANEY | 1 | 138 | 227/201 | 268 | 364 | 360.3 | 135.82 | 134.43 | AP_P1-2_WP-500-DRT21_SRT-SL | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 235463 | 01TANEY | 1 | 138 | 227/201 | 268 | 364 | 360.3 | 135.82 | 134.43 | AP_P2-2_WP-500-DRT16_SRT-SL | Bus |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 205912 | AD1-020 TAP | 204544 | 27LINCOLN | 1 | 115 | 227 | 282 | 390.8 | 378.5 | 138.59 | 134.21 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 205912 | AD1-020 TAP | 204544 | 27LINCOLN | 1 | 115 | 227 | 282 | 390.4 | 378.3 | 138.44 | 134.13 | PECO_P1-2_5012_SRT-A | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 205912 | AD1-020 TAP | 204544 | 27LINCOLN | 1 | 115 | 227 | 282 | 390.4 | 378.3 | 138.44 | 134.13 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 205912 | AD1-020 TAP | 204544 | 27LINCOLN | 1 | 115 | 227 | 282 | 390.4 | 378.2 | 138.43 | 134.13 | PECO_P4_PEACH235_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200004 | CNASTONE | 1 | 500 | 225 | 3949 | 5485.8 | 5295.5 | 138.92 | 134.1 | PECO_P4_PEACH675_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200004 | CNASTONE | 1 | 500 | 225 | 3949 | 5485.8 | 5295.5 | 138.92 | 134.1 | PECO_P7-1_220-0607_SRT-A | Tower |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200004 | CNASTONE | 1 | 500 | 225 | 3949 | 5454.3 | 5275.5 | 138.12 | 133.59 | PJM_500_BG_P4_5_CNSTN_M_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200004 | CNASTONE | 1 | 500 | 225 | 3949 | 5454.3 | 5275.3 | 138.12 | 133.58 | PJM_500_BG_P1_5013_SRT-A | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200004 | CNASTONE | 1 | 500 | 225 | 3949 | 5459.3 | 5269.8 | 138.24 | 133.45 | PECO_P4_NOTTI55_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200004 | CNASTONE | 1 | 500 | 225 | 3949 | 5454.7 | 5265.4 | 138.13 | 133.33 | PECO_P2-2_NOTT230B_SRT-A | Bus |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200004 | CNASTONE | 1 | 500 | 225 | 3949 | 5455.8 | 5264.5 | 138.16 | 133.31 | PECO_P4_NOTTI785_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200004 | CNASTONE | 1 | 500 | 225 | 3949 | 5444.3 | 5258 | 137.86 | 133.15 | PECO_P1-2_220-08_SRT-A | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200004 | CNASTONE | 1 | 500 | 225 | 3949 | 5433 | 5250.2 | 137.58 | 132.95 | PECO_P1-2_220-93_SRT-A | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200004 | CNASTONE | 1 | 500 | 225 | 3949 | 5279.4 | 5239.7 | 133.69 | 132.68 | AEP_P1-1_#4960_05MOUNTN 765_1_SRT-A | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200003 | BRIGHTON | 1 | 500 | 225 | 2812 | 3766.3 | 3723.3 | 133.94 | 132.41 | Base Case | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200004 | CNASTONE | 1 | 500 | 225 | 3949 | 5391.8 | 5198.9 | 136.54 | 131.65 | PECO_P1-2_220-07_SRT-A | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200004 | CNASTONE | 1 | 500 | 225 | 3949 | 5373.5 | 5195.3 | 136.07 | 131.56 | PL_05_P71_000906_SRT-A | Tower |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223938 | DICKH230 | 223937 | DICK 230 | 2 | 230 | 233 | 680 | 911.9 | 892 | 134.1 | 131.18 | DVP_P4-2: 51482_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223938 | DICKH230 | 223937 | DICK 230 | 1 | 230 | 233 | 680 | 911.9 | 892 | 134.1 | 131.18 | DVP_P4-2: 51482_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223938 | DICKH230 | 223937 | DICK 230 | 2 | 230 | 233 | 680 | 911.8 | 891.9 | 134.08 | 131.16 | AP_P1-2_PE-500-407T_SRT-SL | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223938 | DICKH230 | 223937 | DICK 230 | 1 | 230 | 233 | 680 | 911.8 | 891.9 | 134.08 | 131.16 | AP_P1-2_PE-500-407T_SRT-SL | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223938 | DICKH230 | 223937 | DICK 230 | 1 | 230 | 233 | 680 | 911.8 | 891.9 | 134.08 | 131.16 | DVP_P1-2: LN 514_SRT-A | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223938 | DICKH230 | 223937 | DICK 230 | 2 | 230 | 233 | 680 | 911.8 | 891.9 | 134.08 | 131.16 | DVP_P1-2: LN 514_SRT-A | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200532 | 26ROXBURY | 203981 | AD2-062_POI | 1 | 138 | 226 | 268 | 370.8 | 351.4 | 138.34 | 131.12 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200532 | 26ROXBURY | 203981 | AD2-062_POI | 1 | 138 | 226 | 268 | 370.3 | 351.1 | 138.15 | 131.01 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200532 | 26ROXBURY | 203981 | AD2-062_POI | 1 | 138 | 226 | 268 | 370.3 | 351.1 | 138.15 | 131.01 | PECO_P1-2_5012_SRT-A | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200532 | 26ROXBURY | 203981 | AD2-062_POI | 1 | 138 | 226 | 268 | 370.2 | 351.1 | 138.15 | 131.01 | PECO_P4_PEACH235_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200762 | 26GARRETT | 235470 | 01GARRET | 1 | 115 | 226/201 | 160 | 210.1 | 209.5 | 131.3 | 130.96 | PJM_500_BG_P1_5011_SRT-A | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200003 | BRIGHTON | 1 | 500 | 225 | 3099 | 4094.6 | 4057.8 | 132.13 | 130.94 | PJM_500_BG_P4_5_CNSTN_13_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200003 | BRIGHTON | 1 | 500 | 225 | 3099 | 4092.8 | 4056.2 | 132.07 | 130.89 | PJM_500_BG_P4_5_CNSTN_6_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 235463 | 01TANEY | 1 | 138 | 227/201 | 268 | 354 | 350.5 | 132.11 | 130.79 | AP_P2-2_WP-500-DRT17_SRT-SL | Bus |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 235463 | 01TANEY | 1 | 138 | 227/201 | 268 | 353.1 | 350.3 | 131.75 | 130.72 | BG_P7_GRNITE_HIRDG_SRT-A | Tower |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200004 | CNASTONE | 1 | 500 | 225 | 3949 | 5333 | 5159.8 | 135.05 | 130.66 | AP_P2-2_WP-500-DRT16_SRT-SL | Bus |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 814 | 1089.9 | 1062.6 | 133.89 | 130.54 | PECO_P1-2_5012_SRT-A | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 235463 | 01TANEY | 1 | 138 | 227/201 | 268 | 351.7 | 349.1 | 131.24 | 130.26 | AP_P2-2_WP-138-074_SRT-A | Bus |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200003 | BRIGHTON | 1 | 500 | 225 | 3099 | 4072.2 | 4035.1 | 131.4 | 130.21 | BG_P7_GRNITE_HIRDG_SRT-A | Tower |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200762 | 26GARRETT | 235470 | 01GARRET | 1 | 115 | 226/201 | 160 | 208.8 | 208.3 | 130.48 | 130.19 | PJM_500_BG_P4_5_CNSTN_J_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200762 | 26GARRETT | 235470 | 01GARRET | 1 | 115 | 226/201 | 160 | 208.7 | 208.2 | 130.42 | 130.11 | PEPCO_P4_PP40_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 221095 | ROCKRGE2 | 221098 | C.PIPE12 | 1 | 115 | 232 | 217 | 282.9 | 282.1 | 130.38 | 129.98 | BG_P7_GRCTN_RAPHEL_SRT-A | Tower |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200003 | BRIGHTON | 1 | 500 | 225 | 3099 | 4045.8 | 4015.1 | 130.55 | 129.56 | AP_P1-2_WP-500-005A_SRT-A | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200003 | BRIGHTON | 1 | 500 | 225 | 3099 | 4045.8 | 4015.1 | 130.55 | 129.56 | AP_P1-2_WP-500-DRT21_SRT-SL | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200003 | BRIGHTON | 1 | 500 | 225 | 3099 | 4045.8 | 4015 | 130.55 | 129.56 | AP_P2-2_WP-500-DRT16_SRT-SL | Bus |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200003 | BRIGHTON | 1 | 500 | 225 | 3099 | 4045.8 | 4015 | 130.55 | 129.56 | AP_P2-3_WP-500-465_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200003 | BRIGHTON | 1 | 500 | 225 | 3099 | 4045.8 | 4015 | 130.55 | 129.56 | AP_P2-3_WP-500-DRT20_SRT-SL | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200004 | CNASTONE | 1 | 500 | 225 | 3949 | 5294.9 | 5113.1 | 134.08 | 129.48 | PL_04_P71_001014_SRT-A | Tower |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200762 | 26GARRETT | 235470 | 01GARRET | 1 | 115 | 226/201 | 133 | 171.8 | 172.1 | 129.15 | 129.43 | Base Case | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204550 | 27ORRTANNA | 204544 | 27LINCOLN | 1 | 115 | 227 | 160 | 210.4 | 207.1 | 131.51 | 129.43 | ME_P2-3_ME-115-0102-A_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204550 | 27ORRTANNA | 204544 | 27LINCOLN | 1 | 115 | 227 | 160 | 210.4 | 207.1 | 131.51 | 129.43 | ME_P2-2_ME-115-0102-4_SRT-A | Bus |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200004 | CNASTONE | 1 | 500 | 225 | 3949 | 5288.9 | 5109.9 | 133.93 | 129.4 | PL_05_P22_000674_SRT-A | Bus |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 235463 | 01TANEY | 1 | 138 | 227/201 | 268 | 349.7 | 346.6 | 130.49 | 129.31 | AP_P2-2_WP-500-DRT15_SRT-SL | Bus |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 814 | 1078.3 | 1051.2 | 132.47 | 129.14 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 814 | 1078.1 | 1051.1 | 132.44 | 129.13 | PECO_P4_PEACH235_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 235463 | 01TANEY | 1 | 138 | 227/201 | 268 | 348.5 | 345.8 | 130.03 | 129.04 | BG_P7_NWEST_GRNITE_SRT-A | Tower |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200004 | CNASTONE | 1 | 500 | 225 | 3949 | 5268.4 | 5090.8 | 133.41 | 128.91 | AP_P2-2_WP-500-DRT17_SRT-SL | Bus |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208395 | FARO FF | 208393 | FARO DC TIE | 1 | 69/115 | 229 | 77 | 99 | 99.2 | 128.57 | 128.78 | Base Case | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208395 | FARO FF | 208393 | FARO DC TIE | 2 | 69/115 | 229 | 77 | 99 | 99.2 | 128.57 | 128.78 | Base Case | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 814 | 1072.7 | 1048.2 | 131.78 | 128.78 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200004 | CNASTONE | 1 | 500 | 225 | 3949 | 5255.4 | 5076 | 133.08 | 128.54 | DVP_P2-2: BREMO B1_SRT-L | Bus |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 204538 | 27STRABAN | 1 | 115 | 227 | 313 | 412.2 | 402 | 131.71 | 128.43 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200004 | CNASTONE | 1 | 500 | 225 | 3949 | 5248.6 | 5069.1 | 132.91 | 128.36 | PL_04_P71_000904_SRT-A | Tower |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 204538 | 27STRABAN | 1 | 115 | 227 | 313 | 411.8 | 401.7 | 131.56 | 128.35 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 204538 | 27STRABAN | 1 | 115 | 227 | 313 | 411.8 | 401.7 | 131.56 | 128.35 | PECO_P1-2_5012_SRT-A | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200004 | CNASTONE | 1 | 500 | 225 | 3949 | 5248.2 | 5068.7 | 132.9 | 128.35 | PL_04_P71_001822_SRT-A | Tower |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 204538 | 27STRABAN | 1 | 115 | 227 | 313 | 411.8 | 401.7 | 131.55 | 128.35 | PECO_P4_PEACH235_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 204538 | 27STRABAN | 1 | 115 | 227 | 257 | 331 | 329.7 | 128.78 | 128.28 | Base Case | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200003 | BRIGHTON | 1 | 500 | 225 | 3099 | 4010 | 3972.1 | 129.4 | 128.17 | BG_P7_NWEST_GRNITE_SRT-A | Tower |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200003 | BRIGHTON | 1 | 500 | 225 | 3099 | 3984.8 | 3944.3 | 128.58 | 127.28 | PN_P2-3_PN-500-004-DRT-009_SRT-SL | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200003 | BRIGHTON | 1 | 500 | 225 | 3099 | 3989.7 | 3941.9 | 128.74 | 127.2 | PN_P1-2_PN-500-007_SRT-A | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200003 | BRIGHTON | 1 | 500 | 225 | 3099 | 3977 | 3936.8 | 128.33 | 127.03 | PN_P1-2_PN-500-001_SRT-A | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 221098 | C.PIPE12 | 221090 | GLENARM2 | 1 | 115 | 232 | 217 | 274.3 | 275.4 | 126.41 | 126.91 | BG_P7_GRCTN_RAPHEL_SRT-A | Tower |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200762 | 26GARRETT | 235470 | 01GARRET | 1 | 115 | 226/201 | 160 | 203.8 | 202.5 | 127.4 | 126.58 | AP_P1-2_WP-500-DRT21_SRT-SL | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200762 | 26GARRETT | 235470 | 01GARRET | 1 | 115 | 226/201 | 160 | 203.8 | 202.5 | 127.4 | 126.58 | AP_P1-2_WP-500-005A_SRT-A | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200003 | BRIGHTON | 1 | 500 | 225 | 3099 | 3954.2 | 3922.7 | 127.59 | 126.58 | AP_P1-2_PE-500-001_SRT-SL | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200003 | BRIGHTON | 1 | 500 | 225 | 3099 | 3962.7 | 3922.3 | 127.87 | 126.57 | AP_P2-2_WP-500-DRT17_SRT-SL | Bus |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 235463 | 01TANEY | 1 | 138 | 227/201 | 268 | 340.9 | 338.7 | 127.2 | 126.37 | AP_P2-2_PE-138-072_SRT-A | Bus |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200065 | PCHBTM2S | 200064 | PCHBTM1S | Z2 | 500 | 225 | 3022 | 3970.6 | 3818.4 | 131.39 | 126.35 | PECO_P4_PEACH025_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200003 | BRIGHTON | 1 | 500 | 225 | 3099 | 3951.6 | 3910.9 | 127.51 | 126.2 | PJM_500_BG_P2_CNSTN_230-S_SRT-A | Bus |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200003 | BRIGHTON | 1 | 500 | 225 | 3099 | 3951.1 | 3910.4 | 127.49 | 126.18 | PJM_500_BG_P2_CNSTN_230-N_SRT-A | Bus |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 205912 | AD1-020 TAP | 204544 | 27LINCOLN | 1 | 115 | 227 | 282 | 359.9 | 355.4 | 127.61 | 126.03 | ME_P1-2_ME-115-061_SRT-A | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200762 | 26GARRETT | 235470 | 01GARRET | 1 | 115 | 226/201 | 160 | 202.5 | 201.3 | 126.58 | 125.81 | AP_P2-2_WP-500-DRT16_SRT-SL | Bus |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200762 | 26GARRETT | 235470 | 01GARRET | 1 | 115 | 226/201 | 160 | 202.5 | 201.3 | 126.58 | 125.81 | AP_P2-3_WP-500-465_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200762 | 26GARRETT | 235470 | 01GARRET | 1 | 115 | 226/201 | 160 | 202.5 | 201.3 | 126.58 | 125.81 | AP_P2-3_WP-500-DRT20_SRT-SL | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204538 | 27STRABAN | 204529 | 27GERMANTN | 1 | 115 | 227 | 313 | 401.6 | 393.5 | 128.31 | 125.73 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204538 | 27STRABAN | 204529 | 27GERMANTN | 1 | 115 | 227 | 313 | 401.2 | 393.3 | 128.16 | 125.65 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204538 | 27STRABAN | 204529 | 27GERMANTN | 1 | 115 | 227 | 313 | 401.2 | 393.3 | 128.16 | 125.65 | PECO_P1-2_5012_SRT-A | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204538 | 27STRABAN | 204529 | 27GERMANTN | 1 | 115 | 227 | 313 | 401.1 | 393.3 | 128.16 | 125.64 | PECO_P4_PEACH235_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200762 | 26GARRETT | 235470 | 01GARRET | 1 | 115 | 226/201 | 160 | 203.7 | 201 | 127.29 | 125.62 | PECO_P1-2_5012_SRT-A | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 205912 | AD1-020 TAP | 204544 | 27LINCOLN | 1 | 115 | 227 | 282 | 358.4 | 353.9 | 127.08 | 125.51 | PEPCO_P1_5055_SRT-A | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 205912 | AD1-020 TAP | 204544 | 27LINCOLN | 1 | 115 | 227 | 282 | 358.4 | 353.9 | 127.08 | 125.51 | AP_P1-2_PE-500-406T_SRT-SL | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200003 | BRIGHTON | 1 | 500 | 225 | 3099 | 3925.6 | 3886.2 | 126.67 | 125.4 | AP_P2-2_WP-500-DRT15_SRT-SL | Bus |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 203981 | AD2-062_POI | 235188 | 01GREENE | 1 | 138 | 226/201 | 268 | 340.4 | 335.7 | 127.02 | 125.26 | PEPCO_P1_5055_SRT-A | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 203981 | AD2-062_POI | 235188 | 01GREENE | 1 | 138 | 226/201 | 268 | 340.4 | 335.7 | 127.02 | 125.26 | AP_P1-2_PE-500-406T_SRT-SL | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 221096 | ROCKRGE1 | 221097 | C.PIPE11 | 1 | 115 | 232 | 217 | 272.3 | 271.4 | 125.48 | 125.08 | BG_P7_GRCTN_RAPHEL_SRT-A | Tower |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 221097 | C.PIPE11 | 221100 | GLENARM1 | 1 | 115 | 232 | 217 | 272 | 271.4 | 125.34 | 125.07 | BG_P7_GRCTN_RAPHEL_SRT-A | Tower |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204538 | 27STRABAN | 204529 | 27GERMANTN | 1 | 115 | 227 | 257 | 320.3 | 321.2 | 124.64 | 124.99 | Base Case | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200762 | 26GARRETT | 235470 | 01GARRET | 1 | 115 | 226/201 | 160 | 202.4 | 199.8 | 126.5 | 124.87 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 203981 | AD2-062_POI | 235188 | 01GREENE | 1 | 138 | 226/201 | 268 | 338.5 | 334.1 | 126.31 | 124.65 | AP_P2-2_WP-500-DRT16_SRT-SL | Bus |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 203981 | AD2-062_POI | 235188 | 01GREENE | 1 | 138 | 226/201 | 268 | 338.5 | 334.1 | 126.31 | 124.65 | AP_P1-2_WP-500-005A_SRT-A | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 221090 | GLENARM2 | 221089 | WINDYED1 | 1 | 115 | 232 | 216 | 266.9 | 268.1 | 123.59 | 124.11 | BG_P7_GRCTN_RAPHEL_SRT-A | Tower |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204539 | 27HUNTRSTN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 282 | 362.7 | 349.6 | 128.62 | 123.97 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204539 | 27HUNTRSTN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 282 | 362.3 | 349.4 | 128.47 | 123.89 | PECO_P1-2_5012_SRT-A | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204539 | 27HUNTRSTN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 282 | 362.3 | 349.4 | 128.47 | 123.89 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204539 | 27HUNTRSTN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 282 | 362.3 | 349.4 | 128.47 | 123.89 | PECO_P4_PEACH235_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 221095 | ROCKRGE2 | 221098 | C.PIPE12 | 1 | 115 | 232 | 217 | 268.1 | 268.8 | 123.55 | 123.87 | BG_P7_NEAST_RPHLRD_SRT-A | Tower |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 1808.3 | 1767.1 | 126.63 | 123.75 | PEPCO_P1_5070_SRT-A | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204539 | 27HUNTRSTN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 232 | 290.4 | 286.5 | 125.19 | 123.51 | Base Case | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200065 | PCHBTM2S | 200064 | PCHBTM1S | Z1 | 500 | 225 | 3198 | 4110.4 | 3949.7 | 128.53 | 123.51 | PECO_P4_PEACH045_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 203981 | AD2-062_POI | 235188 | 01GREENE | 1 | 138 | 226/201 | 268 | 335.2 | 330.8 | 125.06 | 123.42 | AP_P2-2_PE-138-073_SRT-A | Bus |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 203981 | AD2-062_POI | 235188 | 01GREENE | 1 | 138 | 226/201 | 268 | 335.2 | 330.8 | 125.06 | 123.42 | AP_P7-1_PE-138-022T_SRT-A | Tower |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 203981 | AD2-062_POI | 235188 | 01GREENE | 1 | 138 | 226/201 | 268 | 334.5 | 330.7 | 124.8 | 123.4 | AP_P2-2_PE-138-003_SRT-A | Bus |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 203981 | AD2-062_POI | 235188 | 01GREENE | 1 | 138 | 226/201 | 268 | 334.7 | 329.9 | 124.88 | 123.11 | ME_P2-2_ME-115-003_SRT-A | Bus |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 205912 | AD1-020 TAP | 204544 | 27LINCOLN | 1 | 115 | 227 | 282 | 350.1 | 347 | 124.14 | 123.05 | BG_P7_GRCTN_RAPHEL_SRT-A | Tower |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200762 | 26GARRETT | 235470 | 01GARRET | 1 | 115 | 226/201 | 160 | 198.2 | 196.8 | 123.86 | 123.01 | AP_P1-2_WP-500-008_SRT-A | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 205912 | AD1-020 TAP | 204544 | 27LINCOLN | 1 | 115 | 227 | 282 | 349.8 | 346.7 | 124.04 | 122.95 | BG_P7_CNSTN_NWEST2_SRT-A | Tower |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223938 | DICKH230 | 223937 | DICK 230 | 2 | 230 | 233 | 680 | 854.9 | 835.1 | 125.73 | 122.8 | AP_P2-3_PE-500-019C_SRT-SL | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223938 | DICKH230 | 223937 | DICK 230 | 1 | 230 | 233 | 680 | 854.9 | 835.1 | 125.73 | 122.8 | AP_P2-3_PE-500-019C_SRT-SL | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200065 | PCHBTM2S | 200064 | PCHBTM1S | Z2 | 500 | 225 | 3022 | 3850.9 | 3706.8 | 127.43 | 122.66 | PECO_P1-2_PBTIE1_SRT-A | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 205912 | AD1-020 TAP | 204544 | 27LINCOLN | 1 | 115 | 227 | 282 | 349.4 | 345 | 123.9 | 122.34 | ME_P2-2_ME-115-0102A-8_SRT-A | Bus |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200762 | 26GARRETT | 235470 | 01GARRET | 1 | 115 | 226/201 | 160 | 196.9 | 195.5 | 123.03 | 122.21 | AP_P2-2_WP-500-DRT17_SRT-SL | Bus |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204514 | 27TMI | 204502 | 27JACKSON | 1 | 230 | 227 | 659 | 804.4 | 804.1 | 122.06 | 122.02 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204514 | 27TMI | 204502 | 27JACKSON | 1 | 230 | 227 | 659 | 803.4 | 803.6 | 121.91 | 121.94 | PECO_P1-2_5012_SRT-A | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204514 | 27TMI | 204502 | 27JACKSON | 1 | 230 | 227 | 659 | 803.4 | 803.5 | 121.91 | 121.93 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204514 | 27TMI | 204502 | 27JACKSON | 1 | 230 | 227 | 659 | 803.3 | 803.4 | 121.89 | 121.92 | PECO_P4_PEACH235_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 205912 | AD1-020 TAP | 204544 | 27LINCOLN | 1 | 115 | 227 | 282 | 346.5 | 343.6 | 122.88 | 121.84 | BG_P7_NEAST_RPHLRD_SRT-A | Tower |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200532 | 26ROXBURY | 203981 | AD2-062_POI | 1 | 138 | 226 | 221 | 271.3 | 269.1 | 122.75 | 121.78 | Base Case | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 203981 | AD2-062_POI | 235188 | 01GREENE | 1 | 138 | 226/201 | 268 | 329 | 326.2 | 122.76 | 121.73 | BG_P7_GRCTN_RAPHEL_SRT-A | Tower |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 205912 | AD1-020 TAP | 204544 | 27LINCOLN | 1 | 115 | 227 | 282 | 347.1 | 343.2 | 123.1 | 121.7 | AP_P2-2_WP-500-DRT16_SRT-SL | Bus |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 1776.4 | 1737.3 | 124.4 | 121.66 | DVP_P4-2: 560T571_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 203981 | AD2-062_POI | 235188 | 01GREENE | 1 | 138 | 226/201 | 268 | 328.7 | 325.9 | 122.64 | 121.61 | BG_P7_CNSTN_NWEST2_SRT-A | Tower |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 1775.3 | 1736.5 | 124.32 | 121.6 | DVP_P4-2: H2T560_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 1775.2 | 1736.2 | 124.32 | 121.59 | DVP_P4-2: H1T560_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208395 | FARO FF | 208393 | FARO DC TIE | 1 | 69/115 | 229 | 114 | 142.2 | 138.5 | 124.75 | 121.53 | PL_05_P71_000906_SRT-A | Tower |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 221058 | DOLFD T1 | 221055 | HARRIS1A | 1 | 115 | 232 | 189 | 229.9 | 229.6 | 121.66 | 121.47 | BG_P7_NWEST_GRNITE_SRT-A | Tower |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 203981 | AD2-062_POI | 235188 | 01GREENE | 1 | 138 | 226/201 | 268 | 326.3 | 323.9 | 121.76 | 120.85 | BG_P7_NEAST_RPHLRD_SRT-A | Tower |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 814 | 1010.5 | 983.5 | 124.15 | 120.82 | PECO_P4_PEACH245_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 221098 | C.PIPE12 | 221090 | GLENARM2 | 1 | 115 | 232 | 217 | 259.5 | 262.2 | 119.58 | 120.81 | BG_P7_NEAST_RPHLRD_SRT-A | Tower |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 203981 | AD2-062_POI | 235188 | 01GREENE | 1 | 138 | 226/201 | 268 | 326.5 | 323 | 121.83 | 120.53 | AP_P2-2_WP-500-DRT17_SRT-SL | Bus |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 221092 | FIVE.FOR | 221096 | ROCKRGE1 | 1 | 115 | 232 | 254 | 303.5 | 304.5 | 119.47 | 119.87 | BG_P7_GRCTN_RAPHEL_SRT-A | Tower |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 204538 | 27STRABAN | 1 | 115 | 227 | 313 | 375.7 | 374.4 | 120.03 | 119.63 | AP_P1-2_PE-500-406T_SRT-SL | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 204538 | 27STRABAN | 1 | 115 | 227 | 313 | 375.7 | 374.4 | 120.03 | 119.63 | PEPCO_P1_5055_SRT-A | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208396 | FARO | 208395 | FARO FF | 1 | 69 | 229 | 240 | 284.5 | 286.6 | 118.53 | 119.43 | PL_05_P71_000906_SRT-A | Tower |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 221096 | ROCKRGE1 | 221097 | C.PIPE11 | 1 | 115 | 232 | 217 | 257.5 | 258.4 | 118.67 | 119.07 | BG_P7_NEAST_RPHLRD_SRT-A | Tower |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 221097 | C.PIPE11 | 221100 | GLENARM1 | 1 | 115 | 232 | 217 | 257.2 | 258.3 | 118.53 | 119.05 | BG_P7_NEAST_RPHLRD_SRT-A | Tower |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 797 | 958.3 | 946.5 | 120.24 | 118.75 | PJM_500_BG_P4_5_CNSTN_15_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204529 | 27GERMANTN | 204530 | 27GERMANTN | 1 | 115/138 | 227 | 345 | 413.2 | 408.9 | 119.76 | 118.52 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204529 | 27GERMANTN | 204530 | 27GERMANTN | 1 | 115/138 | 227 | 345 | 412.7 | 408.6 | 119.62 | 118.45 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204529 | 27GERMANTN | 204530 | 27GERMANTN | 1 | 115/138 | 227 | 345 | 412.7 | 408.6 | 119.62 | 118.45 | PECO_P1-2_5012_SRT-A | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204529 | 27GERMANTN | 204530 | 27GERMANTN | 1 | 115/138 | 227 | 345 | 412.7 | 408.6 | 119.62 | 118.44 | PECO_P4_PEACH235_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 205912 | AD1-020 TAP | 204544 | 27LINCOLN | 1 | 115 | 227 | 282 | 338.3 | 333.7 | 119.96 | 118.33 | AP_P2-2_WP-500-DRT17_SRT-SL | Bus |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 205912 | AD1-020 TAP | 204544 | 27LINCOLN | 1 | 115 | 227 | 282 | 337.4 | 333.6 | 119.65 | 118.28 | BG_P7_GRNITE_HIRDG_SRT-A | Tower |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 203981 | AD2-062_POI | 235188 | 01GREENE | 1 | 138 | 226/201 | 268 | 318.9 | 316.5 | 118.98 | 118.11 | BG_P7_GRNITE_HIRDG_SRT-A | Tower |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 221090 | GLENARM2 | 221089 | WINDYED1 | 1 | 115 | 232 | 216 | 252.1 | 254.9 | 116.72 | 117.99 | BG_P7_NEAST_RPHLRD_SRT-A | Tower |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 205912 | AD1-020 TAP | 204544 | 27LINCOLN | 1 | 115 | 227 | 282 | 336.2 | 332.3 | 119.22 | 117.84 | AP_P2-2_WP-138-074_SRT-A | Bus |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200762 | 26GARRETT | 235470 | 01GARRET | 1 | 115 | 226/201 | 160 | 188.8 | 188.1 | 117.97 | 117.58 | AP_P2-2_WP-500-DRT15_SRT-SL | Bus |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 221057 | DOLFD T0 | 221056 | HARRIS0A | 1 | 115 | 232 | 189 | 221.6 | 221.9 | 117.26 | 117.43 | BG_P7_NWEST_GRNITE_SRT-A | Tower |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 204538 | 27STRABAN | 1 | 115 | 227 | 313 | 366.4 | 366.6 | 117.06 | 117.14 | BG_P7_GRCTN_RAPHEL_SRT-A | Tower |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204529 | 27GERMANTN | 204530 | 27GERMANTN | 1 | 115/138 | 227 | 287 | 331.9 | 336.2 | 115.65 | 117.13 | Base Case | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 205912 | AD1-020 TAP | 204544 | 27LINCOLN | 1 | 115 | 227 | 282 | 334.4 | 330 | 118.6 | 117.03 | AP_P2-2_WP-500-DRT15_SRT-SL | Bus |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 204538 | 27STRABAN | 1 | 115 | 227 | 313 | 366.1 | 366.3 | 116.95 | 117.02 | BG_P7_CNSTN_NWEST2_SRT-A | Tower |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204538 | 27STRABAN | 204529 | 27GERMANTN | 1 | 115 | 227 | 313 | 365.1 | 366 | 116.64 | 116.92 | AP_P1-2_PE-500-406T_SRT-SL | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204538 | 27STRABAN | 204529 | 27GERMANTN | 1 | 115 | 227 | 313 | 365.1 | 366 | 116.64 | 116.92 | PEPCO_P1_5055_SRT-A | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 205912 | AD1-020 TAP | 204544 | 27LINCOLN | 1 | 115 | 227 | 282 | 333.3 | 329.4 | 118.2 | 116.79 | BG_P7_NWEST_GRNITE_SRT-A | Tower |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204539 | 27HUNTRSTN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 282 | 332.8 | 328.9 | 118.01 | 116.64 | ME_P1-2_ME-115-061_SRT-A | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 221092 | FIVE.FOR | 221095 | ROCKRGE2 | 1 | 115 | 232 | 254 | 295.8 | 295.5 | 116.45 | 116.35 | BG_P7_GRCTN_RAPHEL_SRT-A | Tower |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200065 | PCHBTM2S | 200064 | PCHBTM1S | Z1 | 500 | 225 | 3198 | 3850.9 | 3706.8 | 120.42 | 115.91 | PECO_P1-2_PBTIE2_SRT-A | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 204538 | 27STRABAN | 1 | 115 | 227 | 313 | 362.4 | 362.8 | 115.78 | 115.9 | BG_P7_NEAST_RPHLRD_SRT-A | Tower |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 204538 | 27STRABAN | 1 | 115 | 227 | 313 | 363.1 | 362.3 | 115.99 | 115.75 | AP_P2-2_WP-500-DRT16_SRT-SL | Bus |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 204538 | 27STRABAN | 1 | 115 | 227 | 313 | 363.1 | 362.3 | 115.99 | 115.75 | AP_P1-2_WP-500-005A_SRT-A | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204539 | 27HUNTRSTN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 282 | 330.1 | 325.9 | 117.07 | 115.55 | AP_P1-2_PE-500-406T_SRT-SL | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204539 | 27HUNTRSTN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 282 | 330.1 | 325.9 | 117.07 | 115.55 | PEPCO_P1_5055_SRT-A | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208078 | SAKR | 208030 | MLWD TR1 | 1 | 230 | 229 | 801 | 923.2 | 925.4 | 115.25 | 115.53 | PECO_P1-2_5012_SRT-A | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208395 | FARO FF | 208393 | FARO DC TIE | 2 | 69/115 | 229 | 120 | 142.2 | 138.5 | 118.52 | 115.45 | PL_05_P71_000906_SRT-A | Tower |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 235105 | 01DOUBS | 1 | 500 | 225/201 | 2598 | 3074.4 | 2991.8 | 118.34 | 115.16 | DVP_P4-2: 560T571_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 235105 | 01DOUBS | 1 | 500 | 225/201 | 2598 | 3071.7 | 2989.2 | 118.23 | 115.06 | PEPCO_P1_5070_SRT-A | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 235105 | 01DOUBS | 1 | 500 | 225/201 | 2598 | 3071.5 | 2988.9 | 118.22 | 115.05 | DVP_P4-2: H1T560_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 235105 | 01DOUBS | 1 | 500 | 225/201 | 2598 | 3071.4 | 2988.9 | 118.22 | 115.05 | DVP_P4-2: H2T560_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220972 | GRANITE1 | 220953 | HOWARD12 | 1 | 230 | 232 | 772 | 909.6 | 886.6 | 117.83 | 114.84 | PJM_500_BG_P1_5011_SRT-A | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208020 | MANO TR3 | 208019 | MANO | 1 | 230 | 229 | 731 | 824.8 | 839.5 | 112.83 | 114.84 | PECO_P1-2_5012_SRT-A | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 801 | 938.8 | 918.6 | 117.21 | 114.68 | PECO_P1-2_5012_SRT-A | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220972 | GRANITE1 | 220953 | HOWARD12 | 1 | 230 | 232 | 772 | 906.9 | 884.6 | 117.47 | 114.58 | PEPCO_P4_PP40_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 221092 | FIVE.FOR | 221096 | ROCKRGE1 | 1 | 115 | 232 | 254 | 288.7 | 290.8 | 113.66 | 114.51 | BG_P7_NEAST_RPHLRD_SRT-A | Tower |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204538 | 27STRABAN | 204529 | 27GERMANTN | 1 | 115 | 227 | 313 | 355.8 | 358.2 | 113.66 | 114.43 | BG_P7_GRCTN_RAPHEL_SRT-A | Tower |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200762 | 26GARRETT | 235470 | 01GARRET | 1 | 115 | 226/201 | 160 | 182.7 | 183 | 114.21 | 114.36 | AP_P2-2_MP-138-001_SRT-A | Bus |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204538 | 27STRABAN | 204529 | 27GERMANTN | 1 | 115 | 227 | 313 | 355.4 | 357.8 | 113.56 | 114.32 | BG_P7_CNSTN_NWEST2_SRT-A | Tower |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220972 | GRANITE1 | 220953 | HOWARD12 | 1 | 230 | 232 | 772 | 904.7 | 882 | 117.19 | 114.26 | PJM_500_BG_P4_5_CNSTN_J_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 801 | 935.4 | 915 | 116.78 | 114.23 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 801 | 935.2 | 914.8 | 116.75 | 114.21 | PECO_P4_PEACH235_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208394 | PPL-BGE TIE | 221092 | FIVE.FOR | 1 | 115 | 229/232 | 247 | 280.2 | 281.9 | 113.42 | 114.13 | PL_05_P71_000906_SRT-A | Tower |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208020 | MANO TR3 | 208019 | MANO | 1 | 230 | 229 | 731 | 820.1 | 834.2 | 112.19 | 114.12 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208020 | MANO TR3 | 208019 | MANO | 1 | 230 | 229 | 731 | 820 | 834.2 | 112.18 | 114.11 | PECO_P4_PEACH235_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204528 | 27GARDNERS | 200504 | 26CARLISLE | 1 | 115 | 226/227 | 160 | 181.6 | 182.5 | 113.48 | 114.09 | PN_P2-3_PN-115-0331-B_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208078 | SAKR | 208030 | MLWD TR1 | 1 | 230 | 229 | 801 | 911.8 | 913 | 113.83 | 113.98 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208078 | SAKR | 208030 | MLWD TR1 | 1 | 230 | 229 | 801 | 911.7 | 912.9 | 113.82 | 113.97 | PECO_P4_PEACH235_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 797 | 918.8 | 907.7 | 115.28 | 113.89 | BG_P7_GRCTN_CNSTN_SRT-A | Tower |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200762 | 26GARRETT | 235470 | 01GARRET | 1 | 115 | 226/201 | 160 | 182 | 182.1 | 113.75 | 113.82 | AP_P2-2_WP-138-043_SRT-A | Bus |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208020 | MANO TR3 | 208019 | MANO | 1 | 230 | 229 | 731 | 815.8 | 832 | 111.61 | 113.81 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208078 | SAKR | 208030 | MLWD TR1 | 1 | 230 | 229 | 801 | 907.5 | 910.7 | 113.3 | 113.7 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 801 | 926.4 | 910.1 | 115.65 | 113.62 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204528 | 27GARDNERS | 200504 | 26CARLISLE | 1 | 115 | 226/227 | 160 | 180.8 | 181.7 | 112.98 | 113.57 | PN_P1-2_PN-115-094_A_SRT-A | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204538 | 27STRABAN | 204529 | 27GERMANTN | 1 | 115 | 227 | 313 | 351.7 | 354.3 | 112.38 | 113.19 | BG_P7_NEAST_RPHLRD_SRT-A | Tower |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204539 | 27HUNTRSTN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 282 | 321.9 | 319.1 | 114.15 | 113.14 | BG_P7_GRCTN_RAPHEL_SRT-A | Tower |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200065 | PCHBTM2S | 200064 | PCHBTM1S | Z1 | 500 | 225 | 3198 | 3758 | 3617.8 | 117.51 | 113.13 | PECO_P4_PEACH055_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204514 | 27TMI | 204502 | 27JACKSON | 1 | 230 | 227 | 659 | 747.3 | 745.3 | 113.4 | 113.09 | PECO_P4_PEACH245_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204538 | 27STRABAN | 204529 | 27GERMANTN | 1 | 115 | 227 | 313 | 352.4 | 353.8 | 112.59 | 113.04 | AP_P1-2_WP-500-005A_SRT-A | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204538 | 27STRABAN | 204529 | 27GERMANTN | 1 | 115 | 227 | 313 | 352.4 | 353.8 | 112.59 | 113.04 | AP_P2-2_WP-500-DRT16_SRT-SL | Bus |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220972 | GRANITE1 | 1 | 230 | 232 | 811 | 940.4 | 916.7 | 115.96 | 113.04 | PEPCO_P4_PP40_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204539 | 27HUNTRSTN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 282 | 321.6 | 318.7 | 114.04 | 113.03 | BG_P7_CNSTN_NWEST2_SRT-A | Tower |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200762 | 26GARRETT | 235470 | 01GARRET | 1 | 115 | 226/201 | 160 | 180.2 | 180.6 | 112.66 | 112.85 | AP_P7-1_MP-138-056_SRT-A | Tower |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220972 | GRANITE1 | 1 | 230 | 232 | 811 | 939 | 915 | 115.78 | 112.83 | PJM_500_BG_P1_5011_SRT-A | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220972 | GRANITE1 | 1 | 230 | 232 | 811 | 938.8 | 914.9 | 115.76 | 112.81 | PJM_500_BG_P4_5_CNSTN_J_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200532 | 26ROXBURY | 203981 | AD2-062_POI | 1 | 138 | 226 | 268 | 307.6 | 302.2 | 114.77 | 112.78 | PEPCO_P1_5055_SRT-A | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200532 | 26ROXBURY | 203981 | AD2-062_POI | 1 | 138 | 226 | 268 | 307.6 | 302.2 | 114.77 | 112.78 | AP_P1-2_PE-500-406T_SRT-SL | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200520 | 26ROXBURY | 200532 | 26ROXBURY | 2 | 115/138 | 226 | 349 | 386.5 | 393.3 | 110.74 | 112.69 | PJM_500_BG_P1_5011_SRT-A | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200520 | 26ROXBURY | 200532 | 26ROXBURY | 2 | 115/138 | 226 | 349 | 386.5 | 393.3 | 110.74 | 112.69 | PJM_500_BG_P4_5_CNSTN_J_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200520 | 26ROXBURY | 200532 | 26ROXBURY | 2 | 115/138 | 226 | 349 | 386.3 | 393 | 110.68 | 112.62 | PEPCO_P4_PP40_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200762 | 26GARRETT | 235470 | 01GARRET | 1 | 115 | 226/201 | 160 | 179.4 | 179.7 | 112.11 | 112.34 | BG_P7_CNSTN_NWEST2_SRT-A | Tower |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 204538 | 27STRABAN | 1 | 115 | 227 | 313 | 353.1 | 351.6 | 112.81 | 112.33 | AP_P2-2_WP-500-DRT17_SRT-SL | Bus |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 204538 | 27STRABAN | 1 | 115 | 227 | 313 | 352.1 | 351.5 | 112.5 | 112.28 | BG_P7_GRNITE_HIRDG_SRT-A | Tower |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200762 | 26GARRETT | 235470 | 01GARRET | 1 | 115 | 226/201 | 160 | 179.3 | 179.6 | 112.05 | 112.27 | BG_P7_GRCTN_RAPHEL_SRT-A | Tower |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200532 | 26ROXBURY | 203981 | AD2-062_POI | 1 | 138 | 226 | 268 | 305.7 | 300.6 | 114.05 | 112.16 | AP_P1-2_WP-500-005A_SRT-A | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200532 | 26ROXBURY | 203981 | AD2-062_POI | 1 | 138 | 226 | 268 | 305.7 | 300.6 | 114.05 | 112.16 | AP_P2-2_WP-500-DRT16_SRT-SL | Bus |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208395 | FARO FF | 208393 | FARO DC TIE | 1 | 69/115 | 229 | 114 | 132.2 | 127.7 | 115.99 | 112.02 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208395 | FARO FF | 208393 | FARO DC TIE | 1 | 69/115 | 229 | 114 | 132.2 | 127.7 | 115.99 | 112.02 | PECO_P1-2_5012_SRT-A | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208395 | FARO FF | 208393 | FARO DC TIE | 1 | 69/115 | 229 | 114 | 132.2 | 127.7 | 115.98 | 112.02 | PECO_P4_PEACH235_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208395 | FARO FF | 208393 | FARO DC TIE | 1 | 69/115 | 229 | 114 | 132.2 | 127.7 | 115.95 | 112.01 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204539 | 27HUNTRSTN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 282 | 318.3 | 315.6 | 112.88 | 111.92 | BG_P7_NEAST_RPHLRD_SRT-A | Tower |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200762 | 26GARRETT | 235470 | 01GARRET | 1 | 115 | 226/201 | 160 | 178.5 | 178.9 | 111.57 | 111.84 | BG_P7_NEAST_RPHLRD_SRT-A | Tower |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 204538 | 27STRABAN | 1 | 115 | 227 | 313 | 350.8 | 350 | 112.06 | 111.83 | AP_P2-2_WP-138-074_SRT-A | Bus |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204539 | 27HUNTRSTN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 282 | 319.3 | 315.3 | 113.24 | 111.81 | ME_P2-2_ME-115-0102A-8_SRT-A | Bus |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204539 | 27HUNTRSTN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 282 | 318.9 | 315.1 | 113.09 | 111.75 | AP_P2-2_WP-500-DRT16_SRT-SL | Bus |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220973 | GRANITE6 | 220954 | HOWARD32 | 1 | 230 | 232 | 772 | 881.6 | 861.7 | 114.2 | 111.62 | PEPCO_P4_PP40_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204528 | 27GARDNERS | 200504 | 26CARLISLE | 1 | 115 | 226/227 | 160 | 177.7 | 178.5 | 111.04 | 111.55 | PJM_500_BG_P1_5011_SRT-A | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220973 | GRANITE6 | 220954 | HOWARD32 | 1 | 230 | 232 | 772 | 881.4 | 861 | 114.17 | 111.53 | PJM_500_BG_P1_5011_SRT-A | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204528 | 27GARDNERS | 200504 | 26CARLISLE | 1 | 115 | 226/227 | 160 | 177.5 | 178.3 | 110.97 | 111.46 | PJM_500_BG_P4_5_CNSTN_J_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204528 | 27GARDNERS | 200504 | 26CARLISLE | 1 | 115 | 226/227 | 160 | 177.4 | 178.2 | 110.88 | 111.36 | PEPCO_P4_PP40_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220973 | GRANITE6 | 220954 | HOWARD32 | 1 | 230 | 232 | 772 | 879.8 | 859.6 | 113.96 | 111.35 | PJM_500_BG_P4_5_CNSTN_J_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200762 | 26GARRETT | 235470 | 01GARRET | 1 | 115 | 226/201 | 160 | 177.8 | 178.1 | 111.14 | 111.3 | AP_P7-1_WPP-138-011_SRT-A | Tower |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220973 | GRANITE6 | 1 | 230 | 232 | 811 | 924.2 | 901.1 | 113.95 | 111.11 | PEPCO_P4_PP40_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 221092 | FIVE.FOR | 221095 | ROCKRGE2 | 1 | 115 | 232 | 254 | 281 | 282.2 | 110.62 | 111.11 | BG_P7_NEAST_RPHLRD_SRT-A | Tower |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 204538 | 27STRABAN | 1 | 115 | 227 | 313 | 348.8 | 347.4 | 111.43 | 111.01 | AP_P2-2_WP-500-DRT15_SRT-SL | Bus |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200532 | 26ROXBURY | 203981 | AD2-062_POI | 1 | 138 | 226 | 268 | 302.3 | 297.3 | 112.81 | 110.93 | AP_P2-2_PE-138-073_SRT-A | Bus |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200532 | 26ROXBURY | 203981 | AD2-062_POI | 1 | 138 | 226 | 268 | 302.3 | 297.3 | 112.81 | 110.93 | AP_P7-1_PE-138-022T_SRT-A | Tower |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220973 | GRANITE6 | 1 | 230 | 232 | 811 | 922.8 | 899.6 | 113.79 | 110.92 | PJM_500_BG_P1_5011_SRT-A | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200532 | 26ROXBURY | 203981 | AD2-062_POI | 1 | 138 | 226 | 268 | 301.6 | 297.2 | 112.55 | 110.91 | AP_P2-2_PE-138-003_SRT-A | Bus |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220973 | GRANITE6 | 1 | 230 | 232 | 811 | 922.7 | 899.4 | 113.77 | 110.9 | PJM_500_BG_P4_5_CNSTN_J_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 204538 | 27STRABAN | 1 | 115 | 227 | 313 | 347.5 | 346.7 | 111.03 | 110.77 | BG_P7_NWEST_GRNITE_SRT-A | Tower |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200532 | 26ROXBURY | 203981 | AD2-062_POI | 1 | 138 | 226 | 268 | 301.8 | 296.5 | 112.63 | 110.62 | ME_P2-2_ME-115-003_SRT-A | Bus |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204529 | 27GERMANTN | 204530 | 27GERMANTN | 1 | 115/138 | 227 | 345 | 376.7 | 381.3 | 109.18 | 110.51 | PEPCO_P1_5055_SRT-A | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204529 | 27GERMANTN | 204530 | 27GERMANTN | 1 | 115/138 | 227 | 345 | 376.7 | 381.3 | 109.18 | 110.51 | AP_P1-2_PE-500-406T_SRT-SL | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 607 | 678.1 | 669.9 | 111.72 | 110.36 | PECO_P1-2_5014_SRT-A | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 607 | 684.7 | 669.9 | 112.8 | 110.36 | PECO_P1-2_5014_SRT-A | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204539 | 27HUNTRSTN | 204550 | 27ORRTANNA | 1 | 115 | 227 | 223 | 248.1 | 245.6 | 111.24 | 110.14 | ME_P1-2_ME-115-068_SRT-A | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208396 | FARO | 208395 | FARO FF | 1 | 69 | 229 | 240 | 264.7 | 264.1 | 110.3 | 110.03 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208396 | FARO | 208395 | FARO FF | 1 | 69 | 229 | 240 | 264.7 | 264.1 | 110.3 | 110.03 | PECO_P1-2_5012_SRT-A | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208396 | FARO | 208395 | FARO FF | 1 | 69 | 229 | 240 | 264.7 | 264.1 | 110.29 | 110.02 | PECO_P4_PEACH235_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208396 | FARO | 208395 | FARO FF | 1 | 69 | 229 | 240 | 264.6 | 264 | 110.26 | 110.01 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 607 | 682 | 667.4 | 112.36 | 109.96 | PECO_P4_PEACH205_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 607 | 675.5 | 667.4 | 111.28 | 109.96 | PECO_P4_PEACH205_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204538 | 27STRABAN | 204529 | 27GERMANTN | 1 | 115 | 227 | 313 | 342.4 | 343.1 | 109.41 | 109.62 | AP_P2-2_WP-500-DRT17_SRT-SL | Bus |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204538 | 27STRABAN | 204529 | 27GERMANTN | 1 | 115 | 227 | 313 | 341.5 | 343 | 109.1 | 109.58 | BG_P7_GRNITE_HIRDG_SRT-A | Tower |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200532 | 26ROXBURY | 203981 | AD2-062_POI | 1 | 138 | 226 | 268 | 296.1 | 292.8 | 110.5 | 109.24 | BG_P7_GRCTN_RAPHEL_SRT-A | Tower |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204538 | 27STRABAN | 204529 | 27GERMANTN | 1 | 115 | 227 | 313 | 340.1 | 341.6 | 108.67 | 109.13 | AP_P2-2_WP-138-074_SRT-A | Bus |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200532 | 26ROXBURY | 203981 | AD2-062_POI | 1 | 138 | 226 | 268 | 295.8 | 292.4 | 110.38 | 109.12 | BG_P7_CNSTN_NWEST2_SRT-A | Tower |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204539 | 27HUNTRSTN | 204550 | 27ORRTANNA | 1 | 115 | 227 | 223 | 245.6 | 243.1 | 110.13 | 109 | ME_P2-3_ME-115-013B_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204539 | 27HUNTRSTN | 204550 | 27ORRTANNA | 1 | 115 | 227 | 223 | 245.4 | 242.8 | 110.03 | 108.9 | ME_P2-3_ME-115-013A_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200747 | 26PENN-MAR | 200762 | 26GARRETT | 1 | 115 | 226 | 179 | 195.2 | 194.8 | 109.04 | 108.82 | PJM_500_BG_P1_5011_SRT-A | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200065 | PCHBTM2S | 200066 | PCHBTM1N | 2 | 500 | 225 | 3022 | 3390.8 | 3276.7 | 112.21 | 108.43 | PECO_P4_PEACH235_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204539 | 27HUNTRSTN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 282 | 310 | 305.8 | 109.95 | 108.42 | AP_P2-2_WP-500-DRT17_SRT-SL | Bus |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204539 | 27HUNTRSTN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 282 | 309.2 | 305.7 | 109.65 | 108.4 | BG_P7_GRNITE_HIRDG_SRT-A | Tower |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200532 | 26ROXBURY | 203981 | AD2-062_POI | 1 | 138 | 226 | 268 | 293.5 | 290.4 | 109.5 | 108.36 | BG_P7_NEAST_RPHLRD_SRT-A | Tower |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 204538 | 27STRABAN | 1 | 115 | 227 | 313 | 340.4 | 339.1 | 108.77 | 108.33 | DVP_P2-2: BREMO B1_SRT-L | Bus |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204538 | 27STRABAN | 204529 | 27GERMANTN | 1 | 115 | 227 | 313 | 338.1 | 339 | 108.03 | 108.3 | AP_P2-2_WP-500-DRT15_SRT-SL | Bus |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208395 | FARO FF | 208393 | FARO DC TIE | 1 | 69/115 | 229 | 114 | 127.2 | 123.4 | 111.6 | 108.28 | PECO_P4_PEACH245_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204529 | 27GERMANTN | 204530 | 27GERMANTN | 1 | 115/138 | 227 | 345 | 367.3 | 373.4 | 106.48 | 108.24 | BG_P7_GRCTN_RAPHEL_SRT-A | Tower |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204528 | 27GARDNERS | 200504 | 26CARLISLE | 1 | 115 | 226/227 | 160 | 172.9 | 173.1 | 108.09 | 108.2 | PN_P2-3_PN-115-58B_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204528 | 27GARDNERS | 200504 | 26CARLISLE | 1 | 115 | 226/227 | 160 | 173.2 | 173.1 | 108.24 | 108.18 | PN_P1-3_PN-115-040_SRT-A | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204528 | 27GARDNERS | 200504 | 26CARLISLE | 1 | 115 | 226/227 | 160 | 173.2 | 173.1 | 108.24 | 108.18 | PN_P2-2_PN-115-030_SRT-A | Bus |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204528 | 27GARDNERS | 200504 | 26CARLISLE | 1 | 115 | 226/227 | 160 | 172.8 | 173.1 | 108.01 | 108.17 | PN_P1-2_PN-115-094_SRT-A | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200747 | 26PENN-MAR | 200762 | 26GARRETT | 1 | 115 | 226 | 179 | 193.9 | 193.6 | 108.31 | 108.15 | PJM_500_BG_P4_5_CNSTN_J_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204529 | 27GERMANTN | 204530 | 27GERMANTN | 1 | 115/138 | 227 | 345 | 367 | 373.1 | 106.38 | 108.14 | BG_P7_CNSTN_NWEST2_SRT-A | Tower |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200747 | 26PENN-MAR | 200762 | 26GARRETT | 1 | 115 | 226 | 179 | 193.8 | 193.5 | 108.25 | 108.08 | PEPCO_P4_PP40_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204538 | 27STRABAN | 204529 | 27GERMANTN | 1 | 115 | 227 | 313 | 336.9 | 338.2 | 107.63 | 108.06 | BG_P7_NWEST_GRNITE_SRT-A | Tower |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200532 | 26ROXBURY | 203981 | AD2-062_POI | 1 | 138 | 226 | 268 | 293.6 | 289.5 | 109.57 | 108.03 | AP_P2-2_WP-500-DRT17_SRT-SL | Bus |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204539 | 27HUNTRSTN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 282 | 308 | 304.4 | 109.22 | 107.95 | AP_P2-2_WP-138-074_SRT-A | Bus |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208031 | MLWD TR2 | 1 | 230 | 229 | 814 | 870.3 | 878.3 | 106.91 | 107.9 | PECO_P1-2_5012_SRT-A | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 1565.2 | 1535.8 | 109.61 | 107.55 | AP_P1-2_PE-500-406T_SRT-SL | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 1565.2 | 1535.8 | 109.61 | 107.55 | PEPCO_P1_5055_SRT-A | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204539 | 27HUNTRSTN | 204550 | 27ORRTANNA | 1 | 115 | 227 | 223 | 240.9 | 239.6 | 108.04 | 107.46 | ME_P2-3_ME-115-035A_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204539 | 27HUNTRSTN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 282 | 306.2 | 302.1 | 108.59 | 107.14 | AP_P2-2_WP-500-DRT15_SRT-SL | Bus |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204529 | 27GERMANTN | 204530 | 27GERMANTN | 1 | 115/138 | 227 | 345 | 363.3 | 369.5 | 105.31 | 107.11 | BG_P7_NEAST_RPHLRD_SRT-A | Tower |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204529 | 27GERMANTN | 204530 | 27GERMANTN | 1 | 115/138 | 227 | 345 | 364 | 369.1 | 105.51 | 106.98 | AP_P2-2_WP-500-DRT16_SRT-SL | Bus |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204529 | 27GERMANTN | 204530 | 27GERMANTN | 1 | 115/138 | 227 | 345 | 364 | 369.1 | 105.51 | 106.97 | AP_P1-2_WP-500-005A_SRT-A | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204539 | 27HUNTRSTN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 282 | 305.1 | 301.5 | 108.2 | 106.92 | BG_P7_NWEST_GRNITE_SRT-A | Tower |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 221100 | GLENARM1 | 221088 | WINDYED2 | 1 | 115 | 232 | 254 | 271 | 271.2 | 106.69 | 106.78 | BG_P7_GRCTN_RAPHEL_SRT-A | Tower |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208031 | MLWD TR2 | 1 | 230 | 229 | 814 | 861.9 | 869.1 | 105.88 | 106.77 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208031 | MLWD TR2 | 1 | 230 | 229 | 814 | 861.8 | 869 | 105.88 | 106.76 | PECO_P4_PEACH235_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200065 | PCHBTM2S | 200064 | PCHBTM1S | Z2 | 500 | 225 | 3022 | 3350.6 | 3225.9 | 110.87 | 106.75 | PECO_P4_PEACH205_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200065 | PCHBTM2S | 200064 | PCHBTM1S | Z2 | 500 | 225 | 3022 | 3342.9 | 3224.1 | 110.62 | 106.69 | PECO_P4_PEACH015_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208395 | FARO FF | 208393 | FARO DC TIE | 1 | 69/115 | 229 | 114 | 123.3 | 121.5 | 108.15 | 106.54 | BG_P7_GRCTN_RAPHEL_SRT-A | Tower |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208031 | MLWD TR2 | 1 | 230 | 229 | 814 | 857.7 | 866.9 | 105.37 | 106.49 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208395 | FARO FF | 208393 | FARO DC TIE | 2 | 69/115 | 229 | 120 | 132.2 | 127.7 | 110.19 | 106.42 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208395 | FARO FF | 208393 | FARO DC TIE | 2 | 69/115 | 229 | 120 | 132.2 | 127.7 | 110.19 | 106.42 | PECO_P1-2_5012_SRT-A | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208395 | FARO FF | 208393 | FARO DC TIE | 2 | 69/115 | 229 | 120 | 132.2 | 127.7 | 110.18 | 106.42 | PECO_P4_PEACH235_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208395 | FARO FF | 208393 | FARO DC TIE | 2 | 69/115 | 229 | 120 | 132.2 | 127.7 | 110.16 | 106.41 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204539 | 27HUNTRSTN | 204550 | 27ORRTANNA | 1 | 115 | 227 | 223 | 238.5 | 237.1 | 106.93 | 106.33 | ME_P2-3_ME-115-035B_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 801 | 874.5 | 851.2 | 109.18 | 106.27 | PECO_P4_PEACH245_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 202650 | 26HIGHPOINT | 200747 | 26PENN-MAR | 1 | 115 | 226 | 179 | 191.4 | 190.2 | 106.93 | 106.27 | PJM_500_BG_P1_5011_SRT-A | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200747 | 26PENN-MAR | 200762 | 26GARRETT | 1 | 115 | 226 | 148 | 156.9 | 157.2 | 106 | 106.23 | Base Case | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208396 | FARO | 208395 | FARO FF | 1 | 69 | 229 | 240 | 254.7 | 254.6 | 106.12 | 106.1 | PECO_P4_PEACH245_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208020 | MANO TR3 | 208019 | MANO | 1 | 230 | 229 | 731 | 767.9 | 774 | 105.05 | 105.88 | PECO_P4_PEACH245_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200520 | 26ROXBURY | 200532 | 26ROXBURY | 2 | 115/138 | 226 | 349 | 370.8 | 369.4 | 106.23 | 105.84 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200520 | 26ROXBURY | 200532 | 26ROXBURY | 2 | 115/138 | 226 | 349 | 370.3 | 369.1 | 106.09 | 105.76 | PECO_P1-2_5012_SRT-A | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200520 | 26ROXBURY | 200532 | 26ROXBURY | 2 | 115/138 | 226 | 349 | 370.3 | 369.1 | 106.09 | 105.76 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200520 | 26ROXBURY | 200532 | 26ROXBURY | 2 | 115/138 | 226 | 349 | 370.2 | 369.1 | 106.08 | 105.76 | PECO_P4_PEACH235_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208078 | SAKR | 208030 | MLWD TR1 | 1 | 230 | 229 | 801 | 851.2 | 846.2 | 106.27 | 105.64 | PECO_P4_PEACH245_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204538 | 27STRABAN | 204529 | 27GERMANTN | 1 | 115 | 227 | 313 | 329.8 | 330.6 | 105.37 | 105.62 | DVP_P2-2: BREMO B1_SRT-L | Bus |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200532 | 26ROXBURY | 203981 | AD2-062_POI | 1 | 138 | 226 | 268 | 286 | 283 | 106.72 | 105.61 | BG_P7_GRNITE_HIRDG_SRT-A | Tower |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 202650 | 26HIGHPOINT | 200747 | 26PENN-MAR | 1 | 115 | 226 | 179 | 190.1 | 189 | 106.21 | 105.6 | PJM_500_BG_P4_5_CNSTN_J_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 202650 | 26HIGHPOINT | 200747 | 26PENN-MAR | 1 | 115 | 226 | 179 | 190 | 188.9 | 106.15 | 105.53 | PEPCO_P4_PP40_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208393 | FARO DC TIE | 208394 | PPL-BGE TIE | 1 | 115 | 229 | 268 | 283.9 | 282 | 105.92 | 105.23 | PL_05_P71_000906_SRT-A | Tower |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208394 | PPL-BGE TIE | 221092 | FIVE.FOR | 1 | 115 | 229/232 | 247 | 260.4 | 259.7 | 105.42 | 105.15 | PECO_P1-2_5012_SRT-A | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208394 | PPL-BGE TIE | 221092 | FIVE.FOR | 1 | 115 | 229/232 | 247 | 260.4 | 259.7 | 105.42 | 105.15 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208394 | PPL-BGE TIE | 221092 | FIVE.FOR | 1 | 115 | 229/232 | 247 | 260.4 | 259.7 | 105.42 | 105.14 | PECO_P4_PEACH235_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208394 | PPL-BGE TIE | 221092 | FIVE.FOR | 1 | 115 | 229/232 | 247 | 260.3 | 259.7 | 105.39 | 105.13 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 607 | 629.6 | 637.2 | 103.72 | 104.98 | PJM_500_BG_P1_5011_SRT-A | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 607 | 636.1 | 637.2 | 104.8 | 104.98 | PJM_500_BG_P1_5011_SRT-A | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200747 | 26PENN-MAR | 200762 | 26GARRETT | 1 | 115 | 226 | 179 | 188.9 | 187.6 | 105.55 | 104.82 | AP_P1-2_WP-500-005A_SRT-A | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200747 | 26PENN-MAR | 200762 | 26GARRETT | 1 | 115 | 226 | 179 | 188.9 | 187.6 | 105.55 | 104.82 | AP_P1-2_WP-500-DRT21_SRT-SL | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208395 | FARO FF | 208393 | FARO DC TIE | 1 | 69/115 | 229 | 114 | 120.1 | 119.5 | 105.31 | 104.81 | PEPCO_P4_PP40_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208395 | FARO FF | 208393 | FARO DC TIE | 1 | 69/115 | 229 | 114 | 120 | 119.4 | 105.26 | 104.75 | PJM_500_BG_P1_5011_SRT-A | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208395 | FARO FF | 208393 | FARO DC TIE | 1 | 69/115 | 229 | 114 | 120.9 | 119.4 | 106.04 | 104.73 | BG_P7_NEAST_RPHLRD_SRT-A | Tower |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208396 | FARO | 208395 | FARO FF | 1 | 69 | 229 | 240 | 246.9 | 251.1 | 102.86 | 104.61 | BG_P7_GRCTN_RAPHEL_SRT-A | Tower |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208396 | FARO | 208395 | FARO FF | 1 | 69 | 229 | 194 | 198.3 | 202.9 | 102.19 | 104.57 | Base Case | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 628 | 663.1 | 655.8 | 105.59 | 104.42 | PECO_P1-2_5014_SRT-A | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208031 | MLWD TR2 | 208020 | MANO TR3 | 1 | 230 | 229 | 801 | 823.2 | 835.6 | 102.77 | 104.32 | PECO_P1-2_5012_SRT-A | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200747 | 26PENN-MAR | 200762 | 26GARRETT | 1 | 115 | 226 | 179 | 187.6 | 186.4 | 104.82 | 104.15 | AP_P2-2_WP-500-DRT16_SRT-SL | Bus |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200747 | 26PENN-MAR | 200762 | 26GARRETT | 1 | 115 | 226 | 179 | 187.6 | 186.4 | 104.82 | 104.15 | AP_P2-3_WP-500-DRT20_SRT-SL | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200747 | 26PENN-MAR | 200762 | 26GARRETT | 1 | 115 | 226 | 179 | 187.6 | 186.4 | 104.82 | 104.15 | AP_P2-3_WP-500-465_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200747 | 26PENN-MAR | 200762 | 26GARRETT | 1 | 115 | 226 | 179 | 188.8 | 186.2 | 105.46 | 104.04 | PECO_P1-2_5012_SRT-A | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 628 | 660.4 | 653.3 | 105.16 | 104.03 | PECO_P4_PEACH205_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204529 | 27GERMANTN | 204530 | 27GERMANTN | 1 | 115/138 | 227 | 345 | 354 | 358.3 | 102.62 | 103.84 | AP_P2-2_WP-500-DRT17_SRT-SL | Bus |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204529 | 27GERMANTN | 204530 | 27GERMANTN | 1 | 115/138 | 227 | 345 | 353.1 | 358.1 | 102.34 | 103.8 | BG_P7_GRNITE_HIRDG_SRT-A | Tower |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208031 | MLWD TR2 | 208020 | MANO TR3 | 1 | 230 | 229 | 801 | 817.1 | 828.8 | 102.01 | 103.47 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208031 | MLWD TR2 | 208020 | MANO TR3 | 1 | 230 | 229 | 801 | 817 | 828.7 | 102 | 103.46 | PECO_P4_PEACH235_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204529 | 27GERMANTN | 204530 | 27GERMANTN | 1 | 115/138 | 227 | 345 | 351.7 | 356.7 | 101.95 | 103.39 | AP_P2-2_WP-138-074_SRT-A | Bus |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200747 | 26PENN-MAR | 200762 | 26GARRETT | 1 | 115 | 226 | 179 | 187.5 | 185.1 | 104.75 | 103.38 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204528 | 27GARDNERS | 200504 | 26CARLISLE | 1 | 115 | 226/227 | 160 | 165.5 | 165.3 | 103.44 | 103.3 | PN_P2-3_PN-230-0014-12_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204528 | 27GARDNERS | 200504 | 26CARLISLE | 1 | 115 | 226/227 | 160 | 165.6 | 165.2 | 103.53 | 103.22 | PN_P1-3_PN-230-020A_SRT-A | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 202650 | 26HIGHPOINT | 200747 | 26PENN-MAR | 1 | 115 | 226 | 148 | 153.1 | 152.7 | 103.46 | 103.2 | Base Case | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208031 | MLWD TR2 | 208020 | MANO TR3 | 1 | 230 | 229 | 801 | 813 | 826.6 | 101.49 | 103.19 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204693 | 27BOONETOWN | 204512 | 27S.RDG | 1 | 230 | 227 | 531 | 544.5 | 547.9 | 102.54 | 103.18 | PECO_P4_PEACH235_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204693 | 27BOONETOWN | 204512 | 27S.RDG | 1 | 230 | 227 | 531 | 544.3 | 547.7 | 102.5 | 103.14 | PECO_P1-2_5012_SRT-A | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204693 | 27BOONETOWN | 204512 | 27S.RDG | 1 | 230 | 227 | 531 | 544.3 | 547.7 | 102.5 | 103.14 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204528 | 27GARDNERS | 200504 | 26CARLISLE | 1 | 115 | 226/227 | 160 | 165.5 | 165 | 103.42 | 103.13 | PN_P2-2_PN-115-031_SRT-A | Bus |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204693 | 27BOONETOWN | 204512 | 27S.RDG | 1 | 230 | 227 | 531 | 543.7 | 547.5 | 102.4 | 103.1 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208395 | FARO FF | 208393 | FARO DC TIE | 2 | 69/115 | 229 | 120 | 127.2 | 123.4 | 106.02 | 102.87 | PECO_P4_PEACH245_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208396 | FARO | 208395 | FARO FF | 1 | 69 | 229 | 240 | 242.1 | 246.4 | 100.86 | 102.65 | BG_P7_NEAST_RPHLRD_SRT-A | Tower |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208396 | FARO | 208395 | FARO FF | 1 | 69 | 229 | 240 | 240.4 | 246.4 | 100.16 | 102.65 | PEPCO_P4_PP40_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204529 | 27GERMANTN | 204530 | 27GERMANTN | 1 | 115/138 | 227 | 345 | 349.7 | 354.1 | 101.37 | 102.63 | AP_P2-2_WP-500-DRT15_SRT-SL | Bus |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208396 | FARO | 208395 | FARO FF | 1 | 69 | 229 | 240 | 240.3 | 246.2 | 100.1 | 102.58 | PJM_500_BG_P1_5011_SRT-A | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204529 | 27GERMANTN | 204530 | 27GERMANTN | 1 | 115/138 | 227 | 345 | 348.5 | 353.3 | 101 | 102.42 | BG_P7_NWEST_GRNITE_SRT-A | Tower |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 510 | 528.1 | 522.1 | 103.54 | 102.37 | Base Case | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 510 | 521.5 | 522.1 | 102.26 | 102.37 | Base Case | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 202650 | 26HIGHPOINT | 200747 | 26PENN-MAR | 1 | 115 | 226 | 179 | 185.2 | 183.1 | 103.45 | 102.27 | AP_P1-2_WP-500-DRT21_SRT-SL | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 202650 | 26HIGHPOINT | 200747 | 26PENN-MAR | 1 | 115 | 226 | 179 | 185.2 | 183.1 | 103.45 | 102.27 | AP_P1-2_WP-500-005A_SRT-A | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 207922 | BRIS | 204515 | 27YORKANA | 1 | 230 | 227/229 | 869 | 894.5 | 888.4 | 102.94 | 102.23 | PECO_P1-2_5012_SRT-A | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 207922 | BRIS | 204515 | 27YORKANA | 1 | 230 | 227/229 | 869 | 894.5 | 888.4 | 102.94 | 102.23 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 207922 | BRIS | 204515 | 27YORKANA | 1 | 230 | 227/229 | 869 | 894.4 | 888.3 | 102.92 | 102.22 | PECO_P4_PEACH235_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208395 | FARO FF | 208393 | FARO DC TIE | 1 | 69/115 | 229 | 114 | 117.7 | 116.5 | 103.25 | 102.19 | PL_04_P12_000257_SRT-A | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208395 | FARO FF | 208393 | FARO DC TIE | 1 | 69/115 | 229 | 114 | 117.7 | 116.5 | 103.26 | 102.19 | PL_05_P22_000674_SRT-A | Bus |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1204 | 1249.7 | 1230.4 | 103.8 | 102.19 | Base Case | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 607 | 626.7 | 620 | 103.25 | 102.14 | BG_P7_GRCTN_CNSTN_SRT-A | Tower |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 607 | 620.2 | 620 | 102.17 | 102.14 | BG_P7_GRCTN_CNSTN_SRT-A | Tower |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204539 | 27HUNTRSTN | 204550 | 27ORRTANNA | 1 | 115 | 227 | 223 | 231.2 | 227.7 | 103.68 | 102.09 | ME_P1-2_ME-115-067_SRT-A | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 797 | 826.6 | 813.4 | 103.71 | 102.06 | PL_04_P12_000260_SRT-A | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 628 | 646.1 | 640.8 | 102.88 | 102.04 | PECO_P1-2_5014_SRT-A | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 207922 | BRIS | 204515 | 27YORKANA | 1 | 230 | 227/229 | 869 | 891.3 | 886.7 | 102.57 | 102.04 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200747 | 26PENN-MAR | 200762 | 26GARRETT | 1 | 115 | 226 | 179 | 183.3 | 182.2 | 102.39 | 101.76 | AP_P1-2_WP-500-008_SRT-A | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 628 | 643.4 | 638.4 | 102.46 | 101.65 | PECO_P4_PEACH205_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 221100 | GLENARM1 | 221088 | WINDYED2 | 1 | 115 | 232 | 254 | 256.2 | 258.2 | 100.87 | 101.64 | BG_P7_NEAST_RPHLRD_SRT-A | Tower |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200102 | AA1-076 MAIN | 200101 | VINCO | 1 | 500 | 225 | 999 | 1041.8 | 1015.2 | 104.28 | 101.62 | PL_02_P12_001029_SRT-A | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200102 | AA1-076 MAIN | 200101 | VINCO | 1 | 500 | 225 | 999 | 1041.8 | 1015.2 | 104.28 | 101.62 | PL_02_P42_001064_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200102 | AA1-076 MAIN | 200101 | VINCO | 1 | 500 | 225 | 999 | 1041.8 | 1015.2 | 104.28 | 101.62 | PL_02_P42_001063_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 202650 | 26HIGHPOINT | 200747 | 26PENN-MAR | 1 | 115 | 226 | 179 | 183.9 | 181.9 | 102.72 | 101.61 | AP_P2-2_WP-500-DRT16_SRT-SL | Bus |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 202650 | 26HIGHPOINT | 200747 | 26PENN-MAR | 1 | 115 | 226 | 179 | 183.9 | 181.9 | 102.72 | 101.61 | AP_P2-3_WP-500-DRT20_SRT-SL | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 202650 | 26HIGHPOINT | 200747 | 26PENN-MAR | 1 | 115 | 226 | 179 | 183.9 | 181.9 | 102.72 | 101.61 | AP_P2-3_WP-500-465_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 202650 | 26HIGHPOINT | 200747 | 26PENN-MAR | 1 | 115 | 226 | 179 | 185 | 181.7 | 103.35 | 101.49 | PECO_P1-2_5012_SRT-A | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200102 | AA1-076 MAIN | 200101 | VINCO | 1 | 500 | 225 | 999 | 1040.1 | 1013.1 | 104.11 | 101.41 | PL_48_P11_000840_SRT-A | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200102 | AA1-076 MAIN | 200101 | VINCO | 1 | 500 | 225 | 999 | 1040 | 1013.1 | 104.11 | 101.41 | PL_48_P12_000189_SRT-A | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200102 | AA1-076 MAIN | 200101 | VINCO | 1 | 500 | 225 | 999 | 1040 | 1013.1 | 104.11 | 101.41 | PL_48_P41_102622_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200102 | AA1-076 MAIN | 200101 | VINCO | 1 | 500 | 225 | 999 | 1040 | 1013.1 | 104.11 | 101.41 | PL_48_P42_100926_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200102 | AA1-076 MAIN | 200101 | VINCO | 1 | 500 | 225 | 999 | 1040 | 1013.1 | 104.11 | 101.41 | PL_48_P42_000438_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200102 | AA1-076 MAIN | 200101 | VINCO | 1 | 500 | 225 | 999 | 1040 | 1013.1 | 104.11 | 101.41 | PL_48_P71_102649_SRT-A | Tower |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200102 | AA1-076 MAIN | 200101 | VINCO | 1 | 500 | 225 | 999 | 1040.5 | 1013 | 104.16 | 101.4 | PL_08_P11_001446_SRT-A | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200102 | AA1-076 MAIN | 200101 | VINCO | 1 | 500 | 225 | 999 | 1040.5 | 1013 | 104.16 | 101.4 | PL_08_P11_001447_SRT-A | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208394 | PPL-BGE TIE | 221092 | FIVE.FOR | 1 | 115 | 229/232 | 247 | 250.4 | 250.4 | 101.37 | 101.39 | PECO_P4_PEACH245_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200102 | AA1-076 MAIN | 200101 | VINCO | 1 | 500 | 225 | 999 | 1038 | 1011.5 | 103.9 | 101.25 | PL_08_P22_102799_SRT-A | Bus |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208395 | FARO FF | 208393 | FARO DC TIE | 2 | 69/115 | 229 | 120 | 123.3 | 121.5 | 102.75 | 101.21 | BG_P7_GRCTN_RAPHEL_SRT-A | Tower |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200102 | AA1-076 MAIN | 200101 | VINCO | 1 | 500 | 225 | 999 | 1040 | 1010.7 | 104.1 | 101.17 | PECO_P7-1_220-9091_SRT-A | Tower |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200747 | 26PENN-MAR | 200762 | 26GARRETT | 1 | 115 | 226 | 179 | 182 | 180.9 | 101.65 | 101.06 | AP_P2-2_WP-500-DRT17_SRT-SL | Bus |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200102 | AA1-076 MAIN | 200101 | VINCO | 1 | 500 | 225 | 999 | 1034.7 | 1009.5 | 103.57 | 101.05 | ME_P2-2_ME-230-004_SRT-A | Bus |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204693 | 27BOONETOWN | 204512 | 27S.RDG | 1 | 230 | 227 | 531 | 537.1 | 535.6 | 101.15 | 100.87 | PECO_P4_PEACH245_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 202650 | 26HIGHPOINT | 200747 | 26PENN-MAR | 1 | 115 | 226 | 179 | 183.7 | 180.5 | 102.65 | 100.84 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200065 | PCHBTM2S | 200064 | PCHBTM1S | Z1 | 500 | 225 | 3198 | 3341.3 | 3223 | 104.48 | 100.78 | PECO_P4_PEACH225_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200102 | AA1-076 MAIN | 200101 | VINCO | 1 | 500 | 225 | 999 | 1036.4 | 1006.5 | 103.74 | 100.75 | PL_11_P22_000176_SRT-A | Bus |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200102 | AA1-076 MAIN | 200101 | VINCO | 1 | 500 | 225 | 999 | 1033.9 | 1003.2 | 103.5 | 100.42 | JC_P2-2_JCC-230-003_SRT-A | Bus |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200102 | AA1-076 MAIN | 200101 | VINCO | 1 | 500 | 225 | 999 | 1032.8 | 1001.4 | 103.38 | 100.24 | PECO_P2-2_EMI230B7_SRT-A | Bus |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204529 | 27GERMANTN | 204530 | 27GERMANTN | 1 | 115/138 | 227 | 345 | 340.8 | 345.1 | 98.78 | 100.03 | PL_05_P22_000674_SRT-A | Bus |  | NO | Related to 2022 Window 3, pending window outcome

## Light Load IPD
| Note | APS and Dominion zones as a whole are quarantined pending Window 3 outcome and are not included in above results
Related to 2022 Window 3, pending window outcome
2028 RTEP PJM Individual Plant Deliverability Result (Light Load)
FG # | Fr Bus | Name | To Bus | Name | CKT | KVs | Areas | Rating | FN DC % | FN AC % | Plant | Cont Label | Conductor/Transformer Rating (MVA) | PJM Accepting Proposals | Reason For Exclusion | Comments
2023W1-IPD-LL1 | 216901 | ATHENIA_138 | 217014 | FAIRLAWN_3 | 1 | 138 | 231 | 181 | 104.86 | 104.65 | AG2-055 | PS_P2-3_FLWN_1-2_SRT-A |  | NO | Below 200 kV Excluaion
N/A | 200762 | 26GARRETT | 235470 | 01GARRET | 1 | 115 | 226/201 | 133 | 100.85 | 101.83 | Y1-033 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 121.12 | 116.05 | 01BACKB | PECO_P4_PEACH035_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.54 | 113.84 | 01BACKB | PECO_P4_PEACH675_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.54 | 113.84 | 01BACKB | PECO_P7-1_220-0607_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3198 | 118.55 | 113.16 | 01BACKB | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 116.16 | 111.4 | 01BACKB | PECO_P1-2_220-07_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 116 | 111.35 | 01BACKB | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.88 | 111.23 | 01BACKB | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.91 | 111.21 | 01BACKB | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.92 | 111.18 | 01BACKB | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.68 | 111.06 | 01BACKB | PECO_P4_NOTTI85_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 113.12 | 108.86 | 01BACKB | AP_P2-3_PE-500-015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200532 | 26ROXBURY | 203981 | AD2-062_POI | 1 | 138 | 226 | 221 | 105.45 | 104.4 | AE1-071 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 118.5 | 117.65 | 01CROSSCHOOL | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 117.13 | 116.33 | 01CROSSCHOOL | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 121.06 | 116 | 01CROSSCHOOL | PECO_P4_PEACH035_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 115.5 | 114.73 | 01CROSSCHOOL | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.84 | 114.41 | 01CROSSCHOOL | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.84 | 114.41 | 01CROSSCHOOL | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.48 | 113.78 | 01CROSSCHOOL | PECO_P7-1_220-0607_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.48 | 113.78 | 01CROSSCHOOL | PECO_P4_PEACH675_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3198 | 118.48 | 113.09 | 01CROSSCHOOL | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200532 | 26ROXBURY | 203981 | AD2-062_POI | 1 | 138 | 226 | 221 | 103.24 | 102.22 | AG2-055 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 113 | 111.82 | 01CROSSCHOOL | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 112.95 | 111.77 | 01CROSSCHOOL | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 116.1 | 111.34 | 01CROSSCHOOL | PECO_P1-2_220-07_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.93 | 111.29 | 01CROSSCHOOL | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.82 | 111.17 | 01CROSSCHOOL | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.85 | 111.15 | 01CROSSCHOOL | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.86 | 111.12 | 01CROSSCHOOL | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.29 | 110.29 | 01CROSSCHOOL | AP_P2-2_WP-500-DRT16_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.29 | 110.29 | 01CROSSCHOOL | AP_P1-2_WP-500-DRT21_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.29 | 110.29 | 01CROSSCHOOL | AP_P1-2_WP-500-005A_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.29 | 110.29 | 01CROSSCHOOL | AP_P2-3_WP-500-DRT20_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.29 | 110.29 | 01CROSSCHOOL | AP_P2-3_WP-500-465_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 607 | 167.42 | 165.74 | 01GRNGAP | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 607 | 168.48 | 165.74 | 01GRNGAP | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 607 | 167.09 | 165.74 | 01GRNGAP | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 607 | 168.16 | 165.74 | 01GRNGAP | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 607 | 167.34 | 165.67 | 01GRNGAP | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 607 | 167.34 | 165.67 | 01GRNGAP | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 607 | 168.4 | 165.67 | 01GRNGAP | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 607 | 168.4 | 165.67 | 01GRNGAP | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 628 | 159.42 | 158.02 | 01GRNGAP | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 628 | 159.11 | 158.01 | 01GRNGAP | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 628 | 159.35 | 157.95 | 01GRNGAP | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 628 | 159.35 | 157.95 | 01GRNGAP | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 628 | 156.72 | 155.73 | 01GRNGAP | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 628 | 156.41 | 155.72 | 01GRNGAP | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 628 | 156.64 | 155.66 | 01GRNGAP | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 628 | 156.64 | 155.66 | 01GRNGAP | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 607 | 153.32 | 151.35 | 01GRNGAP | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 607 | 154.39 | 151.35 | 01GRNGAP | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 628 | 145.8 | 144.1 | 01GRNGAP | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 628 | 143.1 | 141.79 | 01GRNGAP | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 797 | 140.44 | 135.89 | 01GRNGAP | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 797 | 140.69 | 135.83 | 01GRNGAP | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 797 | 140.69 | 135.83 | 01GRNGAP | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 797 | 140.67 | 135.81 | 01GRNGAP | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 136.34 | 133.34 | 01GRNGAP | AP_P1-2_PE-500-407T_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 136.34 | 133.34 | 01GRNGAP | DVP_P1-2: LN 514_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 136.34 | 133.33 | 01GRNGAP | DVP_P4-2: 51482_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 131.21 | 128.2 | 01GRNGAP | AP_P2-3_PE-500-019C_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 797 | 132.32 | 127.52 | 01GRNGAP | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 814 | 130.67 | 126.17 | 01GRNGAP | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 814 | 131.15 | 126.05 | 01GRNGAP | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 814 | 131.15 | 126.05 | 01GRNGAP | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 814 | 131.14 | 126.03 | 01GRNGAP | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 235463 | 01TANEY | 1 | 138 | 227/201 | 221 | 138.13 | 137.02 | AC1-048 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 117.86 | 116.99 | 01GRNGAP | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 814 | 121.83 | 116.93 | 01GRNGAP | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 116.49 | 115.67 | 01GRNGAP | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 120.48 | 115.44 | 01GRNGAP | PECO_P4_PEACH035_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 114.86 | 114.08 | 01GRNGAP | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.23 | 113.84 | 01GRNGAP | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.23 | 113.84 | 01GRNGAP | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 117.89 | 113.22 | 01GRNGAP | PECO_P7-1_220-0607_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 117.89 | 113.22 | 01GRNGAP | PECO_P4_PEACH675_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 814 | 115.6 | 112.61 | 01GRNGAP | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 814 | 115.85 | 112.55 | 01GRNGAP | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 814 | 115.85 | 112.55 | 01GRNGAP | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 814 | 115.83 | 112.53 | 01GRNGAP | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3198 | 117.76 | 112.42 | 01GRNGAP | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 204529 | 27GERMANTN | 1 | 138/115 | 227 | 287 | 106.36 | 107.94 | AC1-048 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 112.39 | 111.19 | 01GRNGAP | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 112.34 | 111.14 | 01GRNGAP | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.51 | 110.78 | 01GRNGAP | PECO_P1-2_220-07_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 797 | 112.18 | 110.72 | 01GRNGAP | PJM_500_BG_P4_5_CNSTN_15_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.3 | 110.68 | 01GRNGAP | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.18 | 110.57 | 01GRNGAP | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.27 | 110.56 | 01GRNGAP | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.21 | 110.55 | 01GRNGAP | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 110.64 | 109.62 | 01GRNGAP | AP_P1-2_WP-500-DRT21_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 110.64 | 109.62 | 01GRNGAP | AP_P2-3_WP-500-DRT20_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 110.64 | 109.62 | 01GRNGAP | AP_P1-2_WP-500-005A_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 110.64 | 109.62 | 01GRNGAP | AP_P2-2_WP-500-DRT16_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 110.64 | 109.62 | 01GRNGAP | AP_P2-3_WP-500-465_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204502 | 27JACKSON | 204514 | 27TMI | 1 | 230 | 227 | 659 | 104.17 | 104.13 | 01GRNGAP | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204502 | 27JACKSON | 204514 | 27TMI | 1 | 230 | 227 | 659 | 104.17 | 104.13 | 01GRNGAP | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204502 | 27JACKSON | 204514 | 27TMI | 1 | 230 | 227 | 659 | 104.23 | 104.11 | 01GRNGAP | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 814 | 107.45 | 104.11 | 01GRNGAP | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204502 | 27JACKSON | 204514 | 27TMI | 1 | 230 | 227 | 659 | 104.15 | 104.11 | 01GRNGAP | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 104.98 | 102.32 | 01GRNGAP | DVP_P4-2: 560T571_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 104.82 | 102.18 | 01GRNGAP | DVP_P4-2: H2T560_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 104.81 | 102.17 | 01GRNGAP | DVP_P4-2: H1T560_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 104.67 | 102.02 | 01GRNGAP | PEPCO_P1_5070_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220972 | GRANITE1 | 1 | 230 | 232 | 811 | 103.27 | 100.35 | 01GRNGAP | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220972 | GRANITE1 | 1 | 230 | 232 | 811 | 103.01 | 100.05 | 01GRNGAP | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220972 | GRANITE1 | 1 | 230 | 232 | 811 | 103.01 | 100.05 | 01GRNGAP | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 235463 | 01TANEY | 1 | 138 | 227/201 | 221 | 136.33 | 135.26 | AD1-020 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 118.42 | 117.57 | 05CELAN | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 117.05 | 116.24 | 05CELAN | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 120.98 | 115.92 | 05CELAN | PECO_P4_PEACH035_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 115.42 | 114.64 | 05CELAN | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.75 | 114.33 | 05CELAN | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.75 | 114.33 | 05CELAN | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.4 | 113.7 | 05CELAN | PECO_P4_PEACH675_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.4 | 113.7 | 05CELAN | PECO_P7-1_220-0607_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3198 | 118.38 | 112.99 | 05CELAN | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204529 | 27GERMANTN | 204538 | 27STRABAN | 1 | 115 | 227 | 257 | 107.15 | 107.62 | AD1-020 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 112.93 | 111.74 | 05CELAN | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 112.88 | 111.69 | 05CELAN | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 116.02 | 111.26 | 05CELAN | PECO_P1-2_220-07_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.84 | 111.2 | 05CELAN | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.73 | 111.08 | 05CELAN | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.75 | 111.06 | 05CELAN | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.78 | 111.04 | 05CELAN | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.23 | 110.23 | 05CELAN | AP_P2-2_WP-500-DRT16_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.23 | 110.23 | 05CELAN | AP_P1-2_WP-500-DRT21_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.23 | 110.23 | 05CELAN | AP_P2-3_WP-500-465_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.23 | 110.23 | 05CELAN | AP_P2-3_WP-500-DRT20_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.23 | 110.23 | 05CELAN | AP_P1-2_WP-500-005A_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 204529 | 27GERMANTN | 1 | 138/115 | 227 | 287 | 104.98 | 106.62 | AD1-020 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 121.08 | 116.02 | 05NTRDAM | PECO_P4_PEACH035_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.87 | 114.44 | 05NTRDAM | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.87 | 114.44 | 05NTRDAM | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.51 | 113.81 | 05NTRDAM | PECO_P4_PEACH675_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.51 | 113.81 | 05NTRDAM | PECO_P7-1_220-0607_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3198 | 118.51 | 113.12 | 05NTRDAM | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 116.13 | 111.36 | 05NTRDAM | PECO_P1-2_220-07_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.96 | 111.31 | 05NTRDAM | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.84 | 111.2 | 05NTRDAM | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.87 | 111.18 | 05NTRDAM | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.89 | 111.15 | 05NTRDAM | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 105.52 | 104.2 | 05NTRDAM | PN_P2-3_PN-500-DRT32_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 105.52 | 104.2 | 05NTRDAM | PN_P2-3_PN-500-004-DRT-002_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 235463 | 01TANEY | 1 | 138 | 227/201 | 221 | 134.42 | 133.38 | AE2-000 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 118.45 | 117.6 | 08HLCRTG | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 117.08 | 116.27 | 08HLCRTG | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 120.97 | 115.91 | 08HLCRTG | PECO_P4_PEACH035_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 115.44 | 114.67 | 08HLCRTG | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.77 | 114.34 | 08HLCRTG | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.77 | 114.34 | 08HLCRTG | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.4 | 113.7 | 08HLCRTG | PECO_P4_PEACH675_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.4 | 113.7 | 08HLCRTG | PECO_P7-1_220-0607_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3198 | 118.38 | 112.99 | 08HLCRTG | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204529 | 27GERMANTN | 204538 | 27STRABAN | 1 | 115 | 227 | 257 | 105.5 | 105.95 | AE2-000 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 112.95 | 111.76 | 08HLCRTG | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 112.9 | 111.72 | 08HLCRTG | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 116.02 | 111.26 | 08HLCRTG | PECO_P1-2_220-07_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.84 | 111.2 | 08HLCRTG | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.73 | 111.08 | 08HLCRTG | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.76 | 111.06 | 08HLCRTG | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.78 | 111.04 | 08HLCRTG | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.25 | 110.25 | 08HLCRTG | AP_P1-2_WP-500-005A_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.25 | 110.25 | 08HLCRTG | AP_P2-3_WP-500-DRT20_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.25 | 110.25 | 08HLCRTG | AP_P2-3_WP-500-465_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.25 | 110.25 | 08HLCRTG | AP_P1-2_WP-500-DRT21_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.25 | 110.25 | 08HLCRTG | AP_P2-2_WP-500-DRT16_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 112.75 | 108.36 | 09PIQUA3 | PL_10_P42_100570_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 112.35 | 107.97 | 09PIQUA3 | PN_P2-3_PN-500-004-DRT-008_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 112.35 | 107.97 | 09PIQUA3 | PN_P2-3_PN-500-DRT31_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 112.29 | 107.92 | 09PIQUA3 | PL_10_P12_000085_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 112.22 | 107.87 | 09PIQUA3 | PL_30_P42_000131_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 204529 | 27GERMANTN | 1 | 138/115 | 227 | 287 | 103.51 | 105.11 | AE2-000 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 121.09 | 116.03 | 15USSILL | PECO_P4_PEACH035_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.53 | 113.83 | 15USSILL | PECO_P7-1_220-0607_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.53 | 113.83 | 15USSILL | PECO_P4_PEACH675_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3198 | 118.55 | 113.15 | 15USSILL | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 116.15 | 111.39 | 15USSILL | PECO_P1-2_220-07_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.99 | 111.34 | 15USSILL | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.87 | 111.22 | 15USSILL | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.9 | 111.2 | 15USSILL | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.91 | 111.17 | 15USSILL | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.67 | 111.05 | 15USSILL | PECO_P4_NOTTI85_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.61 | 111.04 | 15USSILL | PECO_P1-2_220-08_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 136.49 | 133.43 | 1DOMTR10 | DVP_P1-2: LN 514_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 136.49 | 133.43 | 1DOMTR10 | AP_P1-2_PE-500-407T_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 136.49 | 133.41 | 1DOMTR10 | DVP_P4-2: 51482_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 131.39 | 128.3 | 1DOMTR10 | AP_P2-3_PE-500-019C_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 235463 | 01TANEY | 1 | 138 | 227/201 | 221 | 139.31 | 138.17 | AG2-055 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 118.47 | 117.62 | 1DOMTR10 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 117.1 | 116.29 | 1DOMTR10 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 121.06 | 116 | 1DOMTR10 | PECO_P4_PEACH035_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 115.47 | 114.7 | 1DOMTR10 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.81 | 114.39 | 1DOMTR10 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.81 | 114.39 | 1DOMTR10 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.47 | 113.78 | 1DOMTR10 | PECO_P4_PEACH675_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.47 | 113.78 | 1DOMTR10 | PECO_P7-1_220-0607_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3198 | 118.47 | 113.08 | 1DOMTR10 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204529 | 27GERMANTN | 204538 | 27STRABAN | 1 | 115 | 227 | 257 | 109.72 | 110.39 | AG2-055 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 112.97 | 111.79 | 1DOMTR10 | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 112.92 | 111.74 | 1DOMTR10 | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 116.09 | 111.33 | 1DOMTR10 | PECO_P1-2_220-07_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.92 | 111.28 | 1DOMTR10 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.81 | 111.16 | 1DOMTR10 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.84 | 111.14 | 1DOMTR10 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.85 | 111.12 | 1DOMTR10 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.28 | 110.28 | 1DOMTR10 | AP_P1-2_WP-500-DRT21_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.28 | 110.28 | 1DOMTR10 | AP_P2-2_WP-500-DRT16_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.28 | 110.28 | 1DOMTR10 | AP_P2-3_WP-500-DRT20_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.28 | 110.28 | 1DOMTR10 | AP_P1-2_WP-500-005A_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.28 | 110.28 | 1DOMTR10 | AP_P2-3_WP-500-465_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 204529 | 27GERMANTN | 1 | 138/115 | 227 | 287 | 107.28 | 109.12 | AG2-055 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 118.51 | 117.66 | 1DOMTR9 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 117.14 | 116.34 | 1DOMTR9 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 121.1 | 116.03 | 1DOMTR9 | PECO_P4_PEACH035_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 115.51 | 114.74 | 1DOMTR9 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.85 | 114.43 | 1DOMTR9 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.85 | 114.43 | 1DOMTR9 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.51 | 113.81 | 1DOMTR9 | PECO_P7-1_220-0607_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.51 | 113.81 | 1DOMTR9 | PECO_P4_PEACH675_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3198 | 118.52 | 113.12 | 1DOMTR9 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 235463 | 01TANEY | 1 | 138 | 227/201 | 221 | 127.42 | 126.57 | O66 NFTWR | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 113.01 | 111.83 | 1DOMTR9 | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 112.96 | 111.78 | 1DOMTR9 | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 116.13 | 111.37 | 1DOMTR9 | PECO_P1-2_220-07_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.97 | 111.32 | 1DOMTR9 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.85 | 111.2 | 1DOMTR9 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.88 | 111.18 | 1DOMTR9 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.89 | 111.15 | 1DOMTR9 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.32 | 110.32 | 1DOMTR9 | AP_P2-2_WP-500-DRT16_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.32 | 110.32 | 1DOMTR9 | AP_P2-3_WP-500-DRT20_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.32 | 110.32 | 1DOMTR9 | AP_P2-3_WP-500-465_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.32 | 110.32 | 1DOMTR9 | AP_P1-2_WP-500-005A_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.32 | 110.32 | 1DOMTR9 | AP_P1-2_WP-500-DRT21_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 136.48 | 133.41 | 1EDGECMA | DVP_P1-2: LN 514_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 136.48 | 133.41 | 1EDGECMA | AP_P1-2_PE-500-407T_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 136.48 | 133.39 | 1EDGECMA | DVP_P4-2: 51482_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 131.37 | 128.29 | 1EDGECMA | AP_P2-3_PE-500-019C_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 232 | 107.89 | 106.09 | AC1-048 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 118.45 | 117.59 | 1EDGECMA | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 117.08 | 116.27 | 1EDGECMA | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 121.04 | 115.97 | 1EDGECMA | PECO_P4_PEACH035_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 115.44 | 114.67 | 1EDGECMA | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.79 | 114.37 | 1EDGECMA | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.79 | 114.37 | 1EDGECMA | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.45 | 113.75 | 1EDGECMA | PECO_P7-1_220-0607_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.45 | 113.75 | 1EDGECMA | PECO_P4_PEACH675_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3198 | 118.44 | 113.05 | 1EDGECMA | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 232 | 121.43 | 119.5 | AD1-020 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 112.95 | 111.76 | 1EDGECMA | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 112.9 | 111.72 | 1EDGECMA | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 116.07 | 111.31 | 1EDGECMA | PECO_P1-2_220-07_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.9 | 111.25 | 1EDGECMA | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.78 | 111.14 | 1EDGECMA | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.81 | 111.12 | 1EDGECMA | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.83 | 111.09 | 1EDGECMA | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.26 | 110.26 | 1EDGECMA | AP_P2-3_WP-500-465_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.26 | 110.26 | 1EDGECMA | AP_P1-2_WP-500-005A_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.26 | 110.26 | 1EDGECMA | AP_P2-2_WP-500-DRT16_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.26 | 110.26 | 1EDGECMA | AP_P2-3_WP-500-DRT20_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.26 | 110.26 | 1EDGECMA | AP_P1-2_WP-500-DRT21_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 232 | 118.45 | 116.6 | AE2-000 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 118.53 | 117.68 | 1HOLLOMANSOL | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 117.15 | 116.35 | 1HOLLOMANSOL | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 121.11 | 116.05 | 1HOLLOMANSOL | PECO_P4_PEACH035_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 115.52 | 114.75 | 1HOLLOMANSOL | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.87 | 114.44 | 1HOLLOMANSOL | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.87 | 114.44 | 1HOLLOMANSOL | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.52 | 113.82 | 1HOLLOMANSOL | PECO_P4_PEACH675_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.52 | 113.82 | 1HOLLOMANSOL | PECO_P7-1_220-0607_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3198 | 118.53 | 113.13 | 1HOLLOMANSOL | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 113.03 | 111.84 | 1HOLLOMANSOL | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 112.98 | 111.8 | 1HOLLOMANSOL | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 116.14 | 111.38 | 1HOLLOMANSOL | PECO_P1-2_220-07_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.98 | 111.33 | 1HOLLOMANSOL | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.86 | 111.22 | 1HOLLOMANSOL | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.89 | 111.19 | 1HOLLOMANSOL | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.9 | 111.16 | 1HOLLOMANSOL | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.33 | 110.34 | 1HOLLOMANSOL | AP_P2-3_WP-500-DRT20_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.33 | 110.34 | 1HOLLOMANSOL | AP_P2-2_WP-500-DRT16_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.33 | 110.34 | 1HOLLOMANSOL | AP_P1-2_WP-500-DRT21_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.33 | 110.34 | 1HOLLOMANSOL | AP_P1-2_WP-500-005A_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.33 | 110.34 | 1HOLLOMANSOL | AP_P2-3_WP-500-465_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 232 | 122.75 | 120.95 | AG2-055 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 118.51 | 117.66 | 1STONECA | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 117.14 | 116.33 | 1STONECA | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 121.1 | 116.04 | 1STONECA | PECO_P4_PEACH035_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 115.5 | 114.74 | 1STONECA | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.85 | 114.43 | 1STONECA | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.85 | 114.43 | 1STONECA | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.51 | 113.82 | 1STONECA | PECO_P7-1_220-0607_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.51 | 113.82 | 1STONECA | PECO_P4_PEACH675_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3198 | 118.52 | 113.12 | 1STONECA | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 232 | 112.34 | 110.43 | O66 NFTWR | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 113.01 | 111.83 | 1STONECA | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 112.96 | 111.78 | 1STONECA | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 116.13 | 111.37 | 1STONECA | PECO_P1-2_220-07_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.97 | 111.32 | 1STONECA | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.85 | 111.21 | 1STONECA | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.88 | 111.19 | 1STONECA | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.89 | 111.15 | 1STONECA | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.32 | 110.32 | 1STONECA | AP_P2-2_WP-500-DRT16_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.32 | 110.32 | 1STONECA | AP_P2-3_WP-500-465_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.32 | 110.32 | 1STONECA | AP_P2-3_WP-500-DRT20_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.32 | 110.32 | 1STONECA | AP_P1-2_WP-500-005A_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.32 | 110.32 | 1STONECA | AP_P1-2_WP-500-DRT21_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 118.86 | 118.04 | 26ARMNA MT | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 117.49 | 116.71 | 26ARMNA MT | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 115.85 | 115.11 | 26ARMNA MT | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 119.17 | 114.73 | 26ARMNA MT | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 119.17 | 114.73 | 26ARMNA MT | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.67 | 110.7 | 26ARMNA MT | AP_P2-2_WP-500-DRT16_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.67 | 110.7 | 26ARMNA MT | AP_P1-2_WP-500-DRT21_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.67 | 110.7 | 26ARMNA MT | AP_P1-2_WP-500-005A_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.67 | 110.7 | 26ARMNA MT | AP_P2-3_WP-500-465_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.67 | 110.7 | 26ARMNA MT | AP_P2-3_WP-500-DRT20_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.73 | 110.57 | 26ARMNA MT | BG_P7_GRNITE_HIRDG_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 114.92 | 110.53 | 26ARMNA MT | PL_05_P71_000906_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 113.99 | 109.73 | 26ARMNA MT | AP_P2-3_WP-500-465_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 113.99 | 109.73 | 26ARMNA MT | AP_P2-2_WP-500-DRT16_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 113.99 | 109.73 | 26ARMNA MT | AP_P2-3_WP-500-DRT20_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 113.99 | 109.73 | 26ARMNA MT | AP_P1-2_WP-500-DRT21_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 113.99 | 109.73 | 26ARMNA MT | AP_P1-2_WP-500-005A_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 109.16 | 108.1 | 26ARMNA MT | AP_P2-3_PE-500-014_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 111 | 106.26 | 26ARMNA MT | AP_P1-2_WP-230-324AT_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 110.51 | 106.01 | 26ARMNA MT | PN_P2-3_PN-345-1185-3_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200762 | 26GARRETT | 235470 | 01GARRET | 1 | 115 | 226/201 | 160 | 102.22 | 102.49 | 26CSLMN_L13 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200762 | 26GARRETT | 235470 | 01GARRET | 1 | 115 | 226/201 | 160 | 102.22 | 102.49 | 26CSLMN_L13 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200762 | 26GARRETT | 235470 | 01GARRET | 1 | 115 | 226/201 | 160 | 102.15 | 102.41 | 26CSLMN_L13 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200762 | 26GARRETT | 235470 | 01GARRET | 1 | 115 | 226/201 | 160 | 102.18 | 102.3 | 26LOOKOUT | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200762 | 26GARRETT | 235470 | 01GARRET | 1 | 115 | 226/201 | 160 | 102.18 | 102.3 | 26LOOKOUT | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200762 | 26GARRETT | 235470 | 01GARRET | 1 | 115 | 226/201 | 160 | 102.1 | 102.22 | 26LOOKOUT | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200762 | 26GARRETT | 235470 | 01GARRET | 1 | 115 | 226/201 | 160 | 100.47 | 100.59 | 26STNY CRK | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200762 | 26GARRETT | 235470 | 01GARRET | 1 | 115 | 226/201 | 160 | 100.47 | 100.59 | 26STNY CRK | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200762 | 26GARRETT | 235470 | 01GARRET | 1 | 115 | 226/201 | 160 | 100.39 | 100.5 | 26STNY CRK | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204538 | 27STRABAN | 204544 | 27LINCOLN | 1 | 115 | 227 | 257 | 111.35 | 110.92 | AD1-020 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3198 | 118.89 | 113.48 | 28MDLSEXCO | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 116.29 | 111.63 | 28MDLSEXCO | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 116.17 | 111.52 | 28MDLSEXCO | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 116.2 | 111.5 | 28MDLSEXCO | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.97 | 111.34 | 28MDLSEXCO | PECO_P4_NOTTI85_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.91 | 111.33 | 28MDLSEXCO | PECO_P1-2_220-08_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.86 | 111.29 | 28MDLSEXCO | PECO_P4_COOPR125_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.62 | 111.13 | 28MDLSEXCO | PECO_P1-2_220-93_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 110.55 | 106.14 | 28MDLSEXCO | 200105 AA1-076 ST 23.5 _SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 109.86 | 105.53 | 28MDLSEXCO | AP_P2-3_WP-138-390_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 109.74 | 105.47 | 28MDLSEXCO | PL_10_P42_100572_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 113.01 | 108.62 | 28SIXFLAGS | PL_10_P42_100570_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 112.62 | 108.23 | 28SIXFLAGS | PN_P2-3_PN-500-004-DRT-008_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 112.62 | 108.23 | 28SIXFLAGS | PN_P2-3_PN-500-DRT31_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 112.56 | 108.17 | 28SIXFLAGS | PL_10_P12_000085_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 112.49 | 108.14 | 28SIXFLAGS | PL_30_P42_000131_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 109.73 | 105.46 | 28SIXFLAGS | PL_10_P42_100572_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204538 | 27STRABAN | 204544 | 27LINCOLN | 1 | 115 | 227 | 257 | 109.67 | 109.24 | AE2-000 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 121.12 | 116.06 | 3UNCAMP | PECO_P4_PEACH035_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.88 | 114.45 | 3UNCAMP | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.88 | 114.45 | 3UNCAMP | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.53 | 113.83 | 3UNCAMP | PECO_P4_PEACH675_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.53 | 113.83 | 3UNCAMP | PECO_P7-1_220-0607_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3198 | 118.54 | 113.15 | 3UNCAMP | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 116.15 | 111.39 | 3UNCAMP | PECO_P1-2_220-07_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.99 | 111.34 | 3UNCAMP | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.87 | 111.23 | 3UNCAMP | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.9 | 111.21 | 3UNCAMP | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.91 | 111.17 | 3UNCAMP | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204538 | 27STRABAN | 204544 | 27LINCOLN | 1 | 115 | 227 | 257 | 113.96 | 113.68 | AG2-055 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 118.48 | 117.63 | 4E MILL | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 117.11 | 116.3 | 4E MILL | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 121.07 | 116 | 4E MILL | PECO_P4_PEACH035_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 115.48 | 114.71 | 4E MILL | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.82 | 114.4 | 4E MILL | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.82 | 114.4 | 4E MILL | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.48 | 113.78 | 4E MILL | PECO_P7-1_220-0607_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.48 | 113.78 | 4E MILL | PECO_P4_PEACH675_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3198 | 118.48 | 113.08 | 4E MILL | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204538 | 27STRABAN | 204544 | 27LINCOLN | 1 | 115 | 227 | 257 | 103.55 | 102.94 | O66 NFTWR | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 112.98 | 111.8 | 4E MILL | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 112.93 | 111.75 | 4E MILL | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 116.1 | 111.34 | 4E MILL | PECO_P1-2_220-07_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.93 | 111.28 | 4E MILL | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.82 | 111.17 | 4E MILL | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.84 | 111.15 | 4E MILL | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.86 | 111.12 | 4E MILL | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.29 | 110.29 | 4E MILL | AP_P2-3_WP-500-465_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.29 | 110.29 | 4E MILL | AP_P2-3_WP-500-DRT20_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.29 | 110.29 | 4E MILL | AP_P1-2_WP-500-DRT21_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.29 | 110.29 | 4E MILL | AP_P1-2_WP-500-005A_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.29 | 110.29 | 4E MILL | AP_P2-2_WP-500-DRT16_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 203981 | AD2-062_POI | 235188 | 01GREENE | 1 | 138 | 226/201 | 221 | 127.78 | 127.09 | AD2-062 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 118.52 | 117.67 | 6PAPERMILL | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 117.14 | 116.34 | 6PAPERMILL | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 121.11 | 116.04 | 6PAPERMILL | PECO_P4_PEACH035_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 115.51 | 114.74 | 6PAPERMILL | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.86 | 114.43 | 6PAPERMILL | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.86 | 114.43 | 6PAPERMILL | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.52 | 113.82 | 6PAPERMILL | PECO_P7-1_220-0607_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.52 | 113.82 | 6PAPERMILL | PECO_P4_PEACH675_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3198 | 118.53 | 113.13 | 6PAPERMILL | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 203981 | AD2-062_POI | 235188 | 01GREENE | 1 | 138 | 226/201 | 221 | 125.66 | 124.96 | AE1-071 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 113.01 | 111.83 | 6PAPERMILL | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 112.96 | 111.78 | 6PAPERMILL | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 116.14 | 111.38 | 6PAPERMILL | PECO_P1-2_220-07_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.97 | 111.32 | 6PAPERMILL | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.86 | 111.21 | 6PAPERMILL | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.88 | 111.19 | 6PAPERMILL | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.9 | 111.16 | 6PAPERMILL | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.32 | 110.33 | 6PAPERMILL | AP_P2-3_WP-500-465_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.32 | 110.33 | 6PAPERMILL | AP_P2-3_WP-500-DRT20_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.32 | 110.33 | 6PAPERMILL | AP_P2-2_WP-500-DRT16_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.32 | 110.33 | 6PAPERMILL | AP_P1-2_WP-500-005A_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.32 | 110.33 | 6PAPERMILL | AP_P1-2_WP-500-DRT21_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 203981 | AD2-062_POI | 235188 | 01GREENE | 1 | 138 | 226/201 | 221 | 113.74 | 113.05 | AE1-101 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 118.42 | 117.56 | AA1-018 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 117.05 | 116.24 | AA1-018 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 120.93 | 115.87 | AA1-018 | PECO_P4_PEACH035_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 115.41 | 114.64 | AA1-018 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.74 | 114.31 | AA1-018 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.74 | 114.31 | AA1-018 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.36 | 113.67 | AA1-018 | PECO_P4_PEACH675_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.36 | 113.67 | AA1-018 | PECO_P7-1_220-0607_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3198 | 118.34 | 112.95 | AA1-018 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 203981 | AD2-062_POI | 235188 | 01GREENE | 1 | 138 | 226/201 | 221 | 123.47 | 122.78 | AG2-055 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 112.92 | 111.73 | AA1-018 | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 112.87 | 111.69 | AA1-018 | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.98 | 111.23 | AA1-018 | PECO_P1-2_220-07_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.81 | 111.16 | AA1-018 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.69 | 111.05 | AA1-018 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.72 | 111.03 | AA1-018 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.75 | 111.01 | AA1-018 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.22 | 110.22 | AA1-018 | AP_P1-2_WP-500-005A_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.22 | 110.22 | AA1-018 | AP_P2-2_WP-500-DRT16_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.22 | 110.22 | AA1-018 | AP_P2-3_WP-500-DRT20_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.22 | 110.22 | AA1-018 | AP_P2-3_WP-500-465_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.22 | 110.22 | AA1-018 | AP_P1-2_WP-500-DRT21_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 203981 | AD2-062_POI | 235188 | 01GREENE | 1 | 138 | 226/201 | 221 | 114.42 | 113.75 | O66 NFTWR | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 118.47 | 117.62 | AA1-038 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 117.1 | 116.29 | AA1-038 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 121.06 | 115.99 | AA1-038 | PECO_P4_PEACH035_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 115.47 | 114.7 | AA1-038 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.81 | 114.39 | AA1-038 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.81 | 114.39 | AA1-038 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.47 | 113.77 | AA1-038 | PECO_P7-1_220-0607_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.47 | 113.77 | AA1-038 | PECO_P4_PEACH675_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3198 | 118.47 | 113.07 | AA1-038 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 211365 | ASHF TP1 | 211698 | LNFD | 1 | 69 | 229 | 96 | 115.23 | 122.81 | AD1-143 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 112.97 | 111.79 | AA1-038 | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 112.92 | 111.74 | AA1-038 | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 116.09 | 111.33 | AA1-038 | PECO_P1-2_220-07_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.92 | 111.27 | AA1-038 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.8 | 111.16 | AA1-038 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.83 | 111.14 | AA1-038 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.85 | 111.11 | AA1-038 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.28 | 110.28 | AA1-038 | AP_P2-3_WP-500-465_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.28 | 110.28 | AA1-038 | AP_P1-2_WP-500-005A_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.28 | 110.28 | AA1-038 | AP_P1-2_WP-500-DRT21_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.28 | 110.28 | AA1-038 | AP_P2-2_WP-500-DRT16_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.28 | 110.28 | AA1-038 | AP_P2-3_WP-500-DRT20_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.9 | 114.47 | AA1-063 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.9 | 114.47 | AA1-063 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 116.01 | 111.36 | AA1-063 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.89 | 111.24 | AA1-063 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.92 | 111.22 | AA1-063 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.69 | 111.07 | AA1-063 | PECO_P4_NOTTI85_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.63 | 111.06 | AA1-063 | PECO_P1-2_220-08_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 111.31 | 106.94 | AA1-063 | DVP_P4-2: 534T564_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 111.13 | 106.75 | AA1-063 | PL_04_P42_000565_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 111.13 | 106.75 | AA1-063 | PL_04_P12_000261_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 607 | 170.77 | 168.19 | AA1-102 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 607 | 169.68 | 168.19 | AA1-102 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 607 | 170.42 | 168.15 | AA1-102 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 607 | 169.32 | 168.15 | AA1-102 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 607 | 170.7 | 168.12 | AA1-102 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 607 | 170.7 | 168.12 | AA1-102 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 607 | 169.6 | 168.12 | AA1-102 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 607 | 169.6 | 168.12 | AA1-102 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 628 | 161.61 | 160.39 | AA1-102 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 628 | 161.27 | 160.35 | AA1-102 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 628 | 161.54 | 160.32 | AA1-102 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 628 | 161.54 | 160.32 | AA1-102 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 628 | 158.9 | 158.1 | AA1-102 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 628 | 158.56 | 158.06 | AA1-102 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 628 | 158.83 | 158.03 | AA1-102 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 628 | 158.83 | 158.03 | AA1-102 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 607 | 155.56 | 153.57 | AA1-102 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 607 | 156.66 | 153.57 | AA1-102 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 628 | 147.97 | 146.24 | AA1-102 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 628 | 145.26 | 143.93 | AA1-102 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2812 | 114 | 112.49 | 01CROSSCHOOL | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 119.11 | 118.3 | AA1-102 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 117.73 | 116.97 | AA1-102 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 121.88 | 116.79 | AA1-102 | PECO_P4_PEACH035_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 116.09 | 115.37 | AA1-102 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 119.51 | 115.06 | AA1-102 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 119.51 | 115.06 | AA1-102 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 119.22 | 114.5 | AA1-102 | PECO_P4_PEACH675_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 119.22 | 114.5 | AA1-102 | PECO_P7-1_220-0607_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3198 | 119.42 | 113.98 | AA1-102 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2812 | 113.36 | 111.81 | 01GRNGAP | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 113.58 | 112.44 | AA1-102 | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 113.53 | 112.39 | AA1-102 | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 116.74 | 112.07 | AA1-102 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 116.84 | 112.06 | AA1-102 | PECO_P1-2_220-07_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 116.62 | 111.95 | AA1-102 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 116.65 | 111.93 | AA1-102 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 116.6 | 111.84 | AA1-102 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.89 | 110.93 | AA1-102 | AP_P2-3_WP-500-DRT20_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.89 | 110.93 | AA1-102 | AP_P2-3_WP-500-465_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.89 | 110.93 | AA1-102 | AP_P2-2_WP-500-DRT16_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.89 | 110.93 | AA1-102 | AP_P1-2_WP-500-005A_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.89 | 110.93 | AA1-102 | AP_P1-2_WP-500-DRT21_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200065 | PCHBTM2S | 200066 | PCHBTM1N | 2 | 500 | 225 | 3022 | 104.19 | 100.41 | AA1-102 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 105.04 | 100.17 | AA1-102 | PECO_P4_PEACH025_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 136.46 | 133.39 | AA1-139 | DVP_P1-2: LN 514_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 136.46 | 133.39 | AA1-139 | AP_P1-2_PE-500-407T_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 136.46 | 133.37 | AA1-139 | DVP_P4-2: 51482_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 131.35 | 128.27 | AA1-139 | AP_P2-3_PE-500-019C_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2812 | 113.92 | 112.41 | 05CELAN | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 118.46 | 117.61 | AA1-139 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 117.09 | 116.28 | AA1-139 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 121.06 | 115.99 | AA1-139 | PECO_P4_PEACH035_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 115.45 | 114.68 | AA1-139 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.8 | 114.38 | AA1-139 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.8 | 114.38 | AA1-139 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.46 | 113.77 | AA1-139 | PECO_P4_PEACH675_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.46 | 113.77 | AA1-139 | PECO_P7-1_220-0607_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3198 | 118.46 | 113.07 | AA1-139 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2812 | 113.94 | 112.44 | 08HLCRTG | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 112.96 | 111.77 | AA1-139 | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 112.91 | 111.73 | AA1-139 | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 116.09 | 111.32 | AA1-139 | PECO_P1-2_220-07_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.92 | 111.27 | AA1-139 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.8 | 111.15 | AA1-139 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.83 | 111.13 | AA1-139 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.85 | 111.11 | AA1-139 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.27 | 110.27 | AA1-139 | AP_P1-2_WP-500-DRT21_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.27 | 110.27 | AA1-139 | AP_P2-3_WP-500-DRT20_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.27 | 110.27 | AA1-139 | AP_P2-2_WP-500-DRT16_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.27 | 110.27 | AA1-139 | AP_P2-3_WP-500-465_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.27 | 110.27 | AA1-139 | AP_P1-2_WP-500-005A_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2812 | 113.97 | 112.46 | 1DOMTR10 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 121.13 | 116.06 | AA2-053 | PECO_P4_PEACH035_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.88 | 114.46 | AA2-053 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.88 | 114.46 | AA2-053 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.54 | 113.84 | AA2-053 | PECO_P4_PEACH675_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.54 | 113.84 | AA2-053 | PECO_P7-1_220-0607_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3198 | 118.55 | 113.15 | AA2-053 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 116.16 | 111.4 | AA2-053 | PECO_P1-2_220-07_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 116 | 111.35 | AA2-053 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.88 | 111.23 | AA2-053 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.91 | 111.21 | AA2-053 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.92 | 111.18 | AA2-053 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 116.01 | 111.36 | AA2-057 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.89 | 111.25 | AA2-057 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.92 | 111.23 | AA2-057 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.7 | 111.07 | AA2-057 | PECO_P4_NOTTI85_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.63 | 111.06 | AA2-057 | PECO_P1-2_220-08_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.59 | 111.02 | AA2-057 | PECO_P4_COOPR125_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.35 | 110.87 | AA2-057 | PECO_P1-2_220-93_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 114.66 | 110.27 | AA2-057 | PL_05_P71_000906_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 111.13 | 106.75 | AA2-057 | PL_04_P42_000565_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 111.13 | 106.75 | AA2-057 | PL_04_P12_000261_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2812 | 114.01 | 112.5 | 1DOMTR9 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 118.51 | 117.66 | AA2-088 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 117.13 | 116.33 | AA2-088 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 121.1 | 116.03 | AA2-088 | PECO_P4_PEACH035_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 115.5 | 114.73 | AA2-088 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.85 | 114.42 | AA2-088 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.85 | 114.42 | AA2-088 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.51 | 113.81 | AA2-088 | PECO_P7-1_220-0607_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.51 | 113.81 | AA2-088 | PECO_P4_PEACH675_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3198 | 118.51 | 113.11 | AA2-088 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2812 | 113.94 | 112.44 | 1EDGECMA | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 113.01 | 111.82 | AA2-088 | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 112.96 | 111.78 | AA2-088 | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 116.13 | 111.36 | AA2-088 | PECO_P1-2_220-07_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.96 | 111.31 | AA2-088 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.84 | 111.2 | AA2-088 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.87 | 111.18 | AA2-088 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.89 | 111.15 | AA2-088 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.31 | 110.32 | AA2-088 | AP_P2-2_WP-500-DRT16_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.31 | 110.32 | AA2-088 | AP_P2-3_WP-500-DRT20_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.31 | 110.32 | AA2-088 | AP_P2-3_WP-500-465_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.31 | 110.32 | AA2-088 | AP_P1-2_WP-500-005A_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.31 | 110.32 | AA2-088 | AP_P1-2_WP-500-DRT21_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2812 | 114.01 | 112.5 | 1STONECA | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 121.13 | 116.06 | AA2-178 | PECO_P4_PEACH035_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.88 | 114.46 | AA2-178 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.88 | 114.46 | AA2-178 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.54 | 113.84 | AA2-178 | PECO_P7-1_220-0607_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.54 | 113.84 | AA2-178 | PECO_P4_PEACH675_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3198 | 118.55 | 113.15 | AA2-178 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 116.16 | 111.4 | AA2-178 | PECO_P1-2_220-07_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 116 | 111.35 | AA2-178 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.88 | 111.23 | AA2-178 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.91 | 111.21 | AA2-178 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.92 | 111.18 | AA2-178 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2812 | 113.98 | 112.47 | 4E MILL | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 118.33 | 117.47 | AB1-006 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 116.96 | 116.14 | AB1-006 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 120.83 | 115.77 | AB1-006 | PECO_P4_PEACH035_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 115.33 | 114.55 | AB1-006 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.64 | 114.22 | AB1-006 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.64 | 114.22 | AB1-006 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.26 | 113.57 | AB1-006 | PECO_P7-1_220-0607_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.26 | 113.57 | AB1-006 | PECO_P4_PEACH675_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3198 | 118.22 | 112.84 | AB1-006 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2812 | 114.01 | 112.51 | 6PAPERMILL | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 112.84 | 111.64 | AB1-006 | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 112.79 | 111.6 | AB1-006 | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.88 | 111.13 | AB1-006 | PECO_P1-2_220-07_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.7 | 111.06 | AB1-006 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.58 | 110.94 | AB1-006 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.61 | 110.92 | AB1-006 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.64 | 110.91 | AB1-006 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.14 | 110.13 | AB1-006 | AP_P2-3_WP-500-DRT20_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.14 | 110.13 | AB1-006 | AP_P1-2_WP-500-DRT21_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.14 | 110.13 | AB1-006 | AP_P2-2_WP-500-DRT16_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.14 | 110.13 | AB1-006 | AP_P1-2_WP-500-005A_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.14 | 110.13 | AB1-006 | AP_P2-3_WP-500-465_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 607 | 171.99 | 169.45 | AB1-056 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 607 | 170.87 | 169.45 | AB1-056 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 607 | 171.61 | 169.4 | AB1-056 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 607 | 170.5 | 169.4 | AB1-056 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 607 | 171.91 | 169.38 | AB1-056 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 607 | 171.91 | 169.38 | AB1-056 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 607 | 170.79 | 169.38 | AB1-056 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 607 | 170.79 | 169.38 | AB1-056 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 628 | 162.76 | 161.61 | AB1-056 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 628 | 162.4 | 161.56 | AB1-056 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 628 | 162.69 | 161.54 | AB1-056 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 628 | 162.69 | 161.54 | AB1-056 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 628 | 160.05 | 159.32 | AB1-056 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 628 | 159.69 | 159.28 | AB1-056 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 628 | 159.98 | 159.25 | AB1-056 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 628 | 159.98 | 159.25 | AB1-056 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 607 | 156.77 | 154.83 | AB1-056 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 607 | 157.89 | 154.83 | AB1-056 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 628 | 149.14 | 147.46 | AB1-056 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 628 | 146.43 | 145.15 | AB1-056 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 797 | 142.16 | 137.6 | AB1-056 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 797 | 142.47 | 137.57 | AB1-056 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 797 | 142.47 | 137.57 | AB1-056 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 797 | 142.45 | 137.56 | AB1-056 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 137.57 | 134.5 | AB1-056 | AP_P1-2_PE-500-407T_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 137.57 | 134.5 | AB1-056 | DVP_P1-2: LN 514_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 137.57 | 134.48 | AB1-056 | DVP_P4-2: 51482_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 132.45 | 129.36 | AB1-056 | AP_P2-3_PE-500-019C_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 797 | 134.09 | 129.27 | AB1-056 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 814 | 132.56 | 128.02 | AB1-056 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 814 | 133.14 | 127.98 | AB1-056 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 814 | 133.14 | 127.98 | AB1-056 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 814 | 133.12 | 127.97 | AB1-056 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2812 | 113.91 | 112.4 | AA1-018 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 814 | 123.81 | 118.83 | AB1-056 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 119.59 | 118.82 | AB1-056 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 122.63 | 117.52 | AB1-056 | PECO_P4_PEACH035_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 118.21 | 117.49 | AB1-056 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 116.57 | 115.89 | AB1-056 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 120.08 | 115.62 | AB1-056 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 120.08 | 115.62 | AB1-056 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 119.86 | 115.13 | AB1-056 | PECO_P4_PEACH675_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 119.86 | 115.13 | AB1-056 | PECO_P7-1_220-0607_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3198 | 120.26 | 114.78 | AB1-056 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 814 | 117.29 | 114.31 | AB1-056 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 814 | 117.59 | 114.28 | AB1-056 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 814 | 117.59 | 114.28 | AB1-056 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 814 | 117.56 | 114.27 | AB1-056 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2812 | 113.97 | 112.46 | AA1-038 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 114.05 | 112.94 | AB1-056 | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 114 | 112.89 | AB1-056 | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 117.45 | 112.76 | AB1-056 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 117.49 | 112.69 | AB1-056 | PECO_P1-2_220-07_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 117.33 | 112.64 | AB1-056 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 117.36 | 112.62 | AB1-056 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 117.24 | 112.47 | AB1-056 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 112.34 | 111.42 | AB1-056 | AP_P2-2_WP-500-DRT16_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 112.34 | 111.42 | AB1-056 | AP_P2-3_WP-500-DRT20_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 112.34 | 111.42 | AB1-056 | AP_P2-3_WP-500-465_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 112.34 | 111.42 | AB1-056 | AP_P1-2_WP-500-005A_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 112.34 | 111.42 | AB1-056 | AP_P1-2_WP-500-DRT21_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204502 | 27JACKSON | 204514 | 27TMI | 1 | 230 | 227 | 659 | 105.84 | 105.93 | AB1-056 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204502 | 27JACKSON | 204514 | 27TMI | 1 | 230 | 227 | 659 | 105.84 | 105.93 | AB1-056 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204502 | 27JACKSON | 204514 | 27TMI | 1 | 230 | 227 | 659 | 105.9 | 105.93 | AB1-056 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204502 | 27JACKSON | 204514 | 27TMI | 1 | 230 | 227 | 659 | 105.82 | 105.91 | AB1-056 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 814 | 109.18 | 105.84 | AB1-056 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 106.33 | 103.62 | AB1-056 | DVP_P4-2: 560T571_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 106.17 | 103.48 | AB1-056 | DVP_P4-2: H2T560_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 106.16 | 103.46 | AB1-056 | DVP_P4-2: H1T560_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 106.02 | 103.32 | AB1-056 | PEPCO_P1_5070_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220972 | GRANITE1 | 1 | 230 | 232 | 811 | 104.82 | 101.89 | AB1-056 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220972 | GRANITE1 | 1 | 230 | 232 | 811 | 104.57 | 101.61 | AB1-056 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220972 | GRANITE1 | 1 | 230 | 232 | 811 | 104.57 | 101.61 | AB1-056 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 801 | 103.57 | 101.61 | AB1-056 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 801 | 104.06 | 101.57 | AB1-056 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 801 | 104.06 | 101.57 | AB1-056 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 801 | 104.04 | 101.55 | AB1-056 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200065 | PCHBTM2S | 200066 | PCHBTM1N | 2 | 500 | 225 | 3022 | 105.14 | 101.34 | AB1-056 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220953 | HOWARD12 | 220972 | GRANITE1 | 1 | 230 | 232 | 772 | 104.17 | 101.27 | AB1-056 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 106.09 | 101.17 | AB1-056 | PECO_P4_PEACH025_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220953 | HOWARD12 | 220972 | GRANITE1 | 1 | 230 | 232 | 772 | 103.81 | 100.87 | AB1-056 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220953 | HOWARD12 | 220972 | GRANITE1 | 1 | 230 | 232 | 772 | 103.81 | 100.87 | AB1-056 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220973 | GRANITE6 | 1 | 230 | 232 | 811 | 103.07 | 100.22 | AB1-056 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208020 | MANO TR3 | 1 | 230 | 229 | 731 | 97.83 | 100.2 | AB1-056 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208020 | MANO TR3 | 1 | 230 | 229 | 731 | 98.08 | 100.18 | AB1-056 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208020 | MANO TR3 | 1 | 230 | 229 | 731 | 98.08 | 100.18 | AB1-056 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208020 | MANO TR3 | 1 | 230 | 229 | 731 | 98.08 | 100.18 | AB1-056 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3198 | 105.03 | 100.11 | AB1-056 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2812 | 114.6 | 113.13 | AA1-102 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 121.13 | 116.06 | AB1-081 | PECO_P4_PEACH035_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.89 | 114.46 | AB1-081 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.89 | 114.46 | AB1-081 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.54 | 113.84 | AB1-081 | PECO_P4_PEACH675_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.54 | 113.84 | AB1-081 | PECO_P7-1_220-0607_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3198 | 118.56 | 113.16 | AB1-081 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 116.16 | 111.4 | AB1-081 | PECO_P1-2_220-07_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 116 | 111.35 | AB1-081 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.88 | 111.24 | AB1-081 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.91 | 111.22 | AB1-081 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.92 | 111.18 | AB1-081 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 136.5 | 133.44 | AB1-132 | AP_P1-2_PE-500-407T_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 136.5 | 133.44 | AB1-132 | DVP_P1-2: LN 514_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 136.5 | 133.42 | AB1-132 | DVP_P4-2: 51482_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2812 | 113.95 | 112.45 | AA1-139 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 118.47 | 117.62 | AB1-132 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 117.1 | 116.29 | AB1-132 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 121.06 | 116 | AB1-132 | PECO_P4_PEACH035_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 115.47 | 114.7 | AB1-132 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.82 | 114.39 | AB1-132 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.82 | 114.39 | AB1-132 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.47 | 113.78 | AB1-132 | PECO_P4_PEACH675_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.47 | 113.78 | AB1-132 | PECO_P7-1_220-0607_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3198 | 118.47 | 113.08 | AB1-132 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2812 | 114 | 112.5 | AA2-088 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 112.98 | 111.79 | AB1-132 | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 112.92 | 111.74 | AB1-132 | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 116.09 | 111.33 | AB1-132 | PECO_P1-2_220-07_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.92 | 111.28 | AB1-132 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.81 | 111.16 | AB1-132 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.84 | 111.14 | AB1-132 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.85 | 111.12 | AB1-132 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.28 | 110.28 | AB1-132 | AP_P2-2_WP-500-DRT16_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.28 | 110.28 | AB1-132 | AP_P1-2_WP-500-005A_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.28 | 110.28 | AB1-132 | AP_P1-2_WP-500-DRT21_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.28 | 110.28 | AB1-132 | AP_P2-3_WP-500-DRT20_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.28 | 110.28 | AB1-132 | AP_P2-3_WP-500-465_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 607 | 171.21 | 168.64 | AB2-036 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 607 | 170.1 | 168.64 | AB2-036 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 607 | 170.85 | 168.6 | AB2-036 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 607 | 169.74 | 168.6 | AB2-036 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 607 | 171.13 | 168.56 | AB2-036 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 607 | 171.13 | 168.56 | AB2-036 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 607 | 170.02 | 168.56 | AB2-036 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 607 | 170.02 | 168.56 | AB2-036 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 628 | 162.02 | 160.82 | AB2-036 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 628 | 161.67 | 160.78 | AB2-036 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 628 | 161.95 | 160.75 | AB2-036 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 628 | 161.95 | 160.75 | AB2-036 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 628 | 159.31 | 158.53 | AB2-036 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 628 | 158.96 | 158.49 | AB2-036 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 628 | 159.23 | 158.46 | AB2-036 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 628 | 159.23 | 158.46 | AB2-036 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 607 | 155.99 | 154.02 | AB2-036 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 607 | 157.1 | 154.02 | AB2-036 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 628 | 148.38 | 146.67 | AB2-036 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 628 | 145.67 | 144.37 | AB2-036 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 137.31 | 134.24 | AB2-036 | DVP_P1-2: LN 514_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 137.31 | 134.24 | AB2-036 | AP_P1-2_PE-500-407T_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 137.31 | 134.22 | AB2-036 | DVP_P4-2: 51482_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 132.19 | 129.1 | AB2-036 | AP_P2-3_PE-500-019C_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2812 | 113.83 | 112.31 | AB1-006 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 119.25 | 118.46 | AB2-036 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 117.87 | 117.12 | AB2-036 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 122.08 | 116.99 | AB2-036 | PECO_P4_PEACH035_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 116.24 | 115.52 | AB2-036 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 119.67 | 115.22 | AB2-036 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 119.67 | 115.22 | AB2-036 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 119.39 | 114.67 | AB2-036 | PECO_P7-1_220-0607_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 119.39 | 114.67 | AB2-036 | PECO_P4_PEACH675_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3198 | 119.65 | 114.2 | AB2-036 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2812 | 115.08 | 113.64 | AB1-056 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 113.72 | 112.58 | AB2-036 | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 113.67 | 112.54 | AB2-036 | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 116.94 | 112.26 | AB2-036 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 117.02 | 112.23 | AB2-036 | PECO_P1-2_220-07_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 116.83 | 112.15 | AB2-036 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 116.86 | 112.13 | AB2-036 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 116.77 | 112.01 | AB2-036 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 112.02 | 111.07 | AB2-036 | AP_P1-2_WP-500-DRT21_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 112.02 | 111.07 | AB2-036 | AP_P1-2_WP-500-005A_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 112.02 | 111.07 | AB2-036 | AP_P2-3_WP-500-465_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 112.02 | 111.07 | AB2-036 | AP_P2-3_WP-500-DRT20_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 112.02 | 111.07 | AB2-036 | AP_P2-2_WP-500-DRT16_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 106.09 | 103.38 | AB2-036 | DVP_P4-2: 560T571_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 105.93 | 103.24 | AB2-036 | DVP_P4-2: H2T560_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 105.92 | 103.23 | AB2-036 | DVP_P4-2: H1T560_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 105.78 | 103.08 | AB2-036 | PEPCO_P1_5070_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200065 | PCHBTM2S | 200066 | PCHBTM1N | 2 | 500 | 225 | 3022 | 104.42 | 100.64 | AB2-036 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 105.32 | 100.44 | AB2-036 | PECO_P4_PEACH025_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 607 | 171.27 | 168.71 | AB2-037 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 607 | 170.17 | 168.71 | AB2-037 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 607 | 170.91 | 168.67 | AB2-037 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 607 | 169.81 | 168.67 | AB2-037 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 607 | 171.19 | 168.63 | AB2-037 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 607 | 171.19 | 168.63 | AB2-037 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 607 | 170.09 | 168.63 | AB2-037 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 607 | 170.09 | 168.63 | AB2-037 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 628 | 162.09 | 160.89 | AB2-037 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 628 | 161.74 | 160.85 | AB2-037 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 628 | 162.01 | 160.82 | AB2-037 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 628 | 162.01 | 160.82 | AB2-037 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 628 | 159.38 | 158.6 | AB2-037 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 628 | 159.03 | 158.56 | AB2-037 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 628 | 159.3 | 158.53 | AB2-037 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 628 | 159.3 | 158.53 | AB2-037 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 607 | 156.06 | 154.09 | AB2-037 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 607 | 157.16 | 154.09 | AB2-037 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 628 | 148.45 | 146.74 | AB2-037 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 628 | 145.74 | 144.43 | AB2-037 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 137.35 | 134.28 | AB2-037 | AP_P1-2_PE-500-407T_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 137.35 | 134.28 | AB2-037 | DVP_P1-2: LN 514_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 137.35 | 134.26 | AB2-037 | DVP_P4-2: 51482_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 132.23 | 129.14 | AB2-037 | AP_P2-3_PE-500-019C_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 814 | 132.25 | 127.72 | AB2-037 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 814 | 132.81 | 127.66 | AB2-037 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 814 | 132.81 | 127.66 | AB2-037 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 814 | 132.79 | 127.65 | AB2-037 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2812 | 113.97 | 112.46 | AB1-132 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 119.3 | 118.51 | AB2-037 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 814 | 123.47 | 118.51 | AB2-037 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 117.92 | 117.18 | AB2-037 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 122.17 | 117.08 | AB2-037 | PECO_P4_PEACH035_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 116.29 | 115.58 | AB2-037 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 119.74 | 115.28 | AB2-037 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 119.74 | 115.28 | AB2-037 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 119.47 | 114.75 | AB2-037 | PECO_P7-1_220-0607_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 119.47 | 114.75 | AB2-037 | PECO_P4_PEACH675_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3198 | 119.75 | 114.3 | AB2-037 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2812 | 114.74 | 113.28 | AB2-036 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 113.77 | 112.64 | AB2-037 | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 113.72 | 112.59 | AB2-037 | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 117.02 | 112.34 | AB2-037 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 117.09 | 112.31 | AB2-037 | PECO_P1-2_220-07_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 116.91 | 112.23 | AB2-037 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 116.94 | 112.21 | AB2-037 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 116.85 | 112.09 | AB2-037 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 112.07 | 111.13 | AB2-037 | AP_P2-3_WP-500-465_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 112.07 | 111.13 | AB2-037 | AP_P1-2_WP-500-DRT21_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 112.07 | 111.13 | AB2-037 | AP_P2-3_WP-500-DRT20_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 112.07 | 111.13 | AB2-037 | AP_P1-2_WP-500-005A_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 112.07 | 111.13 | AB2-037 | AP_P2-2_WP-500-DRT16_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 106.13 | 103.42 | AB2-037 | DVP_P4-2: 560T571_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 105.96 | 103.28 | AB2-037 | DVP_P4-2: H2T560_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 105.96 | 103.27 | AB2-037 | DVP_P4-2: H1T560_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 105.82 | 103.12 | AB2-037 | PEPCO_P1_5070_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200065 | PCHBTM2S | 200066 | PCHBTM1N | 2 | 500 | 225 | 3022 | 104.55 | 100.76 | AB2-037 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 105.44 | 100.56 | AB2-037 | PECO_P4_PEACH025_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2812 | 114.79 | 113.34 | AB2-037 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 121.13 | 116.07 | AB2-040 | PECO_P4_PEACH035_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.89 | 114.46 | AB2-040 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.89 | 114.46 | AB2-040 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.54 | 113.84 | AB2-040 | PECO_P4_PEACH675_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.54 | 113.84 | AB2-040 | PECO_P7-1_220-0607_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3198 | 118.56 | 113.16 | AB2-040 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 116.16 | 111.4 | AB2-040 | PECO_P1-2_220-07_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 116 | 111.35 | AB2-040 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.88 | 111.24 | AB2-040 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.91 | 111.22 | AB2-040 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.92 | 111.18 | AB2-040 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2812 | 114.01 | 112.51 | AB2-059 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 118.52 | 117.67 | AB2-059 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 117.15 | 116.34 | AB2-059 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 121.1 | 116.04 | AB2-059 | PECO_P4_PEACH035_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 115.51 | 114.75 | AB2-059 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.86 | 114.43 | AB2-059 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.86 | 114.43 | AB2-059 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.51 | 113.81 | AB2-059 | PECO_P7-1_220-0607_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.51 | 113.81 | AB2-059 | PECO_P4_PEACH675_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3198 | 118.52 | 113.12 | AB2-059 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2812 | 113.82 | 112.3 | AB2-070 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 113.02 | 111.83 | AB2-059 | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 112.97 | 111.79 | AB2-059 | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 116.13 | 111.37 | AB2-059 | PECO_P1-2_220-07_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.97 | 111.32 | AB2-059 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.85 | 111.2 | AB2-059 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.88 | 111.18 | AB2-059 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.89 | 111.15 | AB2-059 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.33 | 110.33 | AB2-059 | AP_P1-2_WP-500-DRT21_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.33 | 110.33 | AB2-059 | AP_P1-2_WP-500-005A_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.33 | 110.33 | AB2-059 | AP_P2-3_WP-500-DRT20_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.33 | 110.33 | AB2-059 | AP_P2-2_WP-500-DRT16_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.33 | 110.33 | AB2-059 | AP_P2-3_WP-500-465_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2812 | 113.98 | 112.47 | AB2-085 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 121.13 | 116.06 | AB2-060 | PECO_P4_PEACH035_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.89 | 114.46 | AB2-060 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.89 | 114.46 | AB2-060 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.54 | 113.84 | AB2-060 | PECO_P4_PEACH675_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.54 | 113.84 | AB2-060 | PECO_P7-1_220-0607_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3198 | 118.56 | 113.16 | AB2-060 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 116.16 | 111.4 | AB2-060 | PECO_P1-2_220-07_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 116 | 111.35 | AB2-060 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.88 | 111.24 | AB2-060 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.91 | 111.22 | AB2-060 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.92 | 111.18 | AB2-060 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2812 | 114 | 112.5 | AB2-100 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 118.32 | 117.46 | AB2-070 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 116.95 | 116.14 | AB2-070 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 120.82 | 115.77 | AB2-070 | PECO_P4_PEACH035_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 115.32 | 114.54 | AB2-070 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.64 | 114.22 | AB2-070 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.64 | 114.22 | AB2-070 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.26 | 113.56 | AB2-070 | PECO_P4_PEACH675_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.26 | 113.56 | AB2-070 | PECO_P7-1_220-0607_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3198 | 118.22 | 112.83 | AB2-070 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2812 | 113.91 | 112.4 | AB2-134 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 112.83 | 111.64 | AB2-070 | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 112.78 | 111.59 | AB2-070 | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.88 | 111.12 | AB2-070 | PECO_P1-2_220-07_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.69 | 111.05 | AB2-070 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.58 | 110.94 | AB2-070 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.6 | 110.92 | AB2-070 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.64 | 110.91 | AB2-070 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.13 | 110.12 | AB2-070 | AP_P2-2_WP-500-DRT16_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.13 | 110.12 | AB2-070 | AP_P1-2_WP-500-005A_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.13 | 110.12 | AB2-070 | AP_P1-2_WP-500-DRT21_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.13 | 110.12 | AB2-070 | AP_P2-3_WP-500-DRT20_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.13 | 110.12 | AB2-070 | AP_P2-3_WP-500-465_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 105.3 | 102.61 | AB2-070 | DVP_P4-2: 560T571_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 105.14 | 102.47 | AB2-070 | DVP_P4-2: H2T560_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 105.14 | 102.45 | AB2-070 | DVP_P4-2: H1T560_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 104.99 | 102.31 | AB2-070 | PEPCO_P1_5070_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2812 | 114.36 | 112.87 | AB2-135 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 118.48 | 117.63 | AB2-085 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 117.11 | 116.3 | AB2-085 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 121.01 | 115.94 | AB2-085 | PECO_P4_PEACH035_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 115.48 | 114.71 | AB2-085 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.8 | 114.38 | AB2-085 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.8 | 114.38 | AB2-085 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.43 | 113.74 | AB2-085 | PECO_P7-1_220-0607_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.43 | 113.74 | AB2-085 | PECO_P4_PEACH675_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3198 | 118.43 | 113.03 | AB2-085 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2812 | 113.98 | 112.47 | AB2-158 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 112.98 | 111.8 | AB2-085 | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 112.93 | 111.75 | AB2-085 | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 116.05 | 111.29 | AB2-085 | PECO_P1-2_220-07_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.88 | 111.24 | AB2-085 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.77 | 111.12 | AB2-085 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.79 | 111.1 | AB2-085 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.82 | 111.08 | AB2-085 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.28 | 110.29 | AB2-085 | AP_P2-3_WP-500-DRT20_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.28 | 110.29 | AB2-085 | AP_P1-2_WP-500-DRT21_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.28 | 110.29 | AB2-085 | AP_P2-2_WP-500-DRT16_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.28 | 110.29 | AB2-085 | AP_P2-3_WP-500-465_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.28 | 110.29 | AB2-085 | AP_P1-2_WP-500-005A_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2812 | 113.81 | 112.29 | AB2-160 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 118.51 | 117.66 | AB2-100 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 117.14 | 116.33 | AB2-100 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 121.1 | 116.03 | AB2-100 | PECO_P4_PEACH035_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 115.5 | 114.74 | AB2-100 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.85 | 114.42 | AB2-100 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.85 | 114.42 | AB2-100 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.51 | 113.81 | AB2-100 | PECO_P7-1_220-0607_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.51 | 113.81 | AB2-100 | PECO_P4_PEACH675_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3198 | 118.51 | 113.12 | AB2-100 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2812 | 113.88 | 112.37 | AB2-190 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 113.01 | 111.82 | AB2-100 | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 112.96 | 111.78 | AB2-100 | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 116.13 | 111.37 | AB2-100 | PECO_P1-2_220-07_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.96 | 111.31 | AB2-100 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.84 | 111.2 | AB2-100 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.87 | 111.18 | AB2-100 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.89 | 111.15 | AB2-100 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.32 | 110.32 | AB2-100 | AP_P2-2_WP-500-DRT16_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.32 | 110.32 | AB2-100 | AP_P2-3_WP-500-DRT20_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.32 | 110.32 | AB2-100 | AP_P2-3_WP-500-465_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.32 | 110.32 | AB2-100 | AP_P1-2_WP-500-005A_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.32 | 110.32 | AB2-100 | AP_P1-2_WP-500-DRT21_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2812 | 114 | 112.5 | AC1-033 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 121.48 | 116.4 | AB2-133 | PECO_P4_PEACH035_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 119.19 | 114.76 | AB2-133 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 119.19 | 114.76 | AB2-133 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.87 | 114.16 | AB2-133 | PECO_P4_PEACH675_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.87 | 114.16 | AB2-133 | PECO_P7-1_220-0607_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3198 | 118.97 | 113.55 | AB2-133 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 116.49 | 111.71 | AB2-133 | PECO_P1-2_220-07_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 116.36 | 111.7 | AB2-133 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 116.24 | 111.58 | AB2-133 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 116.27 | 111.56 | AB2-133 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 116.25 | 111.5 | AB2-133 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 136.38 | 133.31 | AB2-134 | AP_P1-2_PE-500-407T_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 136.38 | 133.31 | AB2-134 | DVP_P1-2: LN 514_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 136.38 | 133.29 | AB2-134 | DVP_P4-2: 51482_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 131.27 | 128.19 | AB2-134 | AP_P2-3_PE-500-019C_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2812 | 113.66 | 112.14 | AC1-043 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 118.41 | 117.56 | AB2-134 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 117.04 | 116.23 | AB2-134 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 121.02 | 115.95 | AB2-134 | PECO_P4_PEACH035_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 115.41 | 114.63 | AB2-134 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.76 | 114.34 | AB2-134 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.76 | 114.34 | AB2-134 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.42 | 113.73 | AB2-134 | PECO_P4_PEACH675_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.42 | 113.73 | AB2-134 | PECO_P7-1_220-0607_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3198 | 118.41 | 113.02 | AB2-134 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2812 | 113.82 | 112.3 | AC1-053 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 112.92 | 111.73 | AB2-134 | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 112.87 | 111.68 | AB2-134 | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 116.04 | 111.28 | AB2-134 | PECO_P1-2_220-07_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.87 | 111.23 | AB2-134 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.75 | 111.11 | AB2-134 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.78 | 111.09 | AB2-134 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.8 | 111.07 | AB2-134 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.22 | 110.22 | AB2-134 | AP_P1-2_WP-500-DRT21_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.22 | 110.22 | AB2-134 | AP_P1-2_WP-500-005A_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.22 | 110.22 | AB2-134 | AP_P2-3_WP-500-465_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.22 | 110.22 | AB2-134 | AP_P2-2_WP-500-DRT16_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.22 | 110.22 | AB2-134 | AP_P2-3_WP-500-DRT20_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 105.26 | 102.57 | AB2-134 | DVP_P4-2: 560T571_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 105.1 | 102.42 | AB2-134 | DVP_P4-2: H2T560_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 105.09 | 102.41 | AB2-134 | DVP_P4-2: H1T560_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 104.95 | 102.26 | AB2-134 | PEPCO_P1_5070_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2812 | 113.89 | 112.38 | AC1-065 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 118.87 | 118.04 | AB2-135 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 117.49 | 116.71 | AB2-135 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 121.51 | 116.44 | AB2-135 | PECO_P4_PEACH035_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 115.85 | 115.11 | AB2-135 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 119.22 | 114.79 | AB2-135 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 119.22 | 114.79 | AB2-135 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.9 | 114.19 | AB2-135 | PECO_P7-1_220-0607_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.9 | 114.19 | AB2-135 | PECO_P4_PEACH675_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3198 | 119.01 | 113.58 | AB2-135 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2812 | 113.95 | 112.45 | AC1-078 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 113.35 | 112.19 | AB2-135 | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 113.3 | 112.14 | AB2-135 | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 116.52 | 111.74 | AB2-135 | PECO_P1-2_220-07_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 116.39 | 111.73 | AB2-135 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 116.27 | 111.61 | AB2-135 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 116.3 | 111.59 | AB2-135 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 116.28 | 111.53 | AB2-135 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.73 | 110.57 | AB2-135 | BG_P7_GRNITE_HIRDG_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 110.43 | 109.23 | AB2-135 | BG_P7_NWEST_GRNITE_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 110.11 | 108.61 | AB2-135 | PN_P2-3_PN-500-997-DRT-074_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 110.11 | 108.61 | AB2-135 | PN_P2-3_PN-500-997-DRT-073_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 110.11 | 108.61 | AB2-135 | PN_P1-2_PN-500-007_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2812 | 113.98 | 112.47 | AC1-083 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 121.47 | 116.39 | AB2-136 | PECO_P4_PEACH035_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 119.19 | 114.75 | AB2-136 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 119.19 | 114.75 | AB2-136 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.86 | 114.15 | AB2-136 | PECO_P4_PEACH675_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.86 | 114.15 | AB2-136 | PECO_P7-1_220-0607_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3198 | 118.95 | 113.53 | AB2-136 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 116.48 | 111.7 | AB2-136 | PECO_P1-2_220-07_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 116.34 | 111.68 | AB2-136 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 116.22 | 111.57 | AB2-136 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 116.25 | 111.55 | AB2-136 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 116.24 | 111.49 | AB2-136 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 136.43 | 133.36 | AB2-158 | DVP_P1-2: LN 514_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 136.43 | 133.36 | AB2-158 | AP_P1-2_PE-500-407T_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 136.43 | 133.35 | AB2-158 | DVP_P4-2: 51482_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 131.33 | 128.25 | AB2-158 | AP_P2-3_PE-500-019C_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2812 | 113.7 | 112.18 | AC1-085 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 118.48 | 117.63 | AB2-158 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 117.11 | 116.3 | AB2-158 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 121.09 | 116.02 | AB2-158 | PECO_P4_PEACH035_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 115.47 | 114.71 | AB2-158 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.83 | 114.4 | AB2-158 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.83 | 114.4 | AB2-158 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.49 | 113.79 | AB2-158 | PECO_P4_PEACH675_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.49 | 113.79 | AB2-158 | PECO_P7-1_220-0607_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3198 | 118.49 | 113.1 | AB2-158 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2812 | 113.86 | 112.35 | AC1-086 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 112.98 | 111.8 | AB2-158 | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 112.93 | 111.75 | AB2-158 | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 116.11 | 111.35 | AB2-158 | PECO_P1-2_220-07_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.94 | 111.3 | AB2-158 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.83 | 111.18 | AB2-158 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.86 | 111.16 | AB2-158 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.87 | 111.13 | AB2-158 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.29 | 110.29 | AB2-158 | AP_P2-3_WP-500-DRT20_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.29 | 110.29 | AB2-158 | AP_P1-2_WP-500-DRT21_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.29 | 110.29 | AB2-158 | AP_P2-3_WP-500-465_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.29 | 110.29 | AB2-158 | AP_P2-2_WP-500-DRT16_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.29 | 110.29 | AB2-158 | AP_P1-2_WP-500-005A_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 136.2 | 133.13 | AB2-160 | AP_P1-2_PE-500-407T_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 136.2 | 133.13 | AB2-160 | DVP_P1-2: LN 514_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 136.2 | 133.11 | AB2-160 | DVP_P4-2: 51482_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 131.1 | 128.02 | AB2-160 | AP_P2-3_PE-500-019C_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2812 | 114 | 112.49 | AC1-089 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 118.31 | 117.45 | AB2-160 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 116.94 | 116.12 | AB2-160 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 120.93 | 115.87 | AB2-160 | PECO_P4_PEACH035_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 115.31 | 114.53 | AB2-160 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.67 | 114.24 | AB2-160 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.67 | 114.24 | AB2-160 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.33 | 113.64 | AB2-160 | PECO_P4_PEACH675_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.33 | 113.64 | AB2-160 | PECO_P7-1_220-0607_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3198 | 118.3 | 112.92 | AB2-160 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2812 | 113.87 | 112.36 | AC1-120 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 112.82 | 111.62 | AB2-160 | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 112.77 | 111.58 | AB2-160 | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.96 | 111.2 | AB2-160 | PECO_P1-2_220-07_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.78 | 111.13 | AB2-160 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.66 | 111.02 | AB2-160 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.69 | 111 | AB2-160 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.72 | 110.98 | AB2-160 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.13 | 110.12 | AB2-160 | AP_P2-2_WP-500-DRT16_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.13 | 110.12 | AB2-160 | AP_P1-2_WP-500-005A_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.13 | 110.12 | AB2-160 | AP_P1-2_WP-500-DRT21_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.13 | 110.12 | AB2-160 | AP_P2-3_WP-500-465_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.13 | 110.12 | AB2-160 | AP_P2-3_WP-500-DRT20_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 105.11 | 102.42 | AB2-160 | DVP_P4-2: 560T571_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 104.95 | 102.28 | AB2-160 | DVP_P4-2: H2T560_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 104.95 | 102.26 | AB2-160 | DVP_P4-2: H1T560_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 104.8 | 102.12 | AB2-160 | PEPCO_P1_5070_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.9 | 114.47 | AB2-169 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.9 | 114.47 | AB2-169 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 116.01 | 111.36 | AB2-169 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.89 | 111.25 | AB2-169 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.92 | 111.23 | AB2-169 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.7 | 111.07 | AB2-169 | PECO_P4_NOTTI85_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.63 | 111.06 | AB2-169 | PECO_P1-2_220-08_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.59 | 111.02 | AB2-169 | PECO_P4_COOPR125_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.35 | 110.86 | AB2-169 | PECO_P1-2_220-93_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 114.66 | 110.27 | AB2-169 | PL_05_P71_000906_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2812 | 112.7 | 111.12 | AC1-158 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 121.46 | 116.39 | AB2-172 | PECO_P4_PEACH035_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 119.18 | 114.75 | AB2-172 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 119.18 | 114.75 | AB2-172 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.85 | 114.15 | AB2-172 | PECO_P4_PEACH675_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.85 | 114.15 | AB2-172 | PECO_P7-1_220-0607_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3198 | 118.95 | 113.53 | AB2-172 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 116.48 | 111.7 | AB2-172 | PECO_P1-2_220-07_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 116.34 | 111.68 | AB2-172 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 116.22 | 111.57 | AB2-172 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 116.25 | 111.55 | AB2-172 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 116.23 | 111.49 | AB2-172 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2812 | 113.72 | 112.19 | AC1-161 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 121.13 | 116.07 | AB2-174 | PECO_P4_PEACH035_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.89 | 114.46 | AB2-174 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.89 | 114.46 | AB2-174 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.55 | 113.85 | AB2-174 | PECO_P4_PEACH675_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.55 | 113.85 | AB2-174 | PECO_P7-1_220-0607_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 116.17 | 111.4 | AB2-174 | PECO_P1-2_220-07_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 116 | 111.35 | AB2-174 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.89 | 111.24 | AB2-174 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.91 | 111.22 | AB2-174 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.93 | 111.19 | AB2-174 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2812 | 113.53 | 112 | AC1-164 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 121.45 | 116.37 | AB2-179 | PECO_P4_PEACH035_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 119.17 | 114.74 | AB2-179 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 119.17 | 114.74 | AB2-179 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.84 | 114.14 | AB2-179 | PECO_P7-1_220-0607_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.84 | 114.14 | AB2-179 | PECO_P4_PEACH675_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3198 | 118.94 | 113.52 | AB2-179 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 116.46 | 111.69 | AB2-179 | PECO_P1-2_220-07_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 116.33 | 111.67 | AB2-179 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 116.22 | 111.56 | AB2-179 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 116.25 | 111.54 | AB2-179 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 116.22 | 111.47 | AB2-179 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 136.33 | 133.26 | AB2-190 | AP_P1-2_PE-500-407T_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 136.33 | 133.26 | AB2-190 | DVP_P1-2: LN 514_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 136.33 | 133.24 | AB2-190 | DVP_P4-2: 51482_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 131.22 | 128.14 | AB2-190 | AP_P2-3_PE-500-019C_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2812 | 113.85 | 112.33 | AC1-189 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 118.38 | 117.52 | AB2-190 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 117.01 | 116.2 | AB2-190 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 120.99 | 115.93 | AB2-190 | PECO_P4_PEACH035_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 115.38 | 114.6 | AB2-190 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.73 | 114.31 | AB2-190 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.73 | 114.31 | AB2-190 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.39 | 113.7 | AB2-190 | PECO_P4_PEACH675_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.39 | 113.7 | AB2-190 | PECO_P7-1_220-0607_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3198 | 118.38 | 112.98 | AB2-190 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2812 | 113.8 | 112.28 | AC1-191 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 112.89 | 111.69 | AB2-190 | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 112.84 | 111.65 | AB2-190 | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 116.01 | 111.26 | AB2-190 | PECO_P1-2_220-07_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.84 | 111.19 | AB2-190 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.72 | 111.08 | AB2-190 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.75 | 111.06 | AB2-190 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.78 | 111.04 | AB2-190 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.19 | 110.19 | AB2-190 | AP_P2-3_WP-500-DRT20_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.19 | 110.19 | AB2-190 | AP_P2-2_WP-500-DRT16_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.19 | 110.19 | AB2-190 | AP_P1-2_WP-500-DRT21_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.19 | 110.19 | AB2-190 | AP_P1-2_WP-500-005A_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.19 | 110.19 | AB2-190 | AP_P2-3_WP-500-465_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 105.22 | 102.52 | AB2-190 | DVP_P4-2: 560T571_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 105.05 | 102.38 | AB2-190 | DVP_P4-2: H2T560_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 105.05 | 102.37 | AB2-190 | DVP_P4-2: H1T560_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 104.91 | 102.22 | AB2-190 | PEPCO_P1_5070_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2812 | 114 | 112.49 | AC1-216 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 118.51 | 117.66 | AC1-033 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 117.14 | 116.33 | AC1-033 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 121.04 | 115.98 | AC1-033 | PECO_P4_PEACH035_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 115.5 | 114.74 | AC1-033 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.83 | 114.41 | AC1-033 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.83 | 114.41 | AC1-033 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.47 | 113.77 | AC1-033 | PECO_P4_PEACH675_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.47 | 113.77 | AC1-033 | PECO_P7-1_220-0607_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3198 | 118.47 | 113.07 | AC1-033 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2812 | 113.92 | 112.41 | AC1-221 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 113.01 | 111.82 | AC1-033 | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 112.96 | 111.78 | AC1-033 | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 116.09 | 111.33 | AC1-033 | PECO_P1-2_220-07_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.92 | 111.27 | AC1-033 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.8 | 111.16 | AC1-033 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.83 | 111.14 | AC1-033 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.85 | 111.11 | AC1-033 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.31 | 110.32 | AC1-033 | AP_P1-2_WP-500-005A_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.31 | 110.32 | AC1-033 | AP_P2-2_WP-500-DRT16_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.31 | 110.32 | AC1-033 | AP_P2-3_WP-500-DRT20_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.31 | 110.32 | AC1-033 | AP_P2-3_WP-500-465_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.31 | 110.32 | AC1-033 | AP_P1-2_WP-500-DRT21_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 116.01 | 111.36 | AC1-034 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.9 | 111.25 | AC1-034 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.92 | 111.23 | AC1-034 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.7 | 111.07 | AC1-034 | PECO_P4_NOTTI85_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.63 | 111.06 | AC1-034 | PECO_P1-2_220-08_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.59 | 111.02 | AC1-034 | PECO_P4_COOPR125_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.35 | 110.87 | AC1-034 | PECO_P1-2_220-93_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 114.66 | 110.27 | AC1-034 | PL_05_P71_000906_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 607 | 169 | 166.29 | AC1-043 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 607 | 167.93 | 166.29 | AC1-043 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 607 | 168.67 | 166.28 | AC1-043 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 607 | 167.6 | 166.28 | AC1-043 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 607 | 168.92 | 166.22 | AC1-043 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 607 | 168.92 | 166.22 | AC1-043 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 607 | 167.86 | 166.22 | AC1-043 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 607 | 167.86 | 166.22 | AC1-043 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 628 | 159.92 | 158.55 | AC1-043 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 628 | 159.6 | 158.54 | AC1-043 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 628 | 159.85 | 158.48 | AC1-043 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 628 | 159.85 | 158.48 | AC1-043 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 628 | 157.22 | 156.26 | AC1-043 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 628 | 156.9 | 156.25 | AC1-043 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 628 | 157.14 | 156.19 | AC1-043 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 628 | 157.14 | 156.19 | AC1-043 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 680 | 140.85 | 137.92 | AC1-043 | PEPCO_P4_PP19_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 135.74 | 132.67 | AC1-043 | DVP_P1-2: LN 514_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 135.74 | 132.67 | AC1-043 | AP_P1-2_PE-500-407T_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 135.74 | 132.66 | AC1-043 | DVP_P4-2: 51482_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 2 | 230 | 233 | 680 | 134.39 | 131.57 | AC1-043 | PEPCO_P1_PP1_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 680 | 134.39 | 131.57 | AC1-043 | PEPCO_P1_PP2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 130.65 | 127.57 | AC1-043 | AP_P2-3_PE-500-019C_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 2 | 230 | 233 | 680 | 127.89 | 124.98 | AC1-043 | AP_P1-2_PE-500-407T_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 680 | 127.89 | 124.98 | AC1-043 | AP_P1-2_PE-500-407T_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 680 | 127.89 | 124.98 | AC1-043 | DVP_P1-2: LN 514_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 2 | 230 | 233 | 680 | 127.89 | 124.98 | AC1-043 | DVP_P1-2: LN 514_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 2 | 230 | 233 | 680 | 127.89 | 124.98 | AC1-043 | DVP_P4-2: 51482_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 680 | 127.89 | 124.98 | AC1-043 | DVP_P4-2: 51482_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2812 | 113.92 | 112.41 | AC1-222 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 118.16 | 117.29 | AC1-043 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 116.8 | 115.97 | AC1-043 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 2 | 230 | 233 | 680 | 118.84 | 115.92 | AC1-043 | AP_P2-3_PE-500-019C_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 680 | 118.84 | 115.92 | AC1-043 | AP_P2-3_PE-500-019C_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 120.83 | 115.77 | AC1-043 | PECO_P4_PEACH035_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 115.16 | 114.37 | AC1-043 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.54 | 114.12 | AC1-043 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.54 | 114.12 | AC1-043 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.22 | 113.53 | AC1-043 | PECO_P4_PEACH675_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.22 | 113.53 | AC1-043 | PECO_P7-1_220-0607_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3198 | 118.16 | 112.78 | AC1-043 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2812 | 113.9 | 112.39 | AC2-012 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 112.68 | 111.47 | AC1-043 | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 112.63 | 111.43 | AC1-043 | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.84 | 111.09 | AC1-043 | PECO_P1-2_220-07_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.65 | 111.01 | AC1-043 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.53 | 110.9 | AC1-043 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.56 | 110.88 | AC1-043 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.6 | 110.87 | AC1-043 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 110.98 | 109.97 | AC1-043 | AP_P2-2_WP-500-DRT16_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 110.98 | 109.97 | AC1-043 | AP_P1-2_WP-500-DRT21_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 110.98 | 109.97 | AC1-043 | AP_P1-2_WP-500-005A_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 110.98 | 109.97 | AC1-043 | AP_P2-3_WP-500-465_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 110.98 | 109.97 | AC1-043 | AP_P2-3_WP-500-DRT20_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 104.84 | 102.15 | AC1-043 | DVP_P4-2: 560T571_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 104.68 | 102.01 | AC1-043 | DVP_P4-2: H2T560_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 104.67 | 101.99 | AC1-043 | DVP_P4-2: H1T560_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 104.53 | 101.85 | AC1-043 | PEPCO_P1_5070_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 235463 | 01TANEY | 1 | 138 | 227/201 | 268 | 166.07 | 162.31 | AC1-048 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 235463 | 01TANEY | 1 | 138 | 227/201 | 268 | 166.07 | 162.31 | AC1-048 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 235463 | 01TANEY | 1 | 138 | 227/201 | 268 | 166 | 162.24 | AC1-048 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2812 | 114.01 | 112.51 | AC2-059 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 235463 | 01TANEY | 1 | 138 | 227/201 | 268 | 140.6 | 133.95 | AC1-048 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 235463 | 01TANEY | 1 | 138 | 227/201 | 268 | 140.6 | 133.95 | AC1-048 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 235463 | 01TANEY | 1 | 138 | 227/201 | 268 | 140.59 | 133.95 | AC1-048 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 235463 | 01TANEY | 1 | 138 | 227/201 | 268 | 140.67 | 133.94 | AC1-048 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 282 | 132.78 | 132.26 | AC1-048 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 282 | 132.78 | 132.26 | AC1-048 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 282 | 132.72 | 132.19 | AC1-048 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 204529 | 27GERMANTN | 1 | 138/115 | 227 | 345 | 129.01 | 131.8 | AC1-048 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 204529 | 27GERMANTN | 1 | 138/115 | 227 | 345 | 129.01 | 131.8 | AC1-048 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 204529 | 27GERMANTN | 1 | 138/115 | 227 | 345 | 128.95 | 131.74 | AC1-048 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 235463 | 01TANEY | 1 | 138 | 227/201 | 268 | 132.62 | 130.48 | AC1-048 | PEPCO_P4_PP41_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 235463 | 01TANEY | 1 | 138 | 227/201 | 268 | 129.91 | 128.29 | AC1-048 | AP_P2-3_PE-500-019B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204538 | 27STRABAN | 204544 | 27LINCOLN | 1 | 115 | 227 | 313 | 126.03 | 126.61 | AC1-048 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204538 | 27STRABAN | 204544 | 27LINCOLN | 1 | 115 | 227 | 313 | 126.03 | 126.61 | AC1-048 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 235463 | 01TANEY | 1 | 138 | 227/201 | 268 | 128.44 | 126.56 | AC1-048 | AP_P1-2_PE-500-406T_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204538 | 27STRABAN | 204544 | 27LINCOLN | 1 | 115 | 227 | 313 | 125.97 | 126.54 | AC1-048 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204529 | 27GERMANTN | 204538 | 27STRABAN | 1 | 115 | 227 | 313 | 122.74 | 123.88 | AC1-048 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204529 | 27GERMANTN | 204538 | 27STRABAN | 1 | 115 | 227 | 313 | 122.74 | 123.88 | AC1-048 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204529 | 27GERMANTN | 204538 | 27STRABAN | 1 | 115 | 227 | 313 | 122.67 | 123.81 | AC1-048 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 204550 | 27ORRTANNA | 1 | 115 | 227 | 160 | 114.88 | 113.45 | AC1-048 | ME_P1-2_ME-115-068_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204539 | 27HUNTRSTN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 282 | 113.34 | 112.67 | AC1-048 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204539 | 27HUNTRSTN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 282 | 113.34 | 112.67 | AC1-048 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204539 | 27HUNTRSTN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 282 | 113.28 | 112.6 | AC1-048 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 204550 | 27ORRTANNA | 1 | 115 | 227 | 160 | 113.33 | 111.88 | AC1-048 | ME_P2-3_ME-115-013B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 204550 | 27ORRTANNA | 1 | 115 | 227 | 160 | 113.19 | 111.73 | AC1-048 | ME_P2-3_ME-115-013A_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 204550 | 27ORRTANNA | 1 | 115 | 227 | 160 | 111.08 | 110.31 | AC1-048 | ME_P2-3_ME-115-035A_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 204550 | 27ORRTANNA | 1 | 115 | 227 | 160 | 109.53 | 108.74 | AC1-048 | ME_P2-3_ME-115-035B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 204529 | 27GERMANTN | 1 | 138/115 | 227 | 345 | 109.22 | 108.17 | AC1-048 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 204529 | 27GERMANTN | 1 | 138/115 | 227 | 345 | 109.22 | 108.17 | AC1-048 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 204529 | 27GERMANTN | 1 | 138/115 | 227 | 345 | 109.21 | 108.17 | AC1-048 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 204529 | 27GERMANTN | 1 | 138/115 | 227 | 345 | 109.27 | 108.16 | AC1-048 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2812 | 113.8 | 112.28 | AC2-079 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 282 | 111.29 | 106.91 | AC1-048 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 282 | 111.29 | 106.91 | AC1-048 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 282 | 111.28 | 106.9 | AC1-048 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 282 | 111.34 | 106.9 | AC1-048 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2812 | 113.79 | 112.27 | AC2-103 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 110.43 | 106.06 | AC1-048 | ME_P2-3_ME-115-013C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 110.43 | 106.06 | AC1-048 | ME_P2-3_ME-115-013D_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 110.39 | 106.02 | AC1-048 | ME_P1-2_ME-115-009_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 110.01 | 105.63 | AC1-048 | ME_P2-4_ME-115-0102-B134_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 106.16 | 104.84 | AC1-048 | ME_P2-3_ME-115-013D_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 106.15 | 104.83 | AC1-048 | ME_P2-3_ME-115-013C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 106.07 | 104.76 | AC1-048 | ME_P1-2_ME-115-009_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 106.08 | 104.69 | AC1-048 | ME_P2-4_ME-115-0102-B134_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 204529 | 27GERMANTN | 1 | 138/115 | 227 | 345 | 103.02 | 104.51 | AC1-048 | PEPCO_P4_PP41_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204502 | 27JACKSON | 204514 | 27TMI | 1 | 230 | 227 | 659 | 104.01 | 104.02 | AC1-048 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204502 | 27JACKSON | 204514 | 27TMI | 1 | 230 | 227 | 659 | 104.01 | 104.02 | AC1-048 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204502 | 27JACKSON | 204514 | 27TMI | 1 | 230 | 227 | 659 | 104.07 | 104.01 | AC1-048 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204502 | 27JACKSON | 204514 | 27TMI | 1 | 230 | 227 | 659 | 103.99 | 104 | AC1-048 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 282 | 104.55 | 102.99 | AC1-048 | PEPCO_P4_PP41_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 204529 | 27GERMANTN | 1 | 138/115 | 227 | 345 | 100.92 | 102.67 | AC1-048 | AP_P2-3_PE-500-019B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 204529 | 27GERMANTN | 1 | 138/115 | 227 | 345 | 102.05 | 101.64 | AC1-048 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 282 | 102.26 | 101.02 | AC1-048 | AP_P2-3_PE-500-019B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204538 | 27STRABAN | 204544 | 27LINCOLN | 1 | 115 | 227 | 313 | 104.22 | 100.82 | AC1-048 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204538 | 27STRABAN | 204544 | 27LINCOLN | 1 | 115 | 227 | 313 | 104.22 | 100.82 | AC1-048 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204538 | 27STRABAN | 204544 | 27LINCOLN | 1 | 115 | 227 | 313 | 104.21 | 100.81 | AC1-048 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204538 | 27STRABAN | 204544 | 27LINCOLN | 1 | 115 | 227 | 313 | 104.28 | 100.81 | AC1-048 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2812 | 113.91 | 112.4 | AC2-112 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 118.32 | 117.46 | AC1-053 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 116.95 | 116.14 | AC1-053 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 120.82 | 115.77 | AC1-053 | PECO_P4_PEACH035_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 115.32 | 114.54 | AC1-053 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.64 | 114.22 | AC1-053 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.64 | 114.22 | AC1-053 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.26 | 113.56 | AC1-053 | PECO_P4_PEACH675_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.26 | 113.56 | AC1-053 | PECO_P7-1_220-0607_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3198 | 118.22 | 112.83 | AC1-053 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2812 | 113.72 | 112.2 | AC2-165 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 112.83 | 111.64 | AC1-053 | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 112.78 | 111.59 | AC1-053 | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.88 | 111.12 | AC1-053 | PECO_P1-2_220-07_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.69 | 111.05 | AC1-053 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.58 | 110.94 | AC1-053 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.6 | 110.92 | AC1-053 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.64 | 110.91 | AC1-053 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.13 | 110.12 | AC1-053 | AP_P2-2_WP-500-DRT16_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.13 | 110.12 | AC1-053 | AP_P1-2_WP-500-005A_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.13 | 110.12 | AC1-053 | AP_P1-2_WP-500-DRT21_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.13 | 110.12 | AC1-053 | AP_P2-3_WP-500-DRT20_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.13 | 110.12 | AC1-053 | AP_P2-3_WP-500-465_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 105.3 | 102.61 | AC1-053 | DVP_P4-2: 560T571_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 105.14 | 102.47 | AC1-053 | DVP_P4-2: H2T560_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 105.14 | 102.45 | AC1-053 | DVP_P4-2: H1T560_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 105 | 102.31 | AC1-053 | PEPCO_P1_5070_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 136.35 | 133.28 | AC1-065 | AP_P1-2_PE-500-407T_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 136.35 | 133.28 | AC1-065 | DVP_P1-2: LN 514_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 136.35 | 133.26 | AC1-065 | DVP_P4-2: 51482_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 131.24 | 128.16 | AC1-065 | AP_P2-3_PE-500-019C_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2812 | 113.96 | 112.45 | AC2-176 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 118.4 | 117.54 | AC1-065 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 117.03 | 116.21 | AC1-065 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 121 | 115.94 | AC1-065 | PECO_P4_PEACH035_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 115.39 | 114.62 | AC1-065 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.75 | 114.32 | AC1-065 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.75 | 114.32 | AC1-065 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.41 | 113.71 | AC1-065 | PECO_P7-1_220-0607_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.41 | 113.71 | AC1-065 | PECO_P4_PEACH675_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3198 | 118.39 | 113 | AC1-065 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2812 | 114.39 | 112.91 | AD1-020 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 112.9 | 111.71 | AC1-065 | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 112.85 | 111.66 | AC1-065 | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 116.03 | 111.27 | AC1-065 | PECO_P1-2_220-07_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.86 | 111.21 | AC1-065 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.74 | 111.1 | AC1-065 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.77 | 111.08 | AC1-065 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.79 | 111.05 | AC1-065 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.21 | 110.21 | AC1-065 | AP_P1-2_WP-500-005A_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.21 | 110.21 | AC1-065 | AP_P2-2_WP-500-DRT16_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.21 | 110.21 | AC1-065 | AP_P2-3_WP-500-DRT20_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.21 | 110.21 | AC1-065 | AP_P2-3_WP-500-465_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.21 | 110.21 | AC1-065 | AP_P1-2_WP-500-DRT21_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 105.24 | 102.54 | AC1-065 | DVP_P4-2: 560T571_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 105.07 | 102.4 | AC1-065 | DVP_P4-2: H2T560_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 105.07 | 102.38 | AC1-065 | DVP_P4-2: H1T560_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 104.93 | 102.24 | AC1-065 | PEPCO_P1_5070_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2812 | 113.89 | 112.38 | AD1-025 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 121.13 | 116.06 | AC1-074 | PECO_P4_PEACH035_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.55 | 113.85 | AC1-074 | PECO_P4_PEACH675_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.55 | 113.85 | AC1-074 | PECO_P7-1_220-0607_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 116.17 | 111.4 | AC1-074 | PECO_P1-2_220-07_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 116 | 111.35 | AC1-074 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.89 | 111.24 | AC1-074 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.91 | 111.22 | AC1-074 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.93 | 111.19 | AC1-074 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.69 | 111.06 | AC1-074 | PECO_P4_NOTTI85_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.62 | 111.05 | AC1-074 | PECO_P1-2_220-08_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2812 | 113.97 | 112.46 | AD1-070 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.9 | 114.47 | AC1-075 and AC1-080 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.9 | 114.47 | AC1-075 and AC1-080 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.55 | 113.85 | AC1-075 and AC1-080 | PECO_P4_PEACH675_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.55 | 113.85 | AC1-075 and AC1-080 | PECO_P7-1_220-0607_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 116.17 | 111.41 | AC1-075 and AC1-080 | PECO_P1-2_220-07_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 116.01 | 111.36 | AC1-075 and AC1-080 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.89 | 111.24 | AC1-075 and AC1-080 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.92 | 111.22 | AC1-075 and AC1-080 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.69 | 111.07 | AC1-075 and AC1-080 | PECO_P4_NOTTI85_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 111.31 | 106.94 | AC1-075 and AC1-080 | DVP_P4-2: 534T564_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 116.02 | 111.37 | AC1-076 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.9 | 111.25 | AC1-076 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.93 | 111.23 | AC1-076 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.7 | 111.08 | AC1-076 | PECO_P4_NOTTI85_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.64 | 111.07 | AC1-076 | PECO_P1-2_220-08_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.59 | 111.02 | AC1-076 | PECO_P4_COOPR125_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.35 | 110.87 | AC1-076 | PECO_P1-2_220-93_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 113.73 | 109.47 | AC1-076 | AP_P1-2_WP-500-DRT21_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2812 | 113.72 | 112.2 | AD1-083 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 118.46 | 117.61 | AC1-078 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 117.09 | 116.28 | AC1-078 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 120.97 | 115.91 | AC1-078 | PECO_P4_PEACH035_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 115.45 | 114.69 | AC1-078 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.78 | 114.35 | AC1-078 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.78 | 114.35 | AC1-078 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.4 | 113.71 | AC1-078 | PECO_P7-1_220-0607_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.4 | 113.71 | AC1-078 | PECO_P4_PEACH675_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3198 | 118.39 | 113 | AC1-078 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2812 | 113.98 | 112.47 | AD1-088 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 112.96 | 111.78 | AC1-078 | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 112.91 | 111.73 | AC1-078 | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 116.02 | 111.26 | AC1-078 | PECO_P1-2_220-07_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.85 | 111.2 | AC1-078 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.73 | 111.09 | AC1-078 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.76 | 111.07 | AC1-078 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.78 | 111.05 | AC1-078 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.26 | 110.26 | AC1-078 | AP_P2-3_WP-500-DRT20_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.26 | 110.26 | AC1-078 | AP_P1-2_WP-500-005A_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.26 | 110.26 | AC1-078 | AP_P1-2_WP-500-DRT21_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.26 | 110.26 | AC1-078 | AP_P2-3_WP-500-465_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.26 | 110.26 | AC1-078 | AP_P2-2_WP-500-DRT16_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2812 | 113.93 | 112.42 | AD1-115 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 121.1 | 116.04 | AC1-082 | PECO_P4_PEACH035_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.88 | 114.46 | AC1-082 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.88 | 114.46 | AC1-082 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.52 | 113.83 | AC1-082 | PECO_P7-1_220-0607_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.52 | 113.83 | AC1-082 | PECO_P4_PEACH675_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3198 | 118.54 | 113.14 | AC1-082 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 116.14 | 111.38 | AC1-082 | PECO_P1-2_220-07_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.98 | 111.33 | AC1-082 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.86 | 111.22 | AC1-082 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.89 | 111.2 | AC1-082 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.9 | 111.16 | AC1-082 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2812 | 114.01 | 112.5 | AD1-125 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 118.48 | 117.63 | AC1-083 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 117.11 | 116.31 | AC1-083 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 121.06 | 115.99 | AC1-083 | PECO_P4_PEACH035_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 115.48 | 114.71 | AC1-083 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.82 | 114.39 | AC1-083 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.82 | 114.39 | AC1-083 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.47 | 113.77 | AC1-083 | PECO_P4_PEACH675_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.47 | 113.77 | AC1-083 | PECO_P7-1_220-0607_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3198 | 118.47 | 113.07 | AC1-083 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2812 | 114 | 112.5 | AD1-128 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 112.98 | 111.8 | AC1-083 | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 112.93 | 111.75 | AC1-083 | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 116.09 | 111.33 | AC1-083 | PECO_P1-2_220-07_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.92 | 111.27 | AC1-083 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.81 | 111.16 | AC1-083 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.83 | 111.14 | AC1-083 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.85 | 111.11 | AC1-083 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.29 | 110.29 | AC1-083 | AP_P2-2_WP-500-DRT16_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.29 | 110.29 | AC1-083 | AP_P2-3_WP-500-465_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.29 | 110.29 | AC1-083 | AP_P1-2_WP-500-005A_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.29 | 110.29 | AC1-083 | AP_P1-2_WP-500-DRT21_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.29 | 110.29 | AC1-083 | AP_P2-3_WP-500-DRT20_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 607 | 168.85 | 166.14 | AC1-085 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 607 | 167.78 | 166.14 | AC1-085 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 607 | 168.52 | 166.13 | AC1-085 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 607 | 167.46 | 166.13 | AC1-085 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 607 | 168.77 | 166.07 | AC1-085 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 607 | 168.77 | 166.07 | AC1-085 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 607 | 167.7 | 166.07 | AC1-085 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 607 | 167.7 | 166.07 | AC1-085 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 628 | 159.78 | 158.4 | AC1-085 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 628 | 159.46 | 158.39 | AC1-085 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 628 | 159.7 | 158.33 | AC1-085 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 628 | 159.7 | 158.33 | AC1-085 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 628 | 157.07 | 156.11 | AC1-085 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 628 | 156.76 | 156.1 | AC1-085 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 628 | 157 | 156.04 | AC1-085 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 628 | 157 | 156.04 | AC1-085 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 607 | 154.75 | 151.6 | AC1-085 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 607 | 153.69 | 151.6 | AC1-085 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 628 | 146.15 | 144.33 | AC1-085 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 628 | 143.45 | 142.02 | AC1-085 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 136.51 | 133.44 | AC1-085 | AP_P1-2_PE-500-407T_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 136.51 | 133.44 | AC1-085 | DVP_P1-2: LN 514_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 136.51 | 133.42 | AC1-085 | DVP_P4-2: 51482_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 131.39 | 128.31 | AC1-085 | AP_P2-3_PE-500-019C_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2812 | 113.74 | 112.22 | AD1-140 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 118.21 | 117.33 | AC1-085 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 116.84 | 116.01 | AC1-085 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 120.67 | 115.62 | AC1-085 | PECO_P4_PEACH035_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 115.2 | 114.41 | AC1-085 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.51 | 114.09 | AC1-085 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.51 | 114.09 | AC1-085 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.11 | 113.43 | AC1-085 | PECO_P4_PEACH675_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.11 | 113.43 | AC1-085 | PECO_P7-1_220-0607_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3198 | 118.05 | 112.67 | AC1-085 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2812 | 114.68 | 113.22 | AD1-143 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 112.72 | 111.52 | AC1-085 | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 112.67 | 111.47 | AC1-085 | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.74 | 110.98 | AC1-085 | PECO_P1-2_220-07_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.54 | 110.91 | AC1-085 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.42 | 110.79 | AC1-085 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.45 | 110.77 | AC1-085 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.5 | 110.77 | AC1-085 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.01 | 109.99 | AC1-085 | AP_P2-3_WP-500-465_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.01 | 109.99 | AC1-085 | AP_P1-2_WP-500-005A_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.01 | 109.99 | AC1-085 | AP_P1-2_WP-500-DRT21_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.01 | 109.99 | AC1-085 | AP_P2-3_WP-500-DRT20_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.01 | 109.99 | AC1-085 | AP_P2-2_WP-500-DRT16_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 105.2 | 102.51 | AC1-085 | DVP_P4-2: 560T571_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 105.04 | 102.37 | AC1-085 | DVP_P4-2: H2T560_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 105.04 | 102.36 | AC1-085 | DVP_P4-2: H1T560_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 104.9 | 102.21 | AC1-085 | PEPCO_P1_5070_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 136.33 | 133.26 | AC1-086 | DVP_P1-2: LN 514_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 136.33 | 133.26 | AC1-086 | AP_P1-2_PE-500-407T_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 136.33 | 133.25 | AC1-086 | DVP_P4-2: 51482_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 131.23 | 128.14 | AC1-086 | AP_P2-3_PE-500-019C_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2812 | 113.86 | 112.35 | AD2-016 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 118.36 | 117.5 | AC1-086 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 116.99 | 116.18 | AC1-086 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 120.96 | 115.9 | AC1-086 | PECO_P4_PEACH035_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 115.36 | 114.58 | AC1-086 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.71 | 114.29 | AC1-086 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.71 | 114.29 | AC1-086 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.37 | 113.68 | AC1-086 | PECO_P7-1_220-0607_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.37 | 113.68 | AC1-086 | PECO_P4_PEACH675_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3198 | 118.35 | 112.96 | AC1-086 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2812 | 113.92 | 112.41 | AD2-072 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 112.87 | 111.68 | AC1-086 | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 112.82 | 111.63 | AC1-086 | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.99 | 111.23 | AC1-086 | PECO_P1-2_220-07_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.81 | 111.17 | AC1-086 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.7 | 111.06 | AC1-086 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.73 | 111.04 | AC1-086 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.75 | 111.02 | AC1-086 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.17 | 110.17 | AC1-086 | AP_P2-3_WP-500-DRT20_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.17 | 110.17 | AC1-086 | AP_P2-2_WP-500-DRT16_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.17 | 110.17 | AC1-086 | AP_P1-2_WP-500-005A_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.17 | 110.17 | AC1-086 | AP_P1-2_WP-500-DRT21_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.17 | 110.17 | AC1-086 | AP_P2-3_WP-500-465_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 105.21 | 102.52 | AC1-086 | DVP_P4-2: 560T571_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 105.05 | 102.38 | AC1-086 | DVP_P4-2: H2T560_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 105.04 | 102.36 | AC1-086 | DVP_P4-2: H1T560_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 104.9 | 102.21 | AC1-086 | PEPCO_P1_5070_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2812 | 114.02 | 112.51 | AD2-074 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 118.51 | 117.66 | AC1-089 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 117.13 | 116.33 | AC1-089 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 121.04 | 115.97 | AC1-089 | PECO_P4_PEACH035_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 115.5 | 114.73 | AC1-089 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.83 | 114.4 | AC1-089 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.83 | 114.4 | AC1-089 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.46 | 113.77 | AC1-089 | PECO_P7-1_220-0607_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.46 | 113.77 | AC1-089 | PECO_P4_PEACH675_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3198 | 118.46 | 113.07 | AC1-089 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2812 | 113.93 | 112.42 | AD2-093 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 113.01 | 111.82 | AC1-089 | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 112.96 | 111.78 | AC1-089 | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 116.08 | 111.32 | AC1-089 | PECO_P1-2_220-07_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.91 | 111.27 | AC1-089 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.8 | 111.15 | AC1-089 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.82 | 111.13 | AC1-089 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.84 | 111.1 | AC1-089 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.31 | 110.31 | AC1-089 | AP_P2-2_WP-500-DRT16_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.31 | 110.31 | AC1-089 | AP_P2-3_WP-500-DRT20_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.31 | 110.31 | AC1-089 | AP_P1-2_WP-500-DRT21_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.31 | 110.31 | AC1-089 | AP_P2-3_WP-500-465_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.31 | 110.31 | AC1-089 | AP_P1-2_WP-500-005A_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 136.2 | 133.13 | AC1-120 | DVP_P1-2: LN 514_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 136.2 | 133.13 | AC1-120 | AP_P1-2_PE-500-407T_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 136.2 | 133.11 | AC1-120 | DVP_P4-2: 51482_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 131.1 | 128.02 | AC1-120 | AP_P2-3_PE-500-019C_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2812 | 113.9 | 112.39 | AD2-134 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 118.38 | 117.52 | AC1-120 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 117.01 | 116.19 | AC1-120 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 121 | 115.94 | AC1-120 | PECO_P4_PEACH035_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 115.37 | 114.6 | AC1-120 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.73 | 114.31 | AC1-120 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.73 | 114.31 | AC1-120 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.4 | 113.71 | AC1-120 | PECO_P7-1_220-0607_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.4 | 113.71 | AC1-120 | PECO_P4_PEACH675_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3198 | 118.39 | 112.99 | AC1-120 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2812 | 113.79 | 112.28 | AD2-158 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 112.88 | 111.69 | AC1-120 | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 112.83 | 111.65 | AC1-120 | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 116.02 | 111.27 | AC1-120 | PECO_P1-2_220-07_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.85 | 111.2 | AC1-120 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.73 | 111.09 | AC1-120 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.76 | 111.07 | AC1-120 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.79 | 111.05 | AC1-120 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.19 | 110.19 | AC1-120 | AP_P2-2_WP-500-DRT16_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.19 | 110.19 | AC1-120 | AP_P1-2_WP-500-DRT21_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.19 | 110.19 | AC1-120 | AP_P2-3_WP-500-DRT20_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.19 | 110.19 | AC1-120 | AP_P2-3_WP-500-465_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.19 | 110.19 | AC1-120 | AP_P1-2_WP-500-005A_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 105.17 | 102.48 | AC1-120 | DVP_P4-2: 560T571_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 105.01 | 102.34 | AC1-120 | DVP_P4-2: H2T560_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 105.01 | 102.33 | AC1-120 | DVP_P4-2: H1T560_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 104.87 | 102.18 | AC1-120 | PEPCO_P1_5070_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 116.01 | 111.36 | AC1-122 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.89 | 111.25 | AC1-122 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.92 | 111.22 | AC1-122 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.7 | 111.07 | AC1-122 | PECO_P4_NOTTI85_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 111.13 | 106.75 | AC1-122 | PL_04_P42_000565_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 111.13 | 106.75 | AC1-122 | PL_04_P12_000261_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 111.01 | 106.6 | AC1-122 | AEP_P2-2_#2825_05LAWBG2 345_2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 111.01 | 106.6 | AC1-122 | AEP_P4_#2825_05LAWBG2 345_52-2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 110.28 | 105.89 | AC1-122 | 200105 AA1-076 ST 23.5 _SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 607 | 166.55 | 164.8 | AC1-158 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 607 | 167.6 | 164.8 | AC1-158 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 607 | 167.28 | 164.79 | AC1-158 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 607 | 166.23 | 164.79 | AC1-158 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 607 | 167.52 | 164.73 | AC1-158 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 607 | 167.52 | 164.73 | AC1-158 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 607 | 166.47 | 164.73 | AC1-158 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 607 | 166.47 | 164.73 | AC1-158 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 628 | 158.59 | 157.11 | AC1-158 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 628 | 158.28 | 157.1 | AC1-158 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 628 | 158.51 | 157.04 | AC1-158 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 628 | 158.51 | 157.04 | AC1-158 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 235463 | 01TANEY | 1 | 138 | 227/201 | 268 | 158.68 | 154.87 | AC1-158 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 235463 | 01TANEY | 1 | 138 | 227/201 | 268 | 158.68 | 154.87 | AC1-158 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 628 | 155.88 | 154.81 | AC1-158 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 628 | 155.57 | 154.81 | AC1-158 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 235463 | 01TANEY | 1 | 138 | 227/201 | 268 | 158.6 | 154.79 | AC1-158 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 628 | 155.81 | 154.74 | AC1-158 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 628 | 155.81 | 154.74 | AC1-158 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 607 | 152.47 | 150.43 | AC1-158 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 607 | 153.52 | 150.43 | AC1-158 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 628 | 144.98 | 143.2 | AC1-158 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 628 | 142.27 | 140.89 | AC1-158 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 282 | 137.7 | 137.28 | AC1-158 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 282 | 137.7 | 137.28 | AC1-158 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 282 | 137.64 | 137.21 | AC1-158 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 680 | 139.41 | 136.49 | AC1-158 | PEPCO_P4_PP19_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 797 | 139.7 | 135.14 | AC1-158 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 797 | 139.95 | 135.08 | AC1-158 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 797 | 139.95 | 135.08 | AC1-158 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 797 | 139.92 | 135.06 | AC1-158 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204538 | 27STRABAN | 204544 | 27LINCOLN | 1 | 115 | 227 | 313 | 130.95 | 131.72 | AC1-158 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204538 | 27STRABAN | 204544 | 27LINCOLN | 1 | 115 | 227 | 313 | 130.95 | 131.72 | AC1-158 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204538 | 27STRABAN | 204544 | 27LINCOLN | 1 | 115 | 227 | 313 | 130.89 | 131.65 | AC1-158 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 133.89 | 130.79 | AC1-158 | DVP_P1-2: LN 514_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 133.89 | 130.79 | AC1-158 | AP_P1-2_PE-500-407T_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 133.89 | 130.78 | AC1-158 | DVP_P4-2: 51482_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 680 | 133.17 | 130.36 | AC1-158 | PEPCO_P1_PP2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 2 | 230 | 233 | 680 | 133.17 | 130.36 | AC1-158 | PEPCO_P1_PP1_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204529 | 27GERMANTN | 204538 | 27STRABAN | 1 | 115 | 227 | 313 | 127.57 | 128.99 | AC1-158 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204529 | 27GERMANTN | 204538 | 27STRABAN | 1 | 115 | 227 | 313 | 127.57 | 128.99 | AC1-158 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204529 | 27GERMANTN | 204538 | 27STRABAN | 1 | 115 | 227 | 313 | 127.51 | 128.92 | AC1-158 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 797 | 131.58 | 126.78 | AC1-158 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 204529 | 27GERMANTN | 1 | 138/115 | 227 | 345 | 123.26 | 125.83 | AC1-158 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 204529 | 27GERMANTN | 1 | 138/115 | 227 | 345 | 123.26 | 125.83 | AC1-158 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 128.85 | 125.78 | AC1-158 | AP_P2-3_PE-500-019C_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 204529 | 27GERMANTN | 1 | 138/115 | 227 | 345 | 123.2 | 125.76 | AC1-158 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 814 | 129.93 | 125.42 | AC1-158 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 814 | 130.4 | 125.29 | AC1-158 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 814 | 130.4 | 125.29 | AC1-158 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 814 | 130.39 | 125.28 | AC1-158 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 680 | 126.38 | 123.45 | AC1-158 | DVP_P1-2: LN 514_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 2 | 230 | 233 | 680 | 126.38 | 123.45 | AC1-158 | AP_P1-2_PE-500-407T_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 2 | 230 | 233 | 680 | 126.38 | 123.45 | AC1-158 | DVP_P1-2: LN 514_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 680 | 126.38 | 123.45 | AC1-158 | AP_P1-2_PE-500-407T_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 680 | 126.38 | 123.45 | AC1-158 | DVP_P4-2: 51482_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 2 | 230 | 233 | 680 | 126.38 | 123.45 | AC1-158 | DVP_P4-2: 51482_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2812 | 113.98 | 112.47 | AD2-163 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 235463 | 01TANEY | 1 | 138 | 227/201 | 268 | 124.39 | 119.21 | AC1-158 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204539 | 27HUNTRSTN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 282 | 118.37 | 117.72 | AC1-158 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204539 | 27HUNTRSTN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 282 | 118.37 | 117.72 | AC1-158 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204539 | 27HUNTRSTN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 282 | 118.31 | 117.65 | AC1-158 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 117.19 | 116.24 | AC1-158 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 814 | 121.09 | 116.18 | AC1-158 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 120.01 | 114.97 | AC1-158 | PECO_P4_PEACH035_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 115.83 | 114.93 | AC1-158 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 680 | 117.42 | 114.51 | AC1-158 | AP_P2-3_PE-500-019C_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 2 | 230 | 233 | 680 | 117.42 | 114.51 | AC1-158 | AP_P2-3_PE-500-019C_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 114.2 | 113.34 | AC1-158 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 117.63 | 113.23 | AC1-158 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 117.63 | 113.23 | AC1-158 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 117.36 | 112.69 | AC1-158 | PECO_P4_PEACH675_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 117.36 | 112.69 | AC1-158 | PECO_P7-1_220-0607_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 814 | 114.89 | 111.88 | AC1-158 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 814 | 115.14 | 111.82 | AC1-158 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 814 | 115.14 | 111.82 | AC1-158 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 814 | 115.11 | 111.8 | AC1-158 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3198 | 117.12 | 111.78 | AC1-158 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2812 | 113.95 | 112.45 | AD2-180 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.75 | 110.48 | AC1-158 | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.7 | 110.44 | AC1-158 | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 114.98 | 110.25 | AC1-158 | PECO_P1-2_220-07_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 114.73 | 110.12 | AC1-158 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 797 | 111.53 | 110.04 | AC1-158 | PJM_500_BG_P4_5_CNSTN_15_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 114.74 | 110.04 | AC1-158 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 114.61 | 110 | AC1-158 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 114.64 | 109.98 | AC1-158 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 110.04 | 108.97 | AC1-158 | AP_P1-2_WP-500-DRT21_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 110.04 | 108.97 | AC1-158 | AP_P2-3_WP-500-DRT20_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 110.04 | 108.97 | AC1-158 | AP_P2-2_WP-500-DRT16_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 110.04 | 108.97 | AC1-158 | AP_P1-2_WP-500-005A_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 110.04 | 108.97 | AC1-158 | AP_P2-3_WP-500-465_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 797 | 108.83 | 107.43 | AC1-158 | BG_P7_GRCTN_CNSTN_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204538 | 27STRABAN | 204544 | 27LINCOLN | 1 | 115 | 227 | 313 | 109.48 | 106.23 | AC1-158 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204538 | 27STRABAN | 204544 | 27LINCOLN | 1 | 115 | 227 | 313 | 109.48 | 106.23 | AC1-158 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204538 | 27STRABAN | 204544 | 27LINCOLN | 1 | 115 | 227 | 313 | 109.47 | 106.22 | AC1-158 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204538 | 27STRABAN | 204544 | 27LINCOLN | 1 | 115 | 227 | 313 | 109.53 | 106.21 | AC1-158 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204502 | 27JACKSON | 204514 | 27TMI | 1 | 230 | 227 | 659 | 103.66 | 103.58 | AC1-158 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204502 | 27JACKSON | 204514 | 27TMI | 1 | 230 | 227 | 659 | 103.66 | 103.58 | AC1-158 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204502 | 27JACKSON | 204514 | 27TMI | 1 | 230 | 227 | 659 | 103.72 | 103.56 | AC1-158 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204502 | 27JACKSON | 204514 | 27TMI | 1 | 230 | 227 | 659 | 103.64 | 103.56 | AC1-158 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204529 | 27GERMANTN | 204538 | 27STRABAN | 1 | 115 | 227 | 313 | 106.1 | 103.52 | AC1-158 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204529 | 27GERMANTN | 204538 | 27STRABAN | 1 | 115 | 227 | 313 | 106.1 | 103.52 | AC1-158 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204529 | 27GERMANTN | 204538 | 27STRABAN | 1 | 115 | 227 | 313 | 106.09 | 103.51 | AC1-158 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204529 | 27GERMANTN | 204538 | 27STRABAN | 1 | 115 | 227 | 313 | 106.15 | 103.51 | AC1-158 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 814 | 106.74 | 103.39 | AC1-158 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 204529 | 27GERMANTN | 1 | 138/115 | 227 | 345 | 103.78 | 102.54 | AC1-158 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 204529 | 27GERMANTN | 1 | 138/115 | 227 | 345 | 103.78 | 102.54 | AC1-158 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 204529 | 27GERMANTN | 1 | 138/115 | 227 | 345 | 103.77 | 102.53 | AC1-158 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 204529 | 27GERMANTN | 1 | 138/115 | 227 | 345 | 103.83 | 102.53 | AC1-158 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204538 | 27STRABAN | 204544 | 27LINCOLN | 1 | 115 | 227 | 313 | 102.68 | 102.25 | AC1-158 | PEPCO_P4_PP41_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 103.38 | 100.71 | AC1-158 | DVP_P4-2: 560T571_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 103.22 | 100.57 | AC1-158 | DVP_P4-2: H2T560_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 103.22 | 100.55 | AC1-158 | DVP_P4-2: H1T560_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 103.07 | 100.41 | AC1-158 | PEPCO_P1_5070_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204538 | 27STRABAN | 204544 | 27LINCOLN | 1 | 115 | 227 | 313 | 100.37 | 100.31 | AC1-158 | AP_P2-3_PE-500-019B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 136.04 | 132.98 | AC1-161 | AP_P1-2_PE-500-407T_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 136.04 | 132.98 | AC1-161 | DVP_P1-2: LN 514_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 136.04 | 132.96 | AC1-161 | DVP_P4-2: 51482_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 130.94 | 127.87 | AC1-161 | AP_P2-3_PE-500-019C_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2812 | 113.14 | 111.58 | AE1-044 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 118.22 | 117.35 | AC1-161 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 116.85 | 116.02 | AC1-161 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 120.85 | 115.79 | AC1-161 | PECO_P4_PEACH035_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 115.22 | 114.43 | AC1-161 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.58 | 114.16 | AC1-161 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.58 | 114.16 | AC1-161 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.25 | 113.56 | AC1-161 | PECO_P7-1_220-0607_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.25 | 113.56 | AC1-161 | PECO_P4_PEACH675_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3198 | 118.2 | 112.82 | AC1-161 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2812 | 113.92 | 112.41 | AE1-056 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 112.73 | 111.53 | AC1-161 | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 112.68 | 111.48 | AC1-161 | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.87 | 111.11 | AC1-161 | PECO_P1-2_220-07_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.68 | 111.04 | AC1-161 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.57 | 110.93 | AC1-161 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.59 | 110.91 | AC1-161 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.63 | 110.9 | AC1-161 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.03 | 110.02 | AC1-161 | AP_P2-3_WP-500-DRT20_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.03 | 110.02 | AC1-161 | AP_P2-3_WP-500-465_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.03 | 110.02 | AC1-161 | AP_P1-2_WP-500-DRT21_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.03 | 110.02 | AC1-161 | AP_P2-2_WP-500-DRT16_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.03 | 110.02 | AC1-161 | AP_P1-2_WP-500-005A_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 104.98 | 102.29 | AC1-161 | DVP_P4-2: 560T571_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 104.82 | 102.15 | AC1-161 | DVP_P4-2: H2T560_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 104.81 | 102.13 | AC1-161 | DVP_P4-2: H1T560_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 104.67 | 101.99 | AC1-161 | PEPCO_P1_5070_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 607 | 168.78 | 166.06 | AC1-164 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 607 | 167.72 | 166.06 | AC1-164 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 607 | 168.45 | 166.04 | AC1-164 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 607 | 167.39 | 166.04 | AC1-164 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 607 | 168.7 | 165.99 | AC1-164 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 607 | 168.7 | 165.99 | AC1-164 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 607 | 167.64 | 165.99 | AC1-164 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 607 | 167.64 | 165.99 | AC1-164 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 628 | 159.71 | 158.33 | AC1-164 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 628 | 159.4 | 158.31 | AC1-164 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 628 | 159.64 | 158.26 | AC1-164 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 628 | 159.64 | 158.26 | AC1-164 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 628 | 157.01 | 156.03 | AC1-164 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 628 | 156.69 | 156.02 | AC1-164 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 628 | 156.93 | 155.96 | AC1-164 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 628 | 156.93 | 155.96 | AC1-164 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 607 | 153.61 | 151.51 | AC1-164 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 607 | 154.68 | 151.51 | AC1-164 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 628 | 146.08 | 144.25 | AC1-164 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 628 | 143.38 | 141.94 | AC1-164 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 680 | 140.81 | 137.88 | AC1-164 | PEPCO_P4_PP19_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 797 | 140.61 | 136.05 | AC1-164 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 797 | 140.87 | 135.99 | AC1-164 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 797 | 140.87 | 135.99 | AC1-164 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 797 | 140.85 | 135.98 | AC1-164 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 135.7 | 132.64 | AC1-164 | AP_P1-2_PE-500-407T_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 135.7 | 132.64 | AC1-164 | DVP_P1-2: LN 514_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 135.7 | 132.62 | AC1-164 | DVP_P4-2: 51482_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 680 | 134.36 | 131.55 | AC1-164 | PEPCO_P1_PP2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 2 | 230 | 233 | 680 | 134.36 | 131.55 | AC1-164 | PEPCO_P1_PP1_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 797 | 132.49 | 127.7 | AC1-164 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 130.61 | 127.54 | AC1-164 | AP_P2-3_PE-500-019C_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 814 | 130.85 | 126.34 | AC1-164 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 814 | 131.35 | 126.23 | AC1-164 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 814 | 131.35 | 126.23 | AC1-164 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 814 | 131.34 | 126.22 | AC1-164 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 680 | 127.87 | 124.97 | AC1-164 | AP_P1-2_PE-500-407T_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 2 | 230 | 233 | 680 | 127.87 | 124.97 | AC1-164 | AP_P1-2_PE-500-407T_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 680 | 127.87 | 124.97 | AC1-164 | DVP_P1-2: LN 514_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 2 | 230 | 233 | 680 | 127.87 | 124.97 | AC1-164 | DVP_P1-2: LN 514_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 680 | 127.87 | 124.96 | AC1-164 | DVP_P4-2: 51482_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 2 | 230 | 233 | 680 | 127.87 | 124.96 | AC1-164 | DVP_P4-2: 51482_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2812 | 113.83 | 112.31 | AE1-084 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 118.03 | 117.15 | AC1-164 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 814 | 122.02 | 117.09 | AC1-164 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 680 | 118.82 | 115.9 | AC1-164 | AP_P2-3_PE-500-019C_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 2 | 230 | 233 | 680 | 118.82 | 115.9 | AC1-164 | AP_P2-3_PE-500-019C_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 116.66 | 115.82 | AC1-164 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 120.69 | 115.64 | AC1-164 | PECO_P4_PEACH035_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 115.03 | 114.23 | AC1-164 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.4 | 113.99 | AC1-164 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.4 | 113.99 | AC1-164 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.08 | 113.4 | AC1-164 | PECO_P7-1_220-0607_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.08 | 113.4 | AC1-164 | PECO_P4_PEACH675_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 814 | 115.76 | 112.76 | AC1-164 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 814 | 116.02 | 112.7 | AC1-164 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 814 | 116.02 | 112.7 | AC1-164 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 814 | 115.99 | 112.69 | AC1-164 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3198 | 118 | 112.63 | AC1-164 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2812 | 113.92 | 112.41 | AE1-101 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 112.55 | 111.34 | AC1-164 | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 112.5 | 111.29 | AC1-164 | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.7 | 110.96 | AC1-164 | PECO_P1-2_220-07_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.51 | 110.87 | AC1-164 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.39 | 110.76 | AC1-164 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.47 | 110.74 | AC1-164 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.42 | 110.74 | AC1-164 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 110.85 | 109.83 | AC1-164 | AP_P1-2_WP-500-DRT21_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 110.85 | 109.83 | AC1-164 | AP_P2-3_WP-500-DRT20_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 110.85 | 109.83 | AC1-164 | AP_P2-3_WP-500-465_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 110.85 | 109.83 | AC1-164 | AP_P1-2_WP-500-005A_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 110.85 | 109.83 | AC1-164 | AP_P2-2_WP-500-DRT16_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 814 | 107.6 | 104.28 | AC1-164 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 104.7 | 102.02 | AC1-164 | DVP_P4-2: 560T571_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 104.53 | 101.87 | AC1-164 | DVP_P4-2: H2T560_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 104.53 | 101.85 | AC1-164 | DVP_P4-2: H1T560_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 104.39 | 101.71 | AC1-164 | PEPCO_P1_5070_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 801 | 102.22 | 100.12 | AC1-164 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 801 | 102.64 | 100.02 | AC1-164 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 801 | 102.64 | 100.02 | AC1-164 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 801 | 102.62 | 100 | AC1-164 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2812 | 115.4 | 113.98 | AE1-104 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 121.09 | 116.03 | AC1-168 | PECO_P4_PEACH035_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.88 | 114.45 | AC1-168 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.88 | 114.45 | AC1-168 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.51 | 113.82 | AC1-168 | PECO_P4_PEACH675_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.51 | 113.82 | AC1-168 | PECO_P7-1_220-0607_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3198 | 118.52 | 113.13 | AC1-168 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 116.14 | 111.37 | AC1-168 | PECO_P1-2_220-07_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.97 | 111.32 | AC1-168 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.85 | 111.21 | AC1-168 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.88 | 111.19 | AC1-168 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.89 | 111.16 | AC1-168 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2812 | 113.77 | 112.25 | AE1-143 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 121.1 | 116.04 | AC1-173 GEN | PECO_P4_PEACH035_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.89 | 114.46 | AC1-173 GEN | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.89 | 114.46 | AC1-173 GEN | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.52 | 113.83 | AC1-173 GEN | PECO_P7-1_220-0607_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.52 | 113.83 | AC1-173 GEN | PECO_P4_PEACH675_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3198 | 118.54 | 113.14 | AC1-173 GEN | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 116.15 | 111.38 | AC1-173 GEN | PECO_P1-2_220-07_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.98 | 111.33 | AC1-173 GEN | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.86 | 111.22 | AC1-173 GEN | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.89 | 111.2 | AC1-173 GEN | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.91 | 111.17 | AC1-173 GEN | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2812 | 113.86 | 112.35 | AE1-153 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 121.11 | 116.05 | AC1-174 | PECO_P4_PEACH035_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.9 | 114.47 | AC1-174 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.9 | 114.47 | AC1-174 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.54 | 113.84 | AC1-174 | PECO_P4_PEACH675_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.54 | 113.84 | AC1-174 | PECO_P7-1_220-0607_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3198 | 118.55 | 113.15 | AC1-174 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 116.16 | 111.39 | AC1-174 | PECO_P1-2_220-07_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.99 | 111.34 | AC1-174 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.88 | 111.23 | AC1-174 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.9 | 111.21 | AC1-174 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.92 | 111.18 | AC1-174 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2812 | 113.93 | 112.42 | AE1-155 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 121.11 | 116.05 | AC1-175 | PECO_P4_PEACH035_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.9 | 114.47 | AC1-175 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.9 | 114.47 | AC1-175 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.54 | 113.84 | AC1-175 | PECO_P4_PEACH675_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.54 | 113.84 | AC1-175 | PECO_P7-1_220-0607_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3198 | 118.55 | 113.15 | AC1-175 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 116.16 | 111.39 | AC1-175 | PECO_P1-2_220-07_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.99 | 111.34 | AC1-175 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.88 | 111.23 | AC1-175 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.9 | 111.21 | AC1-175 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.92 | 111.18 | AC1-175 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 136.32 | 133.26 | AC1-189 | DVP_P1-2: LN 514_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 136.32 | 133.26 | AC1-189 | AP_P1-2_PE-500-407T_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 136.32 | 133.24 | AC1-189 | DVP_P4-2: 51482_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 131.22 | 128.14 | AC1-189 | AP_P2-3_PE-500-019C_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2812 | 113.93 | 112.42 | AE1-157 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 118.35 | 117.49 | AC1-189 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 116.98 | 116.16 | AC1-189 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 120.95 | 115.89 | AC1-189 | PECO_P4_PEACH035_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 115.35 | 114.57 | AC1-189 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.7 | 114.27 | AC1-189 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.7 | 114.27 | AC1-189 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.36 | 113.66 | AC1-189 | PECO_P4_PEACH675_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.36 | 113.66 | AC1-189 | PECO_P7-1_220-0607_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3198 | 118.33 | 112.94 | AC1-189 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2812 | 114.55 | 113.08 | AE1-229 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 112.86 | 111.66 | AC1-189 | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 112.81 | 111.62 | AC1-189 | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.98 | 111.22 | AC1-189 | PECO_P1-2_220-07_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.8 | 111.16 | AC1-189 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.68 | 111.04 | AC1-189 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.71 | 111.02 | AC1-189 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.74 | 111 | AC1-189 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.16 | 110.16 | AC1-189 | AP_P2-3_WP-500-DRT20_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.16 | 110.16 | AC1-189 | AP_P1-2_WP-500-DRT21_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.16 | 110.16 | AC1-189 | AP_P1-2_WP-500-005A_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.16 | 110.16 | AC1-189 | AP_P2-2_WP-500-DRT16_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.16 | 110.16 | AC1-189 | AP_P2-3_WP-500-465_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 105.2 | 102.51 | AC1-189 | DVP_P4-2: 560T571_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 105.04 | 102.37 | AC1-189 | DVP_P4-2: H2T560_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 105.03 | 102.35 | AC1-189 | DVP_P4-2: H1T560_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 104.89 | 102.2 | AC1-189 | PEPCO_P1_5070_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 136.16 | 133.09 | AC1-191 | DVP_P1-2: LN 514_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 136.16 | 133.09 | AC1-191 | AP_P1-2_PE-500-407T_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 136.16 | 133.07 | AC1-191 | DVP_P4-2: 51482_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 131.06 | 127.98 | AC1-191 | AP_P2-3_PE-500-019C_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2812 | 116.39 | 115.04 | AE2-000 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 118.3 | 117.44 | AC1-191 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 116.93 | 116.11 | AC1-191 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 120.93 | 115.87 | AC1-191 | PECO_P4_PEACH035_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 115.3 | 114.51 | AC1-191 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.66 | 114.23 | AC1-191 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.66 | 114.23 | AC1-191 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.33 | 113.63 | AC1-191 | PECO_P4_PEACH675_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.33 | 113.63 | AC1-191 | PECO_P7-1_220-0607_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3198 | 118.29 | 112.91 | AC1-191 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2812 | 116 | 114.61 | AE2-020 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 112.81 | 111.61 | AC1-191 | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 112.76 | 111.57 | AC1-191 | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.95 | 111.19 | AC1-191 | PECO_P1-2_220-07_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.77 | 111.12 | AC1-191 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.65 | 111.01 | AC1-191 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.68 | 110.99 | AC1-191 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.71 | 110.97 | AC1-191 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.12 | 110.11 | AC1-191 | AP_P2-2_WP-500-DRT16_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.12 | 110.11 | AC1-191 | AP_P2-3_WP-500-DRT20_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.12 | 110.11 | AC1-191 | AP_P1-2_WP-500-DRT21_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.12 | 110.11 | AC1-191 | AP_P1-2_WP-500-005A_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.12 | 110.11 | AC1-191 | AP_P2-3_WP-500-465_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 105.08 | 102.39 | AC1-191 | DVP_P4-2: 560T571_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 104.92 | 102.25 | AC1-191 | DVP_P4-2: H2T560_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 104.92 | 102.23 | AC1-191 | DVP_P4-2: H1T560_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 104.77 | 102.09 | AC1-191 | PEPCO_P1_5070_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2812 | 116 | 114.61 | AE2-021 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 121.08 | 116.01 | AC1-194 | PECO_P4_PEACH035_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.87 | 114.44 | AC1-194 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.87 | 114.44 | AC1-194 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.5 | 113.8 | AC1-194 | PECO_P7-1_220-0607_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.5 | 113.8 | AC1-194 | PECO_P4_PEACH675_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3198 | 118.51 | 113.11 | AC1-194 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 116.12 | 111.36 | AC1-194 | PECO_P1-2_220-07_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.96 | 111.31 | AC1-194 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.84 | 111.19 | AC1-194 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.87 | 111.17 | AC1-194 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.88 | 111.14 | AC1-194 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 108.91 | 107.61 | AC1-194 | PN_P2-3_PN-500-DRT30_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 108.91 | 107.61 | AC1-194 | PN_P2-3_PN-500-004-DRT-009_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 108.71 | 107.41 | AC1-194 | PN_P2-3_PN-500-001B-DRT_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 108.71 | 107.41 | AC1-194 | PN_P1-2_PN-500-001_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 105.51 | 104.19 | AC1-194 | PN_P2-3_PN-500-DRT32_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 105.51 | 104.19 | AC1-194 | PN_P2-3_PN-500-004-DRT-002_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2812 | 115.09 | 113.65 | AE2-022 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 121.13 | 116.07 | AC1-208 | PECO_P4_PEACH035_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.89 | 114.46 | AC1-208 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.89 | 114.46 | AC1-208 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.54 | 113.85 | AC1-208 | PECO_P4_PEACH675_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.54 | 113.85 | AC1-208 | PECO_P7-1_220-0607_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3198 | 118.56 | 113.16 | AC1-208 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 116.17 | 111.4 | AC1-208 | PECO_P1-2_220-07_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 116 | 111.35 | AC1-208 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.88 | 111.24 | AC1-208 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.91 | 111.22 | AC1-208 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.93 | 111.18 | AC1-208 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2812 | 113.95 | 112.44 | AE2-027 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 121.09 | 116.02 | AC1-214 | PECO_P4_PEACH035_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.87 | 114.45 | AC1-214 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.87 | 114.45 | AC1-214 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.51 | 113.81 | AC1-214 | PECO_P4_PEACH675_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.51 | 113.81 | AC1-214 | PECO_P7-1_220-0607_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3198 | 118.52 | 113.12 | AC1-214 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 116.13 | 111.37 | AC1-214 | PECO_P1-2_220-07_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.97 | 111.32 | AC1-214 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.85 | 111.2 | AC1-214 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.88 | 111.18 | AC1-214 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.89 | 111.15 | AC1-214 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2812 | 114.42 | 112.94 | AE2-046 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 118.5 | 117.65 | AC1-216 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 117.13 | 116.32 | AC1-216 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 121.09 | 116.03 | AC1-216 | PECO_P4_PEACH035_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 115.49 | 114.73 | AC1-216 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.84 | 114.42 | AC1-216 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.84 | 114.42 | AC1-216 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.5 | 113.81 | AC1-216 | PECO_P4_PEACH675_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.5 | 113.81 | AC1-216 | PECO_P7-1_220-0607_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3198 | 118.51 | 113.11 | AC1-216 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2812 | 114.01 | 112.51 | AE2-206 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 113 | 111.82 | AC1-216 | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 112.95 | 111.77 | AC1-216 | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 116.12 | 111.36 | AC1-216 | PECO_P1-2_220-07_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.96 | 111.31 | AC1-216 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.84 | 111.2 | AC1-216 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.87 | 111.17 | AC1-216 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.88 | 111.14 | AC1-216 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.31 | 110.31 | AC1-216 | AP_P1-2_WP-500-005A_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.31 | 110.31 | AC1-216 | AP_P2-3_WP-500-465_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.31 | 110.31 | AC1-216 | AP_P1-2_WP-500-DRT21_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.31 | 110.31 | AC1-216 | AP_P2-2_WP-500-DRT16_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.31 | 110.31 | AC1-216 | AP_P2-3_WP-500-DRT20_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 136.47 | 133.4 | AC1-221 | DVP_P1-2: LN 514_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 136.47 | 133.4 | AC1-221 | AP_P1-2_PE-500-407T_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 136.47 | 133.39 | AC1-221 | DVP_P4-2: 51482_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 131.36 | 128.28 | AC1-221 | AP_P2-3_PE-500-019C_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2812 | 113.73 | 112.21 | AE2-217 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 118.43 | 117.57 | AC1-221 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 117.06 | 116.25 | AC1-221 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 121.01 | 115.95 | AC1-221 | PECO_P4_PEACH035_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 115.42 | 114.65 | AC1-221 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.77 | 114.34 | AC1-221 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.77 | 114.34 | AC1-221 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.42 | 113.73 | AC1-221 | PECO_P4_PEACH675_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.42 | 113.73 | AC1-221 | PECO_P7-1_220-0607_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3198 | 118.41 | 113.02 | AC1-221 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2812 | 113.72 | 112.2 | AE2-218 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 112.93 | 111.74 | AC1-221 | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 112.88 | 111.7 | AC1-221 | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 116.04 | 111.28 | AC1-221 | PECO_P1-2_220-07_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.87 | 111.23 | AC1-221 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.75 | 111.11 | AC1-221 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.78 | 111.09 | AC1-221 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.8 | 111.07 | AC1-221 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.24 | 110.24 | AC1-221 | AP_P2-2_WP-500-DRT16_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.24 | 110.24 | AC1-221 | AP_P2-3_WP-500-465_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.24 | 110.24 | AC1-221 | AP_P1-2_WP-500-DRT21_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.24 | 110.24 | AC1-221 | AP_P2-3_WP-500-DRT20_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.24 | 110.24 | AC1-221 | AP_P1-2_WP-500-005A_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 136.46 | 133.39 | AC1-222 | AP_P1-2_PE-500-407T_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 136.46 | 133.39 | AC1-222 | DVP_P1-2: LN 514_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 136.46 | 133.37 | AC1-222 | DVP_P4-2: 51482_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 131.35 | 128.27 | AC1-222 | AP_P2-3_PE-500-019C_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2812 | 113.82 | 112.31 | AE2-221 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 118.42 | 117.57 | AC1-222 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 117.05 | 116.24 | AC1-222 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 121.01 | 115.95 | AC1-222 | PECO_P4_PEACH035_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 115.42 | 114.65 | AC1-222 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.77 | 114.34 | AC1-222 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.77 | 114.34 | AC1-222 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.42 | 113.73 | AC1-222 | PECO_P7-1_220-0607_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.42 | 113.73 | AC1-222 | PECO_P4_PEACH675_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3198 | 118.41 | 113.02 | AC1-222 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2812 | 113.91 | 112.4 | AE2-230 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 112.93 | 111.74 | AC1-222 | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 112.88 | 111.69 | AC1-222 | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 116.04 | 111.28 | AC1-222 | PECO_P1-2_220-07_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.87 | 111.23 | AC1-222 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.75 | 111.11 | AC1-222 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.78 | 111.09 | AC1-222 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.8 | 111.07 | AC1-222 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.23 | 110.23 | AC1-222 | AP_P2-3_WP-500-DRT20_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.23 | 110.23 | AC1-222 | AP_P1-2_WP-500-DRT21_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.23 | 110.23 | AC1-222 | AP_P2-2_WP-500-DRT16_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.23 | 110.23 | AC1-222 | AP_P2-3_WP-500-465_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.23 | 110.23 | AC1-222 | AP_P1-2_WP-500-005A_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 105.31 | 102.61 | AC1-222 | DVP_P4-2: 560T571_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 105.14 | 102.47 | AC1-222 | DVP_P4-2: H2T560_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 105.14 | 102.46 | AC1-222 | DVP_P4-2: H1T560_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 105 | 102.31 | AC1-222 | PEPCO_P1_5070_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 136.37 | 133.3 | AC2-012 | AP_P1-2_PE-500-407T_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 136.37 | 133.3 | AC2-012 | DVP_P1-2: LN 514_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 136.37 | 133.28 | AC2-012 | DVP_P4-2: 51482_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 131.26 | 128.18 | AC2-012 | AP_P2-3_PE-500-019C_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2812 | 113.99 | 112.49 | AE2-253 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 118.41 | 117.55 | AC2-012 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 117.03 | 116.22 | AC2-012 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 121.01 | 115.95 | AC2-012 | PECO_P4_PEACH035_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 115.4 | 114.63 | AC2-012 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.75 | 114.33 | AC2-012 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.75 | 114.33 | AC2-012 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.42 | 113.72 | AC2-012 | PECO_P7-1_220-0607_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.42 | 113.72 | AC2-012 | PECO_P4_PEACH675_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3198 | 118.4 | 113.01 | AC2-012 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2812 | 114 | 112.49 | AE2-297 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 112.91 | 111.72 | AC2-012 | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 112.86 | 111.67 | AC2-012 | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 116.04 | 111.28 | AC2-012 | PECO_P1-2_220-07_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.86 | 111.22 | AC2-012 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.75 | 111.11 | AC2-012 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.78 | 111.08 | AC2-012 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.8 | 111.06 | AC2-012 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.22 | 110.22 | AC2-012 | AP_P1-2_WP-500-005A_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.22 | 110.22 | AC2-012 | AP_P2-2_WP-500-DRT16_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.22 | 110.22 | AC2-012 | AP_P2-3_WP-500-DRT20_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.22 | 110.22 | AC2-012 | AP_P2-3_WP-500-465_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.22 | 110.22 | AC2-012 | AP_P1-2_WP-500-DRT21_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 105.25 | 102.56 | AC2-012 | DVP_P4-2: 560T571_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 105.09 | 102.42 | AC2-012 | DVP_P4-2: H2T560_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 105.09 | 102.4 | AC2-012 | DVP_P4-2: H1T560_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 104.94 | 102.25 | AC2-012 | PEPCO_P1_5070_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2812 | 113.97 | 112.46 | AE2-333 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 121.45 | 116.37 | AC2-023 | PECO_P4_PEACH035_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 119.17 | 114.73 | AC2-023 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 119.17 | 114.73 | AC2-023 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.84 | 114.13 | AC2-023 | PECO_P4_PEACH675_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.84 | 114.13 | AC2-023 | PECO_P7-1_220-0607_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3198 | 118.93 | 113.51 | AC2-023 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 116.46 | 111.69 | AC2-023 | PECO_P1-2_220-07_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 116.32 | 111.66 | AC2-023 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 116.2 | 111.55 | AC2-023 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 116.23 | 111.53 | AC2-023 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 116.22 | 111.47 | AC2-023 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2812 | 114.02 | 112.51 | AF1-038 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 118.52 | 117.67 | AC2-059 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 117.15 | 116.35 | AC2-059 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 121.05 | 115.99 | AC2-059 | PECO_P4_PEACH035_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 115.51 | 114.75 | AC2-059 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.84 | 114.42 | AC2-059 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.84 | 114.42 | AC2-059 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.48 | 113.78 | AC2-059 | PECO_P7-1_220-0607_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.48 | 113.78 | AC2-059 | PECO_P4_PEACH675_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3198 | 118.48 | 113.08 | AC2-059 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2812 | 114.02 | 112.51 | AF1-050 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 113.02 | 111.84 | AC2-059 | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 112.97 | 111.79 | AC2-059 | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 116.1 | 111.33 | AC2-059 | PECO_P1-2_220-07_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.93 | 111.28 | AC2-059 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.81 | 111.17 | AC2-059 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.84 | 111.15 | AC2-059 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.86 | 111.12 | AC2-059 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.32 | 110.33 | AC2-059 | AP_P1-2_WP-500-005A_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.32 | 110.33 | AC2-059 | AP_P1-2_WP-500-DRT21_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.32 | 110.33 | AC2-059 | AP_P2-3_WP-500-DRT20_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.32 | 110.33 | AC2-059 | AP_P2-3_WP-500-465_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.32 | 110.33 | AC2-059 | AP_P2-2_WP-500-DRT16_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2812 | 113.94 | 112.43 | AF1-147 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 121.08 | 116.02 | AC2-060 | PECO_P4_PEACH035_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.87 | 114.44 | AC2-060 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.87 | 114.44 | AC2-060 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.51 | 113.81 | AC2-060 | PECO_P7-1_220-0607_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.51 | 113.81 | AC2-060 | PECO_P4_PEACH675_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3198 | 118.51 | 113.12 | AC2-060 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 116.13 | 111.36 | AC2-060 | PECO_P1-2_220-07_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.96 | 111.31 | AC2-060 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.84 | 111.2 | AC2-060 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.87 | 111.18 | AC2-060 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.89 | 111.15 | AC2-060 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 108.91 | 107.61 | AC2-060 | PN_P2-3_PN-500-DRT30_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 108.91 | 107.61 | AC2-060 | PN_P2-3_PN-500-004-DRT-009_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 105.52 | 104.2 | AC2-060 | PN_P2-3_PN-500-004-DRT-002_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 105.52 | 104.2 | AC2-060 | PN_P2-3_PN-500-DRT32_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2812 | 113.76 | 112.24 | AF1-227 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 121.08 | 116.02 | AC2-061 | PECO_P4_PEACH035_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.87 | 114.44 | AC2-061 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.87 | 114.44 | AC2-061 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.51 | 113.81 | AC2-061 | PECO_P7-1_220-0607_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.51 | 113.81 | AC2-061 | PECO_P4_PEACH675_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3198 | 118.51 | 113.12 | AC2-061 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 116.13 | 111.36 | AC2-061 | PECO_P1-2_220-07_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.96 | 111.31 | AC2-061 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.84 | 111.2 | AC2-061 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.87 | 111.18 | AC2-061 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.89 | 111.15 | AC2-061 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 108.91 | 107.61 | AC2-061 | PN_P2-3_PN-500-DRT30_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 108.91 | 107.61 | AC2-061 | PN_P2-3_PN-500-004-DRT-009_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 108.71 | 107.41 | AC2-061 | PN_P2-3_PN-500-001B-DRT_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 108.71 | 107.41 | AC2-061 | PN_P1-2_PN-500-001_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 105.52 | 104.2 | AC2-061 | PN_P2-3_PN-500-DRT32_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 105.52 | 104.2 | AC2-061 | PN_P2-3_PN-500-004-DRT-002_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 136.19 | 133.12 | AC2-079 | AP_P1-2_PE-500-407T_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 136.19 | 133.12 | AC2-079 | DVP_P1-2: LN 514_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 136.19 | 133.11 | AC2-079 | DVP_P4-2: 51482_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 131.09 | 128.01 | AC2-079 | AP_P2-3_PE-500-019C_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2812 | 120.39 | 119.31 | AG2-055 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 118.3 | 117.43 | AC2-079 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 116.93 | 116.11 | AC2-079 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 120.92 | 115.86 | AC2-079 | PECO_P4_PEACH035_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 115.29 | 114.51 | AC2-079 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.65 | 114.23 | AC2-079 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.65 | 114.23 | AC2-079 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.32 | 113.63 | AC2-079 | PECO_P7-1_220-0607_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.32 | 113.63 | AC2-079 | PECO_P4_PEACH675_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3198 | 118.28 | 112.9 | AC2-079 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2812 | 114.4 | 112.92 | ALDENE_AB | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 112.81 | 111.61 | AC2-079 | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 112.76 | 111.56 | AC2-079 | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.94 | 111.18 | AC2-079 | PECO_P1-2_220-07_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.76 | 111.12 | AC2-079 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.64 | 111 | AC2-079 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.67 | 110.98 | AC2-079 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.7 | 110.97 | AC2-079 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.11 | 110.1 | AC2-079 | AP_P2-2_WP-500-DRT16_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.11 | 110.1 | AC2-079 | AP_P2-3_WP-500-465_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.11 | 110.1 | AC2-079 | AP_P1-2_WP-500-005A_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.11 | 110.1 | AC2-079 | AP_P1-2_WP-500-DRT21_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.11 | 110.1 | AC2-079 | AP_P2-3_WP-500-DRT20_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 105.1 | 102.41 | AC2-079 | DVP_P4-2: 560T571_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 104.94 | 102.27 | AC2-079 | DVP_P4-2: H2T560_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 104.93 | 102.25 | AC2-079 | DVP_P4-2: H1T560_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 104.79 | 102.11 | AC2-079 | PEPCO_P1_5070_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2812 | 113.74 | 112.22 | BIGSKY | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 121.13 | 116.06 | AC2-088 | PECO_P4_PEACH035_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.55 | 113.85 | AC2-088 | PECO_P4_PEACH675_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.55 | 113.85 | AC2-088 | PECO_P7-1_220-0607_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 116.17 | 111.4 | AC2-088 | PECO_P1-2_220-07_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 116.01 | 111.36 | AC2-088 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.89 | 111.24 | AC2-088 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.92 | 111.22 | AC2-088 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.93 | 111.19 | AC2-088 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.69 | 111.06 | AC2-088 | PECO_P4_NOTTI85_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.63 | 111.06 | AC2-088 | PECO_P1-2_220-08_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 607 | 168.9 | 166.19 | AC2-103 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 607 | 167.83 | 166.19 | AC2-103 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 607 | 168.57 | 166.18 | AC2-103 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 607 | 167.51 | 166.18 | AC2-103 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 607 | 167.75 | 166.12 | AC2-103 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 607 | 167.75 | 166.12 | AC2-103 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 607 | 168.82 | 166.12 | AC2-103 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 607 | 168.82 | 166.12 | AC2-103 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 628 | 159.82 | 158.45 | AC2-103 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 628 | 159.51 | 158.45 | AC2-103 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 628 | 159.75 | 158.38 | AC2-103 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 628 | 159.75 | 158.38 | AC2-103 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 628 | 157.12 | 156.16 | AC2-103 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 628 | 156.8 | 156.15 | AC2-103 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 628 | 157.04 | 156.09 | AC2-103 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 628 | 157.04 | 156.09 | AC2-103 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2812 | 113.82 | 112.3 | BISHOP | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 118.29 | 117.43 | AC2-103 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 116.92 | 116.1 | AC2-103 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 120.68 | 115.63 | AC2-103 | PECO_P4_PEACH035_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 115.29 | 114.51 | AC2-103 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.57 | 114.15 | AC2-103 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.57 | 114.15 | AC2-103 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.14 | 113.45 | AC2-103 | PECO_P4_PEACH675_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.14 | 113.45 | AC2-103 | PECO_P7-1_220-0607_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3198 | 118.08 | 112.71 | AC2-103 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2812 | 113.91 | 112.4 | CAMPGROVE;RU | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 112.8 | 111.6 | AC2-103 | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 112.75 | 111.56 | AC2-103 | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.76 | 111.01 | AC2-103 | PECO_P1-2_220-07_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.57 | 110.93 | AC2-103 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.45 | 110.82 | AC2-103 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.48 | 110.8 | AC2-103 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.52 | 110.79 | AC2-103 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.12 | 110.11 | AC2-103 | AP_P2-3_WP-500-465_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.12 | 110.11 | AC2-103 | AP_P2-2_WP-500-DRT16_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.12 | 110.11 | AC2-103 | AP_P1-2_WP-500-005A_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.12 | 110.11 | AC2-103 | AP_P1-2_WP-500-DRT21_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.12 | 110.11 | AC2-103 | AP_P2-3_WP-500-DRT20_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 112.75 | 108.36 | AC2-111 | PL_10_P42_100570_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 112.35 | 107.98 | AC2-111 | PN_P2-3_PN-500-004-DRT-008_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 112.35 | 107.98 | AC2-111 | PN_P2-3_PN-500-DRT31_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 112.29 | 107.92 | AC2-111 | PL_10_P12_000085_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 112.22 | 107.88 | AC2-111 | PL_30_P42_000131_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 136.5 | 133.43 | AC2-112 | AP_P1-2_PE-500-407T_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 136.5 | 133.43 | AC2-112 | DVP_P1-2: LN 514_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 136.5 | 133.41 | AC2-112 | DVP_P4-2: 51482_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 131.39 | 128.3 | AC2-112 | AP_P2-3_PE-500-019C_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2812 | 113.64 | 112.11 | CAYUGA | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 118.42 | 117.56 | AC2-112 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 117.05 | 116.24 | AC2-112 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 121.01 | 115.95 | AC2-112 | PECO_P4_PEACH035_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 115.41 | 114.64 | AC2-112 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.77 | 114.34 | AC2-112 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.77 | 114.34 | AC2-112 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.42 | 113.73 | AC2-112 | PECO_P7-1_220-0607_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.42 | 113.73 | AC2-112 | PECO_P4_PEACH675_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3198 | 118.41 | 113.02 | AC2-112 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2812 | 114.4 | 112.92 | D05 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 112.92 | 111.73 | AC2-112 | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 112.87 | 111.69 | AC2-112 | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 116.04 | 111.28 | AC2-112 | PECO_P1-2_220-07_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.87 | 111.23 | AC2-112 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.75 | 111.11 | AC2-112 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.78 | 111.09 | AC2-112 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.8 | 111.07 | AC2-112 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.22 | 110.22 | AC2-112 | AP_P1-2_WP-500-DRT21_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.22 | 110.22 | AC2-112 | AP_P2-3_WP-500-DRT20_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.22 | 110.22 | AC2-112 | AP_P1-2_WP-500-005A_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.22 | 110.22 | AC2-112 | AP_P2-2_WP-500-DRT16_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.22 | 110.22 | AC2-112 | AP_P2-3_WP-500-465_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 112.75 | 108.36 | AC2-123 | PL_10_P42_100570_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 112.35 | 107.98 | AC2-123 | PN_P2-3_PN-500-004-DRT-008_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 112.35 | 107.98 | AC2-123 | PN_P2-3_PN-500-DRT31_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 112.29 | 107.92 | AC2-123 | PL_10_P12_000085_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 112.23 | 107.88 | AC2-123 | PL_30_P42_000131_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 136.08 | 133.01 | AC2-165 | DVP_P1-2: LN 514_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 136.08 | 133.01 | AC2-165 | AP_P1-2_PE-500-407T_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 136.08 | 132.99 | AC2-165 | DVP_P4-2: 51482_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 130.98 | 127.9 | AC2-165 | AP_P2-3_PE-500-019C_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2812 | 114.36 | 112.88 | DC1 NUG | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 118.22 | 117.35 | AC2-165 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 116.85 | 116.03 | AC2-165 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 120.85 | 115.79 | AC2-165 | PECO_P4_PEACH035_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 115.22 | 114.43 | AC2-165 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.58 | 114.16 | AC2-165 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.58 | 114.16 | AC2-165 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.25 | 113.56 | AC2-165 | PECO_P4_PEACH675_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.25 | 113.56 | AC2-165 | PECO_P7-1_220-0607_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3198 | 118.2 | 112.82 | AC2-165 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2812 | 114.36 | 112.88 | DC2 NUG | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 112.74 | 111.53 | AC2-165 | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 112.69 | 111.49 | AC2-165 | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.87 | 111.12 | AC2-165 | PECO_P1-2_220-07_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.69 | 111.05 | AC2-165 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.57 | 110.93 | AC2-165 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.6 | 110.91 | AC2-165 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.63 | 110.9 | AC2-165 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.04 | 110.03 | AC2-165 | AP_P1-2_WP-500-DRT21_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.04 | 110.03 | AC2-165 | AP_P2-3_WP-500-DRT20_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.04 | 110.03 | AC2-165 | AP_P2-3_WP-500-465_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.04 | 110.03 | AC2-165 | AP_P2-2_WP-500-DRT16_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.04 | 110.03 | AC2-165 | AP_P1-2_WP-500-005A_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 105.01 | 102.32 | AC2-165 | DVP_P4-2: 560T571_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 104.84 | 102.18 | AC2-165 | DVP_P4-2: H2T560_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 104.84 | 102.16 | AC2-165 | DVP_P4-2: H1T560_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 104.7 | 102.01 | AC2-165 | PEPCO_P1_5070_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2812 | 114 | 112.5 | ECOGROVE ;U1 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 118.46 | 117.61 | AC2-176 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 117.09 | 116.29 | AC2-176 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 120.98 | 115.92 | AC2-176 | PECO_P4_PEACH035_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 115.46 | 114.69 | AC2-176 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.78 | 114.36 | AC2-176 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.78 | 114.36 | AC2-176 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.41 | 113.71 | AC2-176 | PECO_P7-1_220-0607_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.41 | 113.71 | AC2-176 | PECO_P4_PEACH675_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3198 | 118.4 | 113.01 | AC2-176 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2812 | 114.58 | 113.11 | FAIRLAWN_AB | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 112.97 | 111.78 | AC2-176 | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 112.92 | 111.73 | AC2-176 | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 116.03 | 111.27 | AC2-176 | PECO_P1-2_220-07_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.86 | 111.21 | AC2-176 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.74 | 111.1 | AC2-176 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.77 | 111.08 | AC2-176 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.79 | 111.05 | AC2-176 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.27 | 110.27 | AC2-176 | AP_P1-2_WP-500-005A_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.27 | 110.27 | AC2-176 | AP_P1-2_WP-500-DRT21_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.27 | 110.27 | AC2-176 | AP_P2-2_WP-500-DRT16_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.27 | 110.27 | AC2-176 | AP_P2-3_WP-500-465_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.27 | 110.27 | AC2-176 | AP_P2-3_WP-500-DRT20_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2812 | 113.61 | 112.08 | G07 NFTWR | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 121.44 | 116.36 | AC2-185 | PECO_P4_PEACH035_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 119.17 | 114.73 | AC2-185 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 119.17 | 114.73 | AC2-185 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.83 | 114.13 | AC2-185 | PECO_P4_PEACH675_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.83 | 114.13 | AC2-185 | PECO_P7-1_220-0607_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3198 | 118.92 | 113.5 | AC2-185 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 116.45 | 111.68 | AC2-185 | PECO_P1-2_220-07_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 116.31 | 111.66 | AC2-185 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 116.2 | 111.54 | AC2-185 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 116.23 | 111.52 | AC2-185 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 116.21 | 111.46 | AC2-185 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2812 | 113.62 | 112.1 | GR RIDGE | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 121.12 | 116.06 | AC2-195 | PECO_P4_PEACH035_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.55 | 113.85 | AC2-195 | PECO_P4_PEACH675_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.55 | 113.85 | AC2-195 | PECO_P7-1_220-0607_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 116.17 | 111.4 | AC2-195 | PECO_P1-2_220-07_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 116 | 111.35 | AC2-195 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.89 | 111.24 | AC2-195 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.92 | 111.22 | AC2-195 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.93 | 111.19 | AC2-195 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.69 | 111.06 | AC2-195 | PECO_P4_NOTTI85_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.62 | 111.06 | AC2-195 | PECO_P1-2_220-08_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 235463 | 01TANEY | 1 | 138 | 227/201 | 268 | 164.67 | 160.78 | AD1-020 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 235463 | 01TANEY | 1 | 138 | 227/201 | 268 | 164.67 | 160.78 | AD1-020 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 235463 | 01TANEY | 1 | 138 | 227/201 | 268 | 164.6 | 160.71 | AD1-020 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 282 | 143.99 | 143.71 | AD1-020 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 282 | 143.99 | 143.71 | AD1-020 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 282 | 143.93 | 143.64 | AD1-020 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204538 | 27STRABAN | 204544 | 27LINCOLN | 1 | 115 | 227 | 313 | 136.17 | 137.2 | AD1-020 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204538 | 27STRABAN | 204544 | 27LINCOLN | 1 | 115 | 227 | 313 | 136.17 | 137.2 | AD1-020 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204538 | 27STRABAN | 204544 | 27LINCOLN | 1 | 115 | 227 | 313 | 136.1 | 137.13 | AD1-020 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2812 | 113.99 | 112.49 | K28 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204529 | 27GERMANTN | 204538 | 27STRABAN | 1 | 115 | 227 | 313 | 132.72 | 134.47 | AD1-020 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204529 | 27GERMANTN | 204538 | 27STRABAN | 1 | 115 | 227 | 313 | 132.72 | 134.47 | AD1-020 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204529 | 27GERMANTN | 204538 | 27STRABAN | 1 | 115 | 227 | 313 | 132.65 | 134.39 | AD1-020 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 137.26 | 134.19 | AD1-020 | AP_P1-2_PE-500-407T_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 137.26 | 134.19 | AD1-020 | DVP_P1-2: LN 514_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 137.26 | 134.17 | AD1-020 | DVP_P4-2: 51482_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 235463 | 01TANEY | 1 | 138 | 227/201 | 268 | 139.12 | 132.49 | AD1-020 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 235463 | 01TANEY | 1 | 138 | 227/201 | 268 | 139.12 | 132.49 | AD1-020 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 235463 | 01TANEY | 1 | 138 | 227/201 | 268 | 139.11 | 132.49 | AD1-020 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 235463 | 01TANEY | 1 | 138 | 227/201 | 268 | 139.19 | 132.48 | AD1-020 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 204529 | 27GERMANTN | 1 | 138/115 | 227 | 345 | 127.92 | 130.83 | AD1-020 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 204529 | 27GERMANTN | 1 | 138/115 | 227 | 345 | 127.92 | 130.83 | AD1-020 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 204529 | 27GERMANTN | 1 | 138/115 | 227 | 345 | 127.86 | 130.76 | AD1-020 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 132.16 | 129.08 | AD1-020 | AP_P2-3_PE-500-019C_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 235463 | 01TANEY | 1 | 138 | 227/201 | 268 | 131.18 | 129.02 | AD1-020 | PEPCO_P4_PP41_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 814 | 132.19 | 127.71 | AD1-020 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 814 | 132.72 | 127.62 | AD1-020 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 814 | 132.72 | 127.62 | AD1-020 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 814 | 132.7 | 127.61 | AD1-020 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 235463 | 01TANEY | 1 | 138 | 227/201 | 268 | 128.46 | 126.83 | AD1-020 | AP_P2-3_PE-500-019B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 204550 | 27ORRTANNA | 1 | 115 | 227 | 160 | 127.96 | 126.39 | AD1-020 | ME_P1-2_ME-115-068_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 235463 | 01TANEY | 1 | 138 | 227/201 | 268 | 126.99 | 125.1 | AD1-020 | PEPCO_P1_5055_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 204550 | 27ORRTANNA | 1 | 115 | 227 | 160 | 126.41 | 124.82 | AD1-020 | ME_P2-3_ME-115-013B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 204550 | 27ORRTANNA | 1 | 115 | 227 | 160 | 126.27 | 124.67 | AD1-020 | ME_P2-3_ME-115-013A_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2812 | 113.87 | 112.36 | KELLY CRK;1U | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 814 | 123.38 | 118.47 | AD1-020 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 282 | 122.43 | 118.21 | AD1-020 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 282 | 122.43 | 118.21 | AD1-020 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 282 | 122.42 | 118.2 | AD1-020 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 282 | 122.49 | 118.2 | AD1-020 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 118.91 | 118.1 | AD1-020 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 117.54 | 116.77 | AD1-020 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 121.12 | 116.06 | AD1-020 | PECO_P4_PEACH035_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 115.9 | 115.17 | AD1-020 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 282 | 115.73 | 114.17 | AD1-020 | PEPCO_P4_PP41_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2812 | 113.89 | 112.38 | M24 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 113.38 | 112.22 | AD1-020 | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 282 | 113.43 | 112.19 | AD1-020 | AP_P2-3_PE-500-019B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 113.33 | 112.17 | AD1-020 | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 797 | 113.66 | 112.16 | AD1-020 | PJM_500_BG_P4_5_CNSTN_15_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204538 | 27STRABAN | 204544 | 27LINCOLN | 1 | 115 | 227 | 313 | 114.29 | 111.26 | AD1-020 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204538 | 27STRABAN | 204544 | 27LINCOLN | 1 | 115 | 227 | 313 | 114.29 | 111.26 | AD1-020 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204538 | 27STRABAN | 204544 | 27LINCOLN | 1 | 115 | 227 | 313 | 114.28 | 111.25 | AD1-020 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204538 | 27STRABAN | 204544 | 27LINCOLN | 1 | 115 | 227 | 313 | 114.35 | 111.25 | AD1-020 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2812 | 113.82 | 112.31 | MINONK ;1U | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.7 | 110.73 | AD1-020 | AP_P2-3_WP-500-465_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.7 | 110.73 | AD1-020 | AP_P1-2_WP-500-005A_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.7 | 110.73 | AD1-020 | AP_P2-2_WP-500-DRT16_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.7 | 110.73 | AD1-020 | AP_P2-3_WP-500-DRT20_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.7 | 110.73 | AD1-020 | AP_P1-2_WP-500-DRT21_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 282 | 114.65 | 110.68 | AD1-020 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204529 | 27GERMANTN | 204538 | 27STRABAN | 1 | 115 | 227 | 313 | 110.84 | 108.55 | AD1-020 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204529 | 27GERMANTN | 204538 | 27STRABAN | 1 | 115 | 227 | 313 | 110.84 | 108.55 | AD1-020 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204529 | 27GERMANTN | 204538 | 27STRABAN | 1 | 115 | 227 | 313 | 110.83 | 108.54 | AD1-020 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204529 | 27GERMANTN | 204538 | 27STRABAN | 1 | 115 | 227 | 313 | 110.9 | 108.54 | AD1-020 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 112.21 | 107.68 | AD1-020 | PECO_P1-2_5007_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2812 | 113.72 | 112.2 | O09 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 112.04 | 107.53 | AD1-020 | PECO_P4_PEACH025_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204538 | 27STRABAN | 204544 | 27LINCOLN | 1 | 115 | 227 | 313 | 107.49 | 107.19 | AD1-020 | PEPCO_P4_PP41_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 204529 | 27GERMANTN | 1 | 138/115 | 227 | 345 | 108.07 | 107.13 | AD1-020 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 204529 | 27GERMANTN | 1 | 138/115 | 227 | 345 | 108.07 | 107.13 | AD1-020 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 204529 | 27GERMANTN | 1 | 138/115 | 227 | 345 | 108.06 | 107.13 | AD1-020 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 204529 | 27GERMANTN | 1 | 138/115 | 227 | 345 | 108.12 | 107.12 | AD1-020 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 111.37 | 107.01 | AD1-020 | PN_P1-2_PN-500-010T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2812 | 113.77 | 112.25 | O29 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 110.82 | 106.46 | AD1-020 | ME_P2-3_ME-230-018A_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 110.75 | 106.39 | AD1-020 | ME_P1-2_ME-230-008_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 110.75 | 106.39 | AD1-020 | ME_P2-3_ME-230-007C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 110.75 | 106.39 | AD1-020 | ME_P2-3_ME-230-DTR030_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 110.73 | 106.37 | AD1-020 | ME_P2-3_ME-230-007D_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 109.88 | 105.5 | AD1-020 | ME_P2-4_ME-115-0102-B134_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204538 | 27STRABAN | 204544 | 27LINCOLN | 1 | 115 | 227 | 313 | 105.16 | 105.18 | AD1-020 | AP_P2-3_PE-500-019B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204529 | 27GERMANTN | 204538 | 27STRABAN | 1 | 115 | 227 | 313 | 104.04 | 104.48 | AD1-020 | PEPCO_P4_PP41_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204538 | 27STRABAN | 204544 | 27LINCOLN | 1 | 115 | 227 | 313 | 106.39 | 103.61 | AD1-020 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 204529 | 27GERMANTN | 1 | 138/115 | 227 | 345 | 101.9 | 103.45 | AD1-020 | PEPCO_P4_PP41_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 105.85 | 103.18 | AD1-020 | DVP_P4-2: H2T560_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 105.85 | 103.16 | AD1-020 | DVP_P4-2: H1T560_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 105.71 | 103.02 | AD1-020 | PEPCO_P1_5070_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204502 | 27JACKSON | 204514 | 27TMI | 1 | 230 | 227 | 659 | 102.75 | 102.73 | AD1-020 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204502 | 27JACKSON | 204514 | 27TMI | 1 | 230 | 227 | 659 | 102.75 | 102.73 | AD1-020 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204502 | 27JACKSON | 204514 | 27TMI | 1 | 230 | 227 | 659 | 102.81 | 102.72 | AD1-020 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204502 | 27JACKSON | 204514 | 27TMI | 1 | 230 | 227 | 659 | 102.73 | 102.71 | AD1-020 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204529 | 27GERMANTN | 204538 | 27STRABAN | 1 | 115 | 227 | 313 | 101.71 | 102.47 | AD1-020 | AP_P2-3_PE-500-019B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 801 | 103.92 | 101.91 | AD1-020 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 801 | 104.36 | 101.84 | AD1-020 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 801 | 104.36 | 101.84 | AD1-020 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 801 | 104.34 | 101.82 | AD1-020 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204539 | 27HUNTRSTN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 282 | 101.66 | 101.62 | AD1-020 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204539 | 27HUNTRSTN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 282 | 101.66 | 101.62 | AD1-020 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 204529 | 27GERMANTN | 1 | 138/115 | 227 | 345 | 99.79 | 101.61 | AD1-020 | AP_P2-3_PE-500-019B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204539 | 27HUNTRSTN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 282 | 101.6 | 101.55 | AD1-020 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204529 | 27GERMANTN | 204538 | 27STRABAN | 1 | 115 | 227 | 313 | 102.94 | 100.9 | AD1-020 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 204529 | 27GERMANTN | 1 | 138/115 | 227 | 345 | 100.9 | 100.17 | AD1-020 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2812 | 110.62 | 108.93 | O66 NFTWR | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 121.13 | 116.06 | AD1-022 | PECO_P4_PEACH035_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.88 | 114.45 | AD1-022 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.88 | 114.45 | AD1-022 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.54 | 113.84 | AD1-022 | PECO_P7-1_220-0607_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.54 | 113.84 | AD1-022 | PECO_P4_PEACH675_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3198 | 118.55 | 113.15 | AD1-022 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 116.16 | 111.4 | AD1-022 | PECO_P1-2_220-07_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 116 | 111.35 | AD1-022 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.88 | 111.23 | AD1-022 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.91 | 111.21 | AD1-022 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.92 | 111.18 | AD1-022 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 136.34 | 133.28 | AD1-025 | AP_P1-2_PE-500-407T_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 136.34 | 133.28 | AD1-025 | DVP_P1-2: LN 514_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 136.34 | 133.26 | AD1-025 | DVP_P4-2: 51482_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 131.24 | 128.16 | AD1-025 | AP_P2-3_PE-500-019C_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2812 | 114.47 | 113 | P28 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 118.39 | 117.53 | AD1-025 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 117.02 | 116.21 | AD1-025 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 121 | 115.94 | AD1-025 | PECO_P4_PEACH035_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 115.39 | 114.61 | AD1-025 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.74 | 114.32 | AD1-025 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.74 | 114.32 | AD1-025 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.4 | 113.71 | AD1-025 | PECO_P7-1_220-0607_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.4 | 113.71 | AD1-025 | PECO_P4_PEACH675_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3198 | 118.39 | 113 | AD1-025 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2812 | 114 | 112.5 | P59 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 112.9 | 111.7 | AD1-025 | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 112.85 | 111.66 | AD1-025 | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 116.03 | 111.27 | AD1-025 | PECO_P1-2_220-07_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.85 | 111.21 | AD1-025 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.73 | 111.09 | AD1-025 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.76 | 111.07 | AD1-025 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.79 | 111.05 | AD1-025 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.2 | 110.2 | AD1-025 | AP_P1-2_WP-500-005A_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.2 | 110.2 | AD1-025 | AP_P2-2_WP-500-DRT16_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.2 | 110.2 | AD1-025 | AP_P2-3_WP-500-DRT20_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.2 | 110.2 | AD1-025 | AP_P2-3_WP-500-465_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.2 | 110.2 | AD1-025 | AP_P1-2_WP-500-DRT21_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 105.23 | 102.54 | AD1-025 | DVP_P4-2: 560T571_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 105.07 | 102.4 | AD1-025 | DVP_P4-2: H2T560_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 105.06 | 102.38 | AD1-025 | DVP_P4-2: H1T560_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 104.92 | 102.23 | AD1-025 | PEPCO_P1_5070_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.9 | 114.47 | AD1-033 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.9 | 114.47 | AD1-033 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 116.01 | 111.36 | AD1-033 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.9 | 111.25 | AD1-033 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.92 | 111.23 | AD1-033 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.7 | 111.07 | AD1-033 | PECO_P4_NOTTI85_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.63 | 111.06 | AD1-033 | PECO_P1-2_220-08_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.59 | 111.02 | AD1-033 | PECO_P4_COOPR125_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.35 | 110.87 | AD1-033 | PECO_P1-2_220-93_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 114.66 | 110.27 | AD1-033 | PL_05_P71_000906_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2812 | 112.81 | 111.24 | Q01/Q03 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 118.47 | 117.62 | AD1-070 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 117.1 | 116.3 | AD1-070 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 120.97 | 115.91 | AD1-070 | PECO_P4_PEACH035_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 115.47 | 114.7 | AD1-070 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.78 | 114.36 | AD1-070 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.78 | 114.36 | AD1-070 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.4 | 113.71 | AD1-070 | PECO_P7-1_220-0607_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.4 | 113.71 | AD1-070 | PECO_P4_PEACH675_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3198 | 118.39 | 113 | AD1-070 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2812 | 114.5 | 113.03 | Q27 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 112.97 | 111.79 | AD1-070 | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 112.92 | 111.74 | AD1-070 | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 116.03 | 111.27 | AD1-070 | PECO_P1-2_220-07_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.85 | 111.21 | AD1-070 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.73 | 111.09 | AD1-070 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.76 | 111.07 | AD1-070 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.79 | 111.05 | AD1-070 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.28 | 110.28 | AD1-070 | AP_P2-3_WP-500-465_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.28 | 110.28 | AD1-070 | AP_P2-2_WP-500-DRT16_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.28 | 110.28 | AD1-070 | AP_P1-2_WP-500-005A_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.28 | 110.28 | AD1-070 | AP_P1-2_WP-500-DRT21_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.28 | 110.28 | AD1-070 | AP_P2-3_WP-500-DRT20_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 116.02 | 111.37 | AD1-082 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.9 | 111.25 | AD1-082 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.7 | 111.08 | AD1-082 | PECO_P4_NOTTI85_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.64 | 111.07 | AD1-082 | PECO_P1-2_220-08_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.59 | 111.02 | AD1-082 | PECO_P4_COOPR125_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.35 | 110.87 | AD1-082 | PECO_P1-2_220-93_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 113.73 | 109.47 | AD1-082 | AP_P2-3_WP-500-DRT20_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 113.73 | 109.47 | AD1-082 | AP_P1-2_WP-500-005A_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 113.73 | 109.47 | AD1-082 | AP_P1-2_WP-500-DRT21_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 136.38 | 133.32 | AD1-083 | DVP_P1-2: LN 514_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 136.38 | 133.32 | AD1-083 | AP_P1-2_PE-500-407T_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 136.38 | 133.3 | AD1-083 | DVP_P4-2: 51482_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 131.27 | 128.2 | AD1-083 | AP_P2-3_PE-500-019C_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2812 | 113.75 | 112.23 | Q57 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 118.23 | 117.36 | AD1-083 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 116.86 | 116.03 | AD1-083 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 120.85 | 115.79 | AD1-083 | PECO_P4_PEACH035_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 115.23 | 114.44 | AD1-083 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.59 | 114.17 | AD1-083 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.59 | 114.17 | AD1-083 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.25 | 113.56 | AD1-083 | PECO_P4_PEACH675_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.25 | 113.56 | AD1-083 | PECO_P7-1_220-0607_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3198 | 118.21 | 112.82 | AD1-083 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2812 | 113.93 | 112.42 | R49 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 112.74 | 111.54 | AD1-083 | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 112.69 | 111.49 | AD1-083 | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.87 | 111.12 | AD1-083 | PECO_P1-2_220-07_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.69 | 111.05 | AD1-083 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.57 | 110.93 | AD1-083 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.6 | 110.91 | AD1-083 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.63 | 110.9 | AD1-083 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.03 | 110.02 | AD1-083 | AP_P2-3_WP-500-465_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.03 | 110.02 | AD1-083 | AP_P2-2_WP-500-DRT16_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.03 | 110.02 | AD1-083 | AP_P2-3_WP-500-DRT20_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.03 | 110.02 | AD1-083 | AP_P1-2_WP-500-005A_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.03 | 110.02 | AD1-083 | AP_P1-2_WP-500-DRT21_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 105.21 | 102.52 | AD1-083 | DVP_P4-2: 560T571_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 105.05 | 102.39 | AD1-083 | DVP_P4-2: H2T560_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 105.05 | 102.37 | AD1-083 | DVP_P4-2: H1T560_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 104.91 | 102.22 | AD1-083 | PEPCO_P1_5070_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2812 | 113.59 | 112.06 | R60 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 118.49 | 117.63 | AD1-088 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 117.11 | 116.31 | AD1-088 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 121.07 | 116.01 | AD1-088 | PECO_P4_PEACH035_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 115.48 | 114.71 | AD1-088 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.83 | 114.4 | AD1-088 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.83 | 114.4 | AD1-088 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.48 | 113.79 | AD1-088 | PECO_P7-1_220-0607_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.48 | 113.79 | AD1-088 | PECO_P4_PEACH675_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3198 | 118.49 | 113.09 | AD1-088 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2812 | 113.82 | 112.31 | S06 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 112.99 | 111.8 | AD1-088 | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 112.94 | 111.75 | AD1-088 | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 116.11 | 111.34 | AD1-088 | PECO_P1-2_220-07_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.94 | 111.29 | AD1-088 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.82 | 111.18 | AD1-088 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.85 | 111.16 | AD1-088 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.87 | 111.13 | AD1-088 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.29 | 110.3 | AD1-088 | AP_P2-3_WP-500-465_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.29 | 110.3 | AD1-088 | AP_P1-2_WP-500-005A_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.29 | 110.3 | AD1-088 | AP_P1-2_WP-500-DRT21_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.29 | 110.3 | AD1-088 | AP_P2-3_WP-500-DRT20_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.29 | 110.3 | AD1-088 | AP_P2-2_WP-500-DRT16_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2812 | 113.86 | 112.35 | S36 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 121.13 | 116.06 | AD1-105 | PECO_P4_PEACH035_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.88 | 114.45 | AD1-105 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.88 | 114.45 | AD1-105 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.54 | 113.84 | AD1-105 | PECO_P7-1_220-0607_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.54 | 113.84 | AD1-105 | PECO_P4_PEACH675_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3198 | 118.55 | 113.15 | AD1-105 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 116.16 | 111.39 | AD1-105 | PECO_P1-2_220-07_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.99 | 111.34 | AD1-105 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.88 | 111.23 | AD1-105 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.9 | 111.21 | AD1-105 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.92 | 111.18 | AD1-105 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 136.3 | 133.24 | AD1-115 | DVP_P1-2: LN 514_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 136.3 | 133.24 | AD1-115 | AP_P1-2_PE-500-407T_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 136.3 | 133.22 | AD1-115 | DVP_P4-2: 51482_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 131.2 | 128.12 | AD1-115 | AP_P2-3_PE-500-019C_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2812 | 113.97 | 112.47 | S71 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 118.43 | 117.58 | AD1-115 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 117.06 | 116.25 | AD1-115 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 121.05 | 115.98 | AD1-115 | PECO_P4_PEACH035_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 115.43 | 114.65 | AD1-115 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.78 | 114.36 | AD1-115 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.78 | 114.36 | AD1-115 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.45 | 113.75 | AD1-115 | PECO_P7-1_220-0607_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.45 | 113.75 | AD1-115 | PECO_P4_PEACH675_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3198 | 118.44 | 113.05 | AD1-115 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2812 | 114.38 | 112.9 | SEWAREN_IM | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 112.93 | 111.74 | AD1-115 | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 112.88 | 111.7 | AD1-115 | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 116.07 | 111.31 | AD1-115 | PECO_P1-2_220-07_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.9 | 111.25 | AD1-115 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.78 | 111.14 | AD1-115 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.81 | 111.12 | AD1-115 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.83 | 111.09 | AD1-115 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.24 | 110.24 | AD1-115 | AP_P2-2_WP-500-DRT16_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.24 | 110.24 | AD1-115 | AP_P1-2_WP-500-005A_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.24 | 110.24 | AD1-115 | AP_P2-3_WP-500-DRT20_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.24 | 110.24 | AD1-115 | AP_P1-2_WP-500-DRT21_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.24 | 110.24 | AD1-115 | AP_P2-3_WP-500-465_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 105.25 | 102.56 | AD1-115 | DVP_P4-2: 560T571_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 105.09 | 102.42 | AD1-115 | DVP_P4-2: H2T560_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 105.09 | 102.4 | AD1-115 | DVP_P4-2: H1T560_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 104.95 | 102.26 | AD1-115 | PEPCO_P1_5070_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2812 | 113.82 | 112.31 | T126 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 118.51 | 117.67 | AD1-125 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 117.14 | 116.34 | AD1-125 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 121.07 | 116.01 | AD1-125 | PECO_P4_PEACH035_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 115.51 | 114.74 | AD1-125 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.85 | 114.42 | AD1-125 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.85 | 114.42 | AD1-125 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.49 | 113.79 | AD1-125 | PECO_P4_PEACH675_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.49 | 113.79 | AD1-125 | PECO_P7-1_220-0607_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3198 | 118.5 | 113.1 | AD1-125 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2812 | 113.83 | 112.31 | T127 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 113.01 | 111.83 | AD1-125 | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 112.96 | 111.78 | AD1-125 | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 116.11 | 111.35 | AD1-125 | PECO_P1-2_220-07_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.95 | 111.3 | AD1-125 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.83 | 111.18 | AD1-125 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.86 | 111.16 | AD1-125 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.87 | 111.13 | AD1-125 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.31 | 110.31 | AD1-125 | AP_P2-3_WP-500-DRT20_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.31 | 110.31 | AD1-125 | AP_P1-2_WP-500-005A_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.31 | 110.31 | AD1-125 | AP_P2-3_WP-500-465_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.31 | 110.31 | AD1-125 | AP_P1-2_WP-500-DRT21_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.31 | 110.31 | AD1-125 | AP_P2-2_WP-500-DRT16_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2812 | 113.89 | 112.38 | T157 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 118.51 | 117.66 | AD1-128 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 117.14 | 116.33 | AD1-128 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 121.04 | 115.97 | AD1-128 | PECO_P4_PEACH035_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 115.5 | 114.74 | AD1-128 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.83 | 114.4 | AD1-128 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.83 | 114.4 | AD1-128 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.46 | 113.77 | AD1-128 | PECO_P7-1_220-0607_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.46 | 113.77 | AD1-128 | PECO_P4_PEACH675_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3198 | 118.46 | 113.07 | AD1-128 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2812 | 113.64 | 112.12 | TOP CROP | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 113.01 | 111.82 | AD1-128 | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 112.96 | 111.78 | AD1-128 | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 116.08 | 111.32 | AD1-128 | PECO_P1-2_220-07_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.91 | 111.27 | AD1-128 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.8 | 111.15 | AD1-128 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.83 | 111.13 | AD1-128 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.84 | 111.11 | AD1-128 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.31 | 110.32 | AD1-128 | AP_P2-2_WP-500-DRT16_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.31 | 110.32 | AD1-128 | AP_P2-3_WP-500-DRT20_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.31 | 110.32 | AD1-128 | AP_P1-2_WP-500-DRT21_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.31 | 110.32 | AD1-128 | AP_P2-3_WP-500-465_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.31 | 110.32 | AD1-128 | AP_P1-2_WP-500-005A_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 607 | 168.91 | 166.2 | AD1-140 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 607 | 167.84 | 166.2 | AD1-140 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 607 | 167.51 | 166.19 | AD1-140 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 607 | 168.58 | 166.19 | AD1-140 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 607 | 168.83 | 166.13 | AD1-140 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 607 | 167.76 | 166.13 | AD1-140 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 607 | 167.76 | 166.13 | AD1-140 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 607 | 168.83 | 166.13 | AD1-140 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 628 | 159.83 | 158.46 | AD1-140 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 628 | 159.52 | 158.45 | AD1-140 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 628 | 159.76 | 158.39 | AD1-140 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 628 | 159.76 | 158.39 | AD1-140 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 628 | 157.13 | 156.17 | AD1-140 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 628 | 156.81 | 156.16 | AD1-140 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 628 | 157.05 | 156.1 | AD1-140 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 628 | 157.05 | 156.1 | AD1-140 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2812 | 114.01 | 112.51 | TR3_G114 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 118.24 | 117.37 | AD1-140 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 116.87 | 116.05 | AD1-140 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 120.71 | 115.65 | AD1-140 | PECO_P4_PEACH035_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 115.24 | 114.45 | AD1-140 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.55 | 114.13 | AD1-140 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.55 | 114.13 | AD1-140 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.15 | 113.46 | AD1-140 | PECO_P4_PEACH675_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.15 | 113.46 | AD1-140 | PECO_P7-1_220-0607_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3198 | 118.09 | 112.71 | AD1-140 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2812 | 113.46 | 111.92 | TWINGROVE | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 112.75 | 111.55 | AD1-140 | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 112.7 | 111.51 | AD1-140 | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.77 | 111.02 | AD1-140 | PECO_P1-2_220-07_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.58 | 110.94 | AD1-140 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.46 | 110.83 | AD1-140 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.49 | 110.81 | AD1-140 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.53 | 110.8 | AD1-140 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.05 | 110.03 | AD1-140 | AP_P2-3_WP-500-465_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.05 | 110.03 | AD1-140 | AP_P2-3_WP-500-DRT20_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.05 | 110.03 | AD1-140 | AP_P2-2_WP-500-DRT16_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.05 | 110.03 | AD1-140 | AP_P1-2_WP-500-DRT21_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.05 | 110.03 | AD1-140 | AP_P1-2_WP-500-005A_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 105.25 | 102.56 | AD1-140 | DVP_P4-2: 560T571_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 105.09 | 102.42 | AD1-140 | DVP_P4-2: H2T560_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 105.08 | 102.4 | AD1-140 | DVP_P4-2: H1T560_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 104.94 | 102.25 | AD1-140 | PEPCO_P1_5070_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 607 | 170.59 | 168.04 | AD1-143 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 607 | 169.5 | 168.04 | AD1-143 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 607 | 170.23 | 168 | AD1-143 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 607 | 169.14 | 168 | AD1-143 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 607 | 170.51 | 167.96 | AD1-143 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 607 | 170.51 | 167.96 | AD1-143 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 607 | 169.42 | 167.96 | AD1-143 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 607 | 169.42 | 167.96 | AD1-143 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2812 | 113.76 | 112.25 | U2-072 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 628 | 161.44 | 160.24 | AD1-143 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 628 | 161.09 | 160.2 | AD1-143 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 628 | 161.36 | 160.17 | AD1-143 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 628 | 161.36 | 160.17 | AD1-143 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 628 | 158.73 | 157.95 | AD1-143 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 628 | 158.38 | 157.91 | AD1-143 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 628 | 158.65 | 157.88 | AD1-143 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 628 | 158.65 | 157.88 | AD1-143 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 607 | 155.39 | 153.42 | AD1-143 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 607 | 156.48 | 153.42 | AD1-143 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 628 | 147.8 | 146.09 | AD1-143 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 628 | 145.09 | 143.78 | AD1-143 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 797 | 142.03 | 137.44 | AD1-143 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 797 | 142.32 | 137.41 | AD1-143 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 797 | 142.32 | 137.41 | AD1-143 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 797 | 142.29 | 137.39 | AD1-143 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 137.32 | 134.24 | AD1-143 | DVP_P1-2: LN 514_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 137.32 | 134.24 | AD1-143 | AP_P1-2_PE-500-407T_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 137.32 | 134.22 | AD1-143 | DVP_P4-2: 51482_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 132.2 | 129.11 | AD1-143 | AP_P2-3_PE-500-019C_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 797 | 133.93 | 129.11 | AD1-143 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 814 | 132.31 | 127.78 | AD1-143 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 814 | 132.86 | 127.71 | AD1-143 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 814 | 132.86 | 127.71 | AD1-143 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 814 | 132.84 | 127.7 | AD1-143 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2812 | 113.88 | 112.37 | U2-073 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2812 | 113.83 | 112.31 | U2-090 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2812 | 113.65 | 112.13 | U3-002 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 814 | 123.52 | 118.56 | AD1-143 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 119.2 | 118.4 | AD1-143 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 211061 | PSPA TP1 | 211068 | AD1-143 TAP | 1 | 69 | 229 | 91 | 117.88 | 117.28 | AD1-143 | PL_40_P11_000877_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 117.82 | 117.07 | AD1-143 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 121.69 | 116.62 | AD1-143 | PECO_P4_PEACH035_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 116.18 | 115.47 | AD1-143 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 119.52 | 115.07 | AD1-143 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 119.52 | 115.07 | AD1-143 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 119.2 | 114.49 | AD1-143 | PECO_P7-1_220-0607_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 119.2 | 114.49 | AD1-143 | PECO_P4_PEACH675_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 814 | 117.14 | 114.14 | AD1-143 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 814 | 117.43 | 114.1 | AD1-143 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 814 | 117.43 | 114.1 | AD1-143 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 814 | 117.4 | 114.09 | AD1-143 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3198 | 119.41 | 113.96 | AD1-143 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2812 | 114.02 | 112.51 | V1-011 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 113.66 | 112.52 | AD1-143 | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 113.61 | 112.47 | AD1-143 | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 116.83 | 112.04 | AD1-143 | PECO_P1-2_220-07_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 116.71 | 112.04 | AD1-143 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 116.59 | 111.93 | AD1-143 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 116.62 | 111.91 | AD1-143 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 116.58 | 111.82 | AD1-143 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.98 | 111.03 | AD1-143 | AP_P1-2_WP-500-005A_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.98 | 111.03 | AD1-143 | AP_P2-2_WP-500-DRT16_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.98 | 111.03 | AD1-143 | AP_P2-3_WP-500-DRT20_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.98 | 111.03 | AD1-143 | AP_P1-2_WP-500-DRT21_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.98 | 111.03 | AD1-143 | AP_P2-3_WP-500-465_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 814 | 109.01 | 105.67 | AD1-143 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2812 | 113.82 | 112.3 | V3-007 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2812 | 113.82 | 112.31 | V3-028 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 106.08 | 103.37 | AD1-143 | DVP_P4-2: 560T571_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 105.92 | 103.24 | AD1-143 | DVP_P4-2: H2T560_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 105.92 | 103.22 | AD1-143 | DVP_P4-2: H1T560_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 105.77 | 103.08 | AD1-143 | PEPCO_P1_5070_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 801 | 103.86 | 101.36 | AD1-143 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 801 | 103.86 | 101.36 | AD1-143 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 801 | 103.84 | 101.34 | AD1-143 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2812 | 113.54 | 112.01 | W1-029 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 121.13 | 116.06 | AD1-152 | PECO_P4_PEACH035_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.89 | 114.46 | AD1-152 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.89 | 114.46 | AD1-152 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.54 | 113.84 | AD1-152 | PECO_P4_PEACH675_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.54 | 113.84 | AD1-152 | PECO_P7-1_220-0607_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3198 | 118.56 | 113.16 | AD1-152 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 116.16 | 111.4 | AD1-152 | PECO_P1-2_220-07_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 116 | 111.35 | AD1-152 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.88 | 111.24 | AD1-152 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.91 | 111.21 | AD1-152 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.92 | 111.18 | AD1-152 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2812 | 113.62 | 112.1 | W4-005 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 118.53 | 117.69 | AD1-155 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 121.12 | 116.06 | AD1-155 | PECO_P4_PEACH035_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.88 | 114.45 | AD1-155 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.88 | 114.45 | AD1-155 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.53 | 113.84 | AD1-155 | PECO_P4_PEACH675_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.53 | 113.84 | AD1-155 | PECO_P7-1_220-0607_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3198 | 118.55 | 113.15 | AD1-155 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 116.15 | 111.39 | AD1-155 | PECO_P1-2_220-07_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.99 | 111.34 | AD1-155 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.87 | 111.23 | AD1-155 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.9 | 111.21 | AD1-155 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.91 | 111.17 | AD1-155 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.4 | 110.22 | AD1-155 | BG_P7_GRNITE_HIRDG_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 109.85 | 108.81 | AD1-155 | AP_P2-3_PE-500-015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 109.83 | 108.79 | AD1-155 | AP_P2-3_PE-500-016_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 109.61 | 108.59 | AD1-155 | AP_P2-3_PE-500-018D_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 109.61 | 108.59 | AD1-155 | AP_P2-3_PE-500-018C_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 106.79 | 105.6 | AD1-155 | DVP_P4-2: 53672_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 106.79 | 105.55 | AD1-155 | AP_P1-2_WP-500-304T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 106.57 | 105.37 | AD1-155 | DVP_P4-2: 536T550_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 116.02 | 111.37 | AD2-009 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.9 | 111.25 | AD2-009 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.93 | 111.23 | AD2-009 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.7 | 111.07 | AD2-009 | PECO_P4_NOTTI85_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.64 | 111.07 | AD2-009 | PECO_P1-2_220-08_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.59 | 111.02 | AD2-009 | PECO_P4_COOPR125_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.35 | 110.87 | AD2-009 | PECO_P1-2_220-93_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 113.73 | 109.46 | AD2-009 | AP_P2-3_WP-500-465_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 113.73 | 109.46 | AD2-009 | AP_P1-2_WP-500-DRT21_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 113.73 | 109.46 | AD2-009 | AP_P1-2_WP-500-005A_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2812 | 113.84 | 112.33 | X2-022 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 118.37 | 117.51 | AD2-016 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 117 | 116.18 | AD2-016 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 120.86 | 115.8 | AD2-016 | PECO_P4_PEACH035_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 115.36 | 114.58 | AD2-016 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.68 | 114.26 | AD2-016 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.68 | 114.26 | AD2-016 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.3 | 113.6 | AD2-016 | PECO_P7-1_220-0607_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.3 | 113.6 | AD2-016 | PECO_P4_PEACH675_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3198 | 118.27 | 112.88 | AD2-016 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2812 | 113.89 | 112.38 | X2-060 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 112.87 | 111.68 | AD2-016 | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 112.82 | 111.63 | AD2-016 | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.92 | 111.16 | AD2-016 | PECO_P1-2_220-07_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.74 | 111.09 | AD2-016 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.62 | 110.98 | AD2-016 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.65 | 110.96 | AD2-016 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.68 | 110.94 | AD2-016 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.17 | 110.16 | AD2-016 | AP_P2-2_WP-500-DRT16_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.17 | 110.16 | AD2-016 | AP_P1-2_WP-500-005A_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.17 | 110.16 | AD2-016 | AP_P2-3_WP-500-DRT20_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.17 | 110.16 | AD2-016 | AP_P2-3_WP-500-465_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.17 | 110.16 | AD2-016 | AP_P1-2_WP-500-DRT21_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 203981 | AD2-062_POI | 235188 | 01GREENE | 1 | 138 | 226/201 | 268 | 143.83 | 139.79 | AD2-062 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 203981 | AD2-062_POI | 235188 | 01GREENE | 1 | 138 | 226/201 | 268 | 143.83 | 139.79 | AD2-062 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 203981 | AD2-062_POI | 235188 | 01GREENE | 1 | 138 | 226/201 | 268 | 143.73 | 139.69 | AD2-062 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 203981 | AD2-062_POI | 235188 | 01GREENE | 1 | 138 | 226/201 | 268 | 137.93 | 131.26 | AD2-062 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 203981 | AD2-062_POI | 235188 | 01GREENE | 1 | 138 | 226/201 | 268 | 137.93 | 131.26 | AD2-062 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 203981 | AD2-062_POI | 235188 | 01GREENE | 1 | 138 | 226/201 | 268 | 137.92 | 131.25 | AD2-062 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 203981 | AD2-062_POI | 235188 | 01GREENE | 1 | 138 | 226/201 | 268 | 138 | 131.25 | AD2-062 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2812 | 113.25 | 111.71 | Z1-036 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 203981 | AD2-062_POI | 235188 | 01GREENE | 1 | 138 | 226/201 | 268 | 130.19 | 124.81 | AD2-062 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 203981 | AD2-062_POI | 235188 | 01GREENE | 1 | 138 | 226/201 | 268 | 119.99 | 118.03 | AD2-062 | PEPCO_P4_PP41_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 203981 | AD2-062_POI | 235188 | 01GREENE | 1 | 138 | 226/201 | 268 | 118.58 | 116.72 | AD2-062 | AP_P2-3_PE-500-015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200532 | 26ROXBURY | 203981 | AD2-062_POI | 1 | 138 | 226 | 268 | 113.91 | 109.83 | AD2-062 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200532 | 26ROXBURY | 203981 | AD2-062_POI | 1 | 138 | 226 | 268 | 113.91 | 109.83 | AD2-062 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200532 | 26ROXBURY | 203981 | AD2-062_POI | 1 | 138 | 226 | 268 | 113.81 | 109.74 | AD2-062 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 110.63 | 106.29 | AD2-062 | PN_P2-3_PN-115-0331-A_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 110.61 | 106.27 | AD2-062 | PN_P2-3_PN-115-0331-D_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 110.53 | 106.19 | AD2-062 | AP_P1-2_WP-138-340BT_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 110.53 | 106.19 | AD2-062 | PN_P1-3_PN-115-118_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 105.22 | 103.9 | AD2-062 | AP_P1-2_WP-138-340BT_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 105.22 | 103.9 | AD2-062 | PN_P1-3_PN-115-118_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 105.17 | 103.85 | AD2-062 | PN_P2-3_PN-115-0331-D_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 105.15 | 103.83 | AD2-062 | PN_P2-3_PN-115-0331-A_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200532 | 26ROXBURY | 203981 | AD2-062_POI | 1 | 138 | 226 | 268 | 108.01 | 101.27 | AD2-062 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200532 | 26ROXBURY | 203981 | AD2-062_POI | 1 | 138 | 226 | 268 | 108.01 | 101.27 | AD2-062 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200532 | 26ROXBURY | 203981 | AD2-062_POI | 1 | 138 | 226 | 268 | 108 | 101.26 | AD2-062 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200532 | 26ROXBURY | 203981 | AD2-062_POI | 1 | 138 | 226 | 268 | 108.08 | 101.26 | AD2-062 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2812 | 113.81 | 112.29 | Z2-087 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 118.43 | 117.58 | AD2-072 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 117.06 | 116.25 | AD2-072 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 120.95 | 115.89 | AD2-072 | PECO_P4_PEACH035_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 115.42 | 114.65 | AD2-072 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.75 | 114.33 | AD2-072 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.75 | 114.33 | AD2-072 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.38 | 113.69 | AD2-072 | PECO_P4_PEACH675_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.38 | 113.69 | AD2-072 | PECO_P7-1_220-0607_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3198 | 118.36 | 112.97 | AD2-072 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2812 | 114.01 | 112.51 | Z2-088 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 112.93 | 111.74 | AD2-072 | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 112.88 | 111.7 | AD2-072 | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 116 | 111.24 | AD2-072 | PECO_P1-2_220-07_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.83 | 111.18 | AD2-072 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.71 | 111.07 | AD2-072 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.74 | 111.05 | AD2-072 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.76 | 111.03 | AD2-072 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.23 | 110.23 | AD2-072 | AP_P2-2_WP-500-DRT16_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.23 | 110.23 | AD2-072 | AP_P2-3_WP-500-DRT20_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.23 | 110.23 | AD2-072 | AP_P1-2_WP-500-005A_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.23 | 110.23 | AD2-072 | AP_P2-3_WP-500-465_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.23 | 110.23 | AD2-072 | AP_P1-2_WP-500-DRT21_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3369 | 128.23 | 123.15 | 01BACKB | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 118.52 | 117.67 | AD2-074 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 117.15 | 116.35 | AD2-074 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 121.11 | 116.05 | AD2-074 | PECO_P4_PEACH035_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 115.51 | 114.75 | AD2-074 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.86 | 114.44 | AD2-074 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.86 | 114.44 | AD2-074 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.52 | 113.83 | AD2-074 | PECO_P7-1_220-0607_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.52 | 113.83 | AD2-074 | PECO_P4_PEACH675_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3198 | 118.53 | 113.13 | AD2-074 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3369 | 128.16 | 123.09 | 01CROSSCHOOL | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 113.02 | 111.84 | AD2-074 | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 112.97 | 111.79 | AD2-074 | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 116.14 | 111.38 | AD2-074 | PECO_P1-2_220-07_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.98 | 111.33 | AD2-074 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.86 | 111.22 | AD2-074 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.89 | 111.2 | AD2-074 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.9 | 111.16 | AD2-074 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.33 | 110.33 | AD2-074 | AP_P1-2_WP-500-DRT21_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.33 | 110.33 | AD2-074 | AP_P2-3_WP-500-465_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.33 | 110.33 | AD2-074 | AP_P2-3_WP-500-DRT20_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.33 | 110.33 | AD2-074 | AP_P1-2_WP-500-005A_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.33 | 110.33 | AD2-074 | AP_P2-2_WP-500-DRT16_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3369 | 127.46 | 122.4 | 01GRNGAP | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 121.47 | 116.39 | AD2-076 | PECO_P4_PEACH035_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 119.19 | 114.75 | AD2-076 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 119.19 | 114.75 | AD2-076 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.86 | 114.15 | AD2-076 | PECO_P4_PEACH675_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.86 | 114.15 | AD2-076 | PECO_P7-1_220-0607_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3198 | 118.95 | 113.54 | AD2-076 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 116.48 | 111.71 | AD2-076 | PECO_P1-2_220-07_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 116.35 | 111.69 | AD2-076 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 116.23 | 111.57 | AD2-076 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 116.26 | 111.55 | AD2-076 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 116.24 | 111.49 | AD2-076 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3369 | 128.06 | 122.99 | 05CELAN | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 118.43 | 117.58 | AD2-093 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 117.06 | 116.25 | AD2-093 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 120.94 | 115.88 | AD2-093 | PECO_P4_PEACH035_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 115.43 | 114.66 | AD2-093 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.75 | 114.32 | AD2-093 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.75 | 114.32 | AD2-093 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.37 | 113.67 | AD2-093 | PECO_P4_PEACH675_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.37 | 113.67 | AD2-093 | PECO_P7-1_220-0607_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3198 | 118.35 | 112.96 | AD2-093 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3369 | 128.19 | 123.11 | 05NTRDAM | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 112.94 | 111.75 | AD2-093 | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 112.89 | 111.7 | AD2-093 | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.99 | 111.23 | AD2-093 | PECO_P1-2_220-07_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.81 | 111.17 | AD2-093 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.7 | 111.06 | AD2-093 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.72 | 111.03 | AD2-093 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.75 | 111.01 | AD2-093 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.24 | 110.23 | AD2-093 | AP_P1-2_WP-500-005A_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.24 | 110.23 | AD2-093 | AP_P1-2_WP-500-DRT21_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.24 | 110.23 | AD2-093 | AP_P2-3_WP-500-465_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.24 | 110.23 | AD2-093 | AP_P2-3_WP-500-DRT20_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.24 | 110.23 | AD2-093 | AP_P2-2_WP-500-DRT16_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3369 | 128.06 | 122.99 | 08HLCRTG | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 118.41 | 117.55 | AD2-134 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 117.04 | 116.23 | AD2-134 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 120.92 | 115.86 | AD2-134 | PECO_P4_PEACH035_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 115.4 | 114.63 | AD2-134 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.73 | 114.3 | AD2-134 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.73 | 114.3 | AD2-134 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.35 | 113.66 | AD2-134 | PECO_P4_PEACH675_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.35 | 113.66 | AD2-134 | PECO_P7-1_220-0607_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3198 | 118.33 | 112.94 | AD2-134 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3369 | 128.22 | 123.14 | 15USSILL | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 112.91 | 111.72 | AD2-134 | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 112.86 | 111.68 | AD2-134 | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.97 | 111.21 | AD2-134 | PECO_P1-2_220-07_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.79 | 111.15 | AD2-134 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.68 | 111.04 | AD2-134 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.71 | 111.02 | AD2-134 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.73 | 111 | AD2-134 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.21 | 110.21 | AD2-134 | AP_P1-2_WP-500-DRT21_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.21 | 110.21 | AD2-134 | AP_P2-3_WP-500-DRT20_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.21 | 110.21 | AD2-134 | AP_P2-3_WP-500-465_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.21 | 110.21 | AD2-134 | AP_P2-2_WP-500-DRT16_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.21 | 110.21 | AD2-134 | AP_P1-2_WP-500-005A_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 2 | 230 | 233 | 680 | 135.96 | 133.15 | AD2-158 | PEPCO_P1_PP1_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 680 | 135.96 | 133.15 | AD2-158 | PEPCO_P1_PP2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3369 | 128.15 | 123.08 | 1DOMTR10 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 118.3 | 117.44 | AD2-158 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 116.93 | 116.11 | AD2-158 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 120.93 | 115.87 | AD2-158 | PECO_P4_PEACH035_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 115.3 | 114.51 | AD2-158 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.66 | 114.24 | AD2-158 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.66 | 114.24 | AD2-158 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.33 | 113.64 | AD2-158 | PECO_P4_PEACH675_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.33 | 113.64 | AD2-158 | PECO_P7-1_220-0607_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3198 | 118.3 | 112.91 | AD2-158 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3369 | 128.2 | 123.12 | 1DOMTR9 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 112.81 | 111.61 | AD2-158 | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 112.76 | 111.56 | AD2-158 | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.95 | 111.2 | AD2-158 | PECO_P1-2_220-07_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.77 | 111.13 | AD2-158 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.66 | 111.02 | AD2-158 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.68 | 111 | AD2-158 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.71 | 110.98 | AD2-158 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.11 | 110.1 | AD2-158 | AP_P2-3_WP-500-DRT20_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.11 | 110.1 | AD2-158 | AP_P2-2_WP-500-DRT16_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.11 | 110.1 | AD2-158 | AP_P1-2_WP-500-005A_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.11 | 110.1 | AD2-158 | AP_P2-3_WP-500-465_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.11 | 110.1 | AD2-158 | AP_P1-2_WP-500-DRT21_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3369 | 128.12 | 123.05 | 1EDGECMA | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 118.48 | 117.63 | AD2-163 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 117.11 | 116.31 | AD2-163 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 121 | 115.94 | AD2-163 | PECO_P4_PEACH035_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 115.48 | 114.71 | AD2-163 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.8 | 114.38 | AD2-163 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.8 | 114.38 | AD2-163 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.43 | 113.73 | AD2-163 | PECO_P4_PEACH675_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.43 | 113.73 | AD2-163 | PECO_P7-1_220-0607_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3198 | 118.43 | 113.03 | AD2-163 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3369 | 128.21 | 123.13 | 1HOLLOMANSOL | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 112.99 | 111.8 | AD2-163 | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 112.93 | 111.75 | AD2-163 | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 116.05 | 111.29 | AD2-163 | PECO_P1-2_220-07_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.88 | 111.23 | AD2-163 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.76 | 111.12 | AD2-163 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.79 | 111.1 | AD2-163 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.81 | 111.07 | AD2-163 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.29 | 110.29 | AD2-163 | AP_P2-3_WP-500-DRT20_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.29 | 110.29 | AD2-163 | AP_P1-2_WP-500-005A_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.29 | 110.29 | AD2-163 | AP_P2-2_WP-500-DRT16_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.29 | 110.29 | AD2-163 | AP_P2-3_WP-500-465_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.29 | 110.29 | AD2-163 | AP_P1-2_WP-500-DRT21_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3369 | 128.2 | 123.12 | 1STONECA | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 118.46 | 117.61 | AD2-180 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 117.09 | 116.28 | AD2-180 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 121.01 | 115.94 | AD2-180 | PECO_P4_PEACH035_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 115.45 | 114.68 | AD2-180 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.79 | 114.36 | AD2-180 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.79 | 114.36 | AD2-180 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.43 | 113.73 | AD2-180 | PECO_P4_PEACH675_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.43 | 113.73 | AD2-180 | PECO_P7-1_220-0607_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3198 | 118.42 | 113.03 | AD2-180 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3369 | 128.55 | 123.46 | 28MDLSEXCO | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 112.96 | 111.77 | AD2-180 | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 112.91 | 111.73 | AD2-180 | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 116.05 | 111.29 | AD2-180 | PECO_P1-2_220-07_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.88 | 111.23 | AD2-180 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.76 | 111.12 | AD2-180 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.79 | 111.1 | AD2-180 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.81 | 111.07 | AD2-180 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.26 | 110.26 | AD2-180 | AP_P1-2_WP-500-005A_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.26 | 110.26 | AD2-180 | AP_P2-2_WP-500-DRT16_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.26 | 110.26 | AD2-180 | AP_P2-3_WP-500-DRT20_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.26 | 110.26 | AD2-180 | AP_P2-3_WP-500-465_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.26 | 110.26 | AD2-180 | AP_P1-2_WP-500-DRT21_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 607 | 168.25 | 165.49 | AE1-044 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 607 | 167.19 | 165.49 | AE1-044 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 607 | 167.92 | 165.48 | AE1-044 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 607 | 166.86 | 165.48 | AE1-044 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 607 | 168.17 | 165.42 | AE1-044 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 607 | 168.17 | 165.42 | AE1-044 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 607 | 167.11 | 165.42 | AE1-044 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 607 | 167.11 | 165.42 | AE1-044 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 628 | 159.2 | 157.77 | AE1-044 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 628 | 158.89 | 157.76 | AE1-044 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 628 | 159.13 | 157.7 | AE1-044 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 628 | 159.13 | 157.7 | AE1-044 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 628 | 156.5 | 155.48 | AE1-044 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 628 | 156.19 | 155.47 | AE1-044 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 628 | 156.42 | 155.41 | AE1-044 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 628 | 156.42 | 155.41 | AE1-044 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 607 | 153.1 | 151.1 | AE1-044 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 607 | 154.15 | 151.09 | AE1-044 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 628 | 145.58 | 143.85 | AE1-044 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 628 | 142.88 | 141.54 | AE1-044 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 680 | 139.98 | 137.06 | AE1-044 | PEPCO_P4_PP19_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 797 | 140.18 | 135.63 | AE1-044 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 797 | 140.44 | 135.56 | AE1-044 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 797 | 140.44 | 135.56 | AE1-044 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 797 | 140.42 | 135.55 | AE1-044 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 134.61 | 131.53 | AE1-044 | DVP_P4-2: 51482_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 134.61 | 131.5 | AE1-044 | DVP_P1-2: LN 514_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 134.61 | 131.5 | AE1-044 | AP_P1-2_PE-500-407T_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 2 | 230 | 233 | 680 | 133.65 | 130.84 | AE1-044 | PEPCO_P1_PP1_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 680 | 133.65 | 130.84 | AE1-044 | PEPCO_P1_PP2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 797 | 132.07 | 127.26 | AE1-044 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 129.55 | 126.47 | AE1-044 | AP_P2-3_PE-500-019C_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 814 | 130.42 | 125.91 | AE1-044 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 814 | 130.91 | 125.79 | AE1-044 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 814 | 130.91 | 125.79 | AE1-044 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 814 | 130.9 | 125.78 | AE1-044 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 2 | 230 | 233 | 680 | 126.97 | 124.06 | AE1-044 | DVP_P4-2: 51482_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 680 | 126.97 | 124.06 | AE1-044 | DVP_P4-2: 51482_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 680 | 126.97 | 124.03 | AE1-044 | AP_P1-2_PE-500-407T_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 680 | 126.97 | 124.03 | AE1-044 | DVP_P1-2: LN 514_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 2 | 230 | 233 | 680 | 126.97 | 124.03 | AE1-044 | DVP_P1-2: LN 514_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 2 | 230 | 233 | 680 | 126.97 | 124.03 | AE1-044 | AP_P1-2_PE-500-407T_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3369 | 128.22 | 123.15 | 3UNCAMP | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 117.63 | 116.72 | AE1-044 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 814 | 121.59 | 116.67 | AE1-044 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 116.27 | 115.4 | AE1-044 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 120.39 | 115.34 | AE1-044 | PECO_P4_PEACH035_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 2 | 230 | 233 | 680 | 117.97 | 115.05 | AE1-044 | AP_P2-3_PE-500-019C_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 680 | 117.97 | 115.05 | AE1-044 | AP_P2-3_PE-500-019C_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 114.64 | 113.8 | AE1-044 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.04 | 113.63 | AE1-044 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.04 | 113.63 | AE1-044 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 117.76 | 113.08 | AE1-044 | PECO_P4_PEACH675_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 117.76 | 113.08 | AE1-044 | PECO_P7-1_220-0607_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 814 | 115.35 | 112.35 | AE1-044 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 814 | 115.61 | 112.29 | AE1-044 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 814 | 115.61 | 112.29 | AE1-044 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 814 | 115.58 | 112.27 | AE1-044 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3198 | 117.6 | 112.24 | AE1-044 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3369 | 128.16 | 123.09 | 4E MILL | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 112.17 | 110.93 | AE1-044 | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 112.12 | 110.88 | AE1-044 | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.38 | 110.64 | AE1-044 | PECO_P1-2_220-07_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.15 | 110.53 | AE1-044 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 797 | 111.92 | 110.43 | AE1-044 | PJM_500_BG_P4_5_CNSTN_15_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.14 | 110.42 | AE1-044 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.04 | 110.42 | AE1-044 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.07 | 110.4 | AE1-044 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 110.47 | 109.42 | AE1-044 | AP_P1-2_WP-500-DRT21_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 110.47 | 109.42 | AE1-044 | AP_P2-3_WP-500-DRT20_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 110.47 | 109.42 | AE1-044 | AP_P1-2_WP-500-005A_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 110.47 | 109.42 | AE1-044 | AP_P2-3_WP-500-465_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 110.47 | 109.42 | AE1-044 | AP_P2-2_WP-500-DRT16_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 797 | 109.14 | 107.75 | AE1-044 | BG_P7_GRCTN_CNSTN_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204502 | 27JACKSON | 204514 | 27TMI | 1 | 230 | 227 | 659 | 104.04 | 103.98 | AE1-044 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204502 | 27JACKSON | 204514 | 27TMI | 1 | 230 | 227 | 659 | 104.04 | 103.98 | AE1-044 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204502 | 27JACKSON | 204514 | 27TMI | 1 | 230 | 227 | 659 | 104.1 | 103.97 | AE1-044 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204502 | 27JACKSON | 204514 | 27TMI | 1 | 230 | 227 | 659 | 104.02 | 103.96 | AE1-044 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 814 | 107.2 | 103.85 | AE1-044 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 104.01 | 101.33 | AE1-044 | DVP_P4-2: 560T571_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 103.85 | 101.2 | AE1-044 | DVP_P4-2: H2T560_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 103.85 | 101.18 | AE1-044 | DVP_P4-2: H1T560_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 103.71 | 101.03 | AE1-044 | PEPCO_P1_5070_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220972 | GRANITE1 | 1 | 230 | 232 | 811 | 103.03 | 100.12 | AE1-044 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 136.44 | 133.37 | AE1-056 | AP_P1-2_PE-500-407T_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 136.44 | 133.37 | AE1-056 | DVP_P1-2: LN 514_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 136.44 | 133.35 | AE1-056 | DVP_P4-2: 51482_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 131.33 | 128.25 | AE1-056 | AP_P2-3_PE-500-019C_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3369 | 128.2 | 123.13 | 6PAPERMILL | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 118.43 | 117.57 | AE1-056 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 117.05 | 116.24 | AE1-056 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 121.02 | 115.96 | AE1-056 | PECO_P4_PEACH035_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 115.42 | 114.65 | AE1-056 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.77 | 114.35 | AE1-056 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.77 | 114.35 | AE1-056 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.43 | 113.73 | AE1-056 | PECO_P4_PEACH675_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.43 | 113.73 | AE1-056 | PECO_P7-1_220-0607_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3198 | 118.42 | 113.03 | AE1-056 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3369 | 128.02 | 122.95 | AA1-018 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 112.93 | 111.74 | AE1-056 | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 112.88 | 111.69 | AE1-056 | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 116.05 | 111.29 | AE1-056 | PECO_P1-2_220-07_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.88 | 111.23 | AE1-056 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.76 | 111.12 | AE1-056 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.79 | 111.1 | AE1-056 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.81 | 111.07 | AE1-056 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.23 | 110.23 | AE1-056 | AP_P1-2_WP-500-005A_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.23 | 110.23 | AE1-056 | AP_P2-3_WP-500-DRT20_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.23 | 110.23 | AE1-056 | AP_P1-2_WP-500-DRT21_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.23 | 110.23 | AE1-056 | AP_P2-3_WP-500-465_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.23 | 110.23 | AE1-056 | AP_P2-2_WP-500-DRT16_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 105.3 | 102.61 | AE1-056 | DVP_P4-2: 560T571_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 105.14 | 102.47 | AE1-056 | DVP_P4-2: H2T560_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 105.13 | 102.45 | AE1-056 | DVP_P4-2: H1T560_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 104.99 | 102.3 | AE1-056 | PEPCO_P1_5070_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 203981 | AD2-062_POI | 235188 | 01GREENE | 1 | 138 | 226/201 | 268 | 142.1 | 138.02 | AE1-071 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 203981 | AD2-062_POI | 235188 | 01GREENE | 1 | 138 | 226/201 | 268 | 142.1 | 138.02 | AE1-071 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 203981 | AD2-062_POI | 235188 | 01GREENE | 1 | 138 | 226/201 | 268 | 142 | 137.93 | AE1-071 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 203981 | AD2-062_POI | 235188 | 01GREENE | 1 | 138 | 226/201 | 268 | 136.19 | 129.51 | AE1-071 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 203981 | AD2-062_POI | 235188 | 01GREENE | 1 | 138 | 226/201 | 268 | 136.19 | 129.51 | AE1-071 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 203981 | AD2-062_POI | 235188 | 01GREENE | 1 | 138 | 226/201 | 268 | 136.18 | 129.51 | AE1-071 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 203981 | AD2-062_POI | 235188 | 01GREENE | 1 | 138 | 226/201 | 268 | 136.26 | 129.5 | AE1-071 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3369 | 128.15 | 123.07 | AA1-038 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 203981 | AD2-062_POI | 235188 | 01GREENE | 1 | 138 | 226/201 | 268 | 128.45 | 123.29 | AE1-071 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200532 | 26ROXBURY | 203981 | AD2-062_POI | 1 | 138 | 226 | 268 | 125.43 | 121.08 | AE1-071 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200532 | 26ROXBURY | 203981 | AD2-062_POI | 1 | 138 | 226 | 268 | 125.43 | 121.08 | AE1-071 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200532 | 26ROXBURY | 203981 | AD2-062_POI | 1 | 138 | 226 | 268 | 125.33 | 120.98 | AE1-071 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 203981 | AD2-062_POI | 235188 | 01GREENE | 1 | 138 | 226/201 | 268 | 118.25 | 116.27 | AE1-071 | PEPCO_P4_PP41_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 203981 | AD2-062_POI | 235188 | 01GREENE | 1 | 138 | 226/201 | 268 | 116.84 | 114.96 | AE1-071 | AP_P2-3_PE-500-015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200532 | 26ROXBURY | 203981 | AD2-062_POI | 1 | 138 | 226 | 268 | 119.52 | 112.57 | AE1-071 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200532 | 26ROXBURY | 203981 | AD2-062_POI | 1 | 138 | 226 | 268 | 119.52 | 112.57 | AE1-071 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200532 | 26ROXBURY | 203981 | AD2-062_POI | 1 | 138 | 226 | 268 | 119.51 | 112.56 | AE1-071 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200532 | 26ROXBURY | 203981 | AD2-062_POI | 1 | 138 | 226 | 268 | 119.59 | 112.56 | AE1-071 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200532 | 26ROXBURY | 203981 | AD2-062_POI | 1 | 138 | 226 | 268 | 111.78 | 106.34 | AE1-071 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3369 | 129.03 | 123.94 | AA1-102 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 136.38 | 133.31 | AE1-084 | DVP_P1-2: LN 514_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 136.38 | 133.31 | AE1-084 | AP_P1-2_PE-500-407T_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 136.38 | 133.29 | AE1-084 | DVP_P4-2: 51482_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 131.27 | 128.19 | AE1-084 | AP_P2-3_PE-500-019C_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3369 | 128.14 | 123.07 | AA1-139 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 118.33 | 117.47 | AE1-084 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 116.96 | 116.14 | AE1-084 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 120.93 | 115.87 | AE1-084 | PECO_P4_PEACH035_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 115.33 | 114.55 | AE1-084 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.68 | 114.26 | AE1-084 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.68 | 114.26 | AE1-084 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.34 | 113.65 | AE1-084 | PECO_P7-1_220-0607_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.34 | 113.65 | AE1-084 | PECO_P4_PEACH675_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3198 | 118.31 | 112.92 | AE1-084 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3369 | 128.23 | 123.15 | AA2-053 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 112.84 | 111.64 | AE1-084 | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 112.79 | 111.6 | AE1-084 | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.96 | 111.2 | AE1-084 | PECO_P1-2_220-07_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.78 | 111.14 | AE1-084 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.67 | 111.03 | AE1-084 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.69 | 111.01 | AE1-084 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.72 | 110.99 | AE1-084 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.14 | 110.13 | AE1-084 | AP_P1-2_WP-500-DRT21_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.14 | 110.13 | AE1-084 | AP_P2-2_WP-500-DRT16_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.14 | 110.13 | AE1-084 | AP_P2-3_WP-500-465_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.14 | 110.13 | AE1-084 | AP_P2-3_WP-500-DRT20_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.14 | 110.13 | AE1-084 | AP_P1-2_WP-500-005A_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 105.23 | 102.53 | AE1-084 | DVP_P4-2: 560T571_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 105.06 | 102.39 | AE1-084 | DVP_P4-2: H2T560_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 105.06 | 102.38 | AE1-084 | DVP_P4-2: H1T560_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 104.92 | 102.23 | AE1-084 | PEPCO_P1_5070_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 680 | 142.77 | 139.85 | AE1-101 | PEPCO_P4_PP19_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 137.49 | 134.41 | AE1-101 | AP_P1-2_PE-500-407T_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 137.49 | 134.41 | AE1-101 | DVP_P1-2: LN 514_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 137.49 | 134.39 | AE1-101 | DVP_P4-2: 51482_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 680 | 136.31 | 133.5 | AE1-101 | PEPCO_P1_PP2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 2 | 230 | 233 | 680 | 136.31 | 133.5 | AE1-101 | PEPCO_P1_PP1_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 132.41 | 129.32 | AE1-101 | AP_P2-3_PE-500-019C_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 203981 | AD2-062_POI | 235188 | 01GREENE | 1 | 138 | 226/201 | 268 | 132.17 | 127.99 | AE1-101 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 203981 | AD2-062_POI | 235188 | 01GREENE | 1 | 138 | 226/201 | 268 | 132.17 | 127.99 | AE1-101 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 203981 | AD2-062_POI | 235188 | 01GREENE | 1 | 138 | 226/201 | 268 | 132.08 | 127.9 | AE1-101 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 680 | 129.65 | 126.72 | AE1-101 | DVP_P1-2: LN 514_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 680 | 129.65 | 126.72 | AE1-101 | AP_P1-2_PE-500-407T_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 2 | 230 | 233 | 680 | 129.65 | 126.72 | AE1-101 | DVP_P1-2: LN 514_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 2 | 230 | 233 | 680 | 129.65 | 126.72 | AE1-101 | AP_P1-2_PE-500-407T_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 2 | 230 | 233 | 680 | 129.65 | 126.72 | AE1-101 | DVP_P4-2: 51482_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 680 | 129.65 | 126.72 | AE1-101 | DVP_P4-2: 51482_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3369 | 128.19 | 123.12 | AA2-088 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 203981 | AD2-062_POI | 235188 | 01GREENE | 1 | 138 | 226/201 | 268 | 126.29 | 119.51 | AE1-101 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 203981 | AD2-062_POI | 235188 | 01GREENE | 1 | 138 | 226/201 | 268 | 126.29 | 119.51 | AE1-101 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 203981 | AD2-062_POI | 235188 | 01GREENE | 1 | 138 | 226/201 | 268 | 126.29 | 119.51 | AE1-101 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 203981 | AD2-062_POI | 235188 | 01GREENE | 1 | 138 | 226/201 | 268 | 126.36 | 119.5 | AE1-101 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 680 | 120.62 | 117.68 | AE1-101 | AP_P2-3_PE-500-019C_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 2 | 230 | 233 | 680 | 120.62 | 117.68 | AE1-101 | AP_P2-3_PE-500-019C_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 118.43 | 117.58 | AE1-101 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 117.06 | 116.25 | AE1-101 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 121.01 | 115.94 | AE1-101 | PECO_P4_PEACH035_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 115.43 | 114.65 | AE1-101 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.76 | 114.34 | AE1-101 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.76 | 114.34 | AE1-101 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.42 | 113.73 | AE1-101 | PECO_P7-1_220-0607_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.42 | 113.73 | AE1-101 | PECO_P4_PEACH675_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 203981 | AD2-062_POI | 235188 | 01GREENE | 1 | 138 | 226/201 | 268 | 118.55 | 113.1 | AE1-101 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3369 | 128.23 | 123.15 | AA2-178 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3198 | 118.41 | 113.02 | AE1-101 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3369 | 127.9 | 122.83 | AB1-006 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 112.93 | 111.74 | AE1-101 | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 112.88 | 111.69 | AE1-101 | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 116.04 | 111.28 | AE1-101 | PECO_P1-2_220-07_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.87 | 111.22 | AE1-101 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.75 | 111.11 | AE1-101 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.78 | 111.09 | AE1-101 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.8 | 111.07 | AE1-101 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200532 | 26ROXBURY | 203981 | AD2-062_POI | 1 | 138 | 226 | 268 | 115.43 | 111.06 | AE1-101 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200532 | 26ROXBURY | 203981 | AD2-062_POI | 1 | 138 | 226 | 268 | 115.43 | 111.06 | AE1-101 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200532 | 26ROXBURY | 203981 | AD2-062_POI | 1 | 138 | 226 | 268 | 115.33 | 110.97 | AE1-101 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.24 | 110.24 | AE1-101 | AP_P1-2_WP-500-005A_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.24 | 110.24 | AE1-101 | AP_P1-2_WP-500-DRT21_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.24 | 110.24 | AE1-101 | AP_P2-3_WP-500-465_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.24 | 110.24 | AE1-101 | AP_P2-2_WP-500-DRT16_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.24 | 110.24 | AE1-101 | AP_P2-3_WP-500-DRT20_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 203981 | AD2-062_POI | 235188 | 01GREENE | 1 | 138 | 226/201 | 268 | 108.36 | 106.36 | AE1-101 | PEPCO_P4_PP41_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 203981 | AD2-062_POI | 235188 | 01GREENE | 1 | 138 | 226/201 | 268 | 106.94 | 105.04 | AE1-101 | AP_P2-3_PE-500-015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 106.03 | 103.34 | AE1-101 | DVP_P4-2: 560T571_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 105.87 | 103.2 | AE1-101 | DVP_P4-2: H2T560_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 105.86 | 103.19 | AE1-101 | DVP_P4-2: H1T560_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 105.72 | 103.04 | AE1-101 | PEPCO_P1_5070_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200532 | 26ROXBURY | 203981 | AD2-062_POI | 1 | 138 | 226 | 268 | 109.55 | 102.58 | AE1-101 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200532 | 26ROXBURY | 203981 | AD2-062_POI | 1 | 138 | 226 | 268 | 109.55 | 102.58 | AE1-101 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200532 | 26ROXBURY | 203981 | AD2-062_POI | 1 | 138 | 226 | 268 | 109.54 | 102.57 | AE1-101 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200532 | 26ROXBURY | 203981 | AD2-062_POI | 1 | 138 | 226 | 268 | 109.62 | 102.57 | AE1-101 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 607 | 171.39 | 170.03 | AE1-104 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 607 | 172.51 | 170.03 | AE1-104 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 607 | 172.13 | 169.98 | AE1-104 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 607 | 171.01 | 169.98 | AE1-104 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 607 | 171.31 | 169.96 | AE1-104 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 607 | 171.31 | 169.96 | AE1-104 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 607 | 172.43 | 169.96 | AE1-104 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 607 | 172.43 | 169.96 | AE1-104 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 628 | 163.27 | 162.17 | AE1-104 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 628 | 162.9 | 162.12 | AE1-104 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 628 | 163.19 | 162.1 | AE1-104 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 628 | 163.19 | 162.1 | AE1-104 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 628 | 160.55 | 159.89 | AE1-104 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 628 | 160.18 | 159.83 | AE1-104 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 628 | 160.48 | 159.82 | AE1-104 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 628 | 160.48 | 159.82 | AE1-104 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 607 | 157.3 | 155.4 | AE1-104 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 607 | 158.42 | 155.4 | AE1-104 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 628 | 149.65 | 148.01 | AE1-104 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 628 | 146.94 | 145.71 | AE1-104 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 680 | 142.55 | 139.62 | AE1-104 | PEPCO_P4_PP19_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 797 | 142.63 | 138.05 | AE1-104 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 797 | 142.95 | 138.04 | AE1-104 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 797 | 142.95 | 138.04 | AE1-104 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 797 | 142.92 | 138.02 | AE1-104 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 137.87 | 134.79 | AE1-104 | DVP_P1-2: LN 514_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 137.87 | 134.79 | AE1-104 | AP_P1-2_PE-500-407T_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 137.87 | 134.77 | AE1-104 | DVP_P4-2: 51482_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 797 | 134.58 | 129.73 | AE1-104 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 132.75 | 129.66 | AE1-104 | AP_P2-3_PE-500-019C_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 814 | 133.03 | 128.49 | AE1-104 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 814 | 133.63 | 128.46 | AE1-104 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 814 | 133.63 | 128.46 | AE1-104 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 814 | 133.62 | 128.45 | AE1-104 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3369 | 129.8 | 124.68 | AB1-056 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 814 | 124.31 | 119.31 | AE1-104 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 119.92 | 119.17 | AE1-104 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 118.53 | 117.84 | AE1-104 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 122.88 | 117.76 | AE1-104 | PECO_P4_PEACH035_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 116.9 | 116.24 | AE1-104 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 120.4 | 115.93 | AE1-104 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 120.4 | 115.93 | AE1-104 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 120.19 | 115.45 | AE1-104 | PECO_P7-1_220-0607_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 120.19 | 115.45 | AE1-104 | PECO_P4_PEACH675_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3198 | 120.7 | 115.2 | AE1-104 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 814 | 117.75 | 114.77 | AE1-104 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 814 | 118.06 | 114.75 | AE1-104 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 814 | 118.06 | 114.75 | AE1-104 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 814 | 118.04 | 114.74 | AE1-104 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3369 | 128.23 | 123.16 | AB1-081 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 114.36 | 113.26 | AE1-104 | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 114.31 | 113.22 | AE1-104 | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 117.81 | 113.11 | AE1-104 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 117.81 | 113.01 | AE1-104 | PECO_P1-2_220-07_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 117.69 | 112.99 | AE1-104 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 117.72 | 112.97 | AE1-104 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 117.5 | 112.82 | AE1-104 | PECO_P4_NOTTI85_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 797 | 113.49 | 112.01 | AE1-104 | PJM_500_BG_P4_5_CNSTN_15_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 112.66 | 111.76 | AE1-104 | AP_P1-2_WP-500-DRT21_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 112.66 | 111.76 | AE1-104 | AP_P2-2_WP-500-DRT16_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 112.66 | 111.76 | AE1-104 | AP_P1-2_WP-500-005A_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 112.66 | 111.76 | AE1-104 | AP_P2-3_WP-500-465_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 112.66 | 111.76 | AE1-104 | AP_P2-3_WP-500-DRT20_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204502 | 27JACKSON | 204514 | 27TMI | 1 | 230 | 227 | 659 | 106.24 | 106.37 | AE1-104 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204502 | 27JACKSON | 204514 | 27TMI | 1 | 230 | 227 | 659 | 106.24 | 106.37 | AE1-104 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204502 | 27JACKSON | 204514 | 27TMI | 1 | 230 | 227 | 659 | 106.31 | 106.37 | AE1-104 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204502 | 27JACKSON | 204514 | 27TMI | 1 | 230 | 227 | 659 | 106.22 | 106.35 | AE1-104 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 814 | 109.66 | 106.31 | AE1-104 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 106.6 | 103.89 | AE1-104 | DVP_P4-2: 560T571_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 106.44 | 103.75 | AE1-104 | DVP_P4-2: H2T560_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 106.44 | 103.74 | AE1-104 | DVP_P4-2: H1T560_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 106.3 | 103.59 | AE1-104 | PEPCO_P1_5070_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220972 | GRANITE1 | 1 | 230 | 232 | 811 | 105.13 | 102.2 | AE1-104 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 801 | 103.94 | 102 | AE1-104 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 801 | 104.45 | 101.98 | AE1-104 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 801 | 104.45 | 101.98 | AE1-104 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 801 | 104.42 | 101.96 | AE1-104 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220972 | GRANITE1 | 1 | 230 | 232 | 811 | 104.88 | 101.92 | AE1-104 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220972 | GRANITE1 | 1 | 230 | 232 | 811 | 104.88 | 101.92 | AE1-104 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220953 | HOWARD12 | 220972 | GRANITE1 | 1 | 230 | 232 | 772 | 104.52 | 101.62 | AE1-104 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 106.48 | 101.55 | AE1-104 | PECO_P4_PEACH025_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220953 | HOWARD12 | 220972 | GRANITE1 | 1 | 230 | 232 | 772 | 104.17 | 101.22 | AE1-104 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220953 | HOWARD12 | 220972 | GRANITE1 | 1 | 230 | 232 | 772 | 104.17 | 101.22 | AE1-104 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200065 | PCHBTM2S | 200066 | PCHBTM1N | 2 | 500 | 225 | 3022 | 104.69 | 100.91 | AE1-104 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208020 | MANO TR3 | 1 | 230 | 229 | 731 | 98.27 | 100.72 | AE1-104 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208020 | MANO TR3 | 1 | 230 | 229 | 731 | 98.53 | 100.7 | AE1-104 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208020 | MANO TR3 | 1 | 230 | 229 | 731 | 98.53 | 100.7 | AE1-104 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208020 | MANO TR3 | 1 | 230 | 229 | 731 | 98.53 | 100.7 | AE1-104 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3198 | 105.46 | 100.53 | AE1-104 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220973 | GRANITE6 | 1 | 230 | 232 | 811 | 103.37 | 100.52 | AE1-104 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220973 | GRANITE6 | 1 | 230 | 232 | 811 | 103.14 | 100.25 | AE1-104 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220973 | GRANITE6 | 1 | 230 | 232 | 811 | 103.14 | 100.25 | AE1-104 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208078 | SAKR | 1 | 230 | 229 | 801 | 99.6 | 100.19 | AE1-104 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208078 | SAKR | 1 | 230 | 229 | 801 | 99.85 | 100.17 | AE1-104 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208078 | SAKR | 1 | 230 | 229 | 801 | 99.85 | 100.17 | AE1-104 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208078 | SAKR | 1 | 230 | 229 | 801 | 99.84 | 100.17 | AE1-104 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 801 | 103.59 | 101.59 | AE1-129 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 801 | 104.04 | 101.52 | AE1-129 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 801 | 104.04 | 101.52 | AE1-129 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 801 | 104.02 | 101.5 | AE1-129 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 136.46 | 133.39 | AE1-143 | AP_P1-2_PE-500-407T_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 136.46 | 133.39 | AE1-143 | DVP_P1-2: LN 514_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 136.46 | 133.38 | AE1-143 | DVP_P4-2: 51482_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 131.34 | 128.26 | AE1-143 | AP_P2-3_PE-500-019C_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3369 | 128.15 | 123.08 | AB1-132 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 118.27 | 117.41 | AE1-143 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 116.9 | 116.08 | AE1-143 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 120.79 | 115.74 | AE1-143 | PECO_P4_PEACH035_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 115.27 | 114.49 | AE1-143 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.6 | 114.18 | AE1-143 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.6 | 114.18 | AE1-143 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.22 | 113.53 | AE1-143 | PECO_P7-1_220-0607_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.22 | 113.53 | AE1-143 | PECO_P4_PEACH675_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3198 | 118.17 | 112.79 | AE1-143 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3369 | 129.25 | 124.14 | AB2-036 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 112.78 | 111.58 | AE1-143 | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 112.73 | 111.54 | AE1-143 | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.84 | 111.09 | AE1-143 | PECO_P1-2_220-07_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.66 | 111.02 | AE1-143 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.54 | 110.9 | AE1-143 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.57 | 110.88 | AE1-143 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.6 | 110.87 | AE1-143 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.08 | 110.07 | AE1-143 | AP_P2-2_WP-500-DRT16_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.08 | 110.07 | AE1-143 | AP_P1-2_WP-500-005A_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.08 | 110.07 | AE1-143 | AP_P1-2_WP-500-DRT21_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.08 | 110.07 | AE1-143 | AP_P2-3_WP-500-DRT20_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.08 | 110.07 | AE1-143 | AP_P2-3_WP-500-465_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 105.22 | 102.53 | AE1-143 | DVP_P4-2: 560T571_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 105.06 | 102.39 | AE1-143 | DVP_P4-2: H2T560_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 105.06 | 102.37 | AE1-143 | DVP_P4-2: H1T560_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 104.91 | 102.23 | AE1-143 | PEPCO_P1_5070_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 136.18 | 133.11 | AE1-153 | DVP_P1-2: LN 514_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 136.18 | 133.11 | AE1-153 | AP_P1-2_PE-500-407T_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 136.18 | 133.09 | AE1-153 | DVP_P4-2: 51482_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 131.08 | 128 | AE1-153 | AP_P2-3_PE-500-019C_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3369 | 129.34 | 124.23 | AB2-037 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 118.37 | 117.51 | AE1-153 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 117 | 116.18 | AE1-153 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 120.99 | 115.93 | AE1-153 | PECO_P4_PEACH035_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 115.36 | 114.59 | AE1-153 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.72 | 114.3 | AE1-153 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.72 | 114.3 | AE1-153 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.39 | 113.7 | AE1-153 | PECO_P7-1_220-0607_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.39 | 113.7 | AE1-153 | PECO_P4_PEACH675_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3198 | 118.37 | 112.98 | AE1-153 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3369 | 128.23 | 123.16 | AB2-040 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 112.87 | 111.68 | AE1-153 | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 112.82 | 111.63 | AE1-153 | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 116.01 | 111.26 | AE1-153 | PECO_P1-2_220-07_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.84 | 111.19 | AE1-153 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.72 | 111.08 | AE1-153 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.75 | 111.06 | AE1-153 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.77 | 111.04 | AE1-153 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.18 | 110.18 | AE1-153 | AP_P2-2_WP-500-DRT16_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.18 | 110.18 | AE1-153 | AP_P1-2_WP-500-DRT21_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.18 | 110.18 | AE1-153 | AP_P2-3_WP-500-DRT20_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.18 | 110.18 | AE1-153 | AP_P2-3_WP-500-465_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.18 | 110.18 | AE1-153 | AP_P1-2_WP-500-005A_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 105.16 | 102.47 | AE1-153 | DVP_P4-2: 560T571_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 105 | 102.33 | AE1-153 | DVP_P4-2: H2T560_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 105 | 102.31 | AE1-153 | DVP_P4-2: H1T560_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 104.85 | 102.16 | AE1-153 | PEPCO_P1_5070_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 136.41 | 133.34 | AE1-155 | AP_P1-2_PE-500-407T_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 136.41 | 133.34 | AE1-155 | DVP_P1-2: LN 514_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 136.41 | 133.32 | AE1-155 | DVP_P4-2: 51482_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 131.3 | 128.22 | AE1-155 | AP_P2-3_PE-500-019C_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3369 | 128.2 | 123.12 | AB2-059 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 118.44 | 117.58 | AE1-155 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 117.06 | 116.26 | AE1-155 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 121.04 | 115.98 | AE1-155 | PECO_P4_PEACH035_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 115.43 | 114.66 | AE1-155 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.78 | 114.36 | AE1-155 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.78 | 114.36 | AE1-155 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.45 | 113.75 | AE1-155 | PECO_P7-1_220-0607_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.45 | 113.75 | AE1-155 | PECO_P4_PEACH675_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3198 | 118.44 | 113.05 | AE1-155 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3369 | 128.23 | 123.16 | AB2-060 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 112.94 | 111.75 | AE1-155 | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 112.89 | 111.7 | AE1-155 | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 116.07 | 111.31 | AE1-155 | PECO_P1-2_220-07_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.9 | 111.25 | AE1-155 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.78 | 111.14 | AE1-155 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.81 | 111.12 | AE1-155 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.83 | 111.09 | AE1-155 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.25 | 110.25 | AE1-155 | AP_P2-3_WP-500-465_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.25 | 110.25 | AE1-155 | AP_P2-3_WP-500-DRT20_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.25 | 110.25 | AE1-155 | AP_P2-2_WP-500-DRT16_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.25 | 110.25 | AE1-155 | AP_P1-2_WP-500-DRT21_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.25 | 110.25 | AE1-155 | AP_P1-2_WP-500-005A_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 105.29 | 102.59 | AE1-155 | DVP_P4-2: 560T571_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 105.12 | 102.45 | AE1-155 | DVP_P4-2: H2T560_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 105.12 | 102.43 | AE1-155 | DVP_P4-2: H1T560_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 104.98 | 102.29 | AE1-155 | PEPCO_P1_5070_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 136.37 | 133.3 | AE1-157 | DVP_P1-2: LN 514_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 136.37 | 133.3 | AE1-157 | AP_P1-2_PE-500-407T_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 136.37 | 133.29 | AE1-157 | DVP_P4-2: 51482_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 131.27 | 128.19 | AE1-157 | AP_P2-3_PE-500-019C_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3369 | 127.89 | 122.83 | AB2-070 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 118.44 | 117.58 | AE1-157 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 117.06 | 116.25 | AE1-157 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 121.05 | 115.98 | AE1-157 | PECO_P4_PEACH035_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 115.43 | 114.66 | AE1-157 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.78 | 114.36 | AE1-157 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.78 | 114.36 | AE1-157 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.45 | 113.75 | AE1-157 | PECO_P4_PEACH675_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.45 | 113.75 | AE1-157 | PECO_P7-1_220-0607_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3198 | 118.44 | 113.05 | AE1-157 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3369 | 128.1 | 123.03 | AB2-085 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 112.94 | 111.75 | AE1-157 | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 112.89 | 111.7 | AE1-157 | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 116.07 | 111.31 | AE1-157 | PECO_P1-2_220-07_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.9 | 111.25 | AE1-157 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.78 | 111.14 | AE1-157 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.81 | 111.12 | AE1-157 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.83 | 111.09 | AE1-157 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.25 | 110.25 | AE1-157 | AP_P1-2_WP-500-DRT21_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.25 | 110.25 | AE1-157 | AP_P2-3_WP-500-465_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.25 | 110.25 | AE1-157 | AP_P2-2_WP-500-DRT16_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.25 | 110.25 | AE1-157 | AP_P2-3_WP-500-DRT20_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.25 | 110.25 | AE1-157 | AP_P1-2_WP-500-005A_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 105.27 | 102.57 | AE1-157 | DVP_P4-2: 560T571_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 105.1 | 102.43 | AE1-157 | DVP_P4-2: H2T560_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 105.1 | 102.41 | AE1-157 | DVP_P4-2: H1T560_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 104.95 | 102.26 | AE1-157 | PEPCO_P1_5070_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3369 | 128.19 | 123.12 | AB2-100 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 118.54 | 117.69 | AE1-191 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 121.12 | 116.06 | AE1-191 | PECO_P4_PEACH035_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.88 | 114.45 | AE1-191 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.88 | 114.45 | AE1-191 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.53 | 113.84 | AE1-191 | PECO_P4_PEACH675_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.53 | 113.84 | AE1-191 | PECO_P7-1_220-0607_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3198 | 118.55 | 113.15 | AE1-191 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 116.16 | 111.39 | AE1-191 | PECO_P1-2_220-07_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.99 | 111.34 | AE1-191 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.87 | 111.23 | AE1-191 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.9 | 111.21 | AE1-191 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.92 | 111.18 | AE1-191 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3369 | 128.62 | 123.53 | AB2-133 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 121.12 | 116.06 | AE1-212 | PECO_P4_PEACH035_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.54 | 113.84 | AE1-212 | PECO_P4_PEACH675_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.54 | 113.84 | AE1-212 | PECO_P7-1_220-0607_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 116.16 | 111.4 | AE1-212 | PECO_P1-2_220-07_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 116 | 111.35 | AE1-212 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.88 | 111.24 | AE1-212 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.91 | 111.22 | AE1-212 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.92 | 111.18 | AE1-212 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.69 | 111.06 | AE1-212 | PECO_P4_NOTTI85_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 112.84 | 108.4 | AE1-212 | DVP_P1-3: 6SURRY-GSU-1_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3369 | 128.09 | 123.02 | AB2-134 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3369 | 128.65 | 123.57 | AB2-135 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208393 | FARO DC TIE | 208395 | FARO FF | 1 | 115/69 | 229 | 114 | 120.64 | 117.48 | AE1-226 | PL_05_P71_000906_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208395 | FARO FF | 208396 | FARO | 1 | 69 | 229 | 240 | 114.62 | 115.59 | AE1-226 | PL_05_P71_000906_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208393 | FARO DC TIE | 208395 | FARO FF | 2 | 115/69 | 229 | 120 | 114.61 | 111.61 | AE1-226 | PL_05_P71_000906_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208394 | PPL-BGE TIE | 221092 | FIVE.FOR | 1 | 115 | 229/232 | 247 | 109.51 | 110.35 | AE1-226 | PL_05_P71_000906_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208393 | FARO DC TIE | 208395 | FARO FF | 1 | 115/69 | 229 | 114 | 112.13 | 108.31 | AE1-226 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208393 | FARO DC TIE | 208395 | FARO FF | 1 | 115/69 | 229 | 114 | 112.15 | 108.31 | AE1-226 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208393 | FARO DC TIE | 208395 | FARO FF | 1 | 115/69 | 229 | 114 | 112.15 | 108.31 | AE1-226 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208393 | FARO DC TIE | 208395 | FARO FF | 1 | 115/69 | 229 | 114 | 112.14 | 108.3 | AE1-226 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208395 | FARO FF | 208396 | FARO | 1 | 69 | 229 | 240 | 106.54 | 106.38 | AE1-226 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208395 | FARO FF | 208396 | FARO | 1 | 69 | 229 | 240 | 106.56 | 106.38 | AE1-226 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208395 | FARO FF | 208396 | FARO | 1 | 69 | 229 | 240 | 106.56 | 106.38 | AE1-226 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208395 | FARO FF | 208396 | FARO | 1 | 69 | 229 | 240 | 106.55 | 106.37 | AE1-226 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208393 | FARO DC TIE | 208395 | FARO FF | 1 | 115/69 | 229 | 114 | 107.74 | 104.52 | AE1-226 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208393 | FARO DC TIE | 208395 | FARO FF | 1 | 115/69 | 229 | 114 | 105.33 | 103.8 | AE1-226 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208393 | FARO DC TIE | 208395 | FARO FF | 2 | 115/69 | 229 | 120 | 106.53 | 102.89 | AE1-226 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208393 | FARO DC TIE | 208395 | FARO FF | 2 | 115/69 | 229 | 120 | 106.55 | 102.89 | AE1-226 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208393 | FARO DC TIE | 208395 | FARO FF | 2 | 115/69 | 229 | 120 | 106.55 | 102.89 | AE1-226 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208393 | FARO DC TIE | 208395 | FARO FF | 2 | 115/69 | 229 | 120 | 106.54 | 102.88 | AE1-226 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208395 | FARO FF | 208396 | FARO | 1 | 69 | 229 | 240 | 102.37 | 102.42 | AE1-226 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3369 | 128.6 | 123.52 | AB2-136 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208393 | FARO DC TIE | 208395 | FARO FF | 1 | 115/69 | 229 | 114 | 103.23 | 101.99 | AE1-226 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208393 | FARO DC TIE | 208395 | FARO FF | 1 | 115/69 | 229 | 114 | 102.37 | 101.97 | AE1-226 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208393 | FARO DC TIE | 208395 | FARO FF | 1 | 115/69 | 229 | 114 | 102.31 | 101.9 | AE1-226 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208395 | FARO FF | 208396 | FARO | 1 | 69 | 229 | 240 | 100.08 | 101.9 | AE1-226 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208393 | FARO DC TIE | 208394 | PPL-BGE TIE | 1 | 115 | 229 | 268 | 102.41 | 101.75 | AE1-226 | PL_05_P71_000906_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208394 | PPL-BGE TIE | 221092 | FIVE.FOR | 1 | 115 | 229/232 | 247 | 101.66 | 101.56 | AE1-226 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208394 | PPL-BGE TIE | 221092 | FIVE.FOR | 1 | 115 | 229/232 | 247 | 101.67 | 101.56 | AE1-226 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208394 | PPL-BGE TIE | 221092 | FIVE.FOR | 1 | 115 | 229/232 | 247 | 101.67 | 101.56 | AE1-226 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208394 | PPL-BGE TIE | 221092 | FIVE.FOR | 1 | 115 | 229/232 | 247 | 101.67 | 101.55 | AE1-226 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 607 | 170.61 | 168.02 | AE1-229 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 607 | 169.51 | 168.02 | AE1-229 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 607 | 170.25 | 167.99 | AE1-229 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 607 | 169.16 | 167.99 | AE1-229 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 607 | 170.53 | 167.95 | AE1-229 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 607 | 170.53 | 167.95 | AE1-229 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 607 | 169.44 | 167.95 | AE1-229 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 607 | 169.44 | 167.95 | AE1-229 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 628 | 161.45 | 160.22 | AE1-229 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 628 | 161.11 | 160.19 | AE1-229 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 628 | 161.38 | 160.15 | AE1-229 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 628 | 161.38 | 160.15 | AE1-229 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 628 | 158.74 | 157.94 | AE1-229 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 628 | 158.4 | 157.9 | AE1-229 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 628 | 158.67 | 157.87 | AE1-229 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 628 | 158.67 | 157.87 | AE1-229 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 607 | 155.4 | 153.4 | AE1-229 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 607 | 156.49 | 153.4 | AE1-229 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 628 | 147.81 | 146.08 | AE1-229 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 628 | 145.1 | 143.77 | AE1-229 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3369 | 128.17 | 123.1 | AB2-158 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 119.07 | 118.26 | AE1-229 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 117.69 | 116.92 | AE1-229 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 121.75 | 116.66 | AE1-229 | PECO_P4_PEACH035_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 116.05 | 115.33 | AE1-229 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 119.44 | 115 | AE1-229 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 119.44 | 115 | AE1-229 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 119.13 | 114.42 | AE1-229 | PECO_P4_PEACH675_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 119.13 | 114.42 | AE1-229 | PECO_P7-1_220-0607_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3198 | 119.32 | 113.88 | AE1-229 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3369 | 127.99 | 122.92 | AB2-160 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 113.54 | 112.39 | AE1-229 | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 113.49 | 112.34 | AE1-229 | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 116.65 | 111.98 | AE1-229 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 116.75 | 111.97 | AE1-229 | PECO_P1-2_220-07_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 116.53 | 111.87 | AE1-229 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 116.56 | 111.85 | AE1-229 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 116.51 | 111.76 | AE1-229 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.85 | 110.89 | AE1-229 | AP_P2-2_WP-500-DRT16_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.85 | 110.89 | AE1-229 | AP_P2-3_WP-500-465_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.85 | 110.89 | AE1-229 | AP_P2-3_WP-500-DRT20_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.85 | 110.89 | AE1-229 | AP_P1-2_WP-500-DRT21_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.85 | 110.89 | AE1-229 | AP_P1-2_WP-500-005A_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200065 | PCHBTM2S | 200066 | PCHBTM1N | 2 | 500 | 225 | 3022 | 103.78 | 100.02 | AE1-229 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 104.86 | 100.01 | AE1-229 | PECO_P4_PEACH025_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3369 | 128.6 | 123.52 | AB2-172 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 121.43 | 116.35 | AE1-240 | PECO_P4_PEACH035_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 119.17 | 114.73 | AE1-240 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 119.17 | 114.73 | AE1-240 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.83 | 114.13 | AE1-240 | PECO_P4_PEACH675_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.83 | 114.13 | AE1-240 | PECO_P7-1_220-0607_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3198 | 118.92 | 113.51 | AE1-240 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 116.45 | 111.68 | AE1-240 | PECO_P1-2_220-07_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 116.32 | 111.66 | AE1-240 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 116.2 | 111.54 | AE1-240 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 116.23 | 111.52 | AE1-240 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 116.21 | 111.46 | AE1-240 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 607 | 174.49 | 172.17 | AE2-000 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 607 | 173.34 | 172.17 | AE2-000 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 607 | 174.41 | 172.1 | AE2-000 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 607 | 174.41 | 172.1 | AE2-000 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 607 | 173.26 | 172.1 | AE2-000 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 607 | 173.26 | 172.1 | AE2-000 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 607 | 174.07 | 172.08 | AE2-000 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 607 | 172.92 | 172.08 | AE2-000 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 628 | 165.15 | 164.24 | AE2-000 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 628 | 165.07 | 164.17 | AE2-000 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 628 | 165.07 | 164.17 | AE2-000 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 628 | 164.75 | 164.16 | AE2-000 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 628 | 162.43 | 161.96 | AE2-000 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 628 | 162.36 | 161.89 | AE2-000 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 628 | 162.36 | 161.89 | AE2-000 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 628 | 162.03 | 161.87 | AE2-000 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 235463 | 01TANEY | 1 | 138 | 227/201 | 268 | 164.01 | 159.99 | AE2-000 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 235463 | 01TANEY | 1 | 138 | 227/201 | 268 | 164.01 | 159.99 | AE2-000 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 235463 | 01TANEY | 1 | 138 | 227/201 | 268 | 163.94 | 159.92 | AE2-000 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 607 | 159.28 | 157.52 | AE2-000 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 607 | 160.43 | 157.52 | AE2-000 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 628 | 151.56 | 150.07 | AE2-000 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 628 | 148.85 | 147.76 | AE2-000 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 282 | 142.31 | 142.17 | AE2-000 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 282 | 142.31 | 142.17 | AE2-000 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 282 | 142.25 | 142.1 | AE2-000 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 680 | 143.26 | 140.37 | AE2-000 | PEPCO_P4_PP19_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 797 | 144.24 | 139.32 | AE2-000 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 797 | 144.24 | 139.32 | AE2-000 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 797 | 143.89 | 139.31 | AE2-000 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 797 | 144.21 | 139.3 | AE2-000 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204538 | 27STRABAN | 204544 | 27LINCOLN | 1 | 115 | 227 | 313 | 135.57 | 136.69 | AE2-000 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204538 | 27STRABAN | 204544 | 27LINCOLN | 1 | 115 | 227 | 313 | 135.57 | 136.69 | AE2-000 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204538 | 27STRABAN | 204544 | 27LINCOLN | 1 | 115 | 227 | 313 | 135.51 | 136.62 | AE2-000 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 138.74 | 135.66 | AE2-000 | AP_P1-2_PE-500-407T_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 138.74 | 135.66 | AE2-000 | DVP_P1-2: LN 514_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 138.74 | 135.64 | AE2-000 | DVP_P4-2: 51482_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204529 | 27GERMANTN | 204538 | 27STRABAN | 1 | 115 | 227 | 313 | 132.14 | 133.95 | AE2-000 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204529 | 27GERMANTN | 204538 | 27STRABAN | 1 | 115 | 227 | 313 | 132.14 | 133.95 | AE2-000 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204529 | 27GERMANTN | 204538 | 27STRABAN | 1 | 115 | 227 | 313 | 132.08 | 133.88 | AE2-000 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 203981 | AD2-062_POI | 235188 | 01GREENE | 1 | 138 | 226/201 | 268 | 138.01 | 133.47 | AE2-000 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 203981 | AD2-062_POI | 235188 | 01GREENE | 1 | 138 | 226/201 | 268 | 138.01 | 133.47 | AE2-000 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 680 | 136.23 | 133.44 | AE2-000 | PEPCO_P1_PP2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 2 | 230 | 233 | 680 | 136.23 | 133.44 | AE2-000 | PEPCO_P1_PP1_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3369 | 128.24 | 123.16 | AB2-174 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 203981 | AD2-062_POI | 235188 | 01GREENE | 1 | 138 | 226/201 | 268 | 137.92 | 133.38 | AE2-000 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 235463 | 01TANEY | 1 | 138 | 227/201 | 268 | 138.31 | 131.08 | AE2-000 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 235463 | 01TANEY | 1 | 138 | 227/201 | 268 | 138.22 | 131.08 | AE2-000 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 235463 | 01TANEY | 1 | 138 | 227/201 | 268 | 138.22 | 131.08 | AE2-000 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 235463 | 01TANEY | 1 | 138 | 227/201 | 268 | 138.21 | 131.07 | AE2-000 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 797 | 135.89 | 131 | AE2-000 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 133.62 | 130.52 | AE2-000 | AP_P2-3_PE-500-019C_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 204529 | 27GERMANTN | 1 | 138/115 | 227 | 345 | 127.4 | 130.35 | AE2-000 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 204529 | 27GERMANTN | 1 | 138/115 | 227 | 345 | 127.4 | 130.35 | AE2-000 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 204529 | 27GERMANTN | 1 | 138/115 | 227 | 345 | 127.35 | 130.29 | AE2-000 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 814 | 135.03 | 129.84 | AE2-000 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 814 | 135.03 | 129.84 | AE2-000 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 814 | 135.01 | 129.82 | AE2-000 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 814 | 134.36 | 129.81 | AE2-000 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 235463 | 01TANEY | 1 | 138 | 227/201 | 268 | 129.96 | 127.79 | AE2-000 | PEPCO_P4_PP41_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 2 | 230 | 233 | 680 | 130.02 | 127.1 | AE2-000 | AP_P1-2_PE-500-407T_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 680 | 130.02 | 127.1 | AE2-000 | AP_P1-2_PE-500-407T_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 680 | 130.02 | 127.1 | AE2-000 | DVP_P1-2: LN 514_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 2 | 230 | 233 | 680 | 130.02 | 127.1 | AE2-000 | DVP_P1-2: LN 514_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 2 | 230 | 233 | 680 | 130.02 | 127.1 | AE2-000 | DVP_P4-2: 51482_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 680 | 130.02 | 127.1 | AE2-000 | DVP_P4-2: 51482_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3369 | 128.59 | 123.5 | AB2-179 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 235463 | 01TANEY | 1 | 138 | 227/201 | 268 | 127.19 | 125.56 | AE2-000 | AP_P2-3_PE-500-019B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 204550 | 27ORRTANNA | 1 | 115 | 227 | 160 | 126.72 | 125.39 | AE2-000 | ME_P1-2_ME-115-068_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 203981 | AD2-062_POI | 235188 | 01GREENE | 1 | 138 | 226/201 | 268 | 132.27 | 124.88 | AE2-000 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 203981 | AD2-062_POI | 235188 | 01GREENE | 1 | 138 | 226/201 | 268 | 132.18 | 124.88 | AE2-000 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 203981 | AD2-062_POI | 235188 | 01GREENE | 1 | 138 | 226/201 | 268 | 132.18 | 124.88 | AE2-000 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 203981 | AD2-062_POI | 235188 | 01GREENE | 1 | 138 | 226/201 | 268 | 132.17 | 124.88 | AE2-000 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 235463 | 01TANEY | 1 | 138 | 227/201 | 268 | 125.73 | 123.83 | AE2-000 | AP_P1-2_PE-500-406T_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 204550 | 27ORRTANNA | 1 | 115 | 227 | 160 | 125.18 | 123.81 | AE2-000 | ME_P2-3_ME-115-013B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 204550 | 27ORRTANNA | 1 | 115 | 227 | 160 | 125.03 | 123.67 | AE2-000 | ME_P2-3_ME-115-013A_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204539 | 27HUNTRSTN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 282 | 123.04 | 122.6 | AE2-000 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204539 | 27HUNTRSTN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 282 | 123.04 | 122.6 | AE2-000 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204539 | 27HUNTRSTN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 282 | 122.98 | 122.53 | AE2-000 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 204550 | 27ORRTANNA | 1 | 115 | 227 | 160 | 122.81 | 122.24 | AE2-000 | ME_P2-3_ME-115-035A_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 814 | 125.73 | 120.69 | AE2-000 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 204550 | 27ORRTANNA | 1 | 115 | 227 | 160 | 121.26 | 120.66 | AE2-000 | ME_P2-3_ME-115-035B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 120.93 | 120.26 | AE2-000 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 119.53 | 118.92 | AE2-000 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 123.94 | 118.8 | AE2-000 | PECO_P4_PEACH035_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 203981 | AD2-062_POI | 235188 | 01GREENE | 1 | 138 | 226/201 | 268 | 124.47 | 118.77 | AE2-000 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 680 | 120.9 | 117.97 | AE2-000 | AP_P2-3_PE-500-019C_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 2 | 230 | 233 | 680 | 120.9 | 117.97 | AE2-000 | AP_P2-3_PE-500-019C_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 117.89 | 117.31 | AE2-000 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 121.45 | 116.95 | AE2-000 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 121.45 | 116.95 | AE2-000 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3198 | 122.19 | 116.62 | AE2-000 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3369 | 128.06 | 122.99 | AB2-190 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 121.33 | 116.56 | AE2-000 | PECO_P7-1_220-0607_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 121.33 | 116.56 | AE2-000 | PECO_P4_PEACH675_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200532 | 26ROXBURY | 203981 | AD2-062_POI | 1 | 138 | 226 | 268 | 121.3 | 116.52 | AE2-000 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200532 | 26ROXBURY | 203981 | AD2-062_POI | 1 | 138 | 226 | 268 | 121.3 | 116.52 | AE2-000 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200532 | 26ROXBURY | 203981 | AD2-062_POI | 1 | 138 | 226 | 268 | 121.21 | 116.43 | AE2-000 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 282 | 120.63 | 116.24 | AE2-000 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 282 | 120.55 | 116.23 | AE2-000 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 282 | 120.55 | 116.23 | AE2-000 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 282 | 120.55 | 116.22 | AE2-000 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 814 | 119.36 | 116.06 | AE2-000 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 814 | 119.36 | 116.06 | AE2-000 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 814 | 119.02 | 116.05 | AE2-000 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 814 | 119.34 | 116.04 | AE2-000 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3369 | 128.14 | 123.07 | AC1-033 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 119.06 | 114.32 | AE2-000 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 115.31 | 114.29 | AE2-000 | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 115.26 | 114.24 | AE2-000 | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.94 | 114.2 | AE2-000 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.97 | 114.18 | AE2-000 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.95 | 114.11 | AE2-000 | PECO_P1-2_220-07_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.74 | 114.02 | AE2-000 | PECO_P4_NOTTI85_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 797 | 114.38 | 112.9 | AE2-000 | PJM_500_BG_P4_5_CNSTN_15_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 113.62 | 112.79 | AE2-000 | AP_P2-3_WP-500-DRT20_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 113.62 | 112.79 | AE2-000 | AP_P2-2_WP-500-DRT16_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 113.62 | 112.79 | AE2-000 | AP_P2-3_WP-500-465_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 113.62 | 112.79 | AE2-000 | AP_P1-2_WP-500-DRT21_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 113.62 | 112.79 | AE2-000 | AP_P1-2_WP-500-005A_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 282 | 113.58 | 112.1 | AE2-000 | PEPCO_P4_PP41_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 221055 | HARRIS1A | 221058 | DOLFD T1 | 1 | 115 | 232 | 189 | 111.52 | 111.32 | AE2-000 | BG_P7_NWEST_GRNITE_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204538 | 27STRABAN | 204544 | 27LINCOLN | 1 | 115 | 227 | 313 | 113.57 | 110.31 | AE2-000 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204538 | 27STRABAN | 204544 | 27LINCOLN | 1 | 115 | 227 | 313 | 113.49 | 110.3 | AE2-000 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204538 | 27STRABAN | 204544 | 27LINCOLN | 1 | 115 | 227 | 313 | 113.49 | 110.3 | AE2-000 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204538 | 27STRABAN | 204544 | 27LINCOLN | 1 | 115 | 227 | 313 | 113.49 | 110.29 | AE2-000 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 282 | 111.25 | 110.08 | AE2-000 | AP_P2-3_PE-500-019B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 797 | 111.1 | 109.75 | AE2-000 | BG_P7_GRCTN_CNSTN_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3369 | 127.85 | 122.78 | AC1-043 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 282 | 110.42 | 108.86 | AE2-000 | ME_P2-3_ME-115-019A-A_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200532 | 26ROXBURY | 203981 | AD2-062_POI | 1 | 138 | 226 | 268 | 115.56 | 107.94 | AE2-000 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200532 | 26ROXBURY | 203981 | AD2-062_POI | 1 | 138 | 226 | 268 | 115.47 | 107.93 | AE2-000 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200532 | 26ROXBURY | 203981 | AD2-062_POI | 1 | 138 | 226 | 268 | 115.47 | 107.93 | AE2-000 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200532 | 26ROXBURY | 203981 | AD2-062_POI | 1 | 138 | 226 | 268 | 115.46 | 107.93 | AE2-000 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204502 | 27JACKSON | 204514 | 27TMI | 1 | 230 | 227 | 659 | 107.49 | 107.65 | AE2-000 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204502 | 27JACKSON | 204514 | 27TMI | 1 | 230 | 227 | 659 | 107.42 | 107.65 | AE2-000 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204502 | 27JACKSON | 204514 | 27TMI | 1 | 230 | 227 | 659 | 107.42 | 107.65 | AE2-000 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204502 | 27JACKSON | 204514 | 27TMI | 1 | 230 | 227 | 659 | 107.4 | 107.63 | AE2-000 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204529 | 27GERMANTN | 204538 | 27STRABAN | 1 | 115 | 227 | 313 | 110.14 | 107.6 | AE2-000 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204529 | 27GERMANTN | 204538 | 27STRABAN | 1 | 115 | 227 | 313 | 110.07 | 107.6 | AE2-000 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204529 | 27GERMANTN | 204538 | 27STRABAN | 1 | 115 | 227 | 313 | 110.07 | 107.6 | AE2-000 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 814 | 110.98 | 107.6 | AE2-000 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204529 | 27GERMANTN | 204538 | 27STRABAN | 1 | 115 | 227 | 313 | 110.06 | 107.59 | AE2-000 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 221056 | HARRIS0A | 221057 | DOLFD T0 | 1 | 115 | 232 | 189 | 107.12 | 107.28 | AE2-000 | BG_P7_NWEST_GRNITE_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 204529 | 27GERMANTN | 1 | 138/115 | 227 | 345 | 107.44 | 106.25 | AE2-000 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 204529 | 27GERMANTN | 1 | 138/115 | 227 | 345 | 107.37 | 106.24 | AE2-000 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 204529 | 27GERMANTN | 1 | 138/115 | 227 | 345 | 107.37 | 106.24 | AE2-000 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 204529 | 27GERMANTN | 1 | 138/115 | 227 | 345 | 107.36 | 106.23 | AE2-000 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204538 | 27STRABAN | 204544 | 27LINCOLN | 1 | 115 | 227 | 313 | 106.42 | 106.14 | AE2-000 | PEPCO_P4_PP41_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3369 | 127.89 | 122.83 | AC1-053 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3369 | 128.08 | 123 | AC1-065 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 107.4 | 104.67 | AE2-000 | DVP_P4-2: 560T571_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 107.24 | 104.54 | AE2-000 | DVP_P4-2: H2T560_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 107.24 | 104.53 | AE2-000 | DVP_P4-2: H1T560_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 107.1 | 104.38 | AE2-000 | PEPCO_P1_5070_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204538 | 27STRABAN | 204544 | 27LINCOLN | 1 | 115 | 227 | 313 | 104.05 | 104.09 | AE2-000 | AP_P2-3_PE-500-019B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204529 | 27GERMANTN | 204538 | 27STRABAN | 1 | 115 | 227 | 313 | 102.99 | 103.43 | AE2-000 | PEPCO_P4_PP41_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 801 | 105.53 | 103.15 | AE2-000 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 801 | 105.53 | 103.15 | AE2-000 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 801 | 105.51 | 103.13 | AE2-000 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 801 | 104.97 | 103.13 | AE2-000 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220972 | GRANITE1 | 1 | 230 | 232 | 811 | 106.07 | 103.13 | AE2-000 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 108.05 | 103.04 | AE2-000 | PECO_P4_PEACH025_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 204550 | 27ORRTANNA | 1 | 115 | 227 | 160 | 104.97 | 102.96 | AE2-000 | ME_P1-2_ME-115-067_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220972 | GRANITE1 | 1 | 230 | 232 | 811 | 105.82 | 102.85 | AE2-000 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220972 | GRANITE1 | 1 | 230 | 232 | 811 | 105.82 | 102.85 | AE2-000 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220953 | HOWARD12 | 220972 | GRANITE1 | 1 | 230 | 232 | 772 | 105.6 | 102.7 | AE2-000 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204538 | 27STRABAN | 204544 | 27LINCOLN | 1 | 115 | 227 | 313 | 105.63 | 102.67 | AE2-000 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 204529 | 27GERMANTN | 1 | 138/115 | 227 | 345 | 100.96 | 102.48 | AE2-000 | PEPCO_P4_PP41_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220953 | HOWARD12 | 220972 | GRANITE1 | 1 | 230 | 232 | 772 | 105.26 | 102.3 | AE2-000 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220953 | HOWARD12 | 220972 | GRANITE1 | 1 | 230 | 232 | 772 | 105.26 | 102.3 | AE2-000 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208020 | MANO TR3 | 1 | 230 | 229 | 731 | 99.75 | 102.15 | AE2-000 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208020 | MANO TR3 | 1 | 230 | 229 | 731 | 99.75 | 102.15 | AE2-000 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208020 | MANO TR3 | 1 | 230 | 229 | 731 | 99.75 | 102.15 | AE2-000 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208020 | MANO TR3 | 1 | 230 | 229 | 731 | 99.46 | 102.14 | AE2-000 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3198 | 106.99 | 101.99 | AE2-000 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200532 | 26ROXBURY | 203981 | AD2-062_POI | 1 | 138 | 226 | 268 | 107.77 | 101.82 | AE2-000 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208078 | SAKR | 1 | 230 | 229 | 801 | 101.14 | 101.63 | AE2-000 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208078 | SAKR | 1 | 230 | 229 | 801 | 101.14 | 101.63 | AE2-000 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208078 | SAKR | 1 | 230 | 229 | 801 | 101.13 | 101.62 | AE2-000 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208078 | SAKR | 1 | 230 | 229 | 801 | 100.87 | 101.61 | AE2-000 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220973 | GRANITE6 | 1 | 230 | 232 | 811 | 104.29 | 101.42 | AE2-000 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204529 | 27GERMANTN | 204538 | 27STRABAN | 1 | 115 | 227 | 313 | 100.62 | 101.38 | AE2-000 | AP_P2-3_PE-500-019B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220973 | GRANITE6 | 1 | 230 | 232 | 811 | 104.06 | 101.16 | AE2-000 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220973 | GRANITE6 | 1 | 230 | 232 | 811 | 104.06 | 101.16 | AE2-000 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200065 | PCHBTM2S | 200066 | PCHBTM1N | 2 | 500 | 225 | 3022 | 104.75 | 101 | AE2-000 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220954 | HOWARD32 | 220973 | GRANITE6 | 1 | 230 | 232 | 772 | 103.21 | 100.61 | AE2-000 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 204529 | 27GERMANTN | 1 | 138/115 | 227 | 345 | 98.81 | 100.61 | AE2-000 | AP_P2-3_PE-500-019B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220954 | HOWARD32 | 220973 | GRANITE6 | 1 | 230 | 232 | 772 | 102.91 | 100.27 | AE2-000 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220954 | HOWARD32 | 220973 | GRANITE6 | 1 | 230 | 232 | 772 | 102.91 | 100.27 | AE2-000 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200101 | VINCO | 200102 | AA1-076 MAIN | 1 | 500 | 225 | 999 | 103.02 | 100.19 | AE2-000 | PL_02_P42_001064_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200101 | VINCO | 200102 | AA1-076 MAIN | 1 | 500 | 225 | 999 | 103.02 | 100.19 | AE2-000 | PL_02_P12_001029_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200101 | VINCO | 200102 | AA1-076 MAIN | 1 | 500 | 225 | 999 | 103.02 | 100.19 | AE2-000 | PL_02_P42_001063_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 607 | 173.82 | 171.42 | AE2-020 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 607 | 172.68 | 171.42 | AE2-020 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 607 | 172.6 | 171.35 | AE2-020 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 607 | 172.6 | 171.35 | AE2-020 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 607 | 173.74 | 171.35 | AE2-020 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 607 | 173.74 | 171.35 | AE2-020 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 607 | 172.28 | 171.35 | AE2-020 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 607 | 173.42 | 171.35 | AE2-020 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 628 | 164.51 | 163.52 | AE2-020 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 628 | 164.43 | 163.45 | AE2-020 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 628 | 164.43 | 163.45 | AE2-020 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 628 | 164.12 | 163.44 | AE2-020 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 628 | 161.8 | 161.24 | AE2-020 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 628 | 161.72 | 161.17 | AE2-020 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 628 | 161.72 | 161.17 | AE2-020 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 628 | 161.41 | 161.16 | AE2-020 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 235463 | 01TANEY | 1 | 138 | 227/201 | 268 | 163.36 | 159.37 | AE2-020 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 235463 | 01TANEY | 1 | 138 | 227/201 | 268 | 163.36 | 159.37 | AE2-020 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 235463 | 01TANEY | 1 | 138 | 227/201 | 268 | 163.29 | 159.3 | AE2-020 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 607 | 159.75 | 156.79 | AE2-020 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 607 | 158.61 | 156.79 | AE2-020 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 628 | 150.91 | 149.35 | AE2-020 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 628 | 148.19 | 147.05 | AE2-020 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 282 | 141.75 | 141.57 | AE2-020 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 282 | 141.75 | 141.57 | AE2-020 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 282 | 141.69 | 141.5 | AE2-020 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 680 | 142.96 | 140.06 | AE2-020 | PEPCO_P4_PP19_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 797 | 143.63 | 138.72 | AE2-020 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 797 | 143.63 | 138.72 | AE2-020 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 797 | 143.29 | 138.71 | AE2-020 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 797 | 143.6 | 138.7 | AE2-020 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204538 | 27STRABAN | 204544 | 27LINCOLN | 1 | 115 | 227 | 313 | 135.01 | 136.08 | AE2-020 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204538 | 27STRABAN | 204544 | 27LINCOLN | 1 | 115 | 227 | 313 | 135.01 | 136.08 | AE2-020 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204538 | 27STRABAN | 204544 | 27LINCOLN | 1 | 115 | 227 | 313 | 134.95 | 136.01 | AE2-020 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 138.38 | 135.3 | AE2-020 | DVP_P1-2: LN 514_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 138.38 | 135.3 | AE2-020 | AP_P1-2_PE-500-407T_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 138.38 | 135.28 | AE2-020 | DVP_P4-2: 51482_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204529 | 27GERMANTN | 204538 | 27STRABAN | 1 | 115 | 227 | 313 | 131.59 | 133.35 | AE2-020 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204529 | 27GERMANTN | 204538 | 27STRABAN | 1 | 115 | 227 | 313 | 131.59 | 133.35 | AE2-020 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204529 | 27GERMANTN | 204538 | 27STRABAN | 1 | 115 | 227 | 313 | 131.53 | 133.28 | AE2-020 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 680 | 136 | 133.22 | AE2-020 | PEPCO_P1_PP2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 2 | 230 | 233 | 680 | 136 | 133.22 | AE2-020 | PEPCO_P1_PP1_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 797 | 135.27 | 130.39 | AE2-020 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 133.26 | 130.16 | AE2-020 | AP_P2-3_PE-500-019C_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 204529 | 27GERMANTN | 1 | 138/115 | 227 | 345 | 126.9 | 129.8 | AE2-020 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 204529 | 27GERMANTN | 1 | 138/115 | 227 | 345 | 126.9 | 129.8 | AE2-020 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 204529 | 27GERMANTN | 1 | 138/115 | 227 | 345 | 126.85 | 129.73 | AE2-020 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 814 | 134.4 | 129.21 | AE2-020 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 814 | 134.4 | 129.21 | AE2-020 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 814 | 133.75 | 129.2 | AE2-020 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 814 | 134.38 | 129.2 | AE2-020 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 235463 | 01TANEY | 1 | 138 | 227/201 | 268 | 129.43 | 127.27 | AE2-020 | PEPCO_P4_PP41_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 2 | 230 | 233 | 680 | 129.78 | 126.86 | AE2-020 | AP_P1-2_PE-500-407T_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 2 | 230 | 233 | 680 | 129.78 | 126.86 | AE2-020 | DVP_P1-2: LN 514_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 680 | 129.78 | 126.86 | AE2-020 | AP_P1-2_PE-500-407T_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 680 | 129.78 | 126.86 | AE2-020 | DVP_P1-2: LN 514_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 2 | 230 | 233 | 680 | 129.78 | 126.85 | AE2-020 | DVP_P4-2: 51482_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 680 | 129.78 | 126.85 | AE2-020 | DVP_P4-2: 51482_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3369 | 128.24 | 123.16 | AC1-074 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 235463 | 01TANEY | 1 | 138 | 227/201 | 268 | 128.45 | 123.06 | AE2-020 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204539 | 27HUNTRSTN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 282 | 122.45 | 121.98 | AE2-020 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204539 | 27HUNTRSTN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 282 | 122.45 | 121.98 | AE2-020 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204539 | 27HUNTRSTN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 282 | 122.4 | 121.91 | AE2-020 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 814 | 125.08 | 120.06 | AE2-020 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 120.52 | 119.82 | AE2-020 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 123.65 | 118.51 | AE2-020 | PECO_P4_PEACH035_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 119.13 | 118.48 | AE2-020 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 2 | 230 | 233 | 680 | 120.66 | 117.73 | AE2-020 | AP_P2-3_PE-500-019C_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 680 | 120.66 | 117.73 | AE2-020 | AP_P2-3_PE-500-019C_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 117.49 | 116.88 | AE2-020 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 121.06 | 116.57 | AE2-020 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 121.06 | 116.57 | AE2-020 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 120.92 | 116.16 | AE2-020 | PECO_P4_PEACH675_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 120.92 | 116.16 | AE2-020 | PECO_P7-1_220-0607_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3198 | 121.65 | 116.1 | AE2-020 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 282 | 120.13 | 115.73 | AE2-020 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 282 | 120.06 | 115.73 | AE2-020 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 282 | 120.06 | 115.73 | AE2-020 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 282 | 120.05 | 115.72 | AE2-020 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 814 | 118.75 | 115.44 | AE2-020 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 814 | 118.75 | 115.44 | AE2-020 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 814 | 118.42 | 115.44 | AE2-020 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 814 | 118.72 | 115.43 | AE2-020 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3369 | 128.24 | 123.17 | AC1-075 and AC1-080 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.61 | 113.89 | AE2-020 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 114.93 | 113.88 | AE2-020 | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 114.88 | 113.83 | AE2-020 | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.5 | 113.77 | AE2-020 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.52 | 113.75 | AE2-020 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.54 | 113.72 | AE2-020 | PECO_P1-2_220-07_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.3 | 113.59 | AE2-020 | PECO_P4_NOTTI85_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 797 | 113.86 | 112.38 | AE2-020 | PJM_500_BG_P4_5_CNSTN_15_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 113.23 | 112.37 | AE2-020 | AP_P2-3_WP-500-465_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 113.23 | 112.37 | AE2-020 | AP_P2-2_WP-500-DRT16_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 113.23 | 112.37 | AE2-020 | AP_P2-3_WP-500-DRT20_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 113.23 | 112.37 | AE2-020 | AP_P1-2_WP-500-005A_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 113.23 | 112.37 | AE2-020 | AP_P1-2_WP-500-DRT21_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204538 | 27STRABAN | 204544 | 27LINCOLN | 1 | 115 | 227 | 313 | 113.07 | 109.79 | AE2-020 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204538 | 27STRABAN | 204544 | 27LINCOLN | 1 | 115 | 227 | 313 | 113 | 109.79 | AE2-020 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204538 | 27STRABAN | 204544 | 27LINCOLN | 1 | 115 | 227 | 313 | 113 | 109.79 | AE2-020 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204538 | 27STRABAN | 204544 | 27LINCOLN | 1 | 115 | 227 | 313 | 112.99 | 109.79 | AE2-020 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 797 | 110.72 | 109.37 | AE2-020 | BG_P7_GRCTN_CNSTN_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 282 | 112.31 | 108.23 | AE2-020 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204529 | 27GERMANTN | 204538 | 27STRABAN | 1 | 115 | 227 | 313 | 109.65 | 107.09 | AE2-020 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204529 | 27GERMANTN | 204538 | 27STRABAN | 1 | 115 | 227 | 313 | 109.58 | 107.09 | AE2-020 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204529 | 27GERMANTN | 204538 | 27STRABAN | 1 | 115 | 227 | 313 | 109.58 | 107.09 | AE2-020 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204529 | 27GERMANTN | 204538 | 27STRABAN | 1 | 115 | 227 | 313 | 109.57 | 107.08 | AE2-020 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204502 | 27JACKSON | 204514 | 27TMI | 1 | 230 | 227 | 659 | 106.97 | 107.08 | AE2-020 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204502 | 27JACKSON | 204514 | 27TMI | 1 | 230 | 227 | 659 | 106.9 | 107.08 | AE2-020 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204502 | 27JACKSON | 204514 | 27TMI | 1 | 230 | 227 | 659 | 106.9 | 107.08 | AE2-020 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204502 | 27JACKSON | 204514 | 27TMI | 1 | 230 | 227 | 659 | 106.88 | 107.06 | AE2-020 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 814 | 110.35 | 106.98 | AE2-020 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 204529 | 27GERMANTN | 1 | 138/115 | 227 | 345 | 107 | 105.78 | AE2-020 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 204529 | 27GERMANTN | 1 | 138/115 | 227 | 345 | 106.93 | 105.78 | AE2-020 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 204529 | 27GERMANTN | 1 | 138/115 | 227 | 345 | 106.93 | 105.78 | AE2-020 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 204529 | 27GERMANTN | 1 | 138/115 | 227 | 345 | 106.93 | 105.77 | AE2-020 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204538 | 27STRABAN | 204544 | 27LINCOLN | 1 | 115 | 227 | 313 | 105.96 | 105.65 | AE2-020 | PEPCO_P4_PP41_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 107.08 | 104.36 | AE2-020 | DVP_P4-2: 560T571_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 106.92 | 104.23 | AE2-020 | DVP_P4-2: H2T560_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 106.92 | 104.21 | AE2-020 | DVP_P4-2: H1T560_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 106.77 | 104.06 | AE2-020 | PEPCO_P1_5070_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204538 | 27STRABAN | 204544 | 27LINCOLN | 1 | 115 | 227 | 313 | 103.59 | 103.62 | AE2-020 | AP_P2-3_PE-500-019B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204529 | 27GERMANTN | 204538 | 27STRABAN | 1 | 115 | 227 | 313 | 102.53 | 102.94 | AE2-020 | PEPCO_P4_PP41_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220972 | GRANITE1 | 1 | 230 | 232 | 811 | 105.68 | 102.74 | AE2-020 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 801 | 105.04 | 102.61 | AE2-020 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 801 | 105.04 | 102.61 | AE2-020 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 801 | 104.5 | 102.61 | AE2-020 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 801 | 105.01 | 102.59 | AE2-020 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 107.57 | 102.59 | AE2-020 | PECO_P4_PEACH025_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220972 | GRANITE1 | 1 | 230 | 232 | 811 | 105.43 | 102.46 | AE2-020 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220972 | GRANITE1 | 1 | 230 | 232 | 811 | 105.43 | 102.46 | AE2-020 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 204550 | 27ORRTANNA | 1 | 115 | 227 | 160 | 104.38 | 102.37 | AE2-020 | ME_P1-2_ME-115-067_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220953 | HOWARD12 | 220972 | GRANITE1 | 1 | 230 | 232 | 772 | 105.16 | 102.25 | AE2-020 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204538 | 27STRABAN | 204544 | 27LINCOLN | 1 | 115 | 227 | 313 | 105.12 | 102.17 | AE2-020 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 204529 | 27GERMANTN | 1 | 138/115 | 227 | 345 | 100.54 | 102.04 | AE2-020 | PEPCO_P4_PP41_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220953 | HOWARD12 | 220972 | GRANITE1 | 1 | 230 | 232 | 772 | 104.81 | 101.85 | AE2-020 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220953 | HOWARD12 | 220972 | GRANITE1 | 1 | 230 | 232 | 772 | 104.81 | 101.85 | AE2-020 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208020 | MANO TR3 | 1 | 230 | 229 | 731 | 99.18 | 101.47 | AE2-020 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208020 | MANO TR3 | 1 | 230 | 229 | 731 | 99.18 | 101.47 | AE2-020 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208020 | MANO TR3 | 1 | 230 | 229 | 731 | 98.9 | 101.47 | AE2-020 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208020 | MANO TR3 | 1 | 230 | 229 | 731 | 99.17 | 101.47 | AE2-020 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3198 | 106.42 | 101.45 | AE2-020 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200065 | PCHBTM2S | 200066 | PCHBTM1N | 2 | 500 | 225 | 3022 | 105.22 | 101.43 | AE2-020 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220973 | GRANITE6 | 1 | 230 | 232 | 811 | 103.91 | 101.04 | AE2-020 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208078 | SAKR | 1 | 230 | 229 | 801 | 100.53 | 100.94 | AE2-020 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208078 | SAKR | 1 | 230 | 229 | 801 | 100.53 | 100.94 | AE2-020 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208078 | SAKR | 1 | 230 | 229 | 801 | 100.27 | 100.94 | AE2-020 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208078 | SAKR | 1 | 230 | 229 | 801 | 100.52 | 100.94 | AE2-020 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204529 | 27GERMANTN | 204538 | 27STRABAN | 1 | 115 | 227 | 313 | 100.17 | 100.91 | AE2-020 | AP_P2-3_PE-500-019B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220973 | GRANITE6 | 1 | 230 | 232 | 811 | 103.68 | 100.78 | AE2-020 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220973 | GRANITE6 | 1 | 230 | 232 | 811 | 103.68 | 100.78 | AE2-020 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220954 | HOWARD32 | 220973 | GRANITE6 | 1 | 230 | 232 | 772 | 102.79 | 100.19 | AE2-020 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 204529 | 27GERMANTN | 1 | 138/115 | 227 | 345 | 98.4 | 100.17 | AE2-020 | AP_P2-3_PE-500-019B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200101 | VINCO | 200102 | AA1-076 MAIN | 1 | 500 | 225 | 999 | 103.15 | 100.02 | AE2-020 | PECO_P1-2_5034_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200101 | VINCO | 200102 | AA1-076 MAIN | 1 | 500 | 225 | 999 | 103.15 | 100.01 | AE2-020 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 607 | 173.82 | 171.42 | AE2-021 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 607 | 172.68 | 171.42 | AE2-021 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 607 | 172.6 | 171.35 | AE2-021 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 607 | 172.6 | 171.35 | AE2-021 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 607 | 173.74 | 171.35 | AE2-021 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 607 | 173.74 | 171.35 | AE2-021 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 607 | 172.28 | 171.35 | AE2-021 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 607 | 173.42 | 171.35 | AE2-021 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 628 | 164.51 | 163.52 | AE2-021 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 628 | 164.43 | 163.45 | AE2-021 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 628 | 164.43 | 163.45 | AE2-021 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 628 | 164.12 | 163.44 | AE2-021 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 628 | 161.8 | 161.24 | AE2-021 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 628 | 161.72 | 161.17 | AE2-021 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 628 | 161.72 | 161.17 | AE2-021 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 628 | 161.41 | 161.16 | AE2-021 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 235463 | 01TANEY | 1 | 138 | 227/201 | 268 | 163.36 | 159.37 | AE2-021 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 235463 | 01TANEY | 1 | 138 | 227/201 | 268 | 163.36 | 159.37 | AE2-021 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 235463 | 01TANEY | 1 | 138 | 227/201 | 268 | 163.29 | 159.3 | AE2-021 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 607 | 159.75 | 156.79 | AE2-021 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 607 | 158.61 | 156.79 | AE2-021 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 628 | 150.91 | 149.35 | AE2-021 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 628 | 148.19 | 147.05 | AE2-021 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 282 | 141.75 | 141.57 | AE2-021 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 282 | 141.75 | 141.57 | AE2-021 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 282 | 141.69 | 141.5 | AE2-021 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 680 | 142.96 | 140.06 | AE2-021 | PEPCO_P4_PP19_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 797 | 143.63 | 138.72 | AE2-021 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 797 | 143.63 | 138.72 | AE2-021 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 797 | 143.29 | 138.71 | AE2-021 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 797 | 143.6 | 138.7 | AE2-021 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204538 | 27STRABAN | 204544 | 27LINCOLN | 1 | 115 | 227 | 313 | 135.01 | 136.08 | AE2-021 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204538 | 27STRABAN | 204544 | 27LINCOLN | 1 | 115 | 227 | 313 | 135.01 | 136.08 | AE2-021 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204538 | 27STRABAN | 204544 | 27LINCOLN | 1 | 115 | 227 | 313 | 134.95 | 136.01 | AE2-021 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 138.38 | 135.3 | AE2-021 | DVP_P1-2: LN 514_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 138.38 | 135.3 | AE2-021 | AP_P1-2_PE-500-407T_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 138.38 | 135.28 | AE2-021 | DVP_P4-2: 51482_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204529 | 27GERMANTN | 204538 | 27STRABAN | 1 | 115 | 227 | 313 | 131.59 | 133.35 | AE2-021 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204529 | 27GERMANTN | 204538 | 27STRABAN | 1 | 115 | 227 | 313 | 131.59 | 133.35 | AE2-021 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204529 | 27GERMANTN | 204538 | 27STRABAN | 1 | 115 | 227 | 313 | 131.53 | 133.28 | AE2-021 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 680 | 136 | 133.22 | AE2-021 | PEPCO_P1_PP2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 2 | 230 | 233 | 680 | 136 | 133.22 | AE2-021 | PEPCO_P1_PP1_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 797 | 135.27 | 130.39 | AE2-021 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 133.26 | 130.16 | AE2-021 | AP_P2-3_PE-500-019C_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 204529 | 27GERMANTN | 1 | 138/115 | 227 | 345 | 126.9 | 129.8 | AE2-021 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 204529 | 27GERMANTN | 1 | 138/115 | 227 | 345 | 126.9 | 129.8 | AE2-021 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 204529 | 27GERMANTN | 1 | 138/115 | 227 | 345 | 126.85 | 129.73 | AE2-021 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 814 | 134.4 | 129.21 | AE2-021 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 814 | 134.4 | 129.21 | AE2-021 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 814 | 133.75 | 129.2 | AE2-021 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 814 | 134.38 | 129.2 | AE2-021 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 235463 | 01TANEY | 1 | 138 | 227/201 | 268 | 129.43 | 127.27 | AE2-021 | PEPCO_P4_PP41_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 2 | 230 | 233 | 680 | 129.78 | 126.86 | AE2-021 | AP_P1-2_PE-500-407T_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 2 | 230 | 233 | 680 | 129.78 | 126.86 | AE2-021 | DVP_P1-2: LN 514_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 680 | 129.78 | 126.86 | AE2-021 | AP_P1-2_PE-500-407T_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 680 | 129.78 | 126.86 | AE2-021 | DVP_P1-2: LN 514_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 2 | 230 | 233 | 680 | 129.78 | 126.85 | AE2-021 | DVP_P4-2: 51482_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 680 | 129.78 | 126.85 | AE2-021 | DVP_P4-2: 51482_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3369 | 128.07 | 123 | AC1-078 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 235463 | 01TANEY | 1 | 138 | 227/201 | 268 | 128.45 | 123.06 | AE2-021 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204539 | 27HUNTRSTN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 282 | 122.45 | 121.98 | AE2-021 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204539 | 27HUNTRSTN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 282 | 122.45 | 121.98 | AE2-021 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204539 | 27HUNTRSTN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 282 | 122.4 | 121.91 | AE2-021 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 814 | 125.08 | 120.06 | AE2-021 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 120.52 | 119.82 | AE2-021 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 123.65 | 118.51 | AE2-021 | PECO_P4_PEACH035_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 119.13 | 118.48 | AE2-021 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 2 | 230 | 233 | 680 | 120.66 | 117.73 | AE2-021 | AP_P2-3_PE-500-019C_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 680 | 120.66 | 117.73 | AE2-021 | AP_P2-3_PE-500-019C_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 117.49 | 116.88 | AE2-021 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 121.06 | 116.57 | AE2-021 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 121.06 | 116.57 | AE2-021 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 120.92 | 116.16 | AE2-021 | PECO_P4_PEACH675_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 120.92 | 116.16 | AE2-021 | PECO_P7-1_220-0607_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3198 | 121.65 | 116.1 | AE2-021 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 282 | 120.13 | 115.73 | AE2-021 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 282 | 120.06 | 115.73 | AE2-021 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 282 | 120.06 | 115.73 | AE2-021 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 282 | 120.05 | 115.72 | AE2-021 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 814 | 118.75 | 115.44 | AE2-021 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 814 | 118.75 | 115.44 | AE2-021 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 814 | 118.42 | 115.44 | AE2-021 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 814 | 118.72 | 115.43 | AE2-021 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3369 | 128.21 | 123.14 | AC1-082 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.61 | 113.89 | AE2-021 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 114.93 | 113.88 | AE2-021 | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 114.88 | 113.83 | AE2-021 | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.5 | 113.77 | AE2-021 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.52 | 113.75 | AE2-021 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.54 | 113.72 | AE2-021 | PECO_P1-2_220-07_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.3 | 113.59 | AE2-021 | PECO_P4_NOTTI85_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 797 | 113.86 | 112.38 | AE2-021 | PJM_500_BG_P4_5_CNSTN_15_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 113.23 | 112.37 | AE2-021 | AP_P2-3_WP-500-465_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 113.23 | 112.37 | AE2-021 | AP_P2-2_WP-500-DRT16_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 113.23 | 112.37 | AE2-021 | AP_P2-3_WP-500-DRT20_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 113.23 | 112.37 | AE2-021 | AP_P1-2_WP-500-005A_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 113.23 | 112.37 | AE2-021 | AP_P1-2_WP-500-DRT21_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204538 | 27STRABAN | 204544 | 27LINCOLN | 1 | 115 | 227 | 313 | 113.07 | 109.79 | AE2-021 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204538 | 27STRABAN | 204544 | 27LINCOLN | 1 | 115 | 227 | 313 | 113 | 109.79 | AE2-021 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204538 | 27STRABAN | 204544 | 27LINCOLN | 1 | 115 | 227 | 313 | 113 | 109.79 | AE2-021 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204538 | 27STRABAN | 204544 | 27LINCOLN | 1 | 115 | 227 | 313 | 112.99 | 109.79 | AE2-021 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 797 | 110.72 | 109.37 | AE2-021 | BG_P7_GRCTN_CNSTN_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 282 | 112.31 | 108.23 | AE2-021 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204529 | 27GERMANTN | 204538 | 27STRABAN | 1 | 115 | 227 | 313 | 109.65 | 107.09 | AE2-021 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204529 | 27GERMANTN | 204538 | 27STRABAN | 1 | 115 | 227 | 313 | 109.58 | 107.09 | AE2-021 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204529 | 27GERMANTN | 204538 | 27STRABAN | 1 | 115 | 227 | 313 | 109.58 | 107.09 | AE2-021 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204529 | 27GERMANTN | 204538 | 27STRABAN | 1 | 115 | 227 | 313 | 109.57 | 107.08 | AE2-021 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204502 | 27JACKSON | 204514 | 27TMI | 1 | 230 | 227 | 659 | 106.97 | 107.08 | AE2-021 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204502 | 27JACKSON | 204514 | 27TMI | 1 | 230 | 227 | 659 | 106.9 | 107.08 | AE2-021 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204502 | 27JACKSON | 204514 | 27TMI | 1 | 230 | 227 | 659 | 106.9 | 107.08 | AE2-021 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204502 | 27JACKSON | 204514 | 27TMI | 1 | 230 | 227 | 659 | 106.88 | 107.06 | AE2-021 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 814 | 110.35 | 106.98 | AE2-021 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 204529 | 27GERMANTN | 1 | 138/115 | 227 | 345 | 107 | 105.78 | AE2-021 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 204529 | 27GERMANTN | 1 | 138/115 | 227 | 345 | 106.93 | 105.78 | AE2-021 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 204529 | 27GERMANTN | 1 | 138/115 | 227 | 345 | 106.93 | 105.78 | AE2-021 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 204529 | 27GERMANTN | 1 | 138/115 | 227 | 345 | 106.93 | 105.77 | AE2-021 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204538 | 27STRABAN | 204544 | 27LINCOLN | 1 | 115 | 227 | 313 | 105.96 | 105.65 | AE2-021 | PEPCO_P4_PP41_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 107.08 | 104.36 | AE2-021 | DVP_P4-2: 560T571_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 106.92 | 104.23 | AE2-021 | DVP_P4-2: H2T560_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 106.92 | 104.21 | AE2-021 | DVP_P4-2: H1T560_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 106.77 | 104.06 | AE2-021 | PEPCO_P1_5070_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204538 | 27STRABAN | 204544 | 27LINCOLN | 1 | 115 | 227 | 313 | 103.59 | 103.62 | AE2-021 | AP_P2-3_PE-500-019B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204529 | 27GERMANTN | 204538 | 27STRABAN | 1 | 115 | 227 | 313 | 102.53 | 102.94 | AE2-021 | PEPCO_P4_PP41_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220972 | GRANITE1 | 1 | 230 | 232 | 811 | 105.68 | 102.74 | AE2-021 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 801 | 105.04 | 102.61 | AE2-021 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 801 | 105.04 | 102.61 | AE2-021 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 801 | 104.5 | 102.61 | AE2-021 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 801 | 105.01 | 102.59 | AE2-021 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 107.57 | 102.59 | AE2-021 | PECO_P4_PEACH025_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220972 | GRANITE1 | 1 | 230 | 232 | 811 | 105.43 | 102.46 | AE2-021 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220972 | GRANITE1 | 1 | 230 | 232 | 811 | 105.43 | 102.46 | AE2-021 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 204550 | 27ORRTANNA | 1 | 115 | 227 | 160 | 104.38 | 102.37 | AE2-021 | ME_P1-2_ME-115-067_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220953 | HOWARD12 | 220972 | GRANITE1 | 1 | 230 | 232 | 772 | 105.16 | 102.25 | AE2-021 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204538 | 27STRABAN | 204544 | 27LINCOLN | 1 | 115 | 227 | 313 | 105.12 | 102.17 | AE2-021 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 204529 | 27GERMANTN | 1 | 138/115 | 227 | 345 | 100.54 | 102.04 | AE2-021 | PEPCO_P4_PP41_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220953 | HOWARD12 | 220972 | GRANITE1 | 1 | 230 | 232 | 772 | 104.81 | 101.85 | AE2-021 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220953 | HOWARD12 | 220972 | GRANITE1 | 1 | 230 | 232 | 772 | 104.81 | 101.85 | AE2-021 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208020 | MANO TR3 | 1 | 230 | 229 | 731 | 99.18 | 101.47 | AE2-021 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208020 | MANO TR3 | 1 | 230 | 229 | 731 | 99.18 | 101.47 | AE2-021 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208020 | MANO TR3 | 1 | 230 | 229 | 731 | 98.9 | 101.47 | AE2-021 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208020 | MANO TR3 | 1 | 230 | 229 | 731 | 99.17 | 101.47 | AE2-021 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3198 | 106.42 | 101.45 | AE2-021 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200065 | PCHBTM2S | 200066 | PCHBTM1N | 2 | 500 | 225 | 3022 | 105.22 | 101.43 | AE2-021 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220973 | GRANITE6 | 1 | 230 | 232 | 811 | 103.91 | 101.04 | AE2-021 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208078 | SAKR | 1 | 230 | 229 | 801 | 100.53 | 100.94 | AE2-021 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208078 | SAKR | 1 | 230 | 229 | 801 | 100.53 | 100.94 | AE2-021 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208078 | SAKR | 1 | 230 | 229 | 801 | 100.27 | 100.94 | AE2-021 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208078 | SAKR | 1 | 230 | 229 | 801 | 100.52 | 100.94 | AE2-021 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204529 | 27GERMANTN | 204538 | 27STRABAN | 1 | 115 | 227 | 313 | 100.17 | 100.91 | AE2-021 | AP_P2-3_PE-500-019B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220973 | GRANITE6 | 1 | 230 | 232 | 811 | 103.68 | 100.78 | AE2-021 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220973 | GRANITE6 | 1 | 230 | 232 | 811 | 103.68 | 100.78 | AE2-021 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220954 | HOWARD32 | 220973 | GRANITE6 | 1 | 230 | 232 | 772 | 102.79 | 100.19 | AE2-021 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 204529 | 27GERMANTN | 1 | 138/115 | 227 | 345 | 98.4 | 100.17 | AE2-021 | AP_P2-3_PE-500-019B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200101 | VINCO | 200102 | AA1-076 MAIN | 1 | 500 | 225 | 999 | 103.15 | 100.02 | AE2-021 | PECO_P1-2_5034_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200101 | VINCO | 200102 | AA1-076 MAIN | 1 | 500 | 225 | 999 | 103.15 | 100.01 | AE2-021 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 607 | 170.67 | 169.26 | AE2-022 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 607 | 171.78 | 169.26 | AE2-022 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 607 | 171.41 | 169.21 | AE2-022 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 607 | 170.3 | 169.21 | AE2-022 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 607 | 170.59 | 169.19 | AE2-022 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 607 | 170.59 | 169.19 | AE2-022 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 607 | 171.7 | 169.19 | AE2-022 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 607 | 171.7 | 169.19 | AE2-022 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 628 | 162.57 | 161.43 | AE2-022 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 628 | 162.21 | 161.38 | AE2-022 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 628 | 162.49 | 161.36 | AE2-022 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 628 | 162.49 | 161.36 | AE2-022 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 628 | 159.86 | 159.14 | AE2-022 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 628 | 159.5 | 159.09 | AE2-022 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 628 | 159.78 | 159.07 | AE2-022 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 628 | 159.78 | 159.07 | AE2-022 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 607 | 156.57 | 154.64 | AE2-022 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 607 | 157.68 | 154.64 | AE2-022 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 628 | 148.94 | 147.27 | AE2-022 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 628 | 146.23 | 144.96 | AE2-022 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 797 | 142.31 | 137.73 | AE2-022 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 797 | 142.62 | 137.71 | AE2-022 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 797 | 142.62 | 137.71 | AE2-022 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 797 | 142.59 | 137.69 | AE2-022 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 137.62 | 134.54 | AE2-022 | DVP_P1-2: LN 514_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 137.62 | 134.54 | AE2-022 | AP_P1-2_PE-500-407T_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 137.62 | 134.52 | AE2-022 | DVP_P4-2: 51482_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 132.5 | 129.41 | AE2-022 | AP_P2-3_PE-500-019C_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 797 | 134.24 | 129.4 | AE2-022 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 814 | 132.67 | 128.14 | AE2-022 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 814 | 133.25 | 128.09 | AE2-022 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 814 | 133.25 | 128.09 | AE2-022 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 814 | 133.24 | 128.08 | AE2-022 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3369 | 128.15 | 123.07 | AC1-083 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 814 | 123.92 | 118.94 | AE2-022 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 119.61 | 118.84 | AE2-022 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 118.22 | 117.5 | AE2-022 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 122.45 | 117.35 | AE2-022 | PECO_P4_PEACH035_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 116.59 | 115.9 | AE2-022 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 120.04 | 115.58 | AE2-022 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 120.04 | 115.58 | AE2-022 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 119.8 | 115.06 | AE2-022 | PECO_P4_PEACH675_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 119.8 | 115.06 | AE2-022 | PECO_P7-1_220-0607_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3198 | 120.18 | 114.7 | AE2-022 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 814 | 117.43 | 114.44 | AE2-022 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 814 | 117.73 | 114.41 | AE2-022 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 814 | 117.73 | 114.41 | AE2-022 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 814 | 117.7 | 114.4 | AE2-022 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3369 | 127.73 | 122.66 | AC1-085 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 114.06 | 112.94 | AE2-022 | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 114.01 | 112.9 | AE2-022 | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 117.37 | 112.68 | AE2-022 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 117.42 | 112.62 | AE2-022 | PECO_P1-2_220-07_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 117.26 | 112.57 | AE2-022 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 117.29 | 112.55 | AE2-022 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 117.17 | 112.4 | AE2-022 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 112.36 | 111.44 | AE2-022 | AP_P2-2_WP-500-DRT16_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 112.36 | 111.44 | AE2-022 | AP_P1-2_WP-500-005A_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 112.36 | 111.44 | AE2-022 | AP_P1-2_WP-500-DRT21_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 112.36 | 111.44 | AE2-022 | AP_P2-3_WP-500-DRT20_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 112.36 | 111.44 | AE2-022 | AP_P2-3_WP-500-465_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204502 | 27JACKSON | 204514 | 27TMI | 1 | 230 | 227 | 659 | 105.91 | 106.01 | AE2-022 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204502 | 27JACKSON | 204514 | 27TMI | 1 | 230 | 227 | 659 | 105.91 | 106.01 | AE2-022 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204502 | 27JACKSON | 204514 | 27TMI | 1 | 230 | 227 | 659 | 105.98 | 106 | AE2-022 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204502 | 27JACKSON | 204514 | 27TMI | 1 | 230 | 227 | 659 | 105.89 | 105.99 | AE2-022 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 814 | 109.32 | 105.97 | AE2-022 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 106.37 | 103.66 | AE2-022 | DVP_P4-2: 560T571_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 106.21 | 103.52 | AE2-022 | DVP_P4-2: H2T560_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 106.21 | 103.51 | AE2-022 | DVP_P4-2: H1T560_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 106.07 | 103.36 | AE2-022 | PEPCO_P1_5070_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220972 | GRANITE1 | 1 | 230 | 232 | 811 | 104.85 | 101.92 | AE2-022 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 801 | 103.66 | 101.7 | AE2-022 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 801 | 104.15 | 101.66 | AE2-022 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 801 | 104.15 | 101.66 | AE2-022 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 801 | 104.13 | 101.64 | AE2-022 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220972 | GRANITE1 | 1 | 230 | 232 | 811 | 104.6 | 101.63 | AE2-022 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220972 | GRANITE1 | 1 | 230 | 232 | 811 | 104.6 | 101.63 | AE2-022 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220953 | HOWARD12 | 220972 | GRANITE1 | 1 | 230 | 232 | 772 | 104.2 | 101.3 | AE2-022 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 105.86 | 100.96 | AE2-022 | PECO_P4_PEACH025_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220953 | HOWARD12 | 220972 | GRANITE1 | 1 | 230 | 232 | 772 | 103.84 | 100.9 | AE2-022 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220953 | HOWARD12 | 220972 | GRANITE1 | 1 | 230 | 232 | 772 | 103.84 | 100.9 | AE2-022 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200065 | PCHBTM2S | 200066 | PCHBTM1N | 2 | 500 | 225 | 3022 | 104.31 | 100.54 | AE2-022 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208020 | MANO TR3 | 1 | 230 | 229 | 731 | 97.96 | 100.35 | AE2-022 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208020 | MANO TR3 | 1 | 230 | 229 | 731 | 98.21 | 100.32 | AE2-022 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208020 | MANO TR3 | 1 | 230 | 229 | 731 | 98.21 | 100.32 | AE2-022 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208020 | MANO TR3 | 1 | 230 | 229 | 731 | 98.21 | 100.32 | AE2-022 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220973 | GRANITE6 | 1 | 230 | 232 | 811 | 103.09 | 100.24 | AE2-022 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3198 | 104.93 | 100.02 | AE2-022 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 136.44 | 133.37 | AE2-027 | DVP_P1-2: LN 514_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 136.44 | 133.37 | AE2-027 | AP_P1-2_PE-500-407T_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 136.44 | 133.35 | AE2-027 | DVP_P4-2: 51482_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 131.33 | 128.25 | AE2-027 | AP_P2-3_PE-500-019C_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3369 | 128.03 | 122.96 | AC1-086 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 118.45 | 117.6 | AE2-027 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 117.08 | 116.27 | AE2-027 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 121.05 | 115.99 | AE2-027 | PECO_P4_PEACH035_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 115.44 | 114.67 | AE2-027 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.8 | 114.37 | AE2-027 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.8 | 114.37 | AE2-027 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.46 | 113.76 | AE2-027 | PECO_P7-1_220-0607_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.46 | 113.76 | AE2-027 | PECO_P4_PEACH675_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3198 | 118.45 | 113.06 | AE2-027 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3369 | 128.14 | 123.06 | AC1-089 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 112.95 | 111.76 | AE2-027 | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 112.9 | 111.72 | AE2-027 | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 116.08 | 111.32 | AE2-027 | PECO_P1-2_220-07_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.91 | 111.26 | AE2-027 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.79 | 111.15 | AE2-027 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.82 | 111.13 | AE2-027 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.84 | 111.1 | AE2-027 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.26 | 110.26 | AE2-027 | AP_P1-2_WP-500-DRT21_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.26 | 110.26 | AE2-027 | AP_P1-2_WP-500-005A_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.26 | 110.26 | AE2-027 | AP_P2-3_WP-500-DRT20_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.26 | 110.26 | AE2-027 | AP_P2-2_WP-500-DRT16_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.26 | 110.26 | AE2-027 | AP_P2-3_WP-500-465_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 105.15 | 102.48 | AE2-027 | DVP_P4-2: H2T560_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 105.15 | 102.46 | AE2-027 | DVP_P4-2: H1T560_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 105 | 102.31 | AE2-027 | PEPCO_P1_5070_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3369 | 128.07 | 123 | AC1-120 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3198 | 118.89 | 113.48 | AE2-042 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 116.29 | 111.63 | AE2-042 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 116.17 | 111.51 | AE2-042 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 116.2 | 111.49 | AE2-042 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.97 | 111.34 | AE2-042 | PECO_P4_NOTTI85_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.91 | 111.33 | AE2-042 | PECO_P1-2_220-08_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.86 | 111.28 | AE2-042 | PECO_P4_COOPR125_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.62 | 111.13 | AE2-042 | PECO_P1-2_220-93_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 113.11 | 108.66 | AE2-042 | DVP_P1-3: 6SURRY-GSU-1_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 113.18 | 108.41 | AE2-042 | PL_18_P42_000129_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 113.18 | 108.41 | AE2-042 | PL_18_P42_000130_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3369 | 126.83 | 121.8 | AC1-158 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 118.93 | 118.11 | AE2-046 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 117.55 | 116.78 | AE2-046 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 121.45 | 116.38 | AE2-046 | PECO_P4_PEACH035_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 115.92 | 115.18 | AE2-046 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 119.25 | 114.82 | AE2-046 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 119.25 | 114.82 | AE2-046 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.92 | 114.21 | AE2-046 | PECO_P4_PEACH675_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.92 | 114.21 | AE2-046 | PECO_P7-1_220-0607_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3198 | 119.03 | 113.61 | AE2-046 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3369 | 127.88 | 122.82 | AC1-161 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 113.41 | 112.25 | AE2-046 | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 113.36 | 112.2 | AE2-046 | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 116.54 | 111.76 | AE2-046 | PECO_P1-2_220-07_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 116.4 | 111.74 | AE2-046 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 116.28 | 111.63 | AE2-046 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 116.31 | 111.61 | AE2-046 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 116.3 | 111.55 | AE2-046 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.72 | 110.76 | AE2-046 | AP_P1-2_WP-500-005A_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.72 | 110.76 | AE2-046 | AP_P1-2_WP-500-DRT21_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.72 | 110.76 | AE2-046 | AP_P2-2_WP-500-DRT16_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.72 | 110.76 | AE2-046 | AP_P2-3_WP-500-465_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.72 | 110.76 | AE2-046 | AP_P2-3_WP-500-DRT20_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3369 | 127.69 | 122.63 | AC1-164 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 121.46 | 116.38 | AE2-093 | PECO_P4_PEACH035_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 119.18 | 114.75 | AE2-093 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 119.18 | 114.75 | AE2-093 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.85 | 114.14 | AE2-093 | PECO_P4_PEACH675_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.85 | 114.14 | AE2-093 | PECO_P7-1_220-0607_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3198 | 118.95 | 113.53 | AE2-093 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 116.47 | 111.7 | AE2-093 | PECO_P1-2_220-07_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 116.34 | 111.68 | AE2-093 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 116.22 | 111.56 | AE2-093 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 116.25 | 111.54 | AE2-093 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 116.23 | 111.48 | AE2-093 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3369 | 128.2 | 123.12 | AC1-168 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 118.52 | 117.67 | AE2-206 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 117.15 | 116.35 | AE2-206 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 121.05 | 115.98 | AE2-206 | PECO_P4_PEACH035_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 115.51 | 114.75 | AE2-206 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.84 | 114.41 | AE2-206 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.84 | 114.41 | AE2-206 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.47 | 113.78 | AE2-206 | PECO_P7-1_220-0607_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.47 | 113.78 | AE2-206 | PECO_P4_PEACH675_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3198 | 118.48 | 113.08 | AE2-206 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3369 | 128.21 | 123.14 | AC1-173 GEN | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 113.02 | 111.84 | AE2-206 | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 112.97 | 111.79 | AE2-206 | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 116.09 | 111.33 | AE2-206 | PECO_P1-2_220-07_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.93 | 111.28 | AE2-206 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.81 | 111.16 | AE2-206 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.84 | 111.14 | AE2-206 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.85 | 111.12 | AE2-206 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.32 | 110.33 | AE2-206 | AP_P1-2_WP-500-005A_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.32 | 110.33 | AE2-206 | AP_P1-2_WP-500-DRT21_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.32 | 110.33 | AE2-206 | AP_P2-3_WP-500-DRT20_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.32 | 110.33 | AE2-206 | AP_P2-3_WP-500-465_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.32 | 110.33 | AE2-206 | AP_P2-2_WP-500-DRT16_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 607 | 168.88 | 166.17 | AE2-217 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 607 | 167.82 | 166.17 | AE2-217 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 607 | 168.56 | 166.17 | AE2-217 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 607 | 167.49 | 166.17 | AE2-217 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 607 | 168.81 | 166.1 | AE2-217 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 607 | 168.81 | 166.1 | AE2-217 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 607 | 167.74 | 166.1 | AE2-217 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 607 | 167.74 | 166.1 | AE2-217 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 628 | 159.81 | 158.44 | AE2-217 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 628 | 159.5 | 158.43 | AE2-217 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 628 | 159.73 | 158.37 | AE2-217 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 628 | 159.73 | 158.37 | AE2-217 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 628 | 157.1 | 156.15 | AE2-217 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 628 | 156.79 | 156.14 | AE2-217 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 628 | 157.03 | 156.08 | AE2-217 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 628 | 157.03 | 156.08 | AE2-217 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 607 | 153.72 | 151.63 | AE2-217 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 607 | 154.79 | 151.63 | AE2-217 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 628 | 146.19 | 144.36 | AE2-217 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 628 | 143.48 | 142.05 | AE2-217 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3369 | 128.22 | 123.15 | AC1-174 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 118.23 | 117.36 | AE2-217 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 116.86 | 116.04 | AE2-217 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 120.69 | 115.64 | AE2-217 | PECO_P4_PEACH035_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 115.23 | 114.44 | AE2-217 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.53 | 114.12 | AE2-217 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.53 | 114.12 | AE2-217 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.14 | 113.45 | AE2-217 | PECO_P7-1_220-0607_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.14 | 113.45 | AE2-217 | PECO_P4_PEACH675_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3198 | 118.07 | 112.69 | AE2-217 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3369 | 128.22 | 123.15 | AC1-175 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 112.75 | 111.54 | AE2-217 | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 112.7 | 111.5 | AE2-217 | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.76 | 111 | AE2-217 | PECO_P1-2_220-07_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.56 | 110.93 | AE2-217 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.45 | 110.81 | AE2-217 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.47 | 110.79 | AE2-217 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.52 | 110.79 | AE2-217 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.04 | 110.02 | AE2-217 | AP_P1-2_WP-500-005A_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.04 | 110.02 | AE2-217 | AP_P2-3_WP-500-DRT20_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.04 | 110.02 | AE2-217 | AP_P2-3_WP-500-465_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.04 | 110.02 | AE2-217 | AP_P1-2_WP-500-DRT21_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.04 | 110.02 | AE2-217 | AP_P2-2_WP-500-DRT16_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 105.24 | 102.55 | AE2-217 | DVP_P4-2: 560T571_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 105.08 | 102.41 | AE2-217 | DVP_P4-2: H2T560_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 105.08 | 102.4 | AE2-217 | DVP_P4-2: H1T560_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 104.94 | 102.25 | AE2-217 | PEPCO_P1_5070_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 607 | 168.88 | 166.18 | AE2-218 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 607 | 167.82 | 166.18 | AE2-218 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 607 | 167.49 | 166.17 | AE2-218 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 607 | 168.56 | 166.17 | AE2-218 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 607 | 168.81 | 166.1 | AE2-218 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 607 | 167.74 | 166.1 | AE2-218 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 607 | 167.74 | 166.1 | AE2-218 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 607 | 168.81 | 166.1 | AE2-218 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 628 | 159.81 | 158.44 | AE2-218 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 628 | 159.5 | 158.43 | AE2-218 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 628 | 159.74 | 158.37 | AE2-218 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 628 | 159.74 | 158.37 | AE2-218 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 628 | 157.11 | 156.15 | AE2-218 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 628 | 156.79 | 156.14 | AE2-218 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 628 | 157.03 | 156.08 | AE2-218 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 628 | 157.03 | 156.08 | AE2-218 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3369 | 128.01 | 122.94 | AC1-189 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 118.23 | 117.36 | AE2-218 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 116.86 | 116.03 | AE2-218 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 120.69 | 115.64 | AE2-218 | PECO_P4_PEACH035_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 115.22 | 114.44 | AE2-218 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.53 | 114.11 | AE2-218 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.53 | 114.11 | AE2-218 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.14 | 113.45 | AE2-218 | PECO_P4_PEACH675_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.14 | 113.45 | AE2-218 | PECO_P7-1_220-0607_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3198 | 118.07 | 112.69 | AE2-218 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3369 | 127.98 | 122.91 | AC1-191 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 112.74 | 111.54 | AE2-218 | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 112.69 | 111.49 | AE2-218 | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.76 | 111 | AE2-218 | PECO_P1-2_220-07_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.56 | 110.93 | AE2-218 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.45 | 110.81 | AE2-218 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.48 | 110.79 | AE2-218 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.52 | 110.79 | AE2-218 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.03 | 110.02 | AE2-218 | AP_P2-3_WP-500-465_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.03 | 110.02 | AE2-218 | AP_P1-2_WP-500-DRT21_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.03 | 110.02 | AE2-218 | AP_P1-2_WP-500-005A_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.03 | 110.02 | AE2-218 | AP_P2-2_WP-500-DRT16_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.03 | 110.02 | AE2-218 | AP_P2-3_WP-500-DRT20_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 105.23 | 102.53 | AE2-218 | DVP_P4-2: 560T571_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 105.06 | 102.39 | AE2-218 | DVP_P4-2: H2T560_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 105.06 | 102.38 | AE2-218 | DVP_P4-2: H1T560_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 104.92 | 102.23 | AE2-218 | PEPCO_P1_5070_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3369 | 128.18 | 123.11 | AC1-194 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 118.33 | 117.47 | AE2-221 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 116.96 | 116.14 | AE2-221 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 120.82 | 115.77 | AE2-221 | PECO_P4_PEACH035_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 115.33 | 114.55 | AE2-221 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.64 | 114.22 | AE2-221 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.64 | 114.22 | AE2-221 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.26 | 113.57 | AE2-221 | PECO_P7-1_220-0607_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.26 | 113.57 | AE2-221 | PECO_P4_PEACH675_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3198 | 118.22 | 112.83 | AE2-221 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3369 | 128.24 | 123.16 | AC1-208 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 112.84 | 111.64 | AE2-221 | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 112.79 | 111.6 | AE2-221 | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.88 | 111.12 | AE2-221 | PECO_P1-2_220-07_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.69 | 111.05 | AE2-221 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.58 | 110.94 | AE2-221 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.6 | 110.92 | AE2-221 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.64 | 110.91 | AE2-221 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.13 | 110.13 | AE2-221 | AP_P2-3_WP-500-DRT20_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.13 | 110.13 | AE2-221 | AP_P1-2_WP-500-DRT21_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.13 | 110.13 | AE2-221 | AP_P2-2_WP-500-DRT16_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.13 | 110.13 | AE2-221 | AP_P1-2_WP-500-005A_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.13 | 110.13 | AE2-221 | AP_P2-3_WP-500-465_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3369 | 128.2 | 123.12 | AC1-214 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 118.42 | 117.56 | AE2-230 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 117.05 | 116.24 | AE2-230 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 121.02 | 115.96 | AE2-230 | PECO_P4_PEACH035_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 115.41 | 114.64 | AE2-230 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.77 | 114.34 | AE2-230 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.77 | 114.34 | AE2-230 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.43 | 113.73 | AE2-230 | PECO_P4_PEACH675_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.43 | 113.73 | AE2-230 | PECO_P7-1_220-0607_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3198 | 118.42 | 113.02 | AE2-230 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3369 | 128.19 | 123.11 | AC1-216 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 112.92 | 111.73 | AE2-230 | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 112.87 | 111.69 | AE2-230 | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 116.05 | 111.29 | AE2-230 | PECO_P1-2_220-07_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.88 | 111.23 | AE2-230 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.76 | 111.12 | AE2-230 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.79 | 111.1 | AE2-230 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.81 | 111.07 | AE2-230 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.22 | 110.22 | AE2-230 | AP_P2-3_WP-500-465_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.22 | 110.22 | AE2-230 | AP_P1-2_WP-500-005A_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.22 | 110.22 | AE2-230 | AP_P1-2_WP-500-DRT21_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.22 | 110.22 | AE2-230 | AP_P2-3_WP-500-DRT20_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.22 | 110.22 | AE2-230 | AP_P2-2_WP-500-DRT16_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3369 | 128.09 | 123.02 | AC1-221 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 118.5 | 117.65 | AE2-253 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 117.13 | 116.32 | AE2-253 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 121.09 | 116.03 | AE2-253 | PECO_P4_PEACH035_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 115.49 | 114.73 | AE2-253 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.84 | 114.42 | AE2-253 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.84 | 114.42 | AE2-253 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.5 | 113.8 | AE2-253 | PECO_P4_PEACH675_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.5 | 113.8 | AE2-253 | PECO_P7-1_220-0607_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3198 | 118.51 | 113.11 | AE2-253 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3369 | 128.09 | 123.02 | AC1-222 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 113 | 111.81 | AE2-253 | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 112.95 | 111.77 | AE2-253 | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 116.12 | 111.36 | AE2-253 | PECO_P1-2_220-07_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.96 | 111.31 | AE2-253 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.84 | 111.19 | AE2-253 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.87 | 111.17 | AE2-253 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.88 | 111.14 | AE2-253 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.31 | 110.31 | AE2-253 | AP_P1-2_WP-500-005A_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.31 | 110.31 | AE2-253 | AP_P2-3_WP-500-465_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.31 | 110.31 | AE2-253 | AP_P1-2_WP-500-DRT21_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.31 | 110.31 | AE2-253 | AP_P2-2_WP-500-DRT16_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.31 | 110.31 | AE2-253 | AP_P2-3_WP-500-DRT20_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 121.13 | 116.06 | AE2-290 | PECO_P4_PEACH035_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 116.02 | 111.37 | AE2-290 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.9 | 111.25 | AE2-290 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.93 | 111.23 | AE2-290 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.7 | 111.07 | AE2-290 | PECO_P4_NOTTI85_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.64 | 111.07 | AE2-290 | PECO_P1-2_220-08_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.59 | 111.02 | AE2-290 | PECO_P4_COOPR125_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.35 | 110.87 | AE2-290 | PECO_P1-2_220-93_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 110.32 | 105.99 | AE2-290 | PN_P2-3_PN-500-DRT32_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 110.32 | 105.99 | AE2-290 | PN_P2-3_PN-500-004-DRT-002_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3369 | 128.08 | 123.01 | AC2-012 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 118.51 | 117.66 | AE2-297 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 117.13 | 116.33 | AE2-297 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 121.04 | 115.97 | AE2-297 | PECO_P4_PEACH035_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 115.5 | 114.73 | AE2-297 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.83 | 114.4 | AE2-297 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.83 | 114.4 | AE2-297 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.46 | 113.76 | AE2-297 | PECO_P4_PEACH675_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.46 | 113.76 | AE2-297 | PECO_P7-1_220-0607_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3198 | 118.46 | 113.07 | AE2-297 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3369 | 128.58 | 123.5 | AC2-023 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 113.01 | 111.82 | AE2-297 | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 112.96 | 111.78 | AE2-297 | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 116.08 | 111.32 | AE2-297 | PECO_P1-2_220-07_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.91 | 111.27 | AE2-297 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.8 | 111.15 | AE2-297 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.82 | 111.13 | AE2-297 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.84 | 111.1 | AE2-297 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.31 | 110.31 | AE2-297 | AP_P1-2_WP-500-005A_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.31 | 110.31 | AE2-297 | AP_P2-2_WP-500-DRT16_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.31 | 110.31 | AE2-297 | AP_P2-3_WP-500-DRT20_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.31 | 110.31 | AE2-297 | AP_P2-3_WP-500-465_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.31 | 110.31 | AE2-297 | AP_P1-2_WP-500-DRT21_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3369 | 128.15 | 123.08 | AC2-059 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 121.12 | 116.05 | AE2-318 | PECO_P4_PEACH035_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.54 | 113.84 | AE2-318 | PECO_P4_PEACH675_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.54 | 113.84 | AE2-318 | PECO_P7-1_220-0607_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3198 | 118.55 | 113.15 | AE2-318 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 116.16 | 111.4 | AE2-318 | PECO_P1-2_220-07_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 116 | 111.35 | AE2-318 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.88 | 111.23 | AE2-318 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.91 | 111.21 | AE2-318 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.92 | 111.18 | AE2-318 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.68 | 111.05 | AE2-318 | PECO_P4_NOTTI85_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 112.83 | 108.39 | AE2-318 | DVP_P1-3: 6SURRY-GSU-1_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3369 | 128.19 | 123.11 | AC2-060 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 121.12 | 116.05 | AE2-319 | PECO_P4_PEACH035_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.54 | 113.84 | AE2-319 | PECO_P4_PEACH675_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.54 | 113.84 | AE2-319 | PECO_P7-1_220-0607_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3198 | 118.56 | 113.16 | AE2-319 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 116.16 | 111.4 | AE2-319 | PECO_P1-2_220-07_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 116 | 111.35 | AE2-319 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.88 | 111.23 | AE2-319 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.91 | 111.21 | AE2-319 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.92 | 111.18 | AE2-319 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.68 | 111.06 | AE2-319 | PECO_P4_NOTTI85_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 112.83 | 108.39 | AE2-319 | DVP_P1-3: 6SURRY-GSU-1_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3369 | 128.19 | 123.11 | AC2-061 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 118.48 | 117.63 | AE2-333 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 117.1 | 116.3 | AE2-333 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 121.08 | 116.01 | AE2-333 | PECO_P4_PEACH035_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 115.47 | 114.7 | AE2-333 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.83 | 114.4 | AE2-333 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.83 | 114.4 | AE2-333 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.48 | 113.79 | AE2-333 | PECO_P7-1_220-0607_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.48 | 113.79 | AE2-333 | PECO_P4_PEACH675_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3198 | 118.49 | 113.09 | AE2-333 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3369 | 127.97 | 122.9 | AC2-079 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 112.98 | 111.79 | AE2-333 | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 112.93 | 111.74 | AE2-333 | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 116.11 | 111.34 | AE2-333 | PECO_P1-2_220-07_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.94 | 111.29 | AE2-333 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.82 | 111.18 | AE2-333 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.85 | 111.16 | AE2-333 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.87 | 111.13 | AE2-333 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.28 | 110.28 | AE2-333 | AP_P2-3_WP-500-DRT20_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.28 | 110.28 | AE2-333 | AP_P2-3_WP-500-465_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.28 | 110.28 | AE2-333 | AP_P1-2_WP-500-005A_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.28 | 110.28 | AE2-333 | AP_P1-2_WP-500-DRT21_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.28 | 110.28 | AE2-333 | AP_P2-2_WP-500-DRT16_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3369 | 128.24 | 123.16 | AC2-088 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 121.41 | 116.33 | AE2-334 | PECO_P4_PEACH035_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.81 | 114.11 | AE2-334 | PECO_P4_PEACH675_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.81 | 114.11 | AE2-334 | PECO_P7-1_220-0607_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3198 | 118.9 | 113.48 | AE2-334 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 116.43 | 111.66 | AE2-334 | PECO_P1-2_220-07_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 116.29 | 111.64 | AE2-334 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 116.18 | 111.52 | AE2-334 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 116.2 | 111.5 | AE2-334 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 116.19 | 111.44 | AE2-334 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.98 | 111.34 | AE2-334 | PECO_P4_NOTTI85_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.91 | 111.34 | AE2-334 | PECO_P1-2_220-08_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3369 | 127.76 | 122.7 | AC2-103 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 118.52 | 117.67 | AF1-038 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 117.15 | 116.35 | AF1-038 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 121.07 | 116.01 | AF1-038 | PECO_P4_PEACH035_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 115.52 | 114.75 | AF1-038 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.85 | 114.42 | AF1-038 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.85 | 114.42 | AF1-038 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.49 | 113.79 | AF1-038 | PECO_P4_PEACH675_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.49 | 113.79 | AF1-038 | PECO_P7-1_220-0607_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3198 | 118.5 | 113.1 | AF1-038 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3369 | 128.09 | 123.02 | AC2-112 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 113.02 | 111.84 | AF1-038 | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 112.97 | 111.79 | AF1-038 | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 116.11 | 111.35 | AF1-038 | PECO_P1-2_220-07_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.94 | 111.3 | AF1-038 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.83 | 111.18 | AF1-038 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.86 | 111.16 | AF1-038 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.87 | 111.13 | AF1-038 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.33 | 110.33 | AF1-038 | AP_P2-3_WP-500-465_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.33 | 110.33 | AF1-038 | AP_P2-3_WP-500-DRT20_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.33 | 110.33 | AF1-038 | AP_P1-2_WP-500-DRT21_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.33 | 110.33 | AF1-038 | AP_P1-2_WP-500-005A_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.33 | 110.33 | AF1-038 | AP_P2-2_WP-500-DRT16_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3369 | 127.89 | 122.82 | AC2-165 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 118.52 | 117.67 | AF1-050 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 117.15 | 116.35 | AF1-050 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 121.07 | 116.01 | AF1-050 | PECO_P4_PEACH035_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 115.52 | 114.75 | AF1-050 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.85 | 114.42 | AF1-050 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.85 | 114.42 | AF1-050 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.49 | 113.79 | AF1-050 | PECO_P4_PEACH675_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.49 | 113.79 | AF1-050 | PECO_P7-1_220-0607_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3198 | 118.5 | 113.1 | AF1-050 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3369 | 128.08 | 123.01 | AC2-176 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 113.02 | 111.84 | AF1-050 | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 112.97 | 111.79 | AF1-050 | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 116.11 | 111.35 | AF1-050 | PECO_P1-2_220-07_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.94 | 111.3 | AF1-050 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.83 | 111.18 | AF1-050 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.86 | 111.16 | AF1-050 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.87 | 111.13 | AF1-050 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.33 | 110.33 | AF1-050 | AP_P2-3_WP-500-465_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.33 | 110.33 | AF1-050 | AP_P2-3_WP-500-DRT20_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.33 | 110.33 | AF1-050 | AP_P1-2_WP-500-DRT21_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.33 | 110.33 | AF1-050 | AP_P1-2_WP-500-005A_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.33 | 110.33 | AF1-050 | AP_P2-2_WP-500-DRT16_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3369 | 128.58 | 123.49 | AC2-185 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 121.09 | 116.03 | AF1-083 | PECO_P4_PEACH035_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.87 | 114.44 | AF1-083 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.87 | 114.44 | AF1-083 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.51 | 113.81 | AF1-083 | PECO_P4_PEACH675_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.51 | 113.81 | AF1-083 | PECO_P7-1_220-0607_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3198 | 118.52 | 113.12 | AF1-083 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 116.13 | 111.37 | AF1-083 | PECO_P1-2_220-07_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.97 | 111.32 | AF1-083 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.85 | 111.2 | AF1-083 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.88 | 111.18 | AF1-083 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.89 | 111.15 | AF1-083 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 136.11 | 133.04 | AF1-147 | DVP_P1-2: LN 514_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 136.11 | 133.04 | AF1-147 | AP_P1-2_PE-500-407T_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 136.11 | 133.02 | AF1-147 | DVP_P4-2: 51482_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 131.01 | 127.93 | AF1-147 | AP_P2-3_PE-500-019C_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3369 | 128.24 | 123.16 | AC2-195 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 118.45 | 117.59 | AF1-147 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 117.07 | 116.26 | AF1-147 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 121.06 | 116 | AF1-147 | PECO_P4_PEACH035_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 115.44 | 114.67 | AF1-147 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.8 | 114.37 | AF1-147 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.8 | 114.37 | AF1-147 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.47 | 113.77 | AF1-147 | PECO_P4_PEACH675_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.47 | 113.77 | AF1-147 | PECO_P7-1_220-0607_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3198 | 118.46 | 113.07 | AF1-147 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3369 | 128.23 | 123.15 | AD1-022 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 112.95 | 111.76 | AF1-147 | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 112.9 | 111.71 | AF1-147 | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 116.09 | 111.33 | AF1-147 | PECO_P1-2_220-07_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.92 | 111.27 | AF1-147 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.8 | 111.16 | AF1-147 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.83 | 111.14 | AF1-147 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.85 | 111.11 | AF1-147 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.26 | 110.26 | AF1-147 | AP_P2-3_WP-500-DRT20_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.26 | 110.26 | AF1-147 | AP_P1-2_WP-500-DRT21_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.26 | 110.26 | AF1-147 | AP_P2-3_WP-500-465_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.26 | 110.26 | AF1-147 | AP_P1-2_WP-500-005A_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.26 | 110.26 | AF1-147 | AP_P2-2_WP-500-DRT16_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 105.14 | 102.45 | AF1-147 | DVP_P4-2: 560T571_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 104.98 | 102.31 | AF1-147 | DVP_P4-2: H2T560_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 104.98 | 102.29 | AF1-147 | DVP_P4-2: H1T560_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 104.84 | 102.15 | AF1-147 | PEPCO_P1_5070_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 607 | 167.87 | 166.24 | AF1-227 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 607 | 168.94 | 166.24 | AF1-227 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 607 | 168.61 | 166.23 | AF1-227 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 607 | 167.55 | 166.23 | AF1-227 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 607 | 168.86 | 166.16 | AF1-227 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 607 | 168.86 | 166.16 | AF1-227 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 607 | 167.79 | 166.16 | AF1-227 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 607 | 167.79 | 166.16 | AF1-227 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 628 | 159.87 | 158.5 | AF1-227 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 628 | 159.55 | 158.49 | AF1-227 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 628 | 159.79 | 158.43 | AF1-227 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 628 | 159.79 | 158.43 | AF1-227 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 628 | 157.16 | 156.21 | AF1-227 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 628 | 156.84 | 156.2 | AF1-227 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 628 | 157.08 | 156.14 | AF1-227 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 628 | 157.08 | 156.14 | AF1-227 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3369 | 128.07 | 123 | AD1-025 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 118.27 | 117.4 | AF1-227 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 116.9 | 116.08 | AF1-227 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 120.73 | 115.67 | AF1-227 | PECO_P4_PEACH035_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 115.26 | 114.48 | AF1-227 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.57 | 114.15 | AF1-227 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.57 | 114.15 | AF1-227 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.17 | 113.48 | AF1-227 | PECO_P7-1_220-0607_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.17 | 113.48 | AF1-227 | PECO_P4_PEACH675_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3198 | 118.12 | 112.73 | AF1-227 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3369 | 128.07 | 123 | AD1-070 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 112.78 | 111.58 | AF1-227 | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 112.73 | 111.53 | AF1-227 | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.79 | 111.04 | AF1-227 | PECO_P1-2_220-07_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.6 | 110.96 | AF1-227 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.48 | 110.85 | AF1-227 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.51 | 110.83 | AF1-227 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.55 | 110.82 | AF1-227 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.07 | 110.06 | AF1-227 | AP_P1-2_WP-500-005A_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.07 | 110.06 | AF1-227 | AP_P1-2_WP-500-DRT21_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.07 | 110.06 | AF1-227 | AP_P2-3_WP-500-465_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.07 | 110.06 | AF1-227 | AP_P2-3_WP-500-DRT20_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.07 | 110.06 | AF1-227 | AP_P2-2_WP-500-DRT16_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 105.28 | 102.59 | AF1-227 | DVP_P4-2: 560T571_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 105.12 | 102.45 | AF1-227 | DVP_P4-2: H2T560_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 105.12 | 102.43 | AF1-227 | DVP_P4-2: H1T560_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 104.97 | 102.28 | AF1-227 | PEPCO_P1_5070_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3369 | 127.89 | 122.82 | AD1-083 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 121.12 | 116.06 | AF2-317 | PECO_P4_PEACH035_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.54 | 113.84 | AF2-317 | PECO_P4_PEACH675_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.54 | 113.84 | AF2-317 | PECO_P7-1_220-0607_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3198 | 118.56 | 113.16 | AF2-317 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 116.16 | 111.4 | AF2-317 | PECO_P1-2_220-07_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 116 | 111.35 | AF2-317 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.88 | 111.24 | AF2-317 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.91 | 111.22 | AF2-317 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.92 | 111.18 | AF2-317 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.69 | 111.06 | AF2-317 | PECO_P4_NOTTI85_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 112.84 | 108.39 | AF2-317 | DVP_P1-3: 6SURRY-GSU-1_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 607 | 181.09 | 180.46 | AG2-055 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 607 | 182.36 | 180.46 | AG2-055 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 607 | 181.01 | 180.38 | AG2-055 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 607 | 181.01 | 180.38 | AG2-055 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 607 | 182.28 | 180.38 | AG2-055 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 607 | 182.28 | 180.38 | AG2-055 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 607 | 180.54 | 180.25 | AG2-055 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 607 | 181.81 | 180.25 | AG2-055 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 628 | 172.64 | 172.26 | AG2-055 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 628 | 172.56 | 172.19 | AG2-055 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 628 | 172.56 | 172.19 | AG2-055 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 628 | 172.11 | 172.06 | AG2-055 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 628 | 169.91 | 169.99 | AG2-055 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 628 | 169.83 | 169.92 | AG2-055 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 628 | 169.83 | 169.92 | AG2-055 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 628 | 169.38 | 169.8 | AG2-055 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 607 | 167.15 | 165.94 | AG2-055 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 607 | 168.42 | 165.94 | AG2-055 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 235463 | 01TANEY | 1 | 138 | 227/201 | 268 | 169.87 | 165.58 | AG2-055 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 235463 | 01TANEY | 1 | 138 | 227/201 | 268 | 169.87 | 165.58 | AG2-055 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 235463 | 01TANEY | 1 | 138 | 227/201 | 268 | 169.81 | 165.47 | AG2-055 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 628 | 159.17 | 158.21 | AG2-055 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 628 | 156.44 | 155.92 | AG2-055 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 282 | 147.38 | 147.58 | AG2-055 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 282 | 147.38 | 147.58 | AG2-055 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 282 | 147.33 | 147.5 | AG2-055 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 797 | 149.37 | 144.55 | AG2-055 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 797 | 149.37 | 144.55 | AG2-055 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 797 | 149.35 | 144.53 | AG2-055 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 797 | 148.88 | 144.42 | AG2-055 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 680 | 146.12 | 143.19 | AG2-055 | PEPCO_P4_PP19_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204538 | 27STRABAN | 204544 | 27LINCOLN | 1 | 115 | 227 | 313 | 140.66 | 142.19 | AG2-055 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204538 | 27STRABAN | 204544 | 27LINCOLN | 1 | 115 | 227 | 313 | 140.66 | 142.19 | AG2-055 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204538 | 27STRABAN | 204544 | 27LINCOLN | 1 | 115 | 227 | 313 | 140.61 | 142.11 | AG2-055 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204529 | 27GERMANTN | 204538 | 27STRABAN | 1 | 115 | 227 | 313 | 137.17 | 139.45 | AG2-055 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204529 | 27GERMANTN | 204538 | 27STRABAN | 1 | 115 | 227 | 313 | 137.17 | 139.45 | AG2-055 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204529 | 27GERMANTN | 204538 | 27STRABAN | 1 | 115 | 227 | 313 | 137.12 | 139.37 | AG2-055 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 142.26 | 139.15 | AG2-055 | AP_P1-2_PE-500-407T_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 142.26 | 139.15 | AG2-055 | DVP_P1-2: LN 514_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 142.26 | 139.13 | AG2-055 | DVP_P4-2: 51482_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3369 | 128.16 | 123.09 | AD1-088 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 203981 | AD2-062_POI | 235188 | 01GREENE | 1 | 138 | 226/201 | 268 | 142.39 | 137.48 | AG2-055 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 203981 | AD2-062_POI | 235188 | 01GREENE | 1 | 138 | 226/201 | 268 | 142.39 | 137.48 | AG2-055 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 203981 | AD2-062_POI | 235188 | 01GREENE | 1 | 138 | 226/201 | 268 | 142.3 | 137.39 | AG2-055 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 797 | 141.09 | 136.1 | AG2-055 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 235463 | 01TANEY | 1 | 138 | 227/201 | 268 | 143.53 | 135.59 | AG2-055 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 235463 | 01TANEY | 1 | 138 | 227/201 | 268 | 143.42 | 135.57 | AG2-055 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 235463 | 01TANEY | 1 | 138 | 227/201 | 268 | 143.42 | 135.57 | AG2-055 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 235463 | 01TANEY | 1 | 138 | 227/201 | 268 | 143.4 | 135.56 | AG2-055 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 680 | 138.26 | 135.46 | AG2-055 | PEPCO_P1_PP2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 2 | 230 | 233 | 680 | 138.26 | 135.46 | AG2-055 | PEPCO_P1_PP1_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 814 | 140.57 | 135.4 | AG2-055 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 814 | 140.57 | 135.4 | AG2-055 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 814 | 140.55 | 135.39 | AG2-055 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 204529 | 27GERMANTN | 1 | 138/115 | 227 | 345 | 131.96 | 135.35 | AG2-055 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 204529 | 27GERMANTN | 1 | 138/115 | 227 | 345 | 131.96 | 135.35 | AG2-055 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 204529 | 27GERMANTN | 1 | 138/115 | 227 | 345 | 131.91 | 135.28 | AG2-055 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 814 | 139.64 | 135.16 | AG2-055 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 137.12 | 134 | AG2-055 | AP_P2-3_PE-500-019C_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 235463 | 01TANEY | 1 | 138 | 227/201 | 268 | 134.75 | 132.41 | AG2-055 | PEPCO_P4_PP41_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3369 | 128.23 | 123.15 | AD1-105 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 204550 | 27ORRTANNA | 1 | 115 | 227 | 160 | 131.54 | 130.14 | AG2-055 | ME_P1-2_ME-115-068_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 235463 | 01TANEY | 1 | 138 | 227/201 | 268 | 131.88 | 130.1 | AG2-055 | AP_P2-3_PE-500-019B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 2 | 230 | 233 | 680 | 132.29 | 129.37 | AG2-055 | AP_P1-2_PE-500-407T_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 2 | 230 | 233 | 680 | 132.29 | 129.37 | AG2-055 | DVP_P1-2: LN 514_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 680 | 132.29 | 129.37 | AG2-055 | DVP_P1-2: LN 514_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 680 | 132.29 | 129.37 | AG2-055 | AP_P1-2_PE-500-407T_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 2 | 230 | 233 | 680 | 132.29 | 129.36 | AG2-055 | DVP_P4-2: 51482_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 680 | 132.29 | 129.36 | AG2-055 | DVP_P4-2: 51482_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 203981 | AD2-062_POI | 235188 | 01GREENE | 1 | 138 | 226/201 | 268 | 136.74 | 128.69 | AG2-055 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 203981 | AD2-062_POI | 235188 | 01GREENE | 1 | 138 | 226/201 | 268 | 136.61 | 128.67 | AG2-055 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 203981 | AD2-062_POI | 235188 | 01GREENE | 1 | 138 | 226/201 | 268 | 136.61 | 128.67 | AG2-055 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 203981 | AD2-062_POI | 235188 | 01GREENE | 1 | 138 | 226/201 | 268 | 136.61 | 128.66 | AG2-055 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 204550 | 27ORRTANNA | 1 | 115 | 227 | 160 | 129.99 | 128.56 | AG2-055 | ME_P2-3_ME-115-013B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 204550 | 27ORRTANNA | 1 | 115 | 227 | 160 | 129.85 | 128.42 | AG2-055 | ME_P2-3_ME-115-013A_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 235463 | 01TANEY | 1 | 138 | 227/201 | 268 | 130.42 | 128.36 | AG2-055 | PEPCO_P1_5055_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 221095 | ROCKRGE2 | 221098 | C.PIPE12 | 1 | 115 | 232 | 217 | 128.44 | 128.2 | AG2-055 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204539 | 27HUNTRSTN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 282 | 128.32 | 128.11 | AG2-055 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204539 | 27HUNTRSTN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 282 | 128.32 | 128.11 | AG2-055 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204539 | 27HUNTRSTN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 282 | 128.26 | 128.04 | AG2-055 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 204550 | 27ORRTANNA | 1 | 115 | 227 | 160 | 127.59 | 127.17 | AG2-055 | ME_P2-3_ME-115-035A_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 814 | 131.35 | 126.19 | AG2-055 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 204550 | 27ORRTANNA | 1 | 115 | 227 | 160 | 126.04 | 125.6 | AG2-055 | ME_P2-3_ME-115-035B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 221090 | GLENARM2 | 221098 | C.PIPE12 | 1 | 115 | 232 | 217 | 124.43 | 125.13 | AG2-055 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3369 | 128.12 | 123.05 | AD1-115 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3369 | 128.17 | 123.1 | AD1-125 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 124.97 | 124.65 | AG2-055 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 221096 | ROCKRGE1 | 221097 | C.PIPE11 | 1 | 115 | 232 | 217 | 123.55 | 123.3 | AG2-055 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 221097 | C.PIPE11 | 221100 | GLENARM1 | 1 | 115 | 232 | 217 | 123.4 | 123.28 | AG2-055 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 123.54 | 123.27 | AG2-055 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 128.34 | 123.09 | AG2-055 | PECO_P4_PEACH035_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3369 | 128.14 | 123.07 | AD1-128 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 203981 | AD2-062_POI | 235188 | 01GREENE | 1 | 138 | 226/201 | 268 | 128.97 | 122.72 | AG2-055 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3198 | 128.23 | 122.37 | AG2-055 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 221095 | ROCKRGE2 | 221098 | C.PIPE12 | 1 | 115 | 232 | 217 | 121.85 | 122.33 | AG2-055 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 221089 | WINDYED1 | 221090 | GLENARM2 | 1 | 115 | 232 | 216 | 121.59 | 122.32 | AG2-055 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 121.9 | 121.66 | AG2-055 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 814 | 124.5 | 121.35 | AG2-055 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 814 | 124.5 | 121.35 | AG2-055 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 814 | 124.47 | 121.34 | AG2-055 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 814 | 124.02 | 121.23 | AG2-055 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 125.71 | 121.09 | AG2-055 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 125.71 | 121.09 | AG2-055 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 125.96 | 121.07 | AG2-055 | PECO_P4_PEACH675_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 125.96 | 121.07 | AG2-055 | PECO_P7-1_220-0607_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3369 | 127.77 | 122.71 | AD1-140 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 282 | 125.16 | 120.83 | AG2-055 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 282 | 125.06 | 120.81 | AG2-055 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 282 | 125.06 | 120.81 | AG2-055 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 282 | 125.05 | 120.8 | AG2-055 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200532 | 26ROXBURY | 203981 | AD2-062_POI | 1 | 138 | 226 | 268 | 125.71 | 120.54 | AG2-055 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200532 | 26ROXBURY | 203981 | AD2-062_POI | 1 | 138 | 226 | 268 | 125.71 | 120.54 | AG2-055 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200532 | 26ROXBURY | 203981 | AD2-062_POI | 1 | 138 | 226 | 268 | 125.62 | 120.44 | AG2-055 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 680 | 123.14 | 120.22 | AG2-055 | AP_P2-3_PE-500-019C_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 2 | 230 | 233 | 680 | 123.14 | 120.22 | AG2-055 | AP_P2-3_PE-500-019C_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3369 | 129.02 | 123.92 | AD1-143 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 221090 | GLENARM2 | 221098 | C.PIPE12 | 1 | 115 | 232 | 217 | 117.84 | 119.27 | AG2-055 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 124.09 | 119.21 | AG2-055 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 123.98 | 119.1 | AG2-055 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 124 | 119.08 | AG2-055 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 123.77 | 118.92 | AG2-055 | PECO_P4_NOTTI85_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 123.7 | 118.91 | AG2-055 | PECO_P1-2_220-08_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 119.16 | 118.43 | AG2-055 | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 119.11 | 118.38 | AG2-055 | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 221092 | FIVE.FOR | 221096 | ROCKRGE1 | 1 | 115 | 232 | 254 | 117.85 | 118.37 | AG2-055 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208393 | FARO DC TIE | 208395 | FARO FF | 1 | 115/69 | 229 | 114 | 121.36 | 117.86 | AG2-055 | PL_05_P71_000906_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 221096 | ROCKRGE1 | 221097 | C.PIPE11 | 1 | 115 | 232 | 217 | 116.99 | 117.49 | AG2-055 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 221097 | C.PIPE11 | 221100 | GLENARM1 | 1 | 115 | 232 | 217 | 116.84 | 117.47 | AG2-055 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 117.81 | 117.08 | AG2-055 | BG_P7_GRNITE_HIRDG_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 117.48 | 116.95 | AG2-055 | AP_P1-2_WP-500-DRT21_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 117.48 | 116.95 | AG2-055 | AP_P2-2_WP-500-DRT16_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 117.48 | 116.95 | AG2-055 | AP_P1-2_WP-500-005A_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 117.48 | 116.95 | AG2-055 | AP_P2-3_WP-500-465_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 221089 | WINDYED1 | 221090 | GLENARM2 | 1 | 115 | 232 | 216 | 114.97 | 116.43 | AG2-055 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 797 | 117.85 | 116.38 | AG2-055 | PJM_500_BG_P4_5_CNSTN_15_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 282 | 117.74 | 116.36 | AG2-055 | PEPCO_P4_PP41_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208395 | FARO FF | 208396 | FARO | 1 | 69 | 229 | 240 | 115.31 | 116.35 | AG2-055 | PL_05_P71_000906_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 221055 | HARRIS1A | 221058 | DOLFD T1 | 1 | 115 | 232 | 189 | 115.52 | 115.3 | AG2-055 | BG_P7_NWEST_GRNITE_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 203981 | AD2-062_POI | 235188 | 01GREENE | 1 | 138 | 226/201 | 268 | 117.37 | 115.1 | AG2-055 | PEPCO_P4_PP41_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204538 | 27STRABAN | 204544 | 27LINCOLN | 1 | 115 | 227 | 313 | 118.11 | 114.97 | AG2-055 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204538 | 27STRABAN | 204544 | 27LINCOLN | 1 | 115 | 227 | 313 | 118.01 | 114.95 | AG2-055 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204538 | 27STRABAN | 204544 | 27LINCOLN | 1 | 115 | 227 | 313 | 118.01 | 114.95 | AG2-055 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204538 | 27STRABAN | 204544 | 27LINCOLN | 1 | 115 | 227 | 313 | 118 | 114.94 | AG2-055 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 221092 | FIVE.FOR | 221095 | ROCKRGE2 | 1 | 115 | 232 | 254 | 114.82 | 114.84 | AG2-055 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 282 | 115.32 | 114.22 | AG2-055 | AP_P2-3_PE-500-019B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3369 | 128.23 | 123.16 | AD1-152 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 221092 | FIVE.FOR | 221096 | ROCKRGE1 | 1 | 115 | 232 | 254 | 112.24 | 113.31 | AG2-055 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 282 | 117.38 | 113.25 | AG2-055 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 203981 | AD2-062_POI | 235188 | 01GREENE | 1 | 138 | 226/201 | 268 | 114.82 | 112.83 | AG2-055 | AP_P2-3_PE-500-015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 814 | 116.18 | 112.77 | AG2-055 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204502 | 27JACKSON | 204514 | 27TMI | 1 | 230 | 227 | 659 | 112.19 | 112.75 | AG2-055 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204502 | 27JACKSON | 204514 | 27TMI | 1 | 230 | 227 | 659 | 112.08 | 112.72 | AG2-055 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204502 | 27JACKSON | 204514 | 27TMI | 1 | 230 | 227 | 659 | 112.08 | 112.72 | AG2-055 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204502 | 27JACKSON | 204514 | 27TMI | 1 | 230 | 227 | 659 | 112.06 | 112.7 | AG2-055 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 797 | 113.76 | 112.47 | AG2-055 | BG_P7_GRCTN_CNSTN_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204529 | 27GERMANTN | 204538 | 27STRABAN | 1 | 115 | 227 | 313 | 114.62 | 112.27 | AG2-055 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204529 | 27GERMANTN | 204538 | 27STRABAN | 1 | 115 | 227 | 313 | 114.52 | 112.24 | AG2-055 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204529 | 27GERMANTN | 204538 | 27STRABAN | 1 | 115 | 227 | 313 | 114.52 | 112.24 | AG2-055 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204529 | 27GERMANTN | 204538 | 27STRABAN | 1 | 115 | 227 | 313 | 114.51 | 112.23 | AG2-055 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208393 | FARO DC TIE | 208395 | FARO FF | 2 | 115/69 | 229 | 120 | 115.29 | 111.97 | AG2-055 | PL_05_P71_000906_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200532 | 26ROXBURY | 203981 | AD2-062_POI | 1 | 138 | 226 | 268 | 120.06 | 111.75 | AG2-055 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200532 | 26ROXBURY | 203981 | AD2-062_POI | 1 | 138 | 226 | 268 | 119.93 | 111.72 | AG2-055 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200532 | 26ROXBURY | 203981 | AD2-062_POI | 1 | 138 | 226 | 268 | 119.93 | 111.72 | AG2-055 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200532 | 26ROXBURY | 203981 | AD2-062_POI | 1 | 138 | 226 | 268 | 119.92 | 111.72 | AG2-055 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 221056 | HARRIS0A | 221057 | DOLFD T0 | 1 | 115 | 232 | 189 | 111.12 | 111.24 | AG2-055 | BG_P7_NWEST_GRNITE_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208394 | PPL-BGE TIE | 221092 | FIVE.FOR | 1 | 115 | 229/232 | 247 | 110.2 | 111.07 | AG2-055 | PL_05_P71_000906_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 204529 | 27GERMANTN | 1 | 138/115 | 227 | 345 | 111.5 | 110.48 | AG2-055 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204538 | 27STRABAN | 204544 | 27LINCOLN | 1 | 115 | 227 | 313 | 110.58 | 110.48 | AG2-055 | PEPCO_P4_PP41_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 204529 | 27GERMANTN | 1 | 138/115 | 227 | 345 | 111.41 | 110.46 | AG2-055 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 204529 | 27GERMANTN | 1 | 138/115 | 227 | 345 | 111.41 | 110.46 | AG2-055 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 204529 | 27GERMANTN | 1 | 138/115 | 227 | 345 | 111.4 | 110.45 | AG2-055 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3369 | 128.22 | 123.15 | AD1-155 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200017 | SMITHBRG | 967451 | AG2-055 C O1 | 1 | 500 | 225 | 999 | 114.91 | 110.14 | AG2-055 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200017 | SMITHBRG | 967451 | AG2-055 C O1 | 1 | 500 | 225 | 999 | 114.91 | 110.13 | AG2-055 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200017 | SMITHBRG | 967451 | AG2-055 C O1 | 1 | 500 | 225 | 999 | 114.91 | 110.13 | AG2-055 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200017 | SMITHBRG | 967451 | AG2-055 C O1 | 1 | 500 | 225 | 999 | 114.91 | 110.13 | AG2-055 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200017 | SMITHBRG | 967451 | AG2-055 C O1 | 1 | 500 | 225 | 999 | 114.91 | 110.09 | AG2-055 | PECO_P4_PEACH215_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200017 | SMITHBRG | 967451 | AG2-055 C O1 | 1 | 500 | 225 | 999 | 114.91 | 110.04 | AG2-055 | PECO_P4_PEACH205_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200017 | SMITHBRG | 967451 | AG2-055 C O1 | 1 | 500 | 225 | 999 | 114.91 | 110.04 | AG2-055 | PECO_P1-2_5014_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200017 | SMITHBRG | 967451 | AG2-055 C O1 | 1 | 500 | 225 | 999 | 114.91 | 109.87 | AG2-055 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200017 | SMITHBRG | 967451 | AG2-055 C O1 | 1 | 500 | 225 | 999 | 114.91 | 109.84 | AG2-055 | ME_P7-1_ME-230-640T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200017 | SMITHBRG | 967451 | AG2-055 C O1 | 1 | 500 | 225 | 999 | 114.91 | 109.83 | AG2-055 | PL_02_P71_001017_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 221092 | FIVE.FOR | 221095 | ROCKRGE2 | 1 | 115 | 232 | 254 | 109.19 | 109.8 | AG2-055 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3369 | 127.94 | 122.87 | AD2-016 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 114.41 | 109.13 | AG2-055 | PECO_P4_PEACH025_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3369 | 128.04 | 122.97 | AD2-072 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208393 | FARO DC TIE | 208395 | FARO FF | 1 | 115/69 | 229 | 114 | 113.26 | 108.95 | AG2-055 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208393 | FARO DC TIE | 208395 | FARO FF | 1 | 115/69 | 229 | 114 | 113.26 | 108.95 | AG2-055 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208393 | FARO DC TIE | 208395 | FARO FF | 1 | 115/69 | 229 | 114 | 113.26 | 108.95 | AG2-055 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208393 | FARO DC TIE | 208395 | FARO FF | 1 | 115/69 | 229 | 114 | 113.23 | 108.95 | AG2-055 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204538 | 27STRABAN | 204544 | 27LINCOLN | 1 | 115 | 227 | 313 | 108.13 | 108.3 | AG2-055 | AP_P2-3_PE-500-019B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 204550 | 27ORRTANNA | 1 | 115 | 227 | 160 | 110.01 | 108.02 | AG2-055 | ME_P1-2_ME-115-067_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 801 | 109.86 | 107.9 | AG2-055 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 801 | 109.86 | 107.9 | AG2-055 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 110.64 | 107.89 | AG2-055 | DVP_P4-2: 560T571_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 801 | 109.83 | 107.88 | AG2-055 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3198 | 113.12 | 107.86 | AG2-055 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208020 | MANO TR3 | 1 | 230 | 229 | 731 | 104.58 | 107.8 | AG2-055 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208020 | MANO TR3 | 1 | 230 | 229 | 731 | 104.58 | 107.8 | AG2-055 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208020 | MANO TR3 | 1 | 230 | 229 | 731 | 104.57 | 107.79 | AG2-055 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 110.5 | 107.77 | AG2-055 | DVP_P4-2: H2T560_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204529 | 27GERMANTN | 204538 | 27STRABAN | 1 | 115 | 227 | 313 | 107.1 | 107.76 | AG2-055 | PEPCO_P4_PP41_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 110.5 | 107.75 | AG2-055 | DVP_P4-2: H1T560_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 801 | 109.08 | 107.68 | AG2-055 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208020 | MANO TR3 | 1 | 230 | 229 | 731 | 104.18 | 107.68 | AG2-055 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 110.36 | 107.61 | AG2-055 | PEPCO_P1_5070_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208395 | FARO FF | 208396 | FARO | 1 | 69 | 229 | 240 | 107.62 | 107.39 | AG2-055 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208395 | FARO FF | 208396 | FARO | 1 | 69 | 229 | 240 | 107.62 | 107.39 | AG2-055 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208395 | FARO FF | 208396 | FARO | 1 | 69 | 229 | 240 | 107.61 | 107.39 | AG2-055 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208395 | FARO FF | 208396 | FARO | 1 | 69 | 229 | 240 | 107.59 | 107.39 | AG2-055 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208078 | SAKR | 1 | 230 | 229 | 801 | 106.22 | 107.3 | AG2-055 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208078 | SAKR | 1 | 230 | 229 | 801 | 106.22 | 107.3 | AG2-055 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208078 | SAKR | 1 | 230 | 229 | 801 | 106.21 | 107.29 | AG2-055 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204538 | 27STRABAN | 204544 | 27LINCOLN | 1 | 115 | 227 | 313 | 110.2 | 107.27 | AG2-055 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208078 | SAKR | 1 | 230 | 229 | 801 | 105.84 | 107.19 | AG2-055 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220953 | HOWARD12 | 220972 | GRANITE1 | 1 | 230 | 232 | 772 | 109.92 | 107.01 | AG2-055 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220972 | GRANITE1 | 1 | 230 | 232 | 811 | 109.82 | 106.86 | AG2-055 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220953 | HOWARD12 | 220972 | GRANITE1 | 1 | 230 | 232 | 772 | 109.61 | 106.63 | AG2-055 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220953 | HOWARD12 | 220972 | GRANITE1 | 1 | 230 | 232 | 772 | 109.61 | 106.63 | AG2-055 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220972 | GRANITE1 | 1 | 230 | 232 | 811 | 109.6 | 106.59 | AG2-055 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220972 | GRANITE1 | 1 | 230 | 232 | 811 | 109.6 | 106.59 | AG2-055 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 204529 | 27GERMANTN | 1 | 138/115 | 227 | 345 | 104.67 | 106.44 | AG2-055 | PEPCO_P4_PP41_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 110.87 | 105.83 | AG2-055 | PECO_P1-2_PBTIE1_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200532 | 26ROXBURY | 203981 | AD2-062_POI | 1 | 138 | 226 | 268 | 112.29 | 105.77 | AG2-055 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204529 | 27GERMANTN | 204538 | 27STRABAN | 1 | 115 | 227 | 313 | 104.64 | 105.59 | AG2-055 | AP_P2-3_PE-500-019B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 221088 | WINDYED2 | 221100 | GLENARM1 | 1 | 115 | 232 | 254 | 105 | 105.25 | AG2-055 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208393 | FARO DC TIE | 208395 | FARO FF | 1 | 115/69 | 229 | 114 | 108.91 | 105.18 | AG2-055 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220973 | GRANITE6 | 1 | 230 | 232 | 811 | 107.97 | 105.07 | AG2-055 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220973 | GRANITE6 | 1 | 230 | 232 | 811 | 107.76 | 104.82 | AG2-055 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220973 | GRANITE6 | 1 | 230 | 232 | 811 | 107.76 | 104.82 | AG2-055 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220954 | HOWARD32 | 220973 | GRANITE6 | 1 | 230 | 232 | 772 | 107.3 | 104.68 | AG2-055 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204529 | 27GERMANTN | 204538 | 27STRABAN | 1 | 115 | 227 | 313 | 106.71 | 104.56 | AG2-055 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 204529 | 27GERMANTN | 1 | 138/115 | 227 | 345 | 102.45 | 104.46 | AG2-055 | AP_P2-3_PE-500-019B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220954 | HOWARD32 | 220973 | GRANITE6 | 1 | 230 | 232 | 772 | 107.03 | 104.36 | AG2-055 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220954 | HOWARD32 | 220973 | GRANITE6 | 1 | 230 | 232 | 772 | 107.03 | 104.36 | AG2-055 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208393 | FARO DC TIE | 208395 | FARO FF | 1 | 115/69 | 229 | 114 | 105.46 | 103.72 | AG2-055 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204502 | 27JACKSON | 204514 | 27TMI | 1 | 230 | 227 | 659 | 103.59 | 103.67 | AG2-055 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208393 | FARO DC TIE | 208395 | FARO FF | 2 | 115/69 | 229 | 120 | 107.6 | 103.5 | AG2-055 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208393 | FARO DC TIE | 208395 | FARO FF | 2 | 115/69 | 229 | 120 | 107.6 | 103.5 | AG2-055 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208393 | FARO DC TIE | 208395 | FARO FF | 2 | 115/69 | 229 | 120 | 107.6 | 103.5 | AG2-055 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208393 | FARO DC TIE | 208395 | FARO FF | 2 | 115/69 | 229 | 120 | 107.57 | 103.5 | AG2-055 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 204529 | 27GERMANTN | 1 | 138/115 | 227 | 345 | 104.33 | 103.49 | AG2-055 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208395 | FARO FF | 208396 | FARO | 1 | 69 | 229 | 240 | 103.48 | 103.41 | AG2-055 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 204550 | 27ORRTANNA | 1 | 115 | 227 | 160 | 105.34 | 103.25 | AG2-055 | ME_P2-2_ME-115-0102-4_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 204550 | 27ORRTANNA | 1 | 115 | 227 | 160 | 105.34 | 103.25 | AG2-055 | ME_P2-3_ME-115-0102-A_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208394 | PPL-BGE TIE | 221092 | FIVE.FOR | 1 | 115 | 229/232 | 247 | 102.73 | 102.53 | AG2-055 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208394 | PPL-BGE TIE | 221092 | FIVE.FOR | 1 | 115 | 229/232 | 247 | 102.73 | 102.53 | AG2-055 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208394 | PPL-BGE TIE | 221092 | FIVE.FOR | 1 | 115 | 229/232 | 247 | 102.72 | 102.52 | AG2-055 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208394 | PPL-BGE TIE | 221092 | FIVE.FOR | 1 | 115 | 229/232 | 247 | 102.69 | 102.52 | AG2-055 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208393 | FARO DC TIE | 208394 | PPL-BGE TIE | 1 | 115 | 229 | 268 | 103.02 | 102.41 | AG2-055 | PL_05_P71_000906_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3369 | 128.21 | 123.14 | AD2-074 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208395 | FARO FF | 208396 | FARO | 1 | 69 | 229 | 240 | 100.2 | 102.13 | AG2-055 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208393 | FARO DC TIE | 208395 | FARO FF | 1 | 115/69 | 229 | 114 | 102.56 | 102.12 | AG2-055 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208393 | FARO DC TIE | 208395 | FARO FF | 1 | 115/69 | 229 | 114 | 102.5 | 102.06 | AG2-055 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208393 | FARO DC TIE | 208395 | FARO FF | 1 | 115/69 | 229 | 114 | 102.5 | 102.06 | AG2-055 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200065 | PCHBTM2S | 200066 | PCHBTM1N | 2 | 500 | 225 | 3022 | 105.64 | 101.96 | AG2-055 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204512 | 27S.RDG | 204693 | 27BOONETOWN | 1 | 230 | 227 | 531 | 100.81 | 101.92 | AG2-055 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204512 | 27S.RDG | 204693 | 27BOONETOWN | 1 | 230 | 227 | 531 | 100.77 | 101.88 | AG2-055 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204512 | 27S.RDG | 204693 | 27BOONETOWN | 1 | 230 | 227 | 531 | 100.77 | 101.88 | AG2-055 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200762 | 26GARRETT | 235470 | 01GARRET | 1 | 115 | 226/201 | 160 | 101.76 | 101.88 | AG2-055 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200762 | 26GARRETT | 235470 | 01GARRET | 1 | 115 | 226/201 | 160 | 101.76 | 101.88 | AG2-055 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204512 | 27S.RDG | 204693 | 27BOONETOWN | 1 | 230 | 227 | 531 | 100.67 | 101.85 | AG2-055 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200762 | 26GARRETT | 235470 | 01GARRET | 1 | 115 | 226/201 | 160 | 101.69 | 101.8 | AG2-055 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3369 | 128.61 | 123.52 | AD2-076 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204539 | 27HUNTRSTN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 282 | 106.09 | 101.33 | AG2-055 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204539 | 27HUNTRSTN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 282 | 105.99 | 101.31 | AG2-055 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204539 | 27HUNTRSTN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 282 | 105.99 | 101.31 | AG2-055 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204539 | 27HUNTRSTN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 282 | 105.98 | 101.3 | AG2-055 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 103.07 | 101.28 | AG2-055 | DVP_P4-2: GOOSE H1T558_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208031 | MLWD TR2 | 1 | 230 | 229 | 814 | 98.84 | 100.75 | AG2-055 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208031 | MLWD TR2 | 1 | 230 | 229 | 814 | 98.84 | 100.75 | AG2-055 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208031 | MLWD TR2 | 1 | 230 | 229 | 814 | 98.84 | 100.74 | AG2-055 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208031 | MLWD TR2 | 1 | 230 | 229 | 814 | 98.48 | 100.64 | AG2-055 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 102.53 | 100.43 | AG2-055 | AP_P2-3_PE-500-019B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 235105 | 01DOUBS | 1 | 500 | 225/201 | 2598 | 103.38 | 100.33 | AG2-055 | DVP_P4-2: 560T571_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 221088 | WINDYED2 | 221100 | GLENARM1 | 1 | 115 | 232 | 254 | 99.39 | 100.29 | AG2-055 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208395 | FARO FF | 208396 | FARO | 1 | 69 | 229 | 240 | 97.45 | 100.25 | AG2-055 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 235105 | 01DOUBS | 1 | 500 | 225/201 | 2598 | 103.25 | 100.21 | AG2-055 | PEPCO_P1_5070_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 235105 | 01DOUBS | 1 | 500 | 225/201 | 2598 | 103.24 | 100.2 | AG2-055 | DVP_P4-2: H2T560_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 235105 | 01DOUBS | 1 | 500 | 225/201 | 2598 | 103.24 | 100.2 | AG2-055 | DVP_P4-2: H1T560_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208395 | FARO FF | 208396 | FARO | 1 | 69 | 229 | 240 | 97.39 | 100.18 | AG2-055 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208395 | FARO FF | 208396 | FARO | 1 | 69 | 229 | 240 | 97.39 | 100.18 | AG2-055 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3198 | 104.77 | 100.01 | AG2-055 | PECO_P1-2_PBTIE2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3369 | 128.03 | 122.96 | AD2-093 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 118.91 | 118.09 | ALDENE_AB | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 117.54 | 116.76 | ALDENE_AB | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 121.49 | 116.41 | ALDENE_AB | PECO_P4_PEACH035_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 115.9 | 115.17 | ALDENE_AB | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 119.25 | 114.81 | ALDENE_AB | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 119.25 | 114.81 | ALDENE_AB | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.92 | 114.21 | ALDENE_AB | PECO_P4_PEACH675_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.92 | 114.21 | ALDENE_AB | PECO_P7-1_220-0607_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3198 | 119.04 | 113.62 | ALDENE_AB | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3369 | 128.01 | 122.94 | AD2-134 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 113.39 | 112.23 | ALDENE_AB | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 113.34 | 112.19 | ALDENE_AB | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 116.54 | 111.77 | ALDENE_AB | PECO_P1-2_220-07_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 116.41 | 111.75 | ALDENE_AB | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 116.29 | 111.64 | ALDENE_AB | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 116.32 | 111.61 | ALDENE_AB | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 116.3 | 111.55 | ALDENE_AB | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.71 | 110.74 | ALDENE_AB | AP_P2-3_WP-500-465_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.71 | 110.74 | ALDENE_AB | AP_P1-2_WP-500-005A_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.71 | 110.74 | ALDENE_AB | AP_P2-2_WP-500-DRT16_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.71 | 110.74 | ALDENE_AB | AP_P1-2_WP-500-DRT21_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.71 | 110.74 | ALDENE_AB | AP_P2-3_WP-500-DRT20_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 607 | 168.94 | 166.23 | BIGSKY | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 607 | 167.87 | 166.23 | BIGSKY | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 607 | 167.54 | 166.22 | BIGSKY | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 607 | 168.61 | 166.22 | BIGSKY | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 607 | 168.86 | 166.16 | BIGSKY | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 607 | 168.86 | 166.16 | BIGSKY | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 607 | 167.79 | 166.16 | BIGSKY | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 607 | 167.79 | 166.16 | BIGSKY | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 628 | 159.86 | 158.49 | BIGSKY | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 628 | 159.55 | 158.48 | BIGSKY | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 628 | 159.79 | 158.43 | BIGSKY | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 628 | 159.79 | 158.43 | BIGSKY | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 628 | 157.16 | 156.2 | BIGSKY | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 628 | 156.84 | 156.19 | BIGSKY | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 628 | 157.08 | 156.13 | BIGSKY | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 628 | 157.08 | 156.13 | BIGSKY | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 136.51 | 133.44 | BIGSKY | AP_P1-2_PE-500-407T_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 136.51 | 133.44 | BIGSKY | DVP_P1-2: LN 514_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 136.51 | 133.42 | BIGSKY | DVP_P4-2: 51482_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 131.39 | 128.3 | BIGSKY | AP_P2-3_PE-500-019C_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3369 | 127.98 | 122.91 | AD2-158 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 118.25 | 117.38 | BIGSKY | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 116.88 | 116.06 | BIGSKY | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 120.73 | 115.68 | BIGSKY | PECO_P4_PEACH035_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 115.24 | 114.46 | BIGSKY | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.56 | 114.14 | BIGSKY | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.56 | 114.14 | BIGSKY | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.17 | 113.48 | BIGSKY | PECO_P7-1_220-0607_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.17 | 113.48 | BIGSKY | PECO_P4_PEACH675_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3198 | 118.11 | 112.73 | BIGSKY | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3369 | 128.1 | 123.03 | AD2-163 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 112.76 | 111.56 | BIGSKY | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 112.71 | 111.51 | BIGSKY | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.79 | 111.04 | BIGSKY | PECO_P1-2_220-07_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.6 | 110.96 | BIGSKY | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.48 | 110.85 | BIGSKY | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.51 | 110.83 | BIGSKY | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.55 | 110.82 | BIGSKY | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.05 | 110.04 | BIGSKY | AP_P1-2_WP-500-DRT21_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.05 | 110.04 | BIGSKY | AP_P2-2_WP-500-DRT16_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.05 | 110.04 | BIGSKY | AP_P1-2_WP-500-005A_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.05 | 110.04 | BIGSKY | AP_P2-3_WP-500-DRT20_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.05 | 110.04 | BIGSKY | AP_P2-3_WP-500-465_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 105.23 | 102.53 | BIGSKY | DVP_P4-2: 560T571_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 105.06 | 102.4 | BIGSKY | DVP_P4-2: H2T560_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 105.06 | 102.38 | BIGSKY | DVP_P4-2: H1T560_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 104.92 | 102.23 | BIGSKY | PEPCO_P1_5070_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3369 | 128.1 | 123.02 | AD2-180 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 118.32 | 117.46 | BISHOP | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 116.95 | 116.14 | BISHOP | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 120.82 | 115.77 | BISHOP | PECO_P4_PEACH035_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 115.32 | 114.54 | BISHOP | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.64 | 114.22 | BISHOP | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.64 | 114.22 | BISHOP | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.26 | 113.56 | BISHOP | PECO_P4_PEACH675_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.26 | 113.56 | BISHOP | PECO_P7-1_220-0607_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3198 | 118.22 | 112.83 | BISHOP | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3369 | 127.3 | 122.25 | AE1-044 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 112.83 | 111.63 | BISHOP | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 112.78 | 111.59 | BISHOP | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.88 | 111.12 | BISHOP | PECO_P1-2_220-07_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.69 | 111.05 | BISHOP | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.58 | 110.94 | BISHOP | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.6 | 110.92 | BISHOP | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.64 | 110.91 | BISHOP | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.13 | 110.12 | BISHOP | AP_P2-2_WP-500-DRT16_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.13 | 110.12 | BISHOP | AP_P1-2_WP-500-005A_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.13 | 110.12 | BISHOP | AP_P1-2_WP-500-DRT21_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.13 | 110.12 | BISHOP | AP_P2-3_WP-500-DRT20_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.13 | 110.12 | BISHOP | AP_P2-3_WP-500-465_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 105.3 | 102.61 | BISHOP | DVP_P4-2: 560T571_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 105.14 | 102.47 | BISHOP | DVP_P4-2: H2T560_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 105.14 | 102.45 | BISHOP | DVP_P4-2: H1T560_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 104.99 | 102.3 | BISHOP | PEPCO_P1_5070_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3369 | 128.1 | 123.03 | AE1-056 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 121.41 | 116.33 | BRUNSWCK_AB | PECO_P4_PEACH035_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 119.17 | 114.73 | BRUNSWCK_AB | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 119.17 | 114.73 | BRUNSWCK_AB | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.83 | 114.12 | BRUNSWCK_AB | PECO_P4_PEACH675_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.83 | 114.12 | BRUNSWCK_AB | PECO_P7-1_220-0607_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3198 | 118.92 | 113.5 | BRUNSWCK_AB | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 116.45 | 111.68 | BRUNSWCK_AB | PECO_P1-2_220-07_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 116.31 | 111.65 | BRUNSWCK_AB | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 116.19 | 111.54 | BRUNSWCK_AB | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 116.22 | 111.52 | BRUNSWCK_AB | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 116.21 | 111.46 | BRUNSWCK_AB | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3369 | 127.99 | 122.93 | AE1-084 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 118.42 | 117.56 | CAMPGROVE;RU | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 117.04 | 116.23 | CAMPGROVE;RU | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 120.93 | 115.87 | CAMPGROVE;RU | PECO_P4_PEACH035_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 115.41 | 114.64 | CAMPGROVE;RU | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.73 | 114.31 | CAMPGROVE;RU | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.73 | 114.31 | CAMPGROVE;RU | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.36 | 113.67 | CAMPGROVE;RU | PECO_P7-1_220-0607_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.36 | 113.67 | CAMPGROVE;RU | PECO_P4_PEACH675_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3198 | 118.34 | 112.95 | CAMPGROVE;RU | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3369 | 128.09 | 123.02 | AE1-101 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 112.92 | 111.73 | CAMPGROVE;RU | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 112.87 | 111.68 | CAMPGROVE;RU | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.98 | 111.22 | CAMPGROVE;RU | PECO_P1-2_220-07_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.81 | 111.16 | CAMPGROVE;RU | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.69 | 111.05 | CAMPGROVE;RU | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.72 | 111.03 | CAMPGROVE;RU | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.74 | 111.01 | CAMPGROVE;RU | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.22 | 110.22 | CAMPGROVE;RU | AP_P1-2_WP-500-005A_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.22 | 110.22 | CAMPGROVE;RU | AP_P2-2_WP-500-DRT16_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.22 | 110.22 | CAMPGROVE;RU | AP_P2-3_WP-500-465_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.22 | 110.22 | CAMPGROVE;RU | AP_P1-2_WP-500-DRT21_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.22 | 110.22 | CAMPGROVE;RU | AP_P2-3_WP-500-DRT20_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 607 | 168.74 | 166.02 | CAYUGA | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 607 | 167.68 | 166.02 | CAYUGA | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 607 | 168.42 | 166.02 | CAYUGA | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 607 | 167.35 | 166.02 | CAYUGA | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 607 | 168.66 | 165.95 | CAYUGA | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 607 | 168.66 | 165.95 | CAYUGA | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 607 | 167.6 | 165.95 | CAYUGA | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 607 | 167.6 | 165.95 | CAYUGA | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 628 | 159.68 | 158.29 | CAYUGA | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 628 | 159.36 | 158.28 | CAYUGA | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 628 | 159.6 | 158.22 | CAYUGA | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 628 | 159.6 | 158.22 | CAYUGA | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 628 | 156.97 | 156 | CAYUGA | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 628 | 156.66 | 155.99 | CAYUGA | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 628 | 156.89 | 155.93 | CAYUGA | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 628 | 156.89 | 155.93 | CAYUGA | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 607 | 153.59 | 151.48 | CAYUGA | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 607 | 154.65 | 151.48 | CAYUGA | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 628 | 146.06 | 144.22 | CAYUGA | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 628 | 143.35 | 141.91 | CAYUGA | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 136.44 | 133.37 | CAYUGA | DVP_P1-2: LN 514_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 136.44 | 133.37 | CAYUGA | AP_P1-2_PE-500-407T_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 136.44 | 133.35 | CAYUGA | DVP_P4-2: 51482_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 131.32 | 128.23 | CAYUGA | AP_P2-3_PE-500-019C_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 814 | 130.93 | 126.43 | CAYUGA | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 814 | 131.42 | 126.31 | CAYUGA | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 814 | 131.42 | 126.31 | CAYUGA | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 814 | 131.4 | 126.3 | CAYUGA | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3369 | 130.2 | 125.07 | AE1-104 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 118.14 | 117.27 | CAYUGA | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 814 | 122.09 | 117.17 | CAYUGA | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 116.77 | 115.94 | CAYUGA | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 120.6 | 115.55 | CAYUGA | PECO_P4_PEACH035_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 115.14 | 114.35 | CAYUGA | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.45 | 114.03 | CAYUGA | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.45 | 114.03 | CAYUGA | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.05 | 113.36 | CAYUGA | PECO_P4_PEACH675_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.05 | 113.36 | CAYUGA | PECO_P7-1_220-0607_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3198 | 117.97 | 112.59 | CAYUGA | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3369 | 127.85 | 122.79 | AE1-143 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 112.66 | 111.45 | CAYUGA | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 112.61 | 111.41 | CAYUGA | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.67 | 110.92 | CAYUGA | PECO_P1-2_220-07_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.47 | 110.84 | CAYUGA | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.35 | 110.72 | CAYUGA | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.43 | 110.7 | CAYUGA | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.38 | 110.7 | CAYUGA | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 110.95 | 109.93 | CAYUGA | AP_P2-2_WP-500-DRT16_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 110.95 | 109.93 | CAYUGA | AP_P1-2_WP-500-DRT21_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 110.95 | 109.93 | CAYUGA | AP_P1-2_WP-500-005A_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 110.95 | 109.93 | CAYUGA | AP_P2-3_WP-500-465_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 110.95 | 109.93 | CAYUGA | AP_P2-3_WP-500-DRT20_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 105.13 | 102.44 | CAYUGA | DVP_P4-2: 560T571_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 104.97 | 102.3 | CAYUGA | DVP_P4-2: H2T560_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 104.97 | 102.28 | CAYUGA | DVP_P4-2: H1T560_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 104.82 | 102.14 | CAYUGA | PEPCO_P1_5070_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 112.75 | 108.36 | CRESCENT ;1U | PL_10_P42_100570_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 112.35 | 107.98 | CRESCENT ;1U | PN_P2-3_PN-500-004-DRT-008_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 112.35 | 107.98 | CRESCENT ;1U | PN_P2-3_PN-500-DRT31_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 112.29 | 107.92 | CRESCENT ;1U | PL_10_P12_000085_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 112.23 | 107.88 | CRESCENT ;1U | PL_30_P42_000131_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3369 | 128.06 | 122.99 | AE1-153 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 118.91 | 118.09 | D05 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 117.53 | 116.76 | D05 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 121.44 | 116.36 | D05 | PECO_P4_PEACH035_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 115.9 | 115.16 | D05 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 119.24 | 114.8 | D05 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 119.24 | 114.8 | D05 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.9 | 114.19 | D05 | PECO_P4_PEACH675_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.9 | 114.19 | D05 | PECO_P7-1_220-0607_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3198 | 119.01 | 113.59 | D05 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3369 | 128.12 | 123.05 | AE1-155 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 113.39 | 112.23 | D05 | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 113.34 | 112.18 | D05 | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 116.52 | 111.75 | D05 | PECO_P1-2_220-07_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 116.38 | 111.72 | D05 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 116.27 | 111.61 | D05 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 116.29 | 111.59 | D05 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 116.28 | 111.53 | D05 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.71 | 110.74 | D05 | AP_P2-3_WP-500-465_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.71 | 110.74 | D05 | AP_P2-2_WP-500-DRT16_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.71 | 110.74 | D05 | AP_P1-2_WP-500-DRT21_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.71 | 110.74 | D05 | AP_P2-3_WP-500-DRT20_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.71 | 110.74 | D05 | AP_P1-2_WP-500-005A_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3369 | 128.12 | 123.05 | AE1-157 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 118.87 | 118.05 | DC1 NUG | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 117.49 | 116.72 | DC1 NUG | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 121.52 | 116.44 | DC1 NUG | PECO_P4_PEACH035_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 115.86 | 115.12 | DC1 NUG | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 119.23 | 114.79 | DC1 NUG | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 119.23 | 114.79 | DC1 NUG | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.9 | 114.19 | DC1 NUG | PECO_P4_PEACH675_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.9 | 114.19 | DC1 NUG | PECO_P7-1_220-0607_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3198 | 119.01 | 113.59 | DC1 NUG | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3369 | 128.22 | 123.15 | AE1-191 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 113.35 | 112.19 | DC1 NUG | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 113.3 | 112.15 | DC1 NUG | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 116.52 | 111.75 | DC1 NUG | PECO_P1-2_220-07_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 116.4 | 111.73 | DC1 NUG | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 116.28 | 111.62 | DC1 NUG | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 116.31 | 111.6 | DC1 NUG | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 116.28 | 111.53 | DC1 NUG | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.66 | 110.69 | DC1 NUG | AP_P1-2_WP-500-DRT21_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.66 | 110.69 | DC1 NUG | AP_P1-2_WP-500-005A_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.66 | 110.69 | DC1 NUG | AP_P2-3_WP-500-DRT20_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.66 | 110.69 | DC1 NUG | AP_P2-2_WP-500-DRT16_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.66 | 110.69 | DC1 NUG | AP_P2-3_WP-500-465_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3369 | 128.23 | 123.16 | AE1-212 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 118.87 | 118.05 | DC2 NUG | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 117.49 | 116.72 | DC2 NUG | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 121.52 | 116.44 | DC2 NUG | PECO_P4_PEACH035_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 115.86 | 115.12 | DC2 NUG | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 119.23 | 114.79 | DC2 NUG | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 119.23 | 114.79 | DC2 NUG | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.9 | 114.19 | DC2 NUG | PECO_P4_PEACH675_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.9 | 114.19 | DC2 NUG | PECO_P7-1_220-0607_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3198 | 119.01 | 113.59 | DC2 NUG | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3369 | 128.94 | 123.84 | AE1-229 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 113.35 | 112.19 | DC2 NUG | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 113.3 | 112.15 | DC2 NUG | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 116.52 | 111.75 | DC2 NUG | PECO_P1-2_220-07_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 116.4 | 111.73 | DC2 NUG | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 116.28 | 111.62 | DC2 NUG | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 116.31 | 111.6 | DC2 NUG | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 116.28 | 111.53 | DC2 NUG | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.66 | 110.69 | DC2 NUG | AP_P1-2_WP-500-DRT21_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.66 | 110.69 | DC2 NUG | AP_P1-2_WP-500-005A_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.66 | 110.69 | DC2 NUG | AP_P2-3_WP-500-DRT20_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.66 | 110.69 | DC2 NUG | AP_P2-2_WP-500-DRT16_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.66 | 110.69 | DC2 NUG | AP_P2-3_WP-500-465_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3369 | 128.58 | 123.49 | AE1-240 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 118.51 | 117.66 | ECOGROVE ;U1 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 117.14 | 116.33 | ECOGROVE ;U1 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 121.04 | 115.98 | ECOGROVE ;U1 | PECO_P4_PEACH035_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 115.5 | 114.74 | ECOGROVE ;U1 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.83 | 114.41 | ECOGROVE ;U1 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.83 | 114.41 | ECOGROVE ;U1 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.47 | 113.77 | ECOGROVE ;U1 | PECO_P4_PEACH675_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.47 | 113.77 | ECOGROVE ;U1 | PECO_P7-1_220-0607_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3198 | 118.47 | 113.07 | ECOGROVE ;U1 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3369 | 131.56 | 126.39 | AE2-000 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 113.01 | 111.83 | ECOGROVE ;U1 | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 112.96 | 111.78 | ECOGROVE ;U1 | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 116.09 | 111.33 | ECOGROVE ;U1 | PECO_P1-2_220-07_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.92 | 111.27 | ECOGROVE ;U1 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.8 | 111.16 | ECOGROVE ;U1 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.83 | 111.14 | ECOGROVE ;U1 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.85 | 111.11 | ECOGROVE ;U1 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.31 | 110.32 | ECOGROVE ;U1 | AP_P1-2_WP-500-005A_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.31 | 110.32 | ECOGROVE ;U1 | AP_P2-2_WP-500-DRT16_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.31 | 110.32 | ECOGROVE ;U1 | AP_P2-3_WP-500-DRT20_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.31 | 110.32 | ECOGROVE ;U1 | AP_P2-3_WP-500-465_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.31 | 110.32 | ECOGROVE ;U1 | AP_P1-2_WP-500-DRT21_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 137.22 | 134.15 | FAIRLAWN_AB | AP_P1-2_PE-500-407T_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 137.22 | 134.15 | FAIRLAWN_AB | DVP_P1-2: LN 514_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 137.22 | 134.13 | FAIRLAWN_AB | DVP_P4-2: 51482_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 132.1 | 129.01 | FAIRLAWN_AB | AP_P2-3_PE-500-019C_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3369 | 131.08 | 125.92 | AE2-020 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 119.09 | 118.29 | FAIRLAWN_AB | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 117.71 | 116.95 | FAIRLAWN_AB | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 121.66 | 116.58 | FAIRLAWN_AB | PECO_P4_PEACH035_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 116.08 | 115.36 | FAIRLAWN_AB | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 119.43 | 114.99 | FAIRLAWN_AB | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 119.43 | 114.99 | FAIRLAWN_AB | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 119.11 | 114.4 | FAIRLAWN_AB | PECO_P7-1_220-0607_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 119.11 | 114.4 | FAIRLAWN_AB | PECO_P4_PEACH675_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3198 | 119.29 | 113.85 | FAIRLAWN_AB | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3369 | 131.08 | 125.92 | AE2-021 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 113.56 | 112.42 | FAIRLAWN_AB | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 113.51 | 112.37 | FAIRLAWN_AB | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 116.73 | 111.95 | FAIRLAWN_AB | PECO_P1-2_220-07_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 116.62 | 111.95 | FAIRLAWN_AB | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 116.5 | 111.83 | FAIRLAWN_AB | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 116.53 | 111.81 | FAIRLAWN_AB | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 116.49 | 111.73 | FAIRLAWN_AB | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.88 | 110.92 | FAIRLAWN_AB | AP_P1-2_WP-500-005A_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.88 | 110.92 | FAIRLAWN_AB | AP_P2-2_WP-500-DRT16_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.88 | 110.92 | FAIRLAWN_AB | AP_P2-3_WP-500-DRT20_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.88 | 110.92 | FAIRLAWN_AB | AP_P2-3_WP-500-465_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.88 | 110.92 | FAIRLAWN_AB | AP_P1-2_WP-500-DRT21_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 607 | 168.6 | 165.88 | G07 NFTWR | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 607 | 167.54 | 165.88 | G07 NFTWR | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 607 | 168.28 | 165.87 | G07 NFTWR | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 607 | 167.22 | 165.87 | G07 NFTWR | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 607 | 168.53 | 165.8 | G07 NFTWR | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 607 | 168.53 | 165.8 | G07 NFTWR | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 607 | 167.46 | 165.8 | G07 NFTWR | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 607 | 167.46 | 165.8 | G07 NFTWR | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 628 | 159.55 | 158.15 | G07 NFTWR | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 628 | 159.23 | 158.14 | G07 NFTWR | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 628 | 159.47 | 158.08 | G07 NFTWR | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 628 | 159.47 | 158.08 | G07 NFTWR | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 628 | 156.84 | 155.86 | G07 NFTWR | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 628 | 156.53 | 155.85 | G07 NFTWR | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 628 | 156.76 | 155.79 | G07 NFTWR | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 628 | 156.76 | 155.79 | G07 NFTWR | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 607 | 153.4 | 151.29 | G07 NFTWR | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 607 | 154.46 | 151.29 | G07 NFTWR | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 628 | 145.87 | 144.04 | G07 NFTWR | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 628 | 143.17 | 141.72 | G07 NFTWR | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 797 | 140.62 | 136.08 | G07 NFTWR | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 797 | 140.88 | 136.01 | G07 NFTWR | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 797 | 140.88 | 136.01 | G07 NFTWR | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 797 | 140.85 | 135.99 | G07 NFTWR | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 136.36 | 133.29 | G07 NFTWR | DVP_P1-2: LN 514_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 136.36 | 133.29 | G07 NFTWR | AP_P1-2_PE-500-407T_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 136.36 | 133.27 | G07 NFTWR | DVP_P4-2: 51482_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 131.24 | 128.16 | G07 NFTWR | AP_P2-3_PE-500-019C_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 797 | 132.48 | 127.7 | G07 NFTWR | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 814 | 130.84 | 126.34 | G07 NFTWR | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 814 | 131.33 | 126.22 | G07 NFTWR | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 814 | 131.33 | 126.22 | G07 NFTWR | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 814 | 131.31 | 126.21 | G07 NFTWR | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3369 | 129.73 | 124.61 | AE2-022 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 118.11 | 117.23 | G07 NFTWR | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 814 | 121.97 | 117.05 | G07 NFTWR | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 116.74 | 115.91 | G07 NFTWR | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 120.63 | 115.57 | G07 NFTWR | PECO_P4_PEACH035_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 115.11 | 114.31 | G07 NFTWR | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.42 | 114 | G07 NFTWR | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.42 | 114 | G07 NFTWR | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.01 | 113.33 | G07 NFTWR | PECO_P4_PEACH675_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.01 | 113.33 | G07 NFTWR | PECO_P7-1_220-0607_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 814 | 115.74 | 112.75 | G07 NFTWR | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 814 | 115.99 | 112.69 | G07 NFTWR | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 814 | 115.99 | 112.69 | G07 NFTWR | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 814 | 115.96 | 112.67 | G07 NFTWR | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3198 | 117.85 | 112.49 | G07 NFTWR | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3369 | 128.13 | 123.06 | AE2-027 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 112.63 | 111.42 | G07 NFTWR | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 112.58 | 111.38 | G07 NFTWR | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.64 | 110.89 | G07 NFTWR | PECO_P1-2_220-07_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.42 | 110.79 | G07 NFTWR | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.3 | 110.67 | G07 NFTWR | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.4 | 110.67 | G07 NFTWR | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.33 | 110.65 | G07 NFTWR | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 110.94 | 109.92 | G07 NFTWR | AP_P1-2_WP-500-005A_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 110.94 | 109.92 | G07 NFTWR | AP_P2-2_WP-500-DRT16_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 110.94 | 109.92 | G07 NFTWR | AP_P2-3_WP-500-465_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 110.94 | 109.92 | G07 NFTWR | AP_P2-3_WP-500-DRT20_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 110.94 | 109.92 | G07 NFTWR | AP_P1-2_WP-500-DRT21_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 814 | 107.55 | 104.24 | G07 NFTWR | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 105.2 | 102.5 | G07 NFTWR | DVP_P4-2: 560T571_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 105.03 | 102.36 | G07 NFTWR | DVP_P4-2: H2T560_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 105.03 | 102.35 | G07 NFTWR | DVP_P4-2: H1T560_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 104.89 | 102.2 | G07 NFTWR | PEPCO_P1_5070_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 801 | 102.25 | 100.15 | G07 NFTWR | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 801 | 102.66 | 100.04 | G07 NFTWR | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 801 | 102.66 | 100.04 | G07 NFTWR | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 801 | 102.63 | 100.02 | G07 NFTWR | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200762 | 26GARRETT | 235470 | 01GARRET | 1 | 115 | 226/201 | 160 | 103.28 | 103.68 | G21 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200762 | 26GARRETT | 235470 | 01GARRET | 1 | 115 | 226/201 | 160 | 103.28 | 103.68 | G21 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200762 | 26GARRETT | 235470 | 01GARRET | 1 | 115 | 226/201 | 160 | 103.21 | 103.59 | G21 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3369 | 128.55 | 123.46 | AE2-042 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 121.46 | 116.38 | GLOUCSTR_26 | PECO_P4_PEACH035_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 119.2 | 114.76 | GLOUCSTR_26 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 119.2 | 114.76 | GLOUCSTR_26 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.87 | 114.16 | GLOUCSTR_26 | PECO_P4_PEACH675_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.87 | 114.16 | GLOUCSTR_26 | PECO_P7-1_220-0607_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3198 | 118.97 | 113.55 | GLOUCSTR_26 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 116.49 | 111.71 | GLOUCSTR_26 | PECO_P1-2_220-07_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 116.35 | 111.69 | GLOUCSTR_26 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 116.24 | 111.58 | GLOUCSTR_26 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 116.27 | 111.56 | GLOUCSTR_26 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 116.24 | 111.5 | GLOUCSTR_26 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 607 | 168.71 | 165.99 | GR RIDGE | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 607 | 167.65 | 165.99 | GR RIDGE | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 607 | 168.39 | 165.98 | GR RIDGE | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 607 | 167.32 | 165.98 | GR RIDGE | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 607 | 168.63 | 165.92 | GR RIDGE | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 607 | 168.63 | 165.92 | GR RIDGE | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 607 | 167.57 | 165.92 | GR RIDGE | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 607 | 167.57 | 165.92 | GR RIDGE | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 628 | 159.65 | 158.26 | GR RIDGE | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 628 | 159.33 | 158.25 | GR RIDGE | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 628 | 159.57 | 158.19 | GR RIDGE | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 628 | 159.57 | 158.19 | GR RIDGE | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 628 | 156.94 | 155.97 | GR RIDGE | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 628 | 156.63 | 155.96 | GR RIDGE | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 628 | 156.86 | 155.9 | GR RIDGE | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 628 | 156.86 | 155.9 | GR RIDGE | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 607 | 153.55 | 151.45 | GR RIDGE | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 607 | 154.62 | 151.45 | GR RIDGE | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 628 | 146.03 | 144.19 | GR RIDGE | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 628 | 143.32 | 141.88 | GR RIDGE | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 797 | 140.94 | 136.07 | GR RIDGE | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 797 | 140.94 | 136.07 | GR RIDGE | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 797 | 140.92 | 136.06 | GR RIDGE | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 136.42 | 133.36 | GR RIDGE | AP_P1-2_PE-500-407T_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 136.42 | 133.36 | GR RIDGE | DVP_P1-2: LN 514_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 136.42 | 133.34 | GR RIDGE | DVP_P4-2: 51482_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 131.3 | 128.22 | GR RIDGE | AP_P2-3_PE-500-019C_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 797 | 132.57 | 127.78 | GR RIDGE | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 814 | 130.91 | 126.41 | GR RIDGE | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 814 | 131.4 | 126.29 | GR RIDGE | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 814 | 131.4 | 126.29 | GR RIDGE | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 814 | 131.38 | 126.28 | GR RIDGE | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3369 | 128.68 | 123.59 | AE2-046 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 118.13 | 117.25 | GR RIDGE | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 814 | 122.07 | 117.15 | GR RIDGE | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 116.76 | 115.93 | GR RIDGE | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 120.58 | 115.53 | GR RIDGE | PECO_P4_PEACH035_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 115.12 | 114.33 | GR RIDGE | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.43 | 114.01 | GR RIDGE | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.43 | 114.01 | GR RIDGE | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.03 | 113.34 | GR RIDGE | PECO_P7-1_220-0607_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.03 | 113.34 | GR RIDGE | PECO_P4_PEACH675_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3198 | 117.94 | 112.57 | GR RIDGE | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3369 | 128.6 | 123.51 | AE2-093 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 112.64 | 111.43 | GR RIDGE | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 112.59 | 111.39 | GR RIDGE | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.65 | 110.9 | GR RIDGE | PECO_P1-2_220-07_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.45 | 110.81 | GR RIDGE | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.33 | 110.7 | GR RIDGE | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.41 | 110.68 | GR RIDGE | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.36 | 110.68 | GR RIDGE | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 110.93 | 109.91 | GR RIDGE | AP_P2-3_WP-500-465_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 110.93 | 109.91 | GR RIDGE | AP_P2-3_WP-500-DRT20_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 110.93 | 109.91 | GR RIDGE | AP_P1-2_WP-500-DRT21_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 110.93 | 109.91 | GR RIDGE | AP_P1-2_WP-500-005A_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 110.93 | 109.91 | GR RIDGE | AP_P2-2_WP-500-DRT16_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 105.12 | 102.42 | GR RIDGE | DVP_P4-2: 560T571_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 104.95 | 102.29 | GR RIDGE | DVP_P4-2: H2T560_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 104.95 | 102.27 | GR RIDGE | DVP_P4-2: H1T560_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 104.81 | 102.12 | GR RIDGE | PEPCO_P1_5070_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3369 | 128.15 | 123.08 | AE2-206 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 121.09 | 116.02 | GSG-6 ;RU | PECO_P4_PEACH035_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.87 | 114.45 | GSG-6 ;RU | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.87 | 114.45 | GSG-6 ;RU | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.51 | 113.81 | GSG-6 ;RU | PECO_P4_PEACH675_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.51 | 113.81 | GSG-6 ;RU | PECO_P7-1_220-0607_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3198 | 118.52 | 113.12 | GSG-6 ;RU | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 116.13 | 111.37 | GSG-6 ;RU | PECO_P1-2_220-07_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.97 | 111.32 | GSG-6 ;RU | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.85 | 111.2 | GSG-6 ;RU | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.88 | 111.18 | GSG-6 ;RU | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.89 | 111.15 | GSG-6 ;RU | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3369 | 127.75 | 122.69 | AE2-217 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 118.5 | 117.65 | K28 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 117.13 | 116.32 | K28 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 121.04 | 115.98 | K28 | PECO_P4_PEACH035_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 115.49 | 114.72 | K28 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.82 | 114.4 | K28 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.82 | 114.4 | K28 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.46 | 113.76 | K28 | PECO_P7-1_220-0607_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.46 | 113.76 | K28 | PECO_P4_PEACH675_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3198 | 118.46 | 113.07 | K28 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3369 | 127.75 | 122.69 | AE2-218 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 113 | 111.81 | K28 | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 112.95 | 111.77 | K28 | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 116.08 | 111.32 | K28 | PECO_P1-2_220-07_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.91 | 111.27 | K28 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.8 | 111.15 | K28 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.82 | 111.13 | K28 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.84 | 111.1 | K28 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.3 | 110.3 | K28 | AP_P2-2_WP-500-DRT16_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.3 | 110.3 | K28 | AP_P1-2_WP-500-DRT21_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.3 | 110.3 | K28 | AP_P2-3_WP-500-465_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.3 | 110.3 | K28 | AP_P2-3_WP-500-DRT20_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.3 | 110.3 | K28 | AP_P1-2_WP-500-005A_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3369 | 127.89 | 122.83 | AE2-221 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 118.37 | 117.51 | KELLY CRK;1U | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 117 | 116.19 | KELLY CRK;1U | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 120.88 | 115.82 | KELLY CRK;1U | PECO_P4_PEACH035_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 115.37 | 114.59 | KELLY CRK;1U | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.69 | 114.27 | KELLY CRK;1U | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.69 | 114.27 | KELLY CRK;1U | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.31 | 113.62 | KELLY CRK;1U | PECO_P7-1_220-0607_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.31 | 113.62 | KELLY CRK;1U | PECO_P4_PEACH675_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3198 | 118.28 | 112.89 | KELLY CRK;1U | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3369 | 128.1 | 123.03 | AE2-230 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 112.88 | 111.69 | KELLY CRK;1U | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 112.83 | 111.64 | KELLY CRK;1U | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.93 | 111.17 | KELLY CRK;1U | PECO_P1-2_220-07_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.75 | 111.11 | KELLY CRK;1U | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.63 | 110.99 | KELLY CRK;1U | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.66 | 110.97 | KELLY CRK;1U | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.69 | 110.96 | KELLY CRK;1U | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.18 | 110.17 | KELLY CRK;1U | AP_P1-2_WP-500-DRT21_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.18 | 110.17 | KELLY CRK;1U | AP_P2-2_WP-500-DRT16_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.18 | 110.17 | KELLY CRK;1U | AP_P2-3_WP-500-DRT20_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.18 | 110.17 | KELLY CRK;1U | AP_P2-3_WP-500-465_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.18 | 110.17 | KELLY CRK;1U | AP_P1-2_WP-500-005A_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 109.81 | 105.45 | LAURHILL-G | APS-P2-3-WP-230-0403-C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 109.8 | 105.44 | LAURHILL-G | APS-P2-3-WP-230-0403-D_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 109.8 | 105.44 | LAURHILL-G | PN_P1-3_PN-230-029_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 109.8 | 105.44 | LAURHILL-G | PN_P1-2_PN-230-324T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 103.29 | 101.93 | LAURHILL-G | APS-P2-3-WP-230-0403-C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 103.28 | 101.92 | LAURHILL-G | APS-P2-3-WP-230-0403-D_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 103.28 | 101.92 | LAURHILL-G | PN_P1-3_PN-230-029_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 103.28 | 101.92 | LAURHILL-G | PN_P1-2_PN-230-324T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3198 | 118.89 | 113.47 | LINDEN_26 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 116.29 | 111.63 | LINDEN_26 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 116.17 | 111.51 | LINDEN_26 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 116.2 | 111.49 | LINDEN_26 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.97 | 111.34 | LINDEN_26 | PECO_P4_NOTTI85_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.91 | 111.33 | LINDEN_26 | PECO_P1-2_220-08_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.86 | 111.28 | LINDEN_26 | PECO_P4_COOPR125_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.62 | 111.13 | LINDEN_26 | PECO_P1-2_220-93_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 113.11 | 108.66 | LINDEN_26 | DVP_P1-3: 6SURRY-GSU-1_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 109.74 | 105.47 | LINDEN_26 | PL_10_P42_100572_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 109.53 | 105.06 | LINDEN_26 | PL_24_P42_000161_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3369 | 128.18 | 123.11 | AE2-253 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 118.39 | 117.54 | M24 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 117.02 | 116.21 | M24 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 120.92 | 115.86 | M24 | PECO_P4_PEACH035_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 115.39 | 114.61 | M24 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.71 | 114.29 | M24 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.71 | 114.29 | M24 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.34 | 113.65 | M24 | PECO_P7-1_220-0607_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.34 | 113.65 | M24 | PECO_P4_PEACH675_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3198 | 118.32 | 112.93 | M24 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3369 | 128.14 | 123.06 | AE2-297 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 112.9 | 111.71 | M24 | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 112.85 | 111.66 | M24 | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.96 | 111.21 | M24 | PECO_P1-2_220-07_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.79 | 111.14 | M24 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.67 | 111.03 | M24 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.7 | 111.01 | M24 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.72 | 110.99 | M24 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.19 | 110.18 | M24 | AP_P2-3_WP-500-465_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.19 | 110.18 | M24 | AP_P1-2_WP-500-005A_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.19 | 110.18 | M24 | AP_P1-2_WP-500-DRT21_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.19 | 110.18 | M24 | AP_P2-2_WP-500-DRT16_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.19 | 110.18 | M24 | AP_P2-3_WP-500-DRT20_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3369 | 128.23 | 123.15 | AE2-318 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 121.1 | 116.03 | MENDOTA H;RU | PECO_P4_PEACH035_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.88 | 114.45 | MENDOTA H;RU | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.88 | 114.45 | MENDOTA H;RU | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.52 | 113.82 | MENDOTA H;RU | PECO_P4_PEACH675_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.52 | 113.82 | MENDOTA H;RU | PECO_P7-1_220-0607_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3198 | 118.53 | 113.13 | MENDOTA H;RU | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 116.14 | 111.38 | MENDOTA H;RU | PECO_P1-2_220-07_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.97 | 111.33 | MENDOTA H;RU | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.86 | 111.21 | MENDOTA H;RU | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.89 | 111.19 | MENDOTA H;RU | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.9 | 111.16 | MENDOTA H;RU | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3369 | 128.23 | 123.15 | AE2-319 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 118.33 | 117.47 | MINONK ;1U | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 116.96 | 116.14 | MINONK ;1U | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 120.83 | 115.77 | MINONK ;1U | PECO_P4_PEACH035_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 115.32 | 114.55 | MINONK ;1U | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.64 | 114.22 | MINONK ;1U | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.64 | 114.22 | MINONK ;1U | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.26 | 113.57 | MINONK ;1U | PECO_P7-1_220-0607_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.26 | 113.57 | MINONK ;1U | PECO_P4_PEACH675_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3198 | 118.22 | 112.84 | MINONK ;1U | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3369 | 128.16 | 123.09 | AE2-333 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 112.84 | 111.64 | MINONK ;1U | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 112.79 | 111.59 | MINONK ;1U | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.88 | 111.12 | MINONK ;1U | PECO_P1-2_220-07_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.7 | 111.06 | MINONK ;1U | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.58 | 110.94 | MINONK ;1U | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.61 | 110.92 | MINONK ;1U | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.64 | 110.91 | MINONK ;1U | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.13 | 110.12 | MINONK ;1U | AP_P2-3_WP-500-DRT20_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.13 | 110.12 | MINONK ;1U | AP_P1-2_WP-500-DRT21_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.13 | 110.12 | MINONK ;1U | AP_P1-2_WP-500-005A_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.13 | 110.12 | MINONK ;1U | AP_P2-3_WP-500-465_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.13 | 110.12 | MINONK ;1U | AP_P2-2_WP-500-DRT16_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 137.35 | 134.25 | NIH23MW | AP_P1-2_PE-500-407T_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 137.35 | 134.25 | NIH23MW | DVP_P1-2: LN 514_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 137.35 | 134.23 | NIH23MW | DVP_P4-2: 51482_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 132.26 | 129.14 | NIH23MW | AP_P2-3_PE-500-019C_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.89 | 114.46 | NIH23MW | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.89 | 114.46 | NIH23MW | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 116.01 | 111.36 | NIH23MW | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.9 | 111.25 | NIH23MW | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.92 | 111.23 | NIH23MW | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.7 | 111.07 | NIH23MW | PECO_P4_NOTTI85_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.63 | 111.06 | NIH23MW | PECO_P1-2_220-08_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.59 | 111.02 | NIH23MW | PECO_P4_COOPR125_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.35 | 110.87 | NIH23MW | PECO_P1-2_220-93_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 114.66 | 110.27 | NIH23MW | PL_05_P71_000906_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 106.17 | 103.44 | NIH23MW | DVP_P4-2: 560T571_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 106.01 | 103.3 | NIH23MW | DVP_P4-2: H2T560_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 106.01 | 103.29 | NIH23MW | DVP_P4-2: H1T560_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 105.87 | 103.14 | NIH23MW | PEPCO_P1_5070_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 607 | 168.9 | 166.2 | O09 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 607 | 167.84 | 166.2 | O09 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 607 | 168.58 | 166.18 | O09 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 607 | 167.51 | 166.18 | O09 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 607 | 167.76 | 166.12 | O09 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 607 | 167.76 | 166.12 | O09 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 607 | 168.83 | 166.12 | O09 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 607 | 168.83 | 166.12 | O09 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 628 | 159.83 | 158.46 | O09 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 628 | 159.51 | 158.45 | O09 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 628 | 159.75 | 158.39 | O09 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 628 | 159.75 | 158.39 | O09 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 628 | 157.12 | 156.17 | O09 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 628 | 156.81 | 156.16 | O09 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 628 | 157.05 | 156.1 | O09 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 628 | 157.05 | 156.1 | O09 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 136.49 | 133.42 | O09 | AP_P1-2_PE-500-407T_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 136.49 | 133.42 | O09 | DVP_P1-2: LN 514_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 136.49 | 133.4 | O09 | DVP_P4-2: 51482_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 131.37 | 128.29 | O09 | AP_P2-3_PE-500-019C_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3369 | 128.55 | 123.47 | AE2-334 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 118.23 | 117.36 | O09 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 116.86 | 116.03 | O09 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 120.71 | 115.66 | O09 | PECO_P4_PEACH035_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 115.22 | 114.44 | O09 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.54 | 114.12 | O09 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.54 | 114.12 | O09 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.15 | 113.46 | O09 | PECO_P7-1_220-0607_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.15 | 113.46 | O09 | PECO_P4_PEACH675_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3198 | 118.09 | 112.71 | O09 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3369 | 128.17 | 123.1 | AF1-038 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 112.74 | 111.54 | O09 | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 112.69 | 111.49 | O09 | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.77 | 111.02 | O09 | PECO_P1-2_220-07_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.58 | 110.94 | O09 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.46 | 110.83 | O09 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.49 | 110.81 | O09 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.53 | 110.8 | O09 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.03 | 110.02 | O09 | AP_P1-2_WP-500-DRT21_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.03 | 110.02 | O09 | AP_P2-2_WP-500-DRT16_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.03 | 110.02 | O09 | AP_P1-2_WP-500-005A_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.03 | 110.02 | O09 | AP_P2-3_WP-500-DRT20_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.03 | 110.02 | O09 | AP_P2-3_WP-500-465_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 105.21 | 102.51 | O09 | DVP_P4-2: 560T571_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 105.04 | 102.38 | O09 | DVP_P4-2: H2T560_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 105.04 | 102.36 | O09 | DVP_P4-2: H1T560_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 104.9 | 102.21 | O09 | PEPCO_P1_5070_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 607 | 168.99 | 166.29 | O29 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 607 | 167.92 | 166.29 | O29 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 607 | 167.59 | 166.27 | O29 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 607 | 168.66 | 166.27 | O29 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 607 | 167.84 | 166.21 | O29 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 607 | 167.84 | 166.21 | O29 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 607 | 168.91 | 166.21 | O29 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 607 | 168.91 | 166.21 | O29 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 628 | 159.91 | 158.54 | O29 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 628 | 159.59 | 158.53 | O29 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 628 | 159.83 | 158.47 | O29 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 628 | 159.83 | 158.47 | O29 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 628 | 157.2 | 156.25 | O29 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 628 | 156.89 | 156.24 | O29 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 628 | 157.13 | 156.18 | O29 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 628 | 157.13 | 156.18 | O29 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3369 | 128.17 | 123.1 | AF1-050 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 118.28 | 117.41 | O29 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 116.9 | 116.08 | O29 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 120.77 | 115.71 | O29 | PECO_P4_PEACH035_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 115.27 | 114.49 | O29 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.59 | 114.17 | O29 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.59 | 114.17 | O29 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.2 | 113.51 | O29 | PECO_P4_PEACH675_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.2 | 113.51 | O29 | PECO_P7-1_220-0607_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3198 | 118.15 | 112.77 | O29 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3369 | 128.2 | 123.12 | AF1-083 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 112.79 | 111.59 | O29 | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 112.73 | 111.54 | O29 | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.82 | 111.07 | O29 | PECO_P1-2_220-07_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.63 | 110.99 | O29 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.52 | 110.88 | O29 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.54 | 110.86 | O29 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.58 | 110.85 | O29 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.08 | 110.07 | O29 | AP_P2-3_WP-500-DRT20_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.08 | 110.07 | O29 | AP_P2-3_WP-500-465_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.08 | 110.07 | O29 | AP_P2-2_WP-500-DRT16_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.08 | 110.07 | O29 | AP_P1-2_WP-500-DRT21_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.08 | 110.07 | O29 | AP_P1-2_WP-500-005A_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 105.25 | 102.56 | O29 | DVP_P4-2: 560T571_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 105.09 | 102.42 | O29 | DVP_P4-2: H2T560_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 105.09 | 102.4 | O29 | DVP_P4-2: H1T560_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 104.95 | 102.26 | O29 | PEPCO_P1_5070_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 607 | 162.76 | 159.95 | O66 NFTWR | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 607 | 161.77 | 159.95 | O66 NFTWR | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 607 | 162.98 | 159.87 | O66 NFTWR | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 607 | 162 | 159.87 | O66 NFTWR | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 607 | 162.91 | 159.8 | O66 NFTWR | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 607 | 162.91 | 159.8 | O66 NFTWR | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 607 | 161.92 | 159.8 | O66 NFTWR | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 607 | 161.92 | 159.8 | O66 NFTWR | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 628 | 153.97 | 152.41 | O66 NFTWR | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 628 | 154.19 | 152.34 | O66 NFTWR | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 628 | 154.11 | 152.27 | O66 NFTWR | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 628 | 154.11 | 152.27 | O66 NFTWR | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 235463 | 01TANEY | 1 | 138 | 227/201 | 268 | 155.6 | 151.95 | O66 NFTWR | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 235463 | 01TANEY | 1 | 138 | 227/201 | 268 | 155.6 | 151.95 | O66 NFTWR | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 235463 | 01TANEY | 1 | 138 | 227/201 | 268 | 155.52 | 151.87 | O66 NFTWR | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 628 | 151.27 | 150.11 | O66 NFTWR | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 628 | 151.49 | 150.03 | O66 NFTWR | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 628 | 151.41 | 149.96 | O66 NFTWR | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 628 | 151.41 | 149.96 | O66 NFTWR | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 607 | 148.75 | 145.58 | O66 NFTWR | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 607 | 147.76 | 145.58 | O66 NFTWR | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 628 | 140.43 | 138.52 | O66 NFTWR | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 628 | 137.73 | 136.2 | O66 NFTWR | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 680 | 139.13 | 136.19 | O66 NFTWR | PEPCO_P4_PP19_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 282 | 135.05 | 134.5 | O66 NFTWR | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 282 | 135.05 | 134.5 | O66 NFTWR | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 282 | 134.99 | 134.43 | O66 NFTWR | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 797 | 136.81 | 132.3 | O66 NFTWR | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 797 | 136.96 | 132.15 | O66 NFTWR | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 797 | 136.96 | 132.15 | O66 NFTWR | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 797 | 136.94 | 132.13 | O66 NFTWR | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 133.66 | 130.56 | O66 NFTWR | DVP_P1-2: LN 514_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 133.66 | 130.56 | O66 NFTWR | AP_P1-2_PE-500-407T_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 133.66 | 130.54 | O66 NFTWR | DVP_P4-2: 51482_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 680 | 133.26 | 130.43 | O66 NFTWR | PEPCO_P1_PP2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 2 | 230 | 233 | 680 | 133.26 | 130.43 | O66 NFTWR | PEPCO_P1_PP1_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204538 | 27STRABAN | 204544 | 27LINCOLN | 1 | 115 | 227 | 313 | 128.28 | 128.89 | O66 NFTWR | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204538 | 27STRABAN | 204544 | 27LINCOLN | 1 | 115 | 227 | 313 | 128.28 | 128.89 | O66 NFTWR | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204538 | 27STRABAN | 204544 | 27LINCOLN | 1 | 115 | 227 | 313 | 128.22 | 128.81 | O66 NFTWR | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 203981 | AD2-062_POI | 235188 | 01GREENE | 1 | 138 | 226/201 | 268 | 131.62 | 127.54 | O66 NFTWR | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 203981 | AD2-062_POI | 235188 | 01GREENE | 1 | 138 | 226/201 | 268 | 131.62 | 127.54 | O66 NFTWR | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 203981 | AD2-062_POI | 235188 | 01GREENE | 1 | 138 | 226/201 | 268 | 131.52 | 127.44 | O66 NFTWR | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3369 | 128.14 | 123.07 | AF1-147 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204529 | 27GERMANTN | 204538 | 27STRABAN | 1 | 115 | 227 | 313 | 124.94 | 126.16 | O66 NFTWR | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204529 | 27GERMANTN | 204538 | 27STRABAN | 1 | 115 | 227 | 313 | 124.94 | 126.16 | O66 NFTWR | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204529 | 27GERMANTN | 204538 | 27STRABAN | 1 | 115 | 227 | 313 | 124.87 | 126.09 | O66 NFTWR | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 128.56 | 125.49 | O66 NFTWR | AP_P2-3_PE-500-019C_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 235463 | 01TANEY | 1 | 138 | 227/201 | 268 | 130.8 | 124.74 | O66 NFTWR | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 235463 | 01TANEY | 1 | 138 | 227/201 | 268 | 130.8 | 124.74 | O66 NFTWR | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 235463 | 01TANEY | 1 | 138 | 227/201 | 268 | 130.79 | 124.73 | O66 NFTWR | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 235463 | 01TANEY | 1 | 138 | 227/201 | 268 | 130.84 | 124.71 | O66 NFTWR | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 797 | 128.51 | 123.81 | O66 NFTWR | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 680 | 126.71 | 123.75 | O66 NFTWR | AP_P1-2_PE-500-407T_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 2 | 230 | 233 | 680 | 126.71 | 123.75 | O66 NFTWR | AP_P1-2_PE-500-407T_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 2 | 230 | 233 | 680 | 126.71 | 123.75 | O66 NFTWR | DVP_P1-2: LN 514_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 680 | 126.71 | 123.75 | O66 NFTWR | DVP_P1-2: LN 514_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 680 | 126.71 | 123.75 | O66 NFTWR | DVP_P4-2: 51482_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 2 | 230 | 233 | 680 | 126.71 | 123.75 | O66 NFTWR | DVP_P4-2: 51482_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 204529 | 27GERMANTN | 1 | 138/115 | 227 | 345 | 120.87 | 123.25 | O66 NFTWR | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 204529 | 27GERMANTN | 1 | 138/115 | 227 | 345 | 120.87 | 123.25 | O66 NFTWR | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 204529 | 27GERMANTN | 1 | 138/115 | 227 | 345 | 120.81 | 123.18 | O66 NFTWR | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 814 | 126.84 | 122.38 | O66 NFTWR | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 814 | 127.14 | 122.1 | O66 NFTWR | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 814 | 127.14 | 122.1 | O66 NFTWR | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 814 | 127.12 | 122.08 | O66 NFTWR | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 235463 | 01TANEY | 1 | 138 | 227/201 | 268 | 123.13 | 121.17 | O66 NFTWR | PEPCO_P4_PP41_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 221095 | ROCKRGE2 | 221098 | C.PIPE12 | 1 | 115 | 232 | 217 | 120.93 | 120.46 | O66 NFTWR | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 203981 | AD2-062_POI | 235188 | 01GREENE | 1 | 138 | 226/201 | 268 | 125.72 | 119.35 | O66 NFTWR | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 203981 | AD2-062_POI | 235188 | 01GREENE | 1 | 138 | 226/201 | 268 | 125.72 | 119.35 | O66 NFTWR | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 203981 | AD2-062_POI | 235188 | 01GREENE | 1 | 138 | 226/201 | 268 | 125.72 | 119.34 | O66 NFTWR | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 203981 | AD2-062_POI | 235188 | 01GREENE | 1 | 138 | 226/201 | 268 | 125.76 | 119.32 | O66 NFTWR | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 235463 | 01TANEY | 1 | 138 | 227/201 | 268 | 120.5 | 119.07 | O66 NFTWR | AP_P2-3_PE-500-019B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3369 | 127.79 | 122.73 | AF1-227 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 204550 | 27ORRTANNA | 1 | 115 | 227 | 160 | 119.86 | 118.4 | O66 NFTWR | ME_P1-2_ME-115-068_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 221090 | GLENARM2 | 221098 | C.PIPE12 | 1 | 115 | 232 | 217 | 116.98 | 117.4 | O66 NFTWR | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 235463 | 01TANEY | 1 | 138 | 227/201 | 268 | 119.03 | 117.32 | O66 NFTWR | PEPCO_P1_5055_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 204550 | 27ORRTANNA | 1 | 115 | 227 | 160 | 118.31 | 116.83 | O66 NFTWR | ME_P2-3_ME-115-013B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 204550 | 27ORRTANNA | 1 | 115 | 227 | 160 | 118.17 | 116.68 | O66 NFTWR | ME_P2-3_ME-115-013A_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 221096 | ROCKRGE1 | 221097 | C.PIPE11 | 1 | 115 | 232 | 217 | 116.1 | 115.66 | O66 NFTWR | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 221097 | C.PIPE11 | 221100 | GLENARM1 | 1 | 115 | 232 | 217 | 115.96 | 115.65 | O66 NFTWR | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 204550 | 27ORRTANNA | 1 | 115 | 227 | 160 | 115.98 | 115.22 | O66 NFTWR | ME_P2-3_ME-115-035A_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204539 | 27HUNTRSTN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 282 | 115.48 | 114.75 | O66 NFTWR | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204539 | 27HUNTRSTN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 282 | 115.48 | 114.75 | O66 NFTWR | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 2 | 230 | 233 | 680 | 117.63 | 114.71 | O66 NFTWR | AP_P2-3_PE-500-019C_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 680 | 117.63 | 114.71 | O66 NFTWR | AP_P2-3_PE-500-019C_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204539 | 27HUNTRSTN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 282 | 115.41 | 114.68 | O66 NFTWR | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 221095 | ROCKRGE2 | 221098 | C.PIPE12 | 1 | 115 | 232 | 217 | 114.39 | 114.6 | O66 NFTWR | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 221089 | WINDYED1 | 221090 | GLENARM2 | 1 | 115 | 232 | 216 | 114.12 | 114.55 | O66 NFTWR | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 115.09 | 113.99 | O66 NFTWR | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3369 | 128.23 | 123.16 | AF2-317 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 204550 | 27ORRTANNA | 1 | 115 | 227 | 160 | 114.43 | 113.66 | O66 NFTWR | ME_P2-3_ME-115-035B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 814 | 117.71 | 112.93 | O66 NFTWR | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 113.74 | 112.69 | O66 NFTWR | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 203981 | AD2-062_POI | 235188 | 01GREENE | 1 | 138 | 226/201 | 268 | 117.92 | 112.67 | O66 NFTWR | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 117.59 | 112.62 | O66 NFTWR | PECO_P4_PEACH035_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208393 | FARO DC TIE | 208395 | FARO FF | 1 | 115/69 | 229 | 114 | 114.87 | 111.81 | O66 NFTWR | PL_05_P71_000906_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 221092 | FIVE.FOR | 221096 | ROCKRGE1 | 1 | 115 | 232 | 254 | 111.45 | 111.73 | O66 NFTWR | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 221090 | GLENARM2 | 221098 | C.PIPE12 | 1 | 115 | 232 | 217 | 110.45 | 111.55 | O66 NFTWR | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 112.11 | 111.1 | O66 NFTWR | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.33 | 111 | O66 NFTWR | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.33 | 111 | O66 NFTWR | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200532 | 26ROXBURY | 203981 | AD2-062_POI | 1 | 138 | 226 | 268 | 114.88 | 110.6 | O66 NFTWR | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200532 | 26ROXBURY | 203981 | AD2-062_POI | 1 | 138 | 226 | 268 | 114.88 | 110.6 | O66 NFTWR | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200532 | 26ROXBURY | 203981 | AD2-062_POI | 1 | 138 | 226 | 268 | 114.78 | 110.5 | O66 NFTWR | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3369 | 137.09 | 131.75 | AG2-055 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 114.7 | 110.1 | O66 NFTWR | PECO_P4_PEACH675_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 114.7 | 110.1 | O66 NFTWR | PECO_P7-1_220-0607_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208395 | FARO FF | 208396 | FARO | 1 | 69 | 229 | 240 | 109.14 | 109.96 | O66 NFTWR | PL_05_P71_000906_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 221096 | ROCKRGE1 | 221097 | C.PIPE11 | 1 | 115 | 232 | 217 | 109.59 | 109.91 | O66 NFTWR | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 221097 | C.PIPE11 | 221100 | GLENARM1 | 1 | 115 | 232 | 217 | 109.46 | 109.89 | O66 NFTWR | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 282 | 114.13 | 109.83 | O66 NFTWR | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 282 | 114.13 | 109.83 | O66 NFTWR | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 282 | 114.12 | 109.82 | O66 NFTWR | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 282 | 114.16 | 109.8 | O66 NFTWR | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3369 | 128.68 | 123.6 | ALDENE_AB | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 814 | 111.91 | 108.91 | O66 NFTWR | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 814 | 112.07 | 108.77 | O66 NFTWR | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 814 | 112.07 | 108.77 | O66 NFTWR | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 814 | 112.04 | 108.75 | O66 NFTWR | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 221089 | WINDYED1 | 221090 | GLENARM2 | 1 | 115 | 232 | 216 | 107.55 | 108.68 | O66 NFTWR | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 109.76 | 108.37 | O66 NFTWR | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3198 | 113.53 | 108.36 | O66 NFTWR | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 109.71 | 108.32 | O66 NFTWR | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 221092 | FIVE.FOR | 221095 | ROCKRGE2 | 1 | 115 | 232 | 254 | 108.37 | 108.21 | O66 NFTWR | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 797 | 109.52 | 108.04 | O66 NFTWR | PJM_500_BG_P4_5_CNSTN_15_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 112.32 | 107.66 | O66 NFTWR | PECO_P1-2_220-07_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 112.1 | 107.46 | O66 NFTWR | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 111.82 | 107.29 | O66 NFTWR | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 111.7 | 107.17 | O66 NFTWR | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 111.73 | 107.15 | O66 NFTWR | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 108.03 | 106.81 | O66 NFTWR | AP_P2-2_WP-500-DRT16_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 108.03 | 106.81 | O66 NFTWR | AP_P1-2_WP-500-DRT21_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 108.03 | 106.81 | O66 NFTWR | AP_P2-3_WP-500-465_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 108.03 | 106.81 | O66 NFTWR | AP_P2-3_WP-500-DRT20_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 108.03 | 106.81 | O66 NFTWR | AP_P1-2_WP-500-005A_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 221092 | FIVE.FOR | 221096 | ROCKRGE1 | 1 | 115 | 232 | 254 | 105.89 | 106.61 | O66 NFTWR | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 203981 | AD2-062_POI | 235188 | 01GREENE | 1 | 138 | 226/201 | 268 | 108.46 | 106.51 | O66 NFTWR | PEPCO_P4_PP41_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208393 | FARO DC TIE | 208395 | FARO FF | 2 | 115/69 | 229 | 120 | 109.13 | 106.22 | O66 NFTWR | PL_05_P71_000906_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 282 | 107.65 | 106.04 | O66 NFTWR | PEPCO_P4_PP41_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 797 | 107.4 | 105.98 | O66 NFTWR | BG_P7_GRCTN_CNSTN_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 203981 | AD2-062_POI | 235188 | 01GREENE | 1 | 138 | 226/201 | 268 | 107.72 | 105.79 | O66 NFTWR | AP_P2-3_PE-500-015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 221055 | HARRIS1A | 221058 | DOLFD T1 | 1 | 115 | 232 | 189 | 105.79 | 105.63 | O66 NFTWR | BG_P7_NWEST_GRNITE_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208394 | PPL-BGE TIE | 221092 | FIVE.FOR | 1 | 115 | 229/232 | 247 | 104.36 | 104.98 | O66 NFTWR | PL_05_P71_000906_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 282 | 105.44 | 104.21 | O66 NFTWR | AP_P2-3_PE-500-019B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204538 | 27STRABAN | 204544 | 27LINCOLN | 1 | 115 | 227 | 313 | 107.05 | 103.8 | O66 NFTWR | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204538 | 27STRABAN | 204544 | 27LINCOLN | 1 | 115 | 227 | 313 | 107.05 | 103.8 | O66 NFTWR | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204538 | 27STRABAN | 204544 | 27LINCOLN | 1 | 115 | 227 | 313 | 107.04 | 103.79 | O66 NFTWR | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204538 | 27STRABAN | 204544 | 27LINCOLN | 1 | 115 | 227 | 313 | 107.08 | 103.77 | O66 NFTWR | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208393 | FARO DC TIE | 208395 | FARO FF | 1 | 115/69 | 229 | 114 | 107.09 | 103.37 | O66 NFTWR | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208393 | FARO DC TIE | 208395 | FARO FF | 1 | 115/69 | 229 | 114 | 107.1 | 103.37 | O66 NFTWR | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208393 | FARO DC TIE | 208395 | FARO FF | 1 | 115/69 | 229 | 114 | 107.1 | 103.37 | O66 NFTWR | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208393 | FARO DC TIE | 208395 | FARO FF | 1 | 115/69 | 229 | 114 | 107.09 | 103.36 | O66 NFTWR | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 221092 | FIVE.FOR | 221095 | ROCKRGE2 | 1 | 115 | 232 | 254 | 102.78 | 103.22 | O66 NFTWR | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 282 | 104.75 | 103.18 | O66 NFTWR | ME_P2-3_ME-115-019A-A_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3369 | 127.79 | 122.73 | BIGSKY | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200532 | 26ROXBURY | 203981 | AD2-062_POI | 1 | 138 | 226 | 268 | 108.98 | 102.4 | O66 NFTWR | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200532 | 26ROXBURY | 203981 | AD2-062_POI | 1 | 138 | 226 | 268 | 108.98 | 102.4 | O66 NFTWR | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200532 | 26ROXBURY | 203981 | AD2-062_POI | 1 | 138 | 226 | 268 | 108.98 | 102.4 | O66 NFTWR | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200532 | 26ROXBURY | 203981 | AD2-062_POI | 1 | 138 | 226 | 268 | 109.02 | 102.37 | O66 NFTWR | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200101 | VINCO | 200102 | AA1-076 MAIN | 1 | 500 | 225 | 999 | 104.4 | 101.96 | O66 NFTWR | PL_02_P12_001029_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200101 | VINCO | 200102 | AA1-076 MAIN | 1 | 500 | 225 | 999 | 104.4 | 101.96 | O66 NFTWR | PL_02_P42_001064_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200101 | VINCO | 200102 | AA1-076 MAIN | 1 | 500 | 225 | 999 | 104.4 | 101.96 | O66 NFTWR | PL_02_P42_001063_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200101 | VINCO | 200102 | AA1-076 MAIN | 1 | 500 | 225 | 999 | 102.77 | 101.81 | O66 NFTWR | PN_P2-3_PN-500-DRT33_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200101 | VINCO | 200102 | AA1-076 MAIN | 1 | 500 | 225 | 999 | 102.77 | 101.81 | O66 NFTWR | PN_P2-3_PN-500-DRT33_A_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200101 | VINCO | 200102 | AA1-076 MAIN | 1 | 500 | 225 | 999 | 102.77 | 101.8 | O66 NFTWR | PN_P2-3_PN-500-004-DRT-006_A_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200101 | VINCO | 200102 | AA1-076 MAIN | 1 | 500 | 225 | 999 | 102.77 | 101.8 | O66 NFTWR | PN_P2-3_PN-500-004-DRT-006_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200101 | VINCO | 200102 | AA1-076 MAIN | 1 | 500 | 225 | 999 | 104.22 | 101.78 | O66 NFTWR | 200038 SUSQ 2 24.0 _SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200101 | VINCO | 200102 | AA1-076 MAIN | 1 | 500 | 225 | 999 | 102.77 | 101.7 | O66 NFTWR | AP_P1-2_WP-500-008_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200101 | VINCO | 200102 | AA1-076 MAIN | 1 | 500 | 225 | 999 | 102.77 | 101.7 | O66 NFTWR | AP_P2-3_WP-500-DRT45_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 221056 | HARRIS0A | 221057 | DOLFD T0 | 1 | 115 | 232 | 189 | 101.39 | 101.6 | O66 NFTWR | BG_P7_NWEST_GRNITE_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208395 | FARO FF | 208396 | FARO | 1 | 69 | 229 | 240 | 101.75 | 101.51 | O66 NFTWR | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208395 | FARO FF | 208396 | FARO | 1 | 69 | 229 | 240 | 101.76 | 101.5 | O66 NFTWR | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208395 | FARO FF | 208396 | FARO | 1 | 69 | 229 | 240 | 101.76 | 101.5 | O66 NFTWR | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208395 | FARO FF | 208396 | FARO | 1 | 69 | 229 | 240 | 101.75 | 101.49 | O66 NFTWR | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204529 | 27GERMANTN | 204538 | 27STRABAN | 1 | 115 | 227 | 313 | 103.71 | 101.09 | O66 NFTWR | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204529 | 27GERMANTN | 204538 | 27STRABAN | 1 | 115 | 227 | 313 | 103.71 | 101.09 | O66 NFTWR | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204529 | 27GERMANTN | 204538 | 27STRABAN | 1 | 115 | 227 | 313 | 103.7 | 101.09 | O66 NFTWR | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204529 | 27GERMANTN | 204538 | 27STRABAN | 1 | 115 | 227 | 313 | 103.74 | 101.06 | O66 NFTWR | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204502 | 27JACKSON | 204514 | 27TMI | 1 | 230 | 227 | 659 | 100.77 | 100.47 | O66 NFTWR | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204502 | 27JACKSON | 204514 | 27TMI | 1 | 230 | 227 | 659 | 100.77 | 100.47 | O66 NFTWR | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204502 | 27JACKSON | 204514 | 27TMI | 1 | 230 | 227 | 659 | 100.75 | 100.45 | O66 NFTWR | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204502 | 27JACKSON | 204514 | 27TMI | 1 | 230 | 227 | 659 | 100.8 | 100.44 | O66 NFTWR | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 204529 | 27GERMANTN | 1 | 138/115 | 227 | 345 | 101.61 | 100.33 | O66 NFTWR | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 204529 | 27GERMANTN | 1 | 138/115 | 227 | 345 | 101.61 | 100.33 | O66 NFTWR | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 204529 | 27GERMANTN | 1 | 138/115 | 227 | 345 | 101.6 | 100.32 | O66 NFTWR | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 814 | 103.57 | 100.3 | O66 NFTWR | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 204529 | 27GERMANTN | 1 | 138/115 | 227 | 345 | 101.64 | 100.3 | O66 NFTWR | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 102.74 | 100.07 | O66 NFTWR | DVP_P4-2: 560T571_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3369 | 127.89 | 122.83 | BISHOP | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 118.99 | 118.18 | P28 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 117.61 | 116.84 | P28 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 121.44 | 116.37 | P28 | PECO_P4_PEACH035_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 115.97 | 115.25 | P28 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 119.29 | 114.85 | P28 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 119.29 | 114.85 | P28 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.93 | 114.22 | P28 | PECO_P4_PEACH675_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.93 | 114.22 | P28 | PECO_P7-1_220-0607_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3198 | 119.07 | 113.64 | P28 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3369 | 128.57 | 123.49 | BRUNSWCK_AB | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 113.46 | 112.31 | P28 | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 113.41 | 112.26 | P28 | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 116.55 | 111.78 | P28 | PECO_P1-2_220-07_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 116.42 | 111.76 | P28 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 116.3 | 111.64 | P28 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 116.33 | 111.62 | P28 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 116.31 | 111.56 | P28 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.79 | 110.83 | P28 | AP_P2-3_WP-500-DRT20_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.79 | 110.83 | P28 | AP_P1-2_WP-500-005A_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.79 | 110.83 | P28 | AP_P1-2_WP-500-DRT21_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.79 | 110.83 | P28 | AP_P2-2_WP-500-DRT16_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.79 | 110.83 | P28 | AP_P2-3_WP-500-465_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200677 | 26NO MESHO | 200699 | 26MEHOP 3 | 1 | 115 | 226 | 160 | 96.82 | 101.8 | P28 | PN_P2-3_PN-115-0272-B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200677 | 26NO MESHO | 200699 | 26MEHOP 3 | 1 | 115 | 226 | 160 | 96.82 | 101.57 | P28 | PN_P1-2_PN-115-042_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200677 | 26NO MESHO | 200698 | 26MEHOOPNY | 2 | 115 | 226 | 160 | 97.42 | 101.43 | P28 | PN_P2-3_PN-115-43B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200677 | 26NO MESHO | 200698 | 26MEHOOPNY | 2 | 115 | 226 | 160 | 97.42 | 101.43 | P28 | PN_P1-2_PN-115-041_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200677 | 26NO MESHO | 200698 | 26MEHOOPNY | 2 | 115 | 226 | 160 | 96.82 | 101.05 | P28 | PN_P2-3_PN-115-0272-18_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200677 | 26NO MESHO | 200699 | 26MEHOP 3 | 1 | 115 | 226 | 160 | 96.82 | 101.05 | P28 | PN_P2-3_PN-115-0272-14_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3369 | 128.02 | 122.95 | CAMPGROVE;RU | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 118.51 | 117.66 | P59 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 117.14 | 116.34 | P59 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 121.05 | 115.98 | P59 | PECO_P4_PEACH035_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 115.51 | 114.74 | P59 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.84 | 114.41 | P59 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.84 | 114.41 | P59 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.47 | 113.77 | P59 | PECO_P7-1_220-0607_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.47 | 113.77 | P59 | PECO_P4_PEACH675_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3198 | 118.47 | 113.08 | P59 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3369 | 127.65 | 122.59 | CAYUGA | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 113.01 | 111.83 | P59 | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 112.96 | 111.78 | P59 | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 116.09 | 111.33 | P59 | PECO_P1-2_220-07_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.92 | 111.28 | P59 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.81 | 111.16 | P59 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.84 | 111.14 | P59 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.85 | 111.11 | P59 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.3 | 110.31 | P59 | AP_P2-3_WP-500-DRT20_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.3 | 110.31 | P59 | AP_P1-2_WP-500-005A_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.3 | 110.31 | P59 | AP_P1-2_WP-500-DRT21_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.3 | 110.31 | P59 | AP_P2-3_WP-500-465_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.3 | 110.31 | P59 | AP_P2-2_WP-500-DRT16_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3369 | 128.66 | 123.57 | D05 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 121.1 | 116.04 | PROVIDENC;RU | PECO_P4_PEACH035_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.88 | 114.46 | PROVIDENC;RU | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.88 | 114.46 | PROVIDENC;RU | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.52 | 113.83 | PROVIDENC;RU | PECO_P4_PEACH675_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.52 | 113.83 | PROVIDENC;RU | PECO_P7-1_220-0607_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3198 | 118.54 | 113.14 | PROVIDENC;RU | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 116.14 | 111.38 | PROVIDENC;RU | PECO_P1-2_220-07_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.98 | 111.33 | PROVIDENC;RU | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.86 | 111.22 | PROVIDENC;RU | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.89 | 111.2 | PROVIDENC;RU | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.9 | 111.16 | PROVIDENC;RU | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 607 | 165.87 | 164.41 | Q01/Q03 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 607 | 166.91 | 164.41 | Q01/Q03 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 607 | 166.16 | 164.4 | Q01/Q03 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 607 | 167.21 | 164.4 | Q01/Q03 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 607 | 167.13 | 164.33 | Q01/Q03 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 607 | 167.13 | 164.33 | Q01/Q03 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 607 | 166.09 | 164.33 | Q01/Q03 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 607 | 166.09 | 164.33 | Q01/Q03 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 628 | 157.93 | 156.73 | Q01/Q03 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 628 | 158.21 | 156.72 | Q01/Q03 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 628 | 158.14 | 156.65 | Q01/Q03 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 628 | 158.14 | 156.65 | Q01/Q03 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 235463 | 01TANEY | 1 | 138 | 227/201 | 268 | 158.85 | 155.07 | Q01/Q03 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 235463 | 01TANEY | 1 | 138 | 227/201 | 268 | 158.85 | 155.07 | Q01/Q03 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 235463 | 01TANEY | 1 | 138 | 227/201 | 268 | 158.78 | 154.99 | Q01/Q03 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 628 | 155.22 | 154.44 | Q01/Q03 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 628 | 155.51 | 154.42 | Q01/Q03 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 628 | 155.44 | 154.35 | Q01/Q03 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 628 | 155.44 | 154.35 | Q01/Q03 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 607 | 152.13 | 150.1 | Q01/Q03 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 607 | 153.17 | 150.1 | Q01/Q03 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 628 | 144.65 | 142.88 | Q01/Q03 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 628 | 141.94 | 140.57 | Q01/Q03 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 680 | 140.97 | 138.07 | Q01/Q03 | PEPCO_P4_PP19_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 282 | 137.85 | 137.46 | Q01/Q03 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 282 | 137.85 | 137.46 | Q01/Q03 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 282 | 137.79 | 137.38 | Q01/Q03 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 797 | 139.76 | 135.22 | Q01/Q03 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 797 | 139.99 | 135.14 | Q01/Q03 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 797 | 139.99 | 135.14 | Q01/Q03 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 797 | 139.96 | 135.12 | Q01/Q03 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 135.83 | 132.75 | Q01/Q03 | AP_P1-2_PE-500-407T_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 135.83 | 132.75 | Q01/Q03 | DVP_P1-2: LN 514_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 135.83 | 132.73 | Q01/Q03 | DVP_P4-2: 51482_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204538 | 27STRABAN | 204544 | 27LINCOLN | 1 | 115 | 227 | 313 | 131.1 | 131.9 | Q01/Q03 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204538 | 27STRABAN | 204544 | 27LINCOLN | 1 | 115 | 227 | 313 | 131.1 | 131.9 | Q01/Q03 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204538 | 27STRABAN | 204544 | 27LINCOLN | 1 | 115 | 227 | 313 | 131.04 | 131.83 | Q01/Q03 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204529 | 27GERMANTN | 204538 | 27STRABAN | 1 | 115 | 227 | 313 | 127.72 | 129.17 | Q01/Q03 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204529 | 27GERMANTN | 204538 | 27STRABAN | 1 | 115 | 227 | 313 | 127.72 | 129.17 | Q01/Q03 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204529 | 27GERMANTN | 204538 | 27STRABAN | 1 | 115 | 227 | 313 | 127.66 | 129.1 | Q01/Q03 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 130.7 | 127.61 | Q01/Q03 | AP_P2-3_PE-500-019C_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 797 | 131.65 | 126.88 | Q01/Q03 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 204529 | 27GERMANTN | 1 | 138/115 | 227 | 345 | 123.4 | 125.99 | Q01/Q03 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 204529 | 27GERMANTN | 1 | 138/115 | 227 | 345 | 123.4 | 125.99 | Q01/Q03 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 204529 | 27GERMANTN | 1 | 138/115 | 227 | 345 | 123.34 | 125.93 | Q01/Q03 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 814 | 129.93 | 125.45 | Q01/Q03 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 814 | 130.37 | 125.28 | Q01/Q03 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 814 | 130.37 | 125.28 | Q01/Q03 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 814 | 130.35 | 125.27 | Q01/Q03 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3369 | 128.66 | 123.57 | DC1 NUG | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 117.32 | 116.38 | Q01/Q03 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 814 | 121.08 | 116.21 | Q01/Q03 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 115.96 | 115.06 | Q01/Q03 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 119.6 | 114.58 | Q01/Q03 | PECO_P4_PEACH035_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 114.32 | 113.47 | Q01/Q03 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 117.57 | 113.18 | Q01/Q03 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 117.57 | 113.18 | Q01/Q03 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 117.09 | 112.43 | Q01/Q03 | PECO_P7-1_220-0607_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 117.09 | 112.43 | Q01/Q03 | PECO_P4_PEACH675_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 814 | 114.99 | 111.99 | Q01/Q03 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 814 | 115.21 | 111.9 | Q01/Q03 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 814 | 115.21 | 111.9 | Q01/Q03 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 814 | 115.19 | 111.89 | Q01/Q03 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3198 | 116.83 | 111.5 | Q01/Q03 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3369 | 128.66 | 123.57 | DC2 NUG | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.87 | 110.61 | Q01/Q03 | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.82 | 110.56 | Q01/Q03 | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 797 | 111.84 | 110.35 | Q01/Q03 | PJM_500_BG_P4_5_CNSTN_15_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 114.71 | 109.99 | Q01/Q03 | PECO_P1-2_220-07_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 114.44 | 109.84 | Q01/Q03 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 114.48 | 109.78 | Q01/Q03 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 114.33 | 109.73 | Q01/Q03 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 114.36 | 109.71 | Q01/Q03 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 110.12 | 109.04 | Q01/Q03 | AP_P1-2_WP-500-DRT21_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 110.12 | 109.04 | Q01/Q03 | AP_P1-2_WP-500-005A_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 110.12 | 109.04 | Q01/Q03 | AP_P2-2_WP-500-DRT16_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 110.12 | 109.04 | Q01/Q03 | AP_P2-3_WP-500-DRT20_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 110.12 | 109.04 | Q01/Q03 | AP_P2-3_WP-500-465_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 797 | 109.11 | 107.7 | Q01/Q03 | BG_P7_GRCTN_CNSTN_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204538 | 27STRABAN | 204544 | 27LINCOLN | 1 | 115 | 227 | 313 | 109.57 | 106.29 | Q01/Q03 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204529 | 27GERMANTN | 204538 | 27STRABAN | 1 | 115 | 227 | 313 | 106.19 | 103.59 | Q01/Q03 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 814 | 106.84 | 103.52 | Q01/Q03 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204502 | 27JACKSON | 204514 | 27TMI | 1 | 230 | 227 | 659 | 103.47 | 103.38 | Q01/Q03 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204502 | 27JACKSON | 204514 | 27TMI | 1 | 230 | 227 | 659 | 103.47 | 103.38 | Q01/Q03 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204502 | 27JACKSON | 204514 | 27TMI | 1 | 230 | 227 | 659 | 103.52 | 103.36 | Q01/Q03 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204502 | 27JACKSON | 204514 | 27TMI | 1 | 230 | 227 | 659 | 103.45 | 103.36 | Q01/Q03 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 204529 | 27GERMANTN | 1 | 138/115 | 227 | 345 | 103.86 | 102.6 | Q01/Q03 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204538 | 27STRABAN | 204544 | 27LINCOLN | 1 | 115 | 227 | 313 | 102.71 | 102.29 | Q01/Q03 | PEPCO_P4_PP41_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 104.34 | 101.67 | Q01/Q03 | DVP_P4-2: 560T571_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 104.18 | 101.53 | Q01/Q03 | DVP_P4-2: H2T560_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 104.18 | 101.51 | Q01/Q03 | DVP_P4-2: H1T560_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 104.03 | 101.36 | Q01/Q03 | PEPCO_P1_5070_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3369 | 128.15 | 123.07 | ECOGROVE ;U1 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 119.01 | 118.2 | Q27 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 117.64 | 116.87 | Q27 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 121.5 | 116.42 | Q27 | PECO_P4_PEACH035_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 116 | 115.27 | Q27 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 119.33 | 114.89 | Q27 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 119.33 | 114.89 | Q27 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 119 | 114.29 | Q27 | PECO_P7-1_220-0607_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 119 | 114.29 | Q27 | PECO_P4_PEACH675_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3198 | 119.14 | 113.71 | Q27 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3369 | 128.91 | 123.81 | FAIRLAWN_AB | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 113.49 | 112.33 | Q27 | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 113.44 | 112.29 | Q27 | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 116.62 | 111.84 | Q27 | PECO_P1-2_220-07_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 116.49 | 111.82 | Q27 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 116.37 | 111.71 | Q27 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 116.4 | 111.69 | Q27 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 116.38 | 111.62 | Q27 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.81 | 110.85 | Q27 | AP_P1-2_WP-500-005A_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.81 | 110.85 | Q27 | AP_P2-3_WP-500-DRT20_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.81 | 110.85 | Q27 | AP_P2-2_WP-500-DRT16_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.81 | 110.85 | Q27 | AP_P1-2_WP-500-DRT21_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.81 | 110.85 | Q27 | AP_P2-3_WP-500-465_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 607 | 168.94 | 166.24 | Q57 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 607 | 167.88 | 166.24 | Q57 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 607 | 168.62 | 166.23 | Q57 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 607 | 167.55 | 166.23 | Q57 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 607 | 168.87 | 166.17 | Q57 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 607 | 168.87 | 166.17 | Q57 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 607 | 167.8 | 166.17 | Q57 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 607 | 167.8 | 166.17 | Q57 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 628 | 159.87 | 158.5 | Q57 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 628 | 159.55 | 158.49 | Q57 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 628 | 159.79 | 158.43 | Q57 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 628 | 159.79 | 158.43 | Q57 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 628 | 157.16 | 156.21 | Q57 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 628 | 156.85 | 156.2 | Q57 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 628 | 157.09 | 156.14 | Q57 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 628 | 157.09 | 156.14 | Q57 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3369 | 127.6 | 122.54 | G07 NFTWR | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 118.25 | 117.39 | Q57 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 116.88 | 116.06 | Q57 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 120.74 | 115.68 | Q57 | PECO_P4_PEACH035_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 115.25 | 114.46 | Q57 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.56 | 114.14 | Q57 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.56 | 114.14 | Q57 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.17 | 113.48 | Q57 | PECO_P4_PEACH675_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.17 | 113.48 | Q57 | PECO_P7-1_220-0607_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3198 | 118.12 | 112.74 | Q57 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3369 | 128.62 | 123.53 | GLOUCSTR_26 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 112.76 | 111.56 | Q57 | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 112.71 | 111.52 | Q57 | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.8 | 111.04 | Q57 | PECO_P1-2_220-07_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.6 | 110.97 | Q57 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.49 | 110.85 | Q57 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.52 | 110.83 | Q57 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.56 | 110.83 | Q57 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.06 | 110.04 | Q57 | AP_P2-3_WP-500-DRT20_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.06 | 110.04 | Q57 | AP_P2-2_WP-500-DRT16_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.06 | 110.04 | Q57 | AP_P1-2_WP-500-DRT21_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.06 | 110.04 | Q57 | AP_P1-2_WP-500-005A_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.06 | 110.04 | Q57 | AP_P2-3_WP-500-465_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 105.24 | 102.54 | Q57 | DVP_P4-2: 560T571_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 105.07 | 102.4 | Q57 | DVP_P4-2: H2T560_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 105.07 | 102.39 | Q57 | DVP_P4-2: H1T560_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 104.93 | 102.24 | Q57 | PEPCO_P1_5070_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3369 | 127.62 | 122.57 | GR RIDGE | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 118.44 | 117.58 | R49 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 117.06 | 116.26 | R49 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 120.94 | 115.88 | R49 | PECO_P4_PEACH035_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 115.43 | 114.66 | R49 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.75 | 114.33 | R49 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.75 | 114.33 | R49 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.38 | 113.68 | R49 | PECO_P7-1_220-0607_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.38 | 113.68 | R49 | PECO_P4_PEACH675_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3198 | 118.36 | 112.97 | R49 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3369 | 128.2 | 123.12 | GSG-6 ;RU | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 112.94 | 111.75 | R49 | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 112.89 | 111.71 | R49 | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 116 | 111.24 | R49 | PECO_P1-2_220-07_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.82 | 111.18 | R49 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.7 | 111.06 | R49 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.73 | 111.04 | R49 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.76 | 111.02 | R49 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.24 | 110.24 | R49 | AP_P2-2_WP-500-DRT16_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.24 | 110.24 | R49 | AP_P2-3_WP-500-465_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.24 | 110.24 | R49 | AP_P2-3_WP-500-DRT20_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.24 | 110.24 | R49 | AP_P1-2_WP-500-005A_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.24 | 110.24 | R49 | AP_P1-2_WP-500-DRT21_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 607 | 168.62 | 165.89 | R60 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 607 | 167.56 | 165.89 | R60 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 607 | 168.3 | 165.89 | R60 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 607 | 167.23 | 165.89 | R60 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 607 | 168.54 | 165.82 | R60 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 607 | 168.54 | 165.82 | R60 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 607 | 167.48 | 165.82 | R60 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 607 | 167.48 | 165.82 | R60 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 628 | 159.56 | 158.17 | R60 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 628 | 159.25 | 158.16 | R60 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 628 | 159.48 | 158.1 | R60 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 628 | 159.48 | 158.1 | R60 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 628 | 156.85 | 155.87 | R60 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 628 | 156.54 | 155.87 | R60 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 628 | 156.78 | 155.8 | R60 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 628 | 156.78 | 155.8 | R60 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 607 | 153.47 | 151.36 | R60 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 607 | 154.53 | 151.36 | R60 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 628 | 145.94 | 144.11 | R60 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 628 | 143.24 | 141.79 | R60 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 797 | 140.65 | 136.1 | R60 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 797 | 140.9 | 136.04 | R60 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 797 | 140.9 | 136.04 | R60 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 797 | 140.88 | 136.02 | R60 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 136.47 | 133.4 | R60 | AP_P1-2_PE-500-407T_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 136.47 | 133.4 | R60 | DVP_P1-2: LN 514_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 136.47 | 133.38 | R60 | DVP_P4-2: 51482_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 131.34 | 128.25 | R60 | AP_P2-3_PE-500-019C_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 797 | 132.53 | 127.75 | R60 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 814 | 130.87 | 126.37 | R60 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 814 | 131.35 | 126.24 | R60 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 814 | 131.35 | 126.24 | R60 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 814 | 131.33 | 126.23 | R60 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3369 | 128.14 | 123.06 | K28 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 118.1 | 117.22 | R60 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 814 | 122.03 | 117.11 | R60 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 116.73 | 115.89 | R60 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 120.52 | 115.47 | R60 | PECO_P4_PEACH035_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 115.1 | 114.3 | R60 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.39 | 113.97 | R60 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.39 | 113.97 | R60 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 117.97 | 113.29 | R60 | PECO_P4_PEACH675_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 117.97 | 113.29 | R60 | PECO_P7-1_220-0607_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 814 | 115.81 | 112.82 | R60 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 814 | 116.06 | 112.76 | R60 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 814 | 116.06 | 112.76 | R60 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 814 | 116.04 | 112.74 | R60 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3198 | 117.88 | 112.51 | R60 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3369 | 127.95 | 122.89 | KELLY CRK;1U | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 112.62 | 111.41 | R60 | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 112.57 | 111.36 | R60 | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.59 | 110.84 | R60 | PECO_P1-2_220-07_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.39 | 110.76 | R60 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.27 | 110.64 | R60 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.35 | 110.63 | R60 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.3 | 110.62 | R60 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 110.9 | 109.88 | R60 | AP_P1-2_WP-500-DRT21_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 110.9 | 109.88 | R60 | AP_P2-2_WP-500-DRT16_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 110.9 | 109.88 | R60 | AP_P2-3_WP-500-DRT20_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 110.9 | 109.88 | R60 | AP_P2-3_WP-500-465_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 110.9 | 109.88 | R60 | AP_P1-2_WP-500-005A_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 814 | 107.66 | 104.34 | R60 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 105.12 | 102.42 | R60 | DVP_P4-2: 560T571_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 104.95 | 102.29 | R60 | DVP_P4-2: H2T560_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 104.95 | 102.27 | R60 | DVP_P4-2: H1T560_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 104.81 | 102.12 | R60 | PEPCO_P1_5070_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 801 | 102.71 | 100.1 | R60 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 801 | 102.71 | 100.1 | R60 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 801 | 102.68 | 100.08 | R60 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3369 | 128 | 122.93 | M24 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 121.42 | 116.35 | RUTGERS | PECO_P4_PEACH035_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 119.18 | 114.74 | RUTGERS | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 119.18 | 114.74 | RUTGERS | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.84 | 114.14 | RUTGERS | PECO_P4_PEACH675_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.84 | 114.14 | RUTGERS | PECO_P7-1_220-0607_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3198 | 118.94 | 113.52 | RUTGERS | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 116.46 | 111.69 | RUTGERS | PECO_P1-2_220-07_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 116.33 | 111.67 | RUTGERS | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 116.21 | 111.55 | RUTGERS | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 116.24 | 111.53 | RUTGERS | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 116.22 | 111.47 | RUTGERS | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3369 | 128.21 | 123.13 | MENDOTA H;RU | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 118.33 | 117.47 | S06 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 116.96 | 116.14 | S06 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 120.82 | 115.77 | S06 | PECO_P4_PEACH035_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 115.33 | 114.55 | S06 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.64 | 114.22 | S06 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.64 | 114.22 | S06 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.26 | 113.57 | S06 | PECO_P7-1_220-0607_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.26 | 113.57 | S06 | PECO_P4_PEACH675_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3198 | 118.22 | 112.83 | S06 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3369 | 127.9 | 122.83 | MINONK ;1U | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 112.84 | 111.64 | S06 | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 112.79 | 111.6 | S06 | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.88 | 111.12 | S06 | PECO_P1-2_220-07_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.69 | 111.05 | S06 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.58 | 110.94 | S06 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.61 | 110.92 | S06 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.64 | 110.91 | S06 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.13 | 110.13 | S06 | AP_P2-3_WP-500-DRT20_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.13 | 110.13 | S06 | AP_P1-2_WP-500-DRT21_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.13 | 110.13 | S06 | AP_P2-2_WP-500-DRT16_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.13 | 110.13 | S06 | AP_P1-2_WP-500-005A_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.13 | 110.13 | S06 | AP_P2-3_WP-500-465_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3369 | 127.77 | 122.7 | O09 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 121.1 | 116.04 | S14 | PECO_P4_PEACH035_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.88 | 114.45 | S14 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.88 | 114.45 | S14 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.52 | 113.82 | S14 | PECO_P4_PEACH675_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.52 | 113.82 | S14 | PECO_P7-1_220-0607_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3198 | 118.53 | 113.13 | S14 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 116.14 | 111.38 | S14 | PECO_P1-2_220-07_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.98 | 111.33 | S14 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.86 | 111.21 | S14 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.89 | 111.19 | S14 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.9 | 111.16 | S14 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.34 | 110.35 | S14 | AP_P2-3_WP-500-DRT20_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.34 | 110.35 | S14 | AP_P2-3_WP-500-465_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.34 | 110.35 | S14 | AP_P2-2_WP-500-DRT16_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.34 | 110.35 | S14 | AP_P1-2_WP-500-DRT21_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 108.85 | 107.77 | S14 | AP_P2-3_PE-500-014_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 108.85 | 107.77 | S14 | AP_P2-3_WP-500-DRT19_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 108.85 | 107.77 | S14 | AP_P1-2_WP-500-006_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 108.85 | 107.77 | S14 | AP_P1-2_PE-500-004_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 108.85 | 107.77 | S14 | AP_P2-3_WP-500-466_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 103.95 | 102.59 | S14 | PN_P2-3_PN-138-121T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3369 | 127.83 | 122.76 | O29 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 118.37 | 117.51 | S36 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 117 | 116.19 | S36 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 120.87 | 115.82 | S36 | PECO_P4_PEACH035_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 115.37 | 114.59 | S36 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.68 | 114.26 | S36 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.68 | 114.26 | S36 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.3 | 113.61 | S36 | PECO_P7-1_220-0607_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.3 | 113.61 | S36 | PECO_P4_PEACH675_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3198 | 118.27 | 112.89 | S36 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3369 | 123.65 | 118.71 | O66 NFTWR | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 112.88 | 111.68 | S36 | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 112.83 | 111.64 | S36 | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.92 | 111.17 | S36 | PECO_P1-2_220-07_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.74 | 111.1 | S36 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.63 | 110.99 | S36 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.65 | 110.97 | S36 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.68 | 110.95 | S36 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.17 | 110.17 | S36 | AP_P1-2_WP-500-DRT21_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.17 | 110.17 | S36 | AP_P2-2_WP-500-DRT16_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.17 | 110.17 | S36 | AP_P2-3_WP-500-DRT20_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.17 | 110.17 | S36 | AP_P2-3_WP-500-465_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.17 | 110.17 | S36 | AP_P1-2_WP-500-005A_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3369 | 128.7 | 123.61 | P28 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 118.48 | 117.63 | S71 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 117.11 | 116.3 | S71 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 121 | 115.94 | S71 | PECO_P4_PEACH035_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 115.48 | 114.71 | S71 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.8 | 114.38 | S71 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.8 | 114.38 | S71 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.43 | 113.73 | S71 | PECO_P7-1_220-0607_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.43 | 113.73 | S71 | PECO_P4_PEACH675_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3198 | 118.43 | 113.03 | S71 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3369 | 128.15 | 123.08 | P59 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 112.98 | 111.8 | S71 | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 112.93 | 111.75 | S71 | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 116.05 | 111.29 | S71 | PECO_P1-2_220-07_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.88 | 111.23 | S71 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.76 | 111.12 | S71 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.79 | 111.1 | S71 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.81 | 111.07 | S71 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.28 | 110.29 | S71 | AP_P2-3_WP-500-465_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.28 | 110.29 | S71 | AP_P2-3_WP-500-DRT20_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.28 | 110.29 | S71 | AP_P1-2_WP-500-DRT21_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.28 | 110.29 | S71 | AP_P1-2_WP-500-005A_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.28 | 110.29 | S71 | AP_P2-2_WP-500-DRT16_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3369 | 128.21 | 123.14 | PROVIDENC;RU | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 118.89 | 118.07 | SEWAREN_IM | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 117.51 | 116.74 | SEWAREN_IM | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 121.47 | 116.4 | SEWAREN_IM | PECO_P4_PEACH035_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 115.88 | 115.14 | SEWAREN_IM | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 119.23 | 114.8 | SEWAREN_IM | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 119.23 | 114.8 | SEWAREN_IM | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.9 | 114.19 | SEWAREN_IM | PECO_P7-1_220-0607_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.9 | 114.19 | SEWAREN_IM | PECO_P4_PEACH675_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3198 | 119.01 | 113.59 | SEWAREN_IM | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3369 | 126.52 | 121.49 | Q01/Q03 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 113.37 | 112.21 | SEWAREN_IM | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 113.32 | 112.17 | SEWAREN_IM | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 116.52 | 111.75 | SEWAREN_IM | PECO_P1-2_220-07_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 116.39 | 111.73 | SEWAREN_IM | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 116.27 | 111.61 | SEWAREN_IM | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 116.3 | 111.59 | SEWAREN_IM | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 116.28 | 111.53 | SEWAREN_IM | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.69 | 110.72 | SEWAREN_IM | AP_P1-2_WP-500-005A_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.69 | 110.72 | SEWAREN_IM | AP_P2-3_WP-500-465_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.69 | 110.72 | SEWAREN_IM | AP_P1-2_WP-500-DRT21_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.69 | 110.72 | SEWAREN_IM | AP_P2-2_WP-500-DRT16_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.69 | 110.72 | SEWAREN_IM | AP_P2-3_WP-500-DRT20_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3369 | 128.77 | 123.68 | Q27 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 118.33 | 117.47 | T126 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 116.96 | 116.14 | T126 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 120.82 | 115.77 | T126 | PECO_P4_PEACH035_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 115.33 | 114.55 | T126 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.64 | 114.22 | T126 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.64 | 114.22 | T126 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.26 | 113.57 | T126 | PECO_P7-1_220-0607_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.26 | 113.57 | T126 | PECO_P4_PEACH675_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3198 | 118.22 | 112.83 | T126 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3369 | 127.8 | 122.73 | Q57 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 112.84 | 111.64 | T126 | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 112.79 | 111.6 | T126 | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.88 | 111.12 | T126 | PECO_P1-2_220-07_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.69 | 111.05 | T126 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.58 | 110.94 | T126 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.61 | 110.92 | T126 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.64 | 110.91 | T126 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.13 | 110.13 | T126 | AP_P2-3_WP-500-DRT20_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.13 | 110.13 | T126 | AP_P1-2_WP-500-DRT21_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.13 | 110.13 | T126 | AP_P2-2_WP-500-DRT16_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.13 | 110.13 | T126 | AP_P1-2_WP-500-005A_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.13 | 110.13 | T126 | AP_P2-3_WP-500-465_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3369 | 128.03 | 122.96 | R49 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 118.33 | 117.47 | T127 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 116.96 | 116.15 | T127 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 120.83 | 115.77 | T127 | PECO_P4_PEACH035_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 115.33 | 114.55 | T127 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.65 | 114.22 | T127 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.65 | 114.22 | T127 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.26 | 113.57 | T127 | PECO_P7-1_220-0607_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.26 | 113.57 | T127 | PECO_P4_PEACH675_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3198 | 118.22 | 112.84 | T127 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3369 | 127.56 | 122.5 | R60 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 112.84 | 111.65 | T127 | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 112.79 | 111.6 | T127 | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.88 | 111.13 | T127 | PECO_P1-2_220-07_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.7 | 111.06 | T127 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.58 | 110.94 | T127 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.61 | 110.92 | T127 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.64 | 110.91 | T127 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.14 | 110.13 | T127 | AP_P2-3_WP-500-DRT20_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.14 | 110.13 | T127 | AP_P1-2_WP-500-DRT21_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.14 | 110.13 | T127 | AP_P2-2_WP-500-DRT16_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.14 | 110.13 | T127 | AP_P1-2_WP-500-005A_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.14 | 110.13 | T127 | AP_P2-3_WP-500-465_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3369 | 128.59 | 123.5 | RUTGERS | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 118.4 | 117.54 | T157 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 117.03 | 116.22 | T157 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 120.99 | 115.93 | T157 | PECO_P4_PEACH035_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 115.39 | 114.62 | T157 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.75 | 114.32 | T157 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.75 | 114.32 | T157 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.4 | 113.71 | T157 | PECO_P4_PEACH675_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.4 | 113.71 | T157 | PECO_P7-1_220-0607_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3198 | 118.39 | 113 | T157 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3369 | 127.9 | 122.83 | S06 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 112.9 | 111.71 | T157 | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 112.85 | 111.67 | T157 | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 116.02 | 111.26 | T157 | PECO_P1-2_220-07_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.85 | 111.2 | T157 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.73 | 111.09 | T157 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.76 | 111.07 | T157 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.78 | 111.05 | T157 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.2 | 110.19 | T157 | AP_P2-3_WP-500-DRT20_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.2 | 110.19 | T157 | AP_P1-2_WP-500-005A_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.2 | 110.19 | T157 | AP_P2-2_WP-500-DRT16_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.2 | 110.19 | T157 | AP_P1-2_WP-500-DRT21_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.2 | 110.19 | T157 | AP_P2-3_WP-500-465_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 607 | 167.68 | 166.03 | TOP CROP | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 607 | 168.75 | 166.03 | TOP CROP | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 607 | 168.42 | 166.02 | TOP CROP | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 607 | 167.36 | 166.02 | TOP CROP | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 607 | 168.67 | 165.95 | TOP CROP | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 607 | 168.67 | 165.95 | TOP CROP | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 607 | 167.6 | 165.95 | TOP CROP | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 607 | 167.6 | 165.95 | TOP CROP | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 628 | 159.68 | 158.29 | TOP CROP | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 628 | 159.37 | 158.29 | TOP CROP | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 628 | 159.6 | 158.22 | TOP CROP | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 628 | 159.6 | 158.22 | TOP CROP | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 628 | 156.97 | 156 | TOP CROP | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 628 | 156.66 | 155.99 | TOP CROP | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 628 | 156.9 | 155.93 | TOP CROP | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 628 | 156.9 | 155.93 | TOP CROP | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 607 | 153.59 | 151.48 | TOP CROP | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 607 | 154.65 | 151.48 | TOP CROP | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 628 | 146.06 | 144.22 | TOP CROP | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 628 | 143.35 | 141.91 | TOP CROP | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 136.44 | 133.38 | TOP CROP | DVP_P1-2: LN 514_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 136.44 | 133.38 | TOP CROP | AP_P1-2_PE-500-407T_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 136.44 | 133.36 | TOP CROP | DVP_P4-2: 51482_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 131.32 | 128.24 | TOP CROP | AP_P2-3_PE-500-019C_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 814 | 130.93 | 126.44 | TOP CROP | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 814 | 131.42 | 126.31 | TOP CROP | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 814 | 131.42 | 126.31 | TOP CROP | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 814 | 131.41 | 126.3 | TOP CROP | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3369 | 128.21 | 123.13 | S14 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 118.15 | 117.27 | TOP CROP | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 814 | 122.1 | 117.18 | TOP CROP | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 116.78 | 115.95 | TOP CROP | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 120.61 | 115.56 | TOP CROP | PECO_P4_PEACH035_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 115.14 | 114.35 | TOP CROP | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.45 | 114.03 | TOP CROP | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.45 | 114.03 | TOP CROP | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.05 | 113.36 | TOP CROP | PECO_P4_PEACH675_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.05 | 113.36 | TOP CROP | PECO_P7-1_220-0607_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3198 | 117.97 | 112.6 | TOP CROP | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3369 | 127.95 | 122.88 | S36 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 112.66 | 111.46 | TOP CROP | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 112.61 | 111.41 | TOP CROP | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.67 | 110.92 | TOP CROP | PECO_P1-2_220-07_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.47 | 110.84 | TOP CROP | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.35 | 110.72 | TOP CROP | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.43 | 110.71 | TOP CROP | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.38 | 110.7 | TOP CROP | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 110.95 | 109.93 | TOP CROP | AP_P1-2_WP-500-DRT21_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 110.95 | 109.93 | TOP CROP | AP_P1-2_WP-500-005A_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 110.95 | 109.93 | TOP CROP | AP_P2-3_WP-500-465_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 110.95 | 109.93 | TOP CROP | AP_P2-3_WP-500-DRT20_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 110.95 | 109.93 | TOP CROP | AP_P2-2_WP-500-DRT16_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 105.14 | 102.44 | TOP CROP | DVP_P4-2: 560T571_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 104.97 | 102.31 | TOP CROP | DVP_P4-2: H2T560_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 104.97 | 102.29 | TOP CROP | DVP_P4-2: H1T560_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 104.83 | 102.14 | TOP CROP | PEPCO_P1_5070_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3369 | 128.1 | 123.03 | S71 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 118.52 | 117.67 | TR3_G114 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 117.15 | 116.35 | TR3_G114 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 121.05 | 115.99 | TR3_G114 | PECO_P4_PEACH035_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 115.52 | 114.75 | TR3_G114 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.84 | 114.42 | TR3_G114 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.84 | 114.42 | TR3_G114 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.48 | 113.78 | TR3_G114 | PECO_P7-1_220-0607_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.48 | 113.78 | TR3_G114 | PECO_P4_PEACH675_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3198 | 118.48 | 113.08 | TR3_G114 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3369 | 128.66 | 123.57 | SEWAREN_IM | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 113.02 | 111.84 | TR3_G114 | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 112.97 | 111.79 | TR3_G114 | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 116.1 | 111.34 | TR3_G114 | PECO_P1-2_220-07_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.93 | 111.28 | TR3_G114 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.81 | 111.17 | TR3_G114 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.84 | 111.15 | TR3_G114 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.86 | 111.12 | TR3_G114 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.33 | 110.33 | TR3_G114 | AP_P1-2_WP-500-DRT21_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.33 | 110.33 | TR3_G114 | AP_P2-3_WP-500-DRT20_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.33 | 110.33 | TR3_G114 | AP_P2-3_WP-500-465_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.33 | 110.33 | TR3_G114 | AP_P2-2_WP-500-DRT16_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.33 | 110.33 | TR3_G114 | AP_P1-2_WP-500-005A_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 607 | 168.41 | 165.67 | TWINGROVE | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 607 | 167.35 | 165.67 | TWINGROVE | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 607 | 168.1 | 165.67 | TWINGROVE | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 607 | 167.04 | 165.67 | TWINGROVE | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 607 | 168.34 | 165.6 | TWINGROVE | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 607 | 168.34 | 165.6 | TWINGROVE | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 607 | 167.27 | 165.6 | TWINGROVE | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 607 | 167.27 | 165.6 | TWINGROVE | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 628 | 159.36 | 157.95 | TWINGROVE | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 628 | 159.06 | 157.95 | TWINGROVE | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 628 | 159.29 | 157.88 | TWINGROVE | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 628 | 159.29 | 157.88 | TWINGROVE | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 628 | 156.66 | 155.66 | TWINGROVE | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 628 | 156.35 | 155.66 | TWINGROVE | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 628 | 156.58 | 155.59 | TWINGROVE | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 628 | 156.58 | 155.59 | TWINGROVE | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 607 | 153.27 | 151.3 | TWINGROVE | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 607 | 154.33 | 151.29 | TWINGROVE | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 628 | 145.75 | 144.04 | TWINGROVE | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 628 | 143.05 | 141.73 | TWINGROVE | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 797 | 140.5 | 135.95 | TWINGROVE | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 797 | 140.75 | 135.89 | TWINGROVE | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 797 | 140.75 | 135.89 | TWINGROVE | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 797 | 140.73 | 135.87 | TWINGROVE | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 136.29 | 133.28 | TWINGROVE | DVP_P4-2: 51482_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 136.29 | 133.22 | TWINGROVE | DVP_P1-2: LN 514_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 136.29 | 133.22 | TWINGROVE | AP_P1-2_PE-500-407T_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 131.17 | 128.07 | TWINGROVE | AP_P2-3_PE-500-019C_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 797 | 132.38 | 127.58 | TWINGROVE | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 814 | 130.71 | 126.22 | TWINGROVE | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 814 | 131.19 | 126.09 | TWINGROVE | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 814 | 131.19 | 126.09 | TWINGROVE | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 814 | 131.18 | 126.08 | TWINGROVE | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3369 | 127.9 | 122.83 | T126 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 117.96 | 117.07 | TWINGROVE | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 814 | 121.87 | 116.97 | TWINGROVE | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 116.6 | 115.75 | TWINGROVE | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 120.39 | 115.35 | TWINGROVE | PECO_P4_PEACH035_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 114.96 | 114.16 | TWINGROVE | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.26 | 113.85 | TWINGROVE | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.26 | 113.85 | TWINGROVE | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 117.84 | 113.16 | TWINGROVE | PECO_P7-1_220-0607_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 117.84 | 113.16 | TWINGROVE | PECO_P4_PEACH675_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 814 | 115.67 | 112.68 | TWINGROVE | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 814 | 115.92 | 112.61 | TWINGROVE | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 814 | 115.92 | 112.61 | TWINGROVE | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 814 | 115.89 | 112.6 | TWINGROVE | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3198 | 117.72 | 112.36 | TWINGROVE | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3369 | 127.9 | 122.83 | T127 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 112.49 | 111.27 | TWINGROVE | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 112.44 | 111.22 | TWINGROVE | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.47 | 110.72 | TWINGROVE | PECO_P1-2_220-07_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.25 | 110.62 | TWINGROVE | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.13 | 110.51 | TWINGROVE | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.23 | 110.5 | TWINGROVE | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.16 | 110.49 | TWINGROVE | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 110.77 | 109.73 | TWINGROVE | AP_P1-2_WP-500-005A_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 110.77 | 109.73 | TWINGROVE | AP_P1-2_WP-500-DRT21_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 110.77 | 109.73 | TWINGROVE | AP_P2-3_WP-500-465_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 110.77 | 109.73 | TWINGROVE | AP_P2-3_WP-500-DRT20_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 110.77 | 109.73 | TWINGROVE | AP_P2-2_WP-500-DRT16_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 814 | 107.52 | 104.17 | TWINGROVE | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204502 | 27JACKSON | 204514 | 27TMI | 1 | 230 | 227 | 659 | 104.16 | 104.11 | TWINGROVE | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204502 | 27JACKSON | 204514 | 27TMI | 1 | 230 | 227 | 659 | 104.16 | 104.11 | TWINGROVE | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204502 | 27JACKSON | 204514 | 27TMI | 1 | 230 | 227 | 659 | 104.21 | 104.1 | TWINGROVE | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204502 | 27JACKSON | 204514 | 27TMI | 1 | 230 | 227 | 659 | 104.14 | 104.09 | TWINGROVE | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 104.95 | 102.27 | TWINGROVE | DVP_P4-2: 560T571_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 104.79 | 102.13 | TWINGROVE | DVP_P4-2: H2T560_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 104.79 | 102.11 | TWINGROVE | DVP_P4-2: H1T560_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 104.64 | 101.96 | TWINGROVE | PEPCO_P1_5070_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220972 | GRANITE1 | 1 | 230 | 232 | 811 | 103.36 | 100.45 | TWINGROVE | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220972 | GRANITE1 | 1 | 230 | 232 | 811 | 103.1 | 100.16 | TWINGROVE | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220972 | GRANITE1 | 1 | 230 | 232 | 811 | 103.1 | 100.16 | TWINGROVE | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 801 | 102.18 | 100.07 | TWINGROVE | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3369 | 128.07 | 123 | T157 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 121.12 | 116.06 | U2-030 | PECO_P4_PEACH035_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.9 | 114.47 | U2-030 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.9 | 114.47 | U2-030 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.54 | 113.84 | U2-030 | PECO_P4_PEACH675_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.54 | 113.84 | U2-030 | PECO_P7-1_220-0607_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 116.16 | 111.4 | U2-030 | PECO_P1-2_220-07_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 116 | 111.35 | U2-030 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.88 | 111.24 | U2-030 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.91 | 111.22 | U2-030 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.92 | 111.18 | U2-030 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 607 | 168.95 | 166.24 | U2-072 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 607 | 167.88 | 166.24 | U2-072 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 607 | 168.62 | 166.23 | U2-072 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 607 | 167.55 | 166.23 | U2-072 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 607 | 168.87 | 166.17 | U2-072 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 607 | 168.87 | 166.17 | U2-072 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 607 | 167.8 | 166.17 | U2-072 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 607 | 167.8 | 166.17 | U2-072 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 628 | 159.87 | 158.5 | U2-072 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 628 | 159.56 | 158.49 | U2-072 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 628 | 159.79 | 158.43 | U2-072 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 628 | 159.79 | 158.43 | U2-072 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 628 | 157.16 | 156.21 | U2-072 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 628 | 156.85 | 156.2 | U2-072 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 628 | 157.09 | 156.14 | U2-072 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 628 | 157.09 | 156.14 | U2-072 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3369 | 127.65 | 122.59 | TOP CROP | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 118.27 | 117.4 | U2-072 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 116.9 | 116.08 | U2-072 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 120.73 | 115.68 | U2-072 | PECO_P4_PEACH035_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 115.27 | 114.48 | U2-072 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.57 | 114.15 | U2-072 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.57 | 114.15 | U2-072 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.17 | 113.48 | U2-072 | PECO_P7-1_220-0607_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.17 | 113.48 | U2-072 | PECO_P4_PEACH675_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3198 | 118.12 | 112.74 | U2-072 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3369 | 128.15 | 123.08 | TR3_G114 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 112.78 | 111.58 | U2-072 | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 112.73 | 111.54 | U2-072 | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.8 | 111.04 | U2-072 | PECO_P1-2_220-07_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.6 | 110.97 | U2-072 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.49 | 110.85 | U2-072 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.52 | 110.83 | U2-072 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.56 | 110.83 | U2-072 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.08 | 110.06 | U2-072 | AP_P1-2_WP-500-005A_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.08 | 110.06 | U2-072 | AP_P1-2_WP-500-DRT21_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.08 | 110.06 | U2-072 | AP_P2-3_WP-500-465_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.08 | 110.06 | U2-072 | AP_P2-3_WP-500-DRT20_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.08 | 110.06 | U2-072 | AP_P2-2_WP-500-DRT16_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 105.28 | 102.59 | U2-072 | DVP_P4-2: 560T571_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 105.12 | 102.45 | U2-072 | DVP_P4-2: H2T560_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 105.12 | 102.43 | U2-072 | DVP_P4-2: H1T560_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 104.97 | 102.29 | U2-072 | PEPCO_P1_5070_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3369 | 127.41 | 122.35 | TWINGROVE | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 118.39 | 117.53 | U2-073 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 117.02 | 116.21 | U2-073 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 120.94 | 115.88 | U2-073 | PECO_P4_PEACH035_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 115.39 | 114.61 | U2-073 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.72 | 114.3 | U2-073 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.72 | 114.3 | U2-073 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.36 | 113.67 | U2-073 | PECO_P7-1_220-0607_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.36 | 113.67 | U2-073 | PECO_P4_PEACH675_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3198 | 118.34 | 112.95 | U2-073 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3369 | 128.23 | 123.16 | U2-030 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 112.9 | 111.7 | U2-073 | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 112.85 | 111.66 | U2-073 | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.98 | 111.22 | U2-073 | PECO_P1-2_220-07_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.81 | 111.16 | U2-073 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.69 | 111.05 | U2-073 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.72 | 111.03 | U2-073 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.74 | 111.01 | U2-073 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.19 | 110.18 | U2-073 | AP_P1-2_WP-500-DRT21_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.19 | 110.18 | U2-073 | AP_P2-2_WP-500-DRT16_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.19 | 110.18 | U2-073 | AP_P2-3_WP-500-DRT20_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.19 | 110.18 | U2-073 | AP_P1-2_WP-500-005A_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.19 | 110.18 | U2-073 | AP_P2-3_WP-500-465_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3369 | 127.8 | 122.73 | U2-072 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 118.34 | 117.47 | U2-090 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 116.96 | 116.15 | U2-090 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 120.83 | 115.77 | U2-090 | PECO_P4_PEACH035_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 115.33 | 114.55 | U2-090 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.65 | 114.23 | U2-090 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.65 | 114.23 | U2-090 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.26 | 113.57 | U2-090 | PECO_P7-1_220-0607_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.26 | 113.57 | U2-090 | PECO_P4_PEACH675_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3198 | 118.22 | 112.84 | U2-090 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3369 | 128.02 | 122.95 | U2-073 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 112.84 | 111.65 | U2-090 | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 112.79 | 111.6 | U2-090 | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.88 | 111.13 | U2-090 | PECO_P1-2_220-07_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.7 | 111.06 | U2-090 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.58 | 110.95 | U2-090 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.61 | 110.93 | U2-090 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.64 | 110.91 | U2-090 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.14 | 110.13 | U2-090 | AP_P2-3_WP-500-DRT20_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.14 | 110.13 | U2-090 | AP_P1-2_WP-500-DRT21_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.14 | 110.13 | U2-090 | AP_P2-2_WP-500-DRT16_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.14 | 110.13 | U2-090 | AP_P1-2_WP-500-005A_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.14 | 110.13 | U2-090 | AP_P2-3_WP-500-465_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 607 | 167.69 | 166.04 | U3-002 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 607 | 168.76 | 166.04 | U3-002 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 607 | 167.37 | 166.03 | U3-002 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 607 | 168.43 | 166.03 | U3-002 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 607 | 167.61 | 165.97 | U3-002 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 607 | 168.68 | 165.97 | U3-002 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 607 | 168.68 | 165.97 | U3-002 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 607 | 167.61 | 165.97 | U3-002 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 628 | 159.69 | 158.31 | U3-002 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 628 | 159.38 | 158.3 | U3-002 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 628 | 159.62 | 158.24 | U3-002 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 628 | 159.62 | 158.24 | U3-002 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 628 | 156.98 | 156.02 | U3-002 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 628 | 156.67 | 156.01 | U3-002 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 628 | 156.91 | 155.95 | U3-002 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 628 | 156.91 | 155.95 | U3-002 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 607 | 154.67 | 151.5 | U3-002 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 607 | 153.6 | 151.5 | U3-002 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 628 | 146.07 | 144.24 | U3-002 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 628 | 143.36 | 141.93 | U3-002 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 136.46 | 133.4 | U3-002 | AP_P1-2_PE-500-407T_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 136.46 | 133.4 | U3-002 | DVP_P1-2: LN 514_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 136.46 | 133.38 | U3-002 | DVP_P4-2: 51482_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 131.34 | 128.26 | U3-002 | AP_P2-3_PE-500-019C_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 814 | 130.94 | 126.45 | U3-002 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 814 | 131.43 | 126.32 | U3-002 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 814 | 131.43 | 126.32 | U3-002 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 814 | 131.42 | 126.31 | U3-002 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3369 | 127.9 | 122.84 | U2-090 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 118.16 | 117.28 | U3-002 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 814 | 122.11 | 117.19 | U3-002 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 116.79 | 115.96 | U3-002 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 120.61 | 115.56 | U3-002 | PECO_P4_PEACH035_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 115.15 | 114.36 | U3-002 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.46 | 114.04 | U3-002 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.46 | 114.04 | U3-002 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.06 | 113.37 | U3-002 | PECO_P7-1_220-0607_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.06 | 113.37 | U3-002 | PECO_P4_PEACH675_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3198 | 117.98 | 112.6 | U3-002 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3369 | 127.66 | 122.6 | U3-002 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 112.67 | 111.46 | U3-002 | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 112.62 | 111.42 | U3-002 | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.68 | 110.93 | U3-002 | PECO_P1-2_220-07_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.48 | 110.85 | U3-002 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.36 | 110.73 | U3-002 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.44 | 110.71 | U3-002 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.39 | 110.71 | U3-002 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 110.96 | 109.94 | U3-002 | AP_P1-2_WP-500-DRT21_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 110.96 | 109.94 | U3-002 | AP_P1-2_WP-500-005A_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 110.96 | 109.94 | U3-002 | AP_P2-3_WP-500-465_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 110.96 | 109.94 | U3-002 | AP_P2-3_WP-500-DRT20_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 110.96 | 109.94 | U3-002 | AP_P2-2_WP-500-DRT16_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 105.15 | 102.46 | U3-002 | DVP_P4-2: 560T571_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 104.99 | 102.32 | U3-002 | DVP_P4-2: H2T560_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 104.99 | 102.3 | U3-002 | DVP_P4-2: H1T560_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 104.84 | 102.16 | U3-002 | PEPCO_P1_5070_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3369 | 128.15 | 123.08 | V1-011 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 118.52 | 117.68 | V1-011 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 117.15 | 116.35 | V1-011 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 121.05 | 115.99 | V1-011 | PECO_P4_PEACH035_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 115.52 | 114.75 | V1-011 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.84 | 114.42 | V1-011 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.84 | 114.42 | V1-011 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.48 | 113.78 | V1-011 | PECO_P7-1_220-0607_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.48 | 113.78 | V1-011 | PECO_P4_PEACH675_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3198 | 118.48 | 113.08 | V1-011 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3369 | 127.89 | 122.82 | V3-007 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 113.02 | 111.84 | V1-011 | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 112.97 | 111.79 | V1-011 | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 116.1 | 111.34 | V1-011 | PECO_P1-2_220-07_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.93 | 111.28 | V1-011 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.81 | 111.17 | V1-011 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.84 | 111.15 | V1-011 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.86 | 111.12 | V1-011 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.33 | 110.33 | V1-011 | AP_P2-3_WP-500-DRT20_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.33 | 110.33 | V1-011 | AP_P1-2_WP-500-DRT21_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.33 | 110.33 | V1-011 | AP_P2-3_WP-500-465_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.33 | 110.33 | V1-011 | AP_P2-2_WP-500-DRT16_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.33 | 110.33 | V1-011 | AP_P1-2_WP-500-005A_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3369 | 127.88 | 122.81 | V3-028 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 118.33 | 117.46 | V3-007 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 116.95 | 116.14 | V3-007 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 120.82 | 115.76 | V3-007 | PECO_P4_PEACH035_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 115.32 | 114.54 | V3-007 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.64 | 114.22 | V3-007 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.64 | 114.22 | V3-007 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.25 | 113.56 | V3-007 | PECO_P7-1_220-0607_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.25 | 113.56 | V3-007 | PECO_P4_PEACH675_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3198 | 118.21 | 112.83 | V3-007 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3369 | 127.69 | 122.63 | W1-029 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 112.83 | 111.64 | V3-007 | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 112.78 | 111.59 | V3-007 | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.87 | 111.12 | V3-007 | PECO_P1-2_220-07_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.69 | 111.05 | V3-007 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.57 | 110.93 | V3-007 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.6 | 110.91 | V3-007 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.63 | 110.9 | V3-007 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.13 | 110.12 | V3-007 | AP_P2-3_WP-500-DRT20_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.13 | 110.12 | V3-007 | AP_P1-2_WP-500-DRT21_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.13 | 110.12 | V3-007 | AP_P2-2_WP-500-DRT16_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.13 | 110.12 | V3-007 | AP_P1-2_WP-500-005A_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.13 | 110.12 | V3-007 | AP_P2-3_WP-500-465_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3369 | 128.24 | 123.16 | W1-056 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 118.33 | 117.47 | V3-028 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 116.96 | 116.14 | V3-028 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 120.8 | 115.75 | V3-028 | PECO_P4_PEACH035_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 115.33 | 114.55 | V3-028 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.63 | 114.21 | V3-028 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.63 | 114.21 | V3-028 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.24 | 113.55 | V3-028 | PECO_P4_PEACH675_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.24 | 113.55 | V3-028 | PECO_P7-1_220-0607_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3198 | 118.2 | 112.82 | V3-028 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3369 | 127.63 | 122.57 | W4-005 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 112.84 | 111.64 | V3-028 | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 112.79 | 111.6 | V3-028 | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.86 | 111.11 | V3-028 | PECO_P1-2_220-07_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.68 | 111.04 | V3-028 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.56 | 110.92 | V3-028 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.59 | 110.9 | V3-028 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.63 | 110.89 | V3-028 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.13 | 110.13 | V3-028 | AP_P1-2_WP-500-005A_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.13 | 110.13 | V3-028 | AP_P1-2_WP-500-DRT21_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.13 | 110.13 | V3-028 | AP_P2-2_WP-500-DRT16_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.13 | 110.13 | V3-028 | AP_P2-3_WP-500-465_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.13 | 110.13 | V3-028 | AP_P2-3_WP-500-DRT20_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 607 | 168.78 | 166.06 | W1-029 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 607 | 167.71 | 166.06 | W1-029 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 607 | 168.45 | 166.04 | W1-029 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 607 | 167.38 | 166.04 | W1-029 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 607 | 168.7 | 165.98 | W1-029 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 607 | 168.7 | 165.98 | W1-029 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 607 | 167.63 | 165.98 | W1-029 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 607 | 167.63 | 165.98 | W1-029 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 628 | 159.71 | 158.32 | W1-029 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 628 | 159.39 | 158.31 | W1-029 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 628 | 159.63 | 158.25 | W1-029 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 628 | 159.63 | 158.25 | W1-029 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 628 | 157 | 156.03 | W1-029 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 628 | 156.69 | 156.02 | W1-029 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 628 | 156.93 | 155.96 | W1-029 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 628 | 156.93 | 155.96 | W1-029 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 607 | 153.61 | 151.51 | W1-029 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 607 | 154.68 | 151.51 | W1-029 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 628 | 146.08 | 144.25 | W1-029 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 628 | 143.37 | 141.94 | W1-029 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 680 | 140.86 | 137.93 | W1-029 | PEPCO_P4_PP19_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 797 | 140.61 | 136.06 | W1-029 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 797 | 140.88 | 136 | W1-029 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 797 | 140.88 | 136 | W1-029 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 797 | 140.85 | 135.98 | W1-029 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 135.75 | 132.69 | W1-029 | AP_P1-2_PE-500-407T_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 135.75 | 132.69 | W1-029 | DVP_P1-2: LN 514_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 135.75 | 132.67 | W1-029 | DVP_P4-2: 51482_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 797 | 132.5 | 127.71 | W1-029 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 130.66 | 127.59 | W1-029 | AP_P2-3_PE-500-019C_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 814 | 130.86 | 126.35 | W1-029 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 814 | 131.36 | 126.24 | W1-029 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 814 | 131.36 | 126.24 | W1-029 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 814 | 131.34 | 126.23 | W1-029 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 2 | 230 | 233 | 680 | 127.93 | 125.02 | W1-029 | DVP_P1-2: LN 514_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 2 | 230 | 233 | 680 | 127.93 | 125.02 | W1-029 | AP_P1-2_PE-500-407T_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 680 | 127.93 | 125.02 | W1-029 | DVP_P1-2: LN 514_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 680 | 127.93 | 125.02 | W1-029 | AP_P1-2_PE-500-407T_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 2 | 230 | 233 | 680 | 127.93 | 125.02 | W1-029 | DVP_P4-2: 51482_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 680 | 127.93 | 125.02 | W1-029 | DVP_P4-2: 51482_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3369 | 127.93 | 122.86 | X2-022 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 118.04 | 117.15 | W1-029 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 814 | 122.02 | 117.1 | W1-029 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 680 | 118.87 | 115.95 | W1-029 | AP_P2-3_PE-500-019C_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 2 | 230 | 233 | 680 | 118.87 | 115.95 | W1-029 | AP_P2-3_PE-500-019C_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 116.67 | 115.83 | W1-029 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 120.68 | 115.63 | W1-029 | PECO_P4_PEACH035_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 115.04 | 114.24 | W1-029 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.41 | 113.99 | W1-029 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.41 | 113.99 | W1-029 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.08 | 113.39 | W1-029 | PECO_P7-1_220-0607_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.08 | 113.39 | W1-029 | PECO_P4_PEACH675_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 814 | 115.76 | 112.77 | W1-029 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 814 | 116.02 | 112.71 | W1-029 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 814 | 116.02 | 112.71 | W1-029 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 814 | 116 | 112.69 | W1-029 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3198 | 118 | 112.62 | W1-029 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3369 | 128.06 | 122.99 | X2-060 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 112.56 | 111.35 | W1-029 | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 112.51 | 111.3 | W1-029 | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.7 | 110.95 | W1-029 | PECO_P1-2_220-07_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.5 | 110.87 | W1-029 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.39 | 110.75 | W1-029 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.46 | 110.74 | W1-029 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.41 | 110.73 | W1-029 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 110.86 | 109.83 | W1-029 | AP_P1-2_WP-500-DRT21_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 110.86 | 109.83 | W1-029 | AP_P2-3_WP-500-465_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 110.86 | 109.83 | W1-029 | AP_P2-3_WP-500-DRT20_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 110.86 | 109.83 | W1-029 | AP_P2-2_WP-500-DRT16_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 110.86 | 109.83 | W1-029 | AP_P1-2_WP-500-005A_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 814 | 107.61 | 104.29 | W1-029 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 104.74 | 102.05 | W1-029 | DVP_P4-2: 560T571_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 104.57 | 101.91 | W1-029 | DVP_P4-2: H2T560_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 104.57 | 101.89 | W1-029 | DVP_P4-2: H1T560_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 104.42 | 101.74 | W1-029 | PEPCO_P1_5070_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 801 | 102.23 | 100.13 | W1-029 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 801 | 102.65 | 100.03 | W1-029 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 801 | 102.65 | 100.03 | W1-029 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 801 | 102.62 | 100.01 | W1-029 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3369 | 127.38 | 122.32 | Z1-036 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 121.12 | 116.06 | W1-056 | PECO_P4_PEACH035_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.55 | 113.85 | W1-056 | PECO_P4_PEACH675_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.55 | 113.85 | W1-056 | PECO_P7-1_220-0607_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 116.17 | 111.41 | W1-056 | PECO_P1-2_220-07_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 116.01 | 111.36 | W1-056 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.89 | 111.24 | W1-056 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.92 | 111.22 | W1-056 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.93 | 111.19 | W1-056 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.69 | 111.06 | W1-056 | PECO_P4_NOTTI85_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.63 | 111.06 | W1-056 | PECO_P1-2_220-08_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 607 | 168.72 | 166 | W4-005 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 607 | 167.65 | 165.99 | W4-005 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 607 | 168.39 | 165.99 | W4-005 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 607 | 167.33 | 165.99 | W4-005 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 607 | 167.57 | 165.92 | W4-005 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 607 | 167.57 | 165.92 | W4-005 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 607 | 168.64 | 165.92 | W4-005 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 607 | 168.64 | 165.92 | W4-005 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 628 | 159.65 | 158.26 | W4-005 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 628 | 159.34 | 158.26 | W4-005 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 628 | 159.58 | 158.19 | W4-005 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 628 | 159.58 | 158.19 | W4-005 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 628 | 156.94 | 155.97 | W4-005 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 628 | 156.63 | 155.96 | W4-005 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 628 | 156.87 | 155.9 | W4-005 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 628 | 156.87 | 155.9 | W4-005 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 607 | 153.56 | 151.46 | W4-005 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 607 | 154.63 | 151.46 | W4-005 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 628 | 146.03 | 144.2 | W4-005 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 628 | 143.33 | 141.89 | W4-005 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 797 | 140.94 | 136.07 | W4-005 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 797 | 140.94 | 136.07 | W4-005 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 797 | 140.92 | 136.06 | W4-005 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 136.41 | 133.35 | W4-005 | DVP_P1-2: LN 514_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 136.41 | 133.35 | W4-005 | AP_P1-2_PE-500-407T_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 136.41 | 133.33 | W4-005 | DVP_P4-2: 51482_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 131.29 | 128.21 | W4-005 | AP_P2-3_PE-500-019C_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 814 | 130.91 | 126.41 | W4-005 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 814 | 131.4 | 126.29 | W4-005 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 814 | 131.4 | 126.29 | W4-005 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 814 | 131.38 | 126.28 | W4-005 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3369 | 127.88 | 122.82 | Z2-087 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 118.13 | 117.25 | W4-005 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 814 | 122.07 | 117.16 | W4-005 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 116.76 | 115.93 | W4-005 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 120.59 | 115.54 | W4-005 | PECO_P4_PEACH035_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 115.12 | 114.33 | W4-005 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.43 | 114.02 | W4-005 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.43 | 114.02 | W4-005 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.03 | 113.35 | W4-005 | PECO_P4_PEACH675_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.03 | 113.35 | W4-005 | PECO_P7-1_220-0607_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3198 | 117.95 | 112.57 | W4-005 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3369 | 128.2 | 123.12 | Z2-088 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 112.64 | 111.43 | W4-005 | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 112.59 | 111.39 | W4-005 | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.65 | 110.9 | W4-005 | PECO_P1-2_220-07_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.45 | 110.82 | W4-005 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.34 | 110.71 | W4-005 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.41 | 110.69 | W4-005 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.36 | 110.68 | W4-005 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 110.93 | 109.91 | W4-005 | AP_P2-3_WP-500-465_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 110.93 | 109.91 | W4-005 | AP_P1-2_WP-500-DRT21_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 110.93 | 109.91 | W4-005 | AP_P1-2_WP-500-005A_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 110.93 | 109.91 | W4-005 | AP_P2-3_WP-500-DRT20_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 110.93 | 109.91 | W4-005 | AP_P2-2_WP-500-DRT16_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 105.11 | 102.42 | W4-005 | DVP_P4-2: 560T571_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 104.95 | 102.28 | W4-005 | DVP_P4-2: H2T560_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 104.94 | 102.26 | W4-005 | DVP_P4-2: H1T560_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 104.8 | 102.12 | W4-005 | PEPCO_P1_5070_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 112.75 | 108.36 | WESTBROOK C | PL_10_P42_100570_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 112.36 | 107.98 | WESTBROOK C | PN_P2-3_PN-500-004-DRT-008_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 112.36 | 107.98 | WESTBROOK C | PN_P2-3_PN-500-DRT31_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 112.29 | 107.92 | WESTBROOK C | PL_10_P12_000085_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 112.23 | 107.88 | WESTBROOK C | PL_30_P42_000131_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 210404 | EPHA TI1 | 211365 | ASHF TP1 | 1 | 69 | 229 | 96 | 96.01 | 104.62 | AD1-143 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 118.35 | 117.49 | X2-022 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 116.98 | 116.17 | X2-022 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 120.86 | 115.8 | X2-022 | PECO_P4_PEACH035_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 115.35 | 114.57 | X2-022 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.67 | 114.24 | X2-022 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.67 | 114.24 | X2-022 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.29 | 113.6 | X2-022 | PECO_P4_PEACH675_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.29 | 113.6 | X2-022 | PECO_P7-1_220-0607_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3198 | 118.25 | 112.87 | X2-022 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 210404 | EPHA TI1 | 211190 | SSLA 1 | 1 | 69 | 229 | 96 | 96.01 | 104.59 | AD1-143 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 112.86 | 111.66 | X2-022 | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 112.81 | 111.62 | X2-022 | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.91 | 111.15 | X2-022 | PECO_P1-2_220-07_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.73 | 111.08 | X2-022 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.61 | 110.97 | X2-022 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.64 | 110.95 | X2-022 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.67 | 110.94 | X2-022 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.15 | 110.15 | X2-022 | AP_P2-2_WP-500-DRT16_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.15 | 110.15 | X2-022 | AP_P1-2_WP-500-DRT21_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.15 | 110.15 | X2-022 | AP_P2-3_WP-500-DRT20_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.15 | 110.15 | X2-022 | AP_P2-3_WP-500-465_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.15 | 110.15 | X2-022 | AP_P1-2_WP-500-005A_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 136.49 | 133.42 | X2-060 | AP_P1-2_PE-500-407T_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 136.49 | 133.42 | X2-060 | DVP_P1-2: LN 514_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 136.49 | 133.4 | X2-060 | DVP_P4-2: 51482_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 131.37 | 128.29 | X2-060 | AP_P2-3_PE-500-019C_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208393 | FARO DC TIE | 208395 | FARO FF | 1 | 115/69 | 229 | 77 | 125.9 | 126.19 | AE1-226 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 118.39 | 117.53 | X2-060 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 117.02 | 116.21 | X2-060 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 120.99 | 115.93 | X2-060 | PECO_P4_PEACH035_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 115.39 | 114.61 | X2-060 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.74 | 114.31 | X2-060 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.74 | 114.31 | X2-060 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.4 | 113.7 | X2-060 | PECO_P7-1_220-0607_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.4 | 113.7 | X2-060 | PECO_P4_PEACH675_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3198 | 118.38 | 112.99 | X2-060 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208393 | FARO DC TIE | 208395 | FARO FF | 2 | 115/69 | 229 | 77 | 125.9 | 126.19 | AE1-226 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 112.9 | 111.71 | X2-060 | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 112.85 | 111.66 | X2-060 | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 116.02 | 111.26 | X2-060 | PECO_P1-2_220-07_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.84 | 111.2 | X2-060 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.73 | 111.08 | X2-060 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.75 | 111.06 | X2-060 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.78 | 111.04 | X2-060 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.2 | 110.2 | X2-060 | AP_P1-2_WP-500-005A_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.2 | 110.2 | X2-060 | AP_P2-3_WP-500-465_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.2 | 110.2 | X2-060 | AP_P2-2_WP-500-DRT16_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.2 | 110.2 | X2-060 | AP_P2-3_WP-500-DRT20_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.2 | 110.2 | X2-060 | AP_P1-2_WP-500-DRT21_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200762 | 26GARRETT | 235470 | 01GARRET | 1 | 115 | 226/201 | 160 | 105.12 | 105.44 | Y1-033 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200762 | 26GARRETT | 235470 | 01GARRET | 1 | 115 | 226/201 | 160 | 105.12 | 105.44 | Y1-033 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200762 | 26GARRETT | 235470 | 01GARRET | 1 | 115 | 226/201 | 160 | 105.04 | 105.36 | Y1-033 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208393 | FARO DC TIE | 208395 | FARO FF | 1 | 115/69 | 229 | 77 | 124.8 | 125.07 | AG2-055 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200762 | 26GARRETT | 235470 | 01GARRET | 1 | 115 | 226/201 | 160 | 101.37 | 101.19 | Y1-033 | AP_P2-2_WP-500-DRT16_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200762 | 26GARRETT | 235470 | 01GARRET | 1 | 115 | 226/201 | 160 | 101.37 | 101.19 | Y1-033 | AP_P2-3_WP-500-465_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200762 | 26GARRETT | 235470 | 01GARRET | 1 | 115 | 226/201 | 160 | 101.37 | 101.19 | Y1-033 | AP_P2-3_WP-500-DRT20_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200762 | 26GARRETT | 235470 | 01GARRET | 1 | 115 | 226/201 | 160 | 101.37 | 101.19 | Y1-033 | AP_P1-2_WP-500-005A_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200762 | 26GARRETT | 235470 | 01GARRET | 1 | 115 | 226/201 | 160 | 101.37 | 101.19 | Y1-033 | AP_P1-2_WP-500-DRT21_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200762 | 26GARRETT | 235470 | 01GARRET | 1 | 115 | 226/201 | 160 | 101.28 | 100.28 | Y1-033 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200762 | 26GARRETT | 235470 | 01GARRET | 1 | 115 | 226/201 | 160 | 101.28 | 100.28 | Y1-033 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 607 | 167.29 | 165.6 | Z1-036 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 607 | 168.35 | 165.6 | Z1-036 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 607 | 166.97 | 165.59 | Z1-036 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 607 | 168.03 | 165.59 | Z1-036 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 607 | 168.27 | 165.53 | Z1-036 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 607 | 167.21 | 165.53 | Z1-036 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 607 | 167.21 | 165.53 | Z1-036 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 607 | 168.27 | 165.53 | Z1-036 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 628 | 159.3 | 157.88 | Z1-036 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 628 | 158.99 | 157.87 | Z1-036 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 628 | 159.23 | 157.81 | Z1-036 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 628 | 159.23 | 157.81 | Z1-036 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 628 | 156.6 | 155.59 | Z1-036 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 628 | 156.28 | 155.58 | Z1-036 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 628 | 156.52 | 155.52 | Z1-036 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 628 | 156.52 | 155.52 | Z1-036 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 607 | 153.2 | 151.21 | Z1-036 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 607 | 154.26 | 151.21 | Z1-036 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 628 | 145.68 | 143.96 | Z1-036 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 628 | 142.98 | 141.65 | Z1-036 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 680 | 140.48 | 137.55 | Z1-036 | PEPCO_P4_PP19_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 797 | 140.3 | 135.74 | Z1-036 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 797 | 140.55 | 135.68 | Z1-036 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 797 | 140.55 | 135.68 | Z1-036 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 797 | 140.53 | 135.67 | Z1-036 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 135.27 | 132.22 | Z1-036 | DVP_P1-2: LN 514_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 135.27 | 132.22 | Z1-036 | AP_P1-2_PE-500-407T_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 135.27 | 132.2 | Z1-036 | DVP_P4-2: 51482_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 680 | 134.1 | 131.28 | Z1-036 | PEPCO_P1_PP2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 2 | 230 | 233 | 680 | 134.1 | 131.28 | Z1-036 | PEPCO_P1_PP1_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 797 | 132.18 | 127.37 | Z1-036 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 130.19 | 127.12 | Z1-036 | AP_P2-3_PE-500-019C_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 814 | 130.53 | 126.03 | Z1-036 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 814 | 131.02 | 125.91 | Z1-036 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 814 | 131.02 | 125.91 | Z1-036 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 814 | 131.01 | 125.9 | Z1-036 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 2 | 230 | 233 | 680 | 127.55 | 124.65 | Z1-036 | DVP_P1-2: LN 514_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 2 | 230 | 233 | 680 | 127.55 | 124.65 | Z1-036 | AP_P1-2_PE-500-407T_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 680 | 127.55 | 124.65 | Z1-036 | AP_P1-2_PE-500-407T_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 680 | 127.55 | 124.65 | Z1-036 | DVP_P1-2: LN 514_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 2 | 230 | 233 | 680 | 127.55 | 124.64 | Z1-036 | DVP_P4-2: 51482_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 680 | 127.55 | 124.64 | Z1-036 | DVP_P4-2: 51482_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208393 | FARO DC TIE | 208395 | FARO FF | 2 | 115/69 | 229 | 77 | 124.8 | 125.07 | AG2-055 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 117.75 | 116.84 | Z1-036 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 814 | 121.7 | 116.79 | Z1-036 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 680 | 118.51 | 115.59 | Z1-036 | AP_P2-3_PE-500-019C_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 2 | 230 | 233 | 680 | 118.51 | 115.59 | Z1-036 | AP_P2-3_PE-500-019C_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 116.39 | 115.53 | Z1-036 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 120.43 | 115.38 | Z1-036 | PECO_P4_PEACH035_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 114.75 | 113.93 | Z1-036 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.13 | 113.72 | Z1-036 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.13 | 113.72 | Z1-036 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 117.82 | 113.14 | Z1-036 | PECO_P4_PEACH675_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 117.82 | 113.14 | Z1-036 | PECO_P7-1_220-0607_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 814 | 115.47 | 112.46 | Z1-036 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 814 | 115.72 | 112.41 | Z1-036 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 814 | 115.72 | 112.41 | Z1-036 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 814 | 115.69 | 112.39 | Z1-036 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3198 | 117.68 | 112.32 | Z1-036 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208395 | FARO FF | 208396 | FARO | 1 | 69 | 229 | 194 | 99.96 | 102.37 | AE1-226 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 112.29 | 111.05 | Z1-036 | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 112.24 | 111.01 | Z1-036 | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.44 | 110.7 | Z1-036 | PECO_P1-2_220-07_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.22 | 110.59 | Z1-036 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 797 | 112.03 | 110.54 | Z1-036 | PJM_500_BG_P4_5_CNSTN_15_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.2 | 110.48 | Z1-036 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.1 | 110.48 | Z1-036 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.13 | 110.46 | Z1-036 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 110.58 | 109.54 | Z1-036 | AP_P2-3_WP-500-DRT20_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 110.58 | 109.54 | Z1-036 | AP_P1-2_WP-500-005A_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 110.58 | 109.54 | Z1-036 | AP_P2-3_WP-500-465_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 110.58 | 109.54 | Z1-036 | AP_P1-2_WP-500-DRT21_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 110.58 | 109.54 | Z1-036 | AP_P2-2_WP-500-DRT16_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 797 | 109.24 | 107.84 | Z1-036 | BG_P7_GRCTN_CNSTN_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204502 | 27JACKSON | 204514 | 27TMI | 1 | 230 | 227 | 659 | 104.11 | 104.05 | Z1-036 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204502 | 27JACKSON | 204514 | 27TMI | 1 | 230 | 227 | 659 | 104.11 | 104.05 | Z1-036 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204502 | 27JACKSON | 204514 | 27TMI | 1 | 230 | 227 | 659 | 104.16 | 104.04 | Z1-036 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204502 | 27JACKSON | 204514 | 27TMI | 1 | 230 | 227 | 659 | 104.09 | 104.03 | Z1-036 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 814 | 107.31 | 103.96 | Z1-036 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 104.33 | 101.65 | Z1-036 | DVP_P4-2: 560T571_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 104.16 | 101.5 | Z1-036 | DVP_P4-2: H2T560_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 104.16 | 101.49 | Z1-036 | DVP_P4-2: H1T560_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 104.02 | 101.34 | Z1-036 | PEPCO_P1_5070_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220972 | GRANITE1 | 1 | 230 | 232 | 811 | 103.14 | 100.23 | Z1-036 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208395 | FARO FF | 208396 | FARO | 1 | 69 | 229 | 194 | 99.09 | 101.66 | AG2-055 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 118.32 | 117.45 | Z2-087 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 116.94 | 116.13 | Z2-087 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 120.81 | 115.76 | Z2-087 | PECO_P4_PEACH035_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 115.31 | 114.53 | Z2-087 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.63 | 114.21 | Z2-087 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.63 | 114.21 | Z2-087 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.25 | 113.56 | Z2-087 | PECO_P7-1_220-0607_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.25 | 113.56 | Z2-087 | PECO_P4_PEACH675_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3198 | 118.2 | 112.82 | Z2-087 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 211061 | PSPA TP1 | 211068 | AD1-143 TAP | 1 | 69 | 229 | 68 | 157.75 | 161 | AD1-143 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 112.82 | 111.63 | Z2-087 | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 112.77 | 111.58 | Z2-087 | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.87 | 111.11 | Z2-087 | PECO_P1-2_220-07_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.68 | 111.04 | Z2-087 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.57 | 110.93 | Z2-087 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.59 | 110.91 | Z2-087 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.63 | 110.9 | Z2-087 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.12 | 110.11 | Z2-087 | AP_P2-2_WP-500-DRT16_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.12 | 110.11 | Z2-087 | AP_P2-3_WP-500-465_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.12 | 110.11 | Z2-087 | AP_P2-3_WP-500-DRT20_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.12 | 110.11 | Z2-087 | AP_P1-2_WP-500-DRT21_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.12 | 110.11 | Z2-087 | AP_P1-2_WP-500-005A_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 105.3 | 102.6 | Z2-087 | DVP_P4-2: 560T571_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 105.13 | 102.46 | Z2-087 | DVP_P4-2: H2T560_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 105.13 | 102.45 | Z2-087 | DVP_P4-2: H1T560_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1428 | 104.99 | 102.3 | Z2-087 | PEPCO_P1_5070_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 211061 | PSPA TP1 | 211698 | LNFD | 1 | 69 | 229 | 96 | 122.51 | 125.02 | AD1-143 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 118.52 | 117.67 | Z2-088 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 117.15 | 116.34 | Z2-088 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 121.1 | 116.04 | Z2-088 | PECO_P4_PEACH035_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 115.51 | 114.75 | Z2-088 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.86 | 114.43 | Z2-088 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.86 | 114.43 | Z2-088 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.51 | 113.82 | Z2-088 | PECO_P7-1_220-0607_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 118.51 | 113.82 | Z2-088 | PECO_P4_PEACH675_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3198 | 118.52 | 113.12 | Z2-088 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200017 | SMITHBRG | 967451 | AG2-055 C O1 | 1 | 500 | 225 | 999 | 114.91 | 109.3 | AG2-055 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 113.02 | 111.84 | Z2-088 | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 112.97 | 111.79 | Z2-088 | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 116.14 | 111.37 | Z2-088 | PECO_P1-2_220-07_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.97 | 111.32 | Z2-088 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.85 | 111.21 | Z2-088 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.88 | 111.19 | Z2-088 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3949 | 115.9 | 111.16 | Z2-088 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.33 | 110.33 | Z2-088 | AP_P2-3_WP-500-465_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.33 | 110.33 | Z2-088 | AP_P2-2_WP-500-DRT16_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.33 | 110.33 | Z2-088 | AP_P1-2_WP-500-DRT21_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.33 | 110.33 | Z2-088 | AP_P1-2_WP-500-005A_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3099 | 111.33 | 110.33 | Z2-088 | AP_P2-3_WP-500-DRT20_SRT-SL |  | NO | Related to 2022 Window 3, pending window outcome