## Summary
2028 RTEP Short Circuit Result
Flowgate # | TO | BUS_NO | BUS | BREAKER | RATINGTYPE | Notes | DUTY_P | DUTY_A | BKR_CAPA | PJM Accepting Proposals | Reason for Exclusion | Comments
2023W1-SC-1 | AEP | 243481 | 05CANAL 138.kV | 3 | S | 40kA | 102.4 | 40967.3 | 40000 | NO | Below 200 kV exclusion | Violation found in 2025 case also.
2023W1-SC-2 | AEP | 243481 | 05CANAL 138.kV | 5 | S | 40kA | 100.4 | 40172.3 | 40000 | NO | Below 200 kV exclusion | Violation found in 2025 case also.
2023W1-SC-3 | AEP | 243491 | 05CORRID 138.kV | 106N | S | 63kA | 100.9 | 63554.5 | 63000 | NO | Below 200 kV exclusion | Violation found in 2025 case also.
2023W1-SC-4 | AEP | 243229 | 05OLIVE 345.kV | D | S | 50kA | 102.7 | 51371.8 | 50000 | Yes |  | Violation found in 2025 case also.
2023W1-SC-5 | AEP | 243092 | 05SCANTO 138.kV | J1 | S | 63kA | 114.7 | 72283.6 | 63000 | NO | Below 200 kV exclusion | Violation found in 2025 case also.
2023W1-SC-6 | AEP | 243092 | 05SCANTO 138.kV | N1 | S | 63kA | 112.2 | 70667.4 | 63000 | NO | Below 200 kV exclusion | Violation found in 2025 case also.
2023W1-SC-7 | AEP | 243233 | 05TANNER 345.kV | R1 | S | 50kA | 103.8 | 51897.5 | 50000 | NO | Immediate Need Exclusion | Violation found in 2025 case also.
2023W1-SC-8 | AEP | 243778 | 05TIMKEN B 138.kV | A | S | 18kA | 134.6 | 23549.5 | 17500 | NO | Below 200 kV exclusion | Violation found in 2025 case also.
2023W1-SC-9 | AEP | 243778 | 05TIMKEN B 138.kV | B | S | 18kA | 134.6 | 23549.5 | 17500 | NO | Below 200 kV exclusion | Violation found in 2025 case also.
2023W1-SC-10 | AEP | 248000 | 06CLIFTY 345.kV | G | S | 46kA | 107.1 | 48723.3 | 45500 | NO | Immediate Need Exclusion | Violation found in 2025 case also.
2023W1-SC-11 | AEP | 248000 | 06CLIFTY 345.kV | J | S | 46kA | 101.8 | 46298 | 45500 | NO | Immediate Need Exclusion | Violation found in 2025 case also.
2023W1-SC-12 | AEP | 248000 | 06CLIFTY 345.kV | P | S | 46kA | 101.8 | 46298 | 45500 | NO | Immediate Need Exclusion | Violation found in 2025 case also.
2023W1-SC-13 | AEP | 248000 | 06CLIFTY 345.kV | A | S | 16kA | 100.9 | 50426.9 | 50000 | NO | Immediate Need Exclusion | Violation found in 2025 case also.
2023W1-SC-14 | AEP | 248000 | 06CLIFTY 345.kV | D | S | 50kA | 100.5 | 50225.2 | 50000 | NO | Immediate Need Exclusion | Violation found in 2025 case also.