## Summer GenDeliv
| Note | APS and Dominion zones as a whole are quarantined pending Window 3 outcome and are not included in above results
Related to 2022 Window 3, pending window outcome
Flowgate is caused by suspended queue project(s).
Flowgate can be addressed by existing network upgrade
2028 RTEP PJM Generation Deliverability Result (Summer)
FG # | Fr Bus | Name | To Bus | Name | CKT | KVs | Areas | Rating | FN DC Flow | FN AC Flow | FN DC % | FN AC % | Cont Label | Cont Type | Conductor/Transformer Rating (MVA) | PJM Accepting Proposals | Reason For Exclusion | Comments
2023W1-GD-S548 | 270737 | ELWOOD ; R | 270769 | GOODINGS ;2R | 1 | 345 | 222 | 1528 | 1946.3 | 1929.3 | 127.38 | 126.27 | COMED_P4_116-45-L11613__SRT-A | Breaker | 1334/1726/1837/2084 (SN/SE/SSTE/SLD) | Yes
2023W1-GD-S1259 | 270737 | ELWOOD ; R | 270769 | GOODINGS ;2R | 1 | 345 | 222 | 1528 | 1928.9 | 1910 | 126.24 | 125 | COMED_P2-2_116_GG-345B__4_SRT-A | Bus | 1334/1726/1837/2084 (SN/SE/SSTE/SLD) | Yes
2023W1-GD-S554 | 270737 | ELWOOD ; R | 270769 | GOODINGS ;2R | 1 | 345 | 222 | 1528 | 1928.9 | 1910 | 126.24 | 125 | COMED_P4_116-45-TR84____SRT-A | Breaker | 1334/1726/1837/2084 (SN/SE/SSTE/SLD) | Yes
2023W1-GD-S563 | 270736 | ELWOOD ; B | 270770 | GOODINGS ;4B | 1 | 345 | 222 | 1528 | 1917.6 | 1903.3 | 125.5 | 124.56 | COMED_P4_116-45-L11614__SRT-A | Breaker | 1334/1726/1837/2084 (SN/SE/SSTE/SLD) | Yes
2023W1-GD-S570 | 270736 | ELWOOD ; B | 270770 | GOODINGS ;4B | 1 | 345 | 222 | 1528 | 1902.9 | 1886.9 | 124.54 | 123.49 | COMED_P4_116-45-TR82____SRT-A | Breaker | 1334/1726/1837/2084 (SN/SE/SSTE/SLD) | Yes
2023W1-GD-S1260 | 270736 | ELWOOD ; B | 270770 | GOODINGS ;4B | 1 | 345 | 222 | 1528 | 1903.2 | 1886.9 | 124.55 | 123.49 | COMED_P2-2_116_GG-345R__2_SRT-A | Bus | 1334/1726/1837/2084 (SN/SE/SSTE/SLD) | Yes
2023W1-GD-S571 | 270736 | ELWOOD ; B | 270770 | GOODINGS ;4B | 1 | 345 | 222 | 1528 | 1902.8 | 1886.3 | 124.53 | 123.45 | COMED_P4_116-45-L0303___SRT-A | Breaker | 1334/1726/1837/2084 (SN/SE/SSTE/SLD) | Yes
2023W1-GD-S520 | 243598 | 05BCKSKI | 253030 | 09GRNFLD | 1 | 69 | 205/209 | 72 | 93.9 | 94.5 | 130.46 | 131.26 | AEP_P4_#14130_05BCKSKI 69.0_A_SRT-A | Breaker | AEP side: 146/165/162/176 Dayton side: 80/98/110/122 | No | Below 200 kV exclusion | Dayton-2023-002 solution will address this issue
2023W1-GD-S583 | 239289 | 02HAYES | 238569 | 02BEAVER | 1 | 345 | 202 | 1376 | 1655.6 | 1667.3 | 120.32 | 121.17 | ATSI_P2-3_OEC-345-006_SRT-SL | Breaker | 1542/1878/2120 (SN/SE/SLD) | No | Substation Equipment Exclusion
2023W1-GD-S595 | 242516 | 05MOUNTN | 242920 | 05BELMON | 1 | 765 | 205 | 4571 | 5389.8 | 5414.9 | 117.91 | 118.46 | AEP_P4_#8980_05KAMMER 765_QQ2_SRT-A | Breaker | 6249/6249/7897/7897 (SN/SE/WN/WE) | No | Substation Equipment Exclusion
2023W1-GD-S671 | 242516 | 05MOUNTN | 242920 | 05BELMON | 1 | 765 | 205 | 4571 | 5127.8 | 5149.9 | 112.18 | 112.67 | AEP_P4_#17219_05GUERNSEY 765_A_SRT-A | Breaker | 6249/6249/7897/7897 (SN/SE/WN/WE) | No | Substation Equipment Exclusion
2023W1-GD-S642 | 275165 | CHERRY VA;1M | 271193 | CHERRY VA; R | 1 | 138 | 222 | 480 | 542.7 | 552.4 | 113.06 | 115.08 | COMED_P4_156-45-TR83____SRT-A | Breaker | 420/480/520/530 (SN/SE/SSTE/SLD) | Yes |  | Substation upgrades available
2023W1-GD-S641 | 270695 | CHERRY VA; R | 275165 | CHERRY VA;1M | 1 | 345/138 | 222 | 480 | 542.7 | 552.4 | 113.07 | 115.08 | COMED_P4_156-45-TR83____SRT-A | Breaker | 420/480/520/530 (SN/SE/SSTE/SLD) | Yes |  | Substation upgrades available
2023W1-GD-S1262 | 270695 | CHERRY VA; R | 275165 | CHERRY VA;1M | 1 | 345/138 | 222 | 480 | 542.7 | 552.4 | 113.07 | 115.08 | COMED_P2-2_156_CV-345R_10_SRT-A | Bus | 420/480/520/530 (SN/SE/SSTE/SLD) | Yes |  | Substation upgrades available
2023W1-GD-S1263 | 275165 | CHERRY VA;1M | 271193 | CHERRY VA; R | 1 | 138 | 222 | 480 | 542.7 | 552.4 | 113.06 | 115.08 | COMED_P2-2_156_CV-345R_10_SRT-A | Bus | 420/480/520/530 (SN/SE/SSTE/SLD) | Yes |  | Substation upgrades available
2023W1-GD-S726 | 242516 | 05MOUNTN | 242920 | 05BELMON | 1 | 765 | 205 | 4571 | 4888.6 | 4915 | 106.95 | 107.53 | AEP_P4_#8075_05MARYSV 765_A2_SRT-A | Breaker | 6249/6249/7897/7897 (SN/SE/WN/WE) | No | Substation Equipment Exclusion
2023W1-GD-S820 | 242516 | 05MOUNTN | 242920 | 05BELMON | 1 | 765 | 205 | 4571 | 4697.7 | 4734.5 | 102.77 | 103.58 | AEP_P4_#7217_05VASSEL 765_C1_SRT-A | Breaker | 6249/6249/7897/7897 (SN/SE/WN/WE) | No | Substation Equipment Exclusion
2023W1-GD-S662 | 270695 | CHERRY VA; R | 275165 | CHERRY VA;1M | 1 | 345/138 | 222 | 480 | 533.4 | 543 | 111.13 | 113.13 | COMED_P4_156-45-BT10-13_SRT-A | Breaker | 420/480/520/530 (SN/SE/SSTE/SLD) | Yes |  | Substation upgrades available
2023W1-GD-S663 | 275165 | CHERRY VA;1M | 271193 | CHERRY VA; R | 1 | 138 | 222 | 480 | 533.3 | 543 | 111.11 | 113.13 | COMED_P4_156-45-BT10-13_SRT-A | Breaker | 420/480/520/530 (SN/SE/SSTE/SLD) | Yes |  | Substation upgrades available
2023W1-GD-S834 | 242516 | 05MOUNTN | 242920 | 05BELMON | 1 | 765 | 205 | 4571 | 4663.4 | 4698.7 | 102.02 | 102.79 | AEP_P4_#7422_05CLOVRD 500_EE2_SRT-A | Breaker | 6249/6249/7897/7897 (SN/SE/WN/WE) | No | Substation Equipment Exclusion
2023W1-GD-S108 | 213925 | RIDLEY | 213775 | MACDADE | 1 | 230 | 230 | 927 | 1034.9 | 1021.6 | 111.64 | 110.2 | PECO_P1-2_220-23_SRT-A | Single | 1462/1770/1644/1956 (SN/SE/WN/WE) | No | Substation Equipment Exclusion
2023W1-GD-S693 | 213925 | RIDLEY | 213775 | MACDADE | 1 | 230 | 230 | 927 | 1030.7 | 1018.8 | 111.18 | 109.9 | PECO_P4_ISLDRD235_SRT-SW | Breaker | 1462/1770/1644/1956 (SN/SE/WN/WE) | No | Substation Equipment Exclusion
2023W1-GD-S704 | 213925 | RIDLEY | 213775 | MACDADE | 1 | 230 | 230 | 927 | 1021.2 | 1009.8 | 110.16 | 108.93 | PECO_P4_NAVYY1-75_SRT-SW | Breaker | 1462/1770/1644/1956 (SN/SE/WN/WE) | No | Substation Equipment Exclusion
2023W1-GD-S705 | 213925 | RIDLEY | 213775 | MACDADE | 1 | 230 | 230 | 927 | 1021.2 | 1009.7 | 110.16 | 108.92 | PECO_P4_NAVYY75-1T_SRT-SW | Breaker | 1462/1770/1644/1956 (SN/SE/WN/WE) | No | Substation Equipment Exclusion
2023W1-GD-S1267 | 213925 | RIDLEY | 213775 | MACDADE | 1 | 230 | 230 | 927 | 1019.1 | 1007.2 | 109.94 | 108.65 | PECO_CBO_ISLD235_SRT-A | Bus | 1462/1770/1644/1956 (SN/SE/WN/WE) | No | Substation Equipment Exclusion
2023W1-GD-S1397 | 213925 | RIDLEY | 213775 | MACDADE | 1 | 230 | 230 | 927 | 1009.9 | 998.9 | 108.94 | 107.75 | PECO_P7-1_220-75_IR_PR_SRT-SW | Tower | 1462/1770/1644/1956 (SN/SE/WN/WE) | No | Substation Equipment Exclusion
2023W1-GD-S1286 | 242516 | 05MOUNTN | 242920 | 05BELMON | 1 | 765 | 205 | 4571 | 4578.4 | 4602.6 | 100.16 | 100.69 | AEP_P2-2_#7222_05MALIS 765_1_SRT-A | Bus | 6249/6249/7897/7897 (SN/SE/WN/WE) | No | Substation Equipment Exclusion
2023W1-GD-S134 | 213925 | RIDLEY | 213775 | MACDADE | 1 | 230 | 230 | 927 | 1005.4 | 993.9 | 108.46 | 107.22 | PECO_P1-2_220-75_IR_SRT-SW | Single | 1462/1770/1644/1956 (SN/SE/WN/WE) | No | Substation Equipment Exclusion
2023W1-GD-S765 | 232013 | SILVER RUN | 232002 | CEDAR CK | 1 | 230 | 235/231 | 805 | 828.4 | 849.8 | 102.91 | 105.56 | DPL_P4-2_DP6_SRT-A | Breaker | 635/808/752/910 | Yes
2023W1-GD-S766 | 231130 | CECIL138 | 231124 | GLASGOW | 1 | 138 | 235 | 348 | 366.3 | 366.9 | 105.27 | 105.42 | PECO_P4_NOTTI895_SRT-A | Breaker | 309/378/305/405 | No | Below 200 kV exclusion
2023W1-GD-S771 | 232241 | VIENN_69 | 232838 | MARDELA | 1 | 69 | 235 | 64 | 67.1 | 67.2 | 104.83 | 105.01 | DPL_P4-2_DP56_SRT-A | Breaker | 64/64/81/81 | No | Below 200 kV exclusion
2023W1-GD-S582 | 248005 | 06KYGER | 242528 | 05SPORN | 1 | 345 | 205/206 | 1204 | 1447.2 | 1459 | 120.2 | 121.18 | AEP_P4_#1558_05BAKER 765_Q_SRT-A | Breaker | 1800/1800/2367/2367 | No | Substation Equipment Exclusion
2023W1-GD-S798 | 232003 | CARTANZA | 232004 | MILF_230 | 1 | 230 | 235 | 800 | 832.2 | 834 | 104.02 | 104.25 | DPL_P4-2_DPCEDAR231_SRT-A | Breaker | 653/808/752/910 | Yes
2023W1-GD-S158 | 232003 | CARTANZA | 232004 | MILF_230 | 1 | 230 | 235 | 800 | 832.2 | 834 | 104.02 | 104.25 | DPL_P1-2_CKT 23030_SRT-A | Single | 653/808/752/910 | Yes
2023W1-GD-S802 | 232003 | CARTANZA | 232004 | MILF_230 | 1 | 230 | 235 | 800 | 828.5 | 831.7 | 103.56 | 103.97 | DPL_P4-2_DPCEDAR230_SRT-A | Breaker | 653/808/752/910 | Yes
2023W1-GD-S803 | 232003 | CARTANZA | 232004 | MILF_230 | 1 | 230 | 235 | 800 | 826.6 | 831.7 | 103.32 | 103.97 | DPL_P4-2_DPCEDAR233_SRT-A | Breaker | 653/808/752/910 | Yes
2023W1-GD-S584 | 248005 | 06KYGER | 242528 | 05SPORN | 1 | 345 | 205/206 | 1204 | 1440.1 | 1453.8 | 119.61 | 120.75 | AEP_P4_#309_05HANG R 765_B2_SRT-A | Breaker | 1800/1800/2367/2367 | No | Substation Equipment Exclusion
2023W1-GD-S1276 | 213925 | RIDLEY | 213775 | MACDADE | 1 | 230 | 230 | 927 | 966.6 | 953.8 | 104.27 | 102.89 | PECO_P2-2_EDD230B3_SRT-A | Bus | 1462/1770/1644/1956 (SN/SE/WN/WE) | No | Substation Equipment Exclusion
2023W1-GD-S833 | 213925 | RIDLEY | 213775 | MACDADE | 1 | 230 | 230 | 927 | 965.9 | 953.7 | 104.2 | 102.88 | PECO_P4_EDDYS235_SRT-A | Breaker | 1462/1770/1644/1956 (SN/SE/WN/WE) | No | Substation Equipment Exclusion
2023W1-GD-S590 | 248005 | 06KYGER | 242528 | 05SPORN | 1 | 345 | 205/206 | 1204 | 1437.5 | 1450.9 | 119.39 | 120.51 | AEP_P4_#1560_05BAKER 765_Q2_SRT-A | Breaker | 1800/1800/2367/2367 | No | Substation Equipment Exclusion
2023W1-GD-S845 | 213925 | RIDLEY | 213775 | MACDADE | 1 | 230 | 230 | 927 | 956 | 943.2 | 103.13 | 101.75 | PECO_P4_EDDYS335_SRT-A | Breaker | 1462/1770/1644/1956 | No | Substation Equipment Exclusion
2023W1-GD-S849 | 232241 | VIENN_69 | 232838 | MARDELA | 1 | 69 | 235 | 64 | 64.8 | 64.9 | 101.32 | 101.44 | DPL_P4-2_DPVIENNA8110_SRT-A | Breaker | 64/64/81/81 | No | Below 200 kV exclusion
2023W1-GD-S646 | 248005 | 06KYGER | 242528 | 05SPORN | 1 | 345 | 205/206 | 1204 | 1373.6 | 1383.3 | 114.09 | 114.89 | AEP_P4_#3145_05GAVIN 765_B_SRT-A | Breaker | 1800/1800/2367/2367 | No | Substation Equipment Exclusion
2023W1-GD-S878 | 232241 | VIENN_69 | 232838 | MARDELA | 1 | 69 | 235 | 64 | 64.5 | 64.6 | 100.73 | 100.96 | DPL_P4-2_DP55_SRT-A | Breaker | 64/64/81/81 | No | Below 200 kV exclusion
2023W1-GD-S650 | 248005 | 06KYGER | 242528 | 05SPORN | 1 | 345 | 205/206 | 1204 | 1363.6 | 1377.9 | 113.26 | 114.44 | AEP_P4_#708_05GAVIN 765_B1_SRT-A | Breaker | 1800/1800/2367/2367 | No | Substation Equipment Exclusion
2023W1-GD-S190 | 270737 | ELWOOD ; R | 270769 | GOODINGS ;2R | 1 | 345 | 222 | 1334 | 1356.7 | 1340.2 | 101.71 | 100.47 | Base Case | Single | 1334/1726/1837/2084 (SN/SE/SSTE/SLD) | Yes
2023W1-GD-S1436 | 232003 | CARTANZA | 232004 | MILF_230 | 1 | 230 | 235 | 800 | 794.6 | 802.4 | 99.32 | 100.3 | DPL_P7_1_DBL_1NCB_FSA_SRT-SL | Tower | 653/808/752/910 | Yes
2023W1-GD-S499 | 242920 | 05BELMON | 235102 | 01BELMNT | 5 | 765/500 | 201/205 | 2492 | 3459 | 3475.3 | 138.81 | 139.46 | AEP_P4_#8975_05KAMMER 765_MM2_SRT-A | Breaker | 2351/3148/3600 MVA SN/SE/SLD | Yes
2023W1-GD-S500 | 242920 | 05BELMON | 235102 | 01BELMNT | 5 | 765/500 | 201/205 | 2492 | 3458.4 | 3475 | 138.78 | 139.45 | AP_P2-3_WP-500-DRT7A_SRT-SL | Breaker | 2351/3148/3600 MVA SN/SE/SLD | Yes
2023W1-GD-S501 | 242920 | 05BELMON | 235102 | 01BELMNT | 5 | 765/500 | 201/205 | 2492 | 3457.1 | 3474.4 | 138.73 | 139.42 | AP_P2-3_WP-500-DRT10A_SRT-SL | Breaker | 2351/3148/3600 MVA SN/SE/SLD | Yes
2023W1-GD-S87 | 242920 | 05BELMON | 235102 | 01BELMNT | 5 | 765/500 | 201/205 | 2492 | 2861.3 | 2876.9 | 114.82 | 115.44 | AP_P1-3_MP-765-502T_SRT-A | Single | 2351/3148/3600 MVA SN/SE/SLD | Yes
2023W1-GD-S80 | 242920 | 05BELMON | 235102 | 01BELMNT | 5 | 765/500 | 201/205 | 2492 | 2860.8 | 2876.8 | 114.8 | 115.44 | AP_P1-2_MP-500-028_SRT-A | Single | 2351/3148/3600 MVA SN/SE/SLD | Yes
2023W1-GD-S89 | 242920 | 05BELMON | 235102 | 01BELMNT | 5 | 765/500 | 201/205 | 2492 | 2860.3 | 2876.6 | 114.78 | 115.43 | AP_P1-2_WP-500-305T_SRT-A | Single | 2351/3148/3600 MVA SN/SE/SLD | Yes
2023W1-GD-S772 | 214206 | RICHRE29 | 214274 | RICHMOND29 | 1 | 230 | 230 | 1336 | 1413.6 | 1401.8 | 105.81 | 104.92 | PECO_P4_PEACH215_SRT-A | Breaker | 1462/1770/1644/1956 (SN/SE/WN/WE) | No | Related to 2022 Window 3, pending window outcome
2023W1-GD-S785 | 214206 | RICHRE29 | 214274 | RICHMOND29 | 1 | 230 | 230 | 1336 | 1418.2 | 1396.8 | 106.15 | 104.55 | PECO_P4_CHICH045_SRT-A | Breaker | 1462/1770/1644/1956 (SN/SE/WN/WE) | No | Related to 2022 Window 3, pending window outcome
2023W1-GD-S1271 | 214206 | RICHRE29 | 214274 | RICHMOND29 | 1 | 230 | 230 | 1336 | 1417.9 | 1396.8 | 106.13 | 104.55 | PECO_P2-2_CHI230B1_SRT-A | Bus | 1462/1770/1644/1956 (SN/SE/WN/WE) | No | Related to 2022 Window 3, pending window outcome
2023W1-GD-S786 | 214206 | RICHRE29 | 214274 | RICHMOND29 | 1 | 230 | 230 | 1336 | 1418.3 | 1396.8 | 106.16 | 104.55 | PECO_P4_CHICH195_SRT-A | Breaker | 1462/1770/1644/1956 (SN/SE/WN/WE) | No | Related to 2022 Window 3, pending window outcome
2023W1-GD-S788 | 214206 | RICHRE29 | 214274 | RICHMOND29 | 1 | 230 | 230 | 1336 | 1418 | 1396.7 | 106.14 | 104.55 | PECO_P4_CHICH435_SRT-A | Breaker | 1462/1770/1644/1956 (SN/SE/WN/WE) | No | Related to 2022 Window 3, pending window outcome
2023W1-GD-S836 | 214206 | RICHRE29 | 214274 | RICHMOND29 | 1 | 230 | 230 | 1336 | 1377.8 | 1370.7 | 103.13 | 102.6 | PECO_P4_PEACH205_SRT-A | Breaker | 1462/1770/1644/1956 | No | Related to 2022 Window 3, pending window outcome
2023W1-GD-S624 | 214277 | RICHMOND35 | 214012 | WANEETA3 | 1 | 230 | 230 | 1180 | 1385.5 | 1366.6 | 117.41 | 115.81 | PECO_P4_CHICH045_SRT-A | Breaker | 760(UGT)1098(OHT)/1180(UGT)1247(OHT)/803(UGT)1150(OHT)/1201(UGT)1299(OHT) | No | Related to 2022 Window 3, pending window outcome
2023W1-GD-S1261 | 214277 | RICHMOND35 | 214012 | WANEETA3 | 1 | 230 | 230 | 1180 | 1385.2 | 1366.5 | 117.39 | 115.81 | PECO_P2-2_CHI230B1_SRT-A | Bus | 760(UGT)1098(OHT)/1180(UGT)1247(OHT)/803(UGT)1150(OHT)/1201(UGT)1299(OHT) | No | Related to 2022 Window 3, pending window outcome
2023W1-GD-S625 | 214277 | RICHMOND35 | 214012 | WANEETA3 | 1 | 230 | 230 | 1180 | 1385.6 | 1366.5 | 117.42 | 115.81 | PECO_P4_CHICH195_SRT-A | Breaker | 760(UGT)1098(OHT)/1180(UGT)1247(OHT)/803(UGT)1150(OHT)/1201(UGT)1299(OHT) | No | Related to 2022 Window 3, pending window outcome
2023W1-GD-S626 | 214277 | RICHMOND35 | 214012 | WANEETA3 | 1 | 230 | 230 | 1180 | 1385.3 | 1366.5 | 117.4 | 115.8 | PECO_P4_CHICH435_SRT-A | Breaker | 760(UGT)1098(OHT)/1180(UGT)1247(OHT)/803(UGT)1150(OHT)/1201(UGT)1299(OHT) | No | Related to 2022 Window 3, pending window outcome
2023W1-GD-S666 | 214277 | RICHMOND35 | 214012 | WANEETA3 | 1 | 230 | 230 | 1180 | 1341.1 | 1332.6 | 113.66 | 112.93 | PECO_P4_PEACH215_SRT-A | Breaker | 760(UGT)1098(OHT)/1180(UGT)1247(OHT)/803(UGT)1150(OHT)/1201(UGT)1299(OHT) | No | Related to 2022 Window 3, pending window outcome
2023W1-GD-S695 | 214277 | RICHMOND35 | 214012 | WANEETA3 | 1 | 230 | 230 | 1180 | 1301.4 | 1295.3 | 110.29 | 109.77 | PECO_P4_PEACH205_SRT-A | Breaker | 760(UGT)1098(OHT)/1180(UGT)1247(OHT)/803(UGT)1150(OHT)/1201(UGT)1299(OHT) | No | Related to 2022 Window 3, pending window outcome
2023W1-GD-S773 | 219125 | CAMDEN | 214206 | RICHRE29 | 1 | 230 | 230/231 | 1336 | 1413.8 | 1401.8 | 105.82 | 104.92 | PECO_P4_PEACH215_SRT-A | Breaker | 1462/1770/1644/1956 (SN/SE/WN/WE) | No | Related to 2022 Window 3, pending window outcome
2023W1-GD-S784 | 219125 | CAMDEN | 214206 | RICHRE29 | 1 | 230 | 230/231 | 1336 | 1418.4 | 1396.8 | 106.17 | 104.55 | PECO_P4_CHICH045_SRT-A | Breaker | 1462/1770/1644/1956 (SN/SE/WN/WE) | No | Related to 2022 Window 3, pending window outcome
2023W1-GD-S1272 | 219125 | CAMDEN | 214206 | RICHRE29 | 1 | 230 | 230/231 | 1336 | 1418.1 | 1396.8 | 106.14 | 104.55 | PECO_P2-2_CHI230B1_SRT-A | Bus | 1462/1770/1644/1956 (SN/SE/WN/WE) | No | Related to 2022 Window 3, pending window outcome
2023W1-GD-S787 | 219125 | CAMDEN | 214206 | RICHRE29 | 1 | 230 | 230/231 | 1336 | 1418.5 | 1396.8 | 106.17 | 104.55 | PECO_P4_CHICH195_SRT-A | Breaker | 1462/1770/1644/1956 (SN/SE/WN/WE) | No | Related to 2022 Window 3, pending window outcome
2023W1-GD-S789 | 219125 | CAMDEN | 214206 | RICHRE29 | 1 | 230 | 230/231 | 1336 | 1418.2 | 1396.7 | 106.15 | 104.55 | PECO_P4_CHICH435_SRT-A | Breaker | 1462/1770/1644/1956 (SN/SE/WN/WE) | No | Related to 2022 Window 3, pending window outcome
2023W1-GD-S837 | 219125 | CAMDEN | 214206 | RICHRE29 | 1 | 230 | 230/231 | 1336 | 1378 | 1370.7 | 103.14 | 102.6 | PECO_P4_PEACH205_SRT-A | Breaker | 1462/1770/1644/1956 (SN/SE/WN/WE) | No | Related to 2022 Window 3, pending window outcome
2023W1-GD-S2408 | 214012 | WANEETA3 | 214010 | WANEETA2 | Z | 230 | 230 | 1008 | 1014.9 | 1008.2 | 100.68 | 100.02 | PECO_P4_CHICH045_SRT-A | Breaker | 863/1008 (SN/SE) | No | Related to 2022 Window 3, pending window outcome
2023W1-GD-S2407 | 214012 | WANEETA3 | 214010 | WANEETA2 | Z | 230 | 230 | 1008 | 1015 | 1008.2 | 100.7 | 100.02 | PECO_P4_CHICH195_SRT-A | Breaker | 863/1008 (SN/SE) | No | Related to 2022 Window 3, pending window outcome
2023W1-GD-S989 | 214012 | WANEETA3 | 214010 | WANEETA2 | Z | 230 | 230 | 1008 | 1014.6 | 1008.2 | 100.66 | 100.02 | PECO_P2-2_CHI230B1_SRT-A | Bus | 863/1008 (SN/SE) | No | Related to 2022 Window 3, pending window outcome
2023W1-GD-S2410 | 214012 | WANEETA3 | 214010 | WANEETA2 | Z | 230 | 230 | 1008 | 1014.7 | 1008.2 | 100.66 | 100.02 | PECO_P4_CHICH435_SRT-A | Breaker | 863/1008 (SN/SE) | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 797 | 3045.2 | 2967.1 | 382.09 | 372.28 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | Breaker | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 797 | 3044.8 | 2966.7 | 382.04 | 372.24 | PECO_P4_PEACH235_SRT-A | Breaker | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 797 | 3046.8 | 2965.8 | 382.28 | 372.13 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | Breaker | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 797 | 2919.2 | 2855.7 | 366.27 | 358.31 | PECO_P4_PEACH245_SRT-A | Breaker | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 814 | 2870.1 | 2801.4 | 352.59 | 344.15 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | Breaker | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 814 | 2869.7 | 2801.1 | 352.54 | 344.11 | PECO_P4_PEACH235_SRT-A | Breaker | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 814 | 2871.7 | 2800 | 352.79 | 343.98 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | Breaker | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 814 | 2742 | 2687.4 | 336.86 | 330.15 | PECO_P4_PEACH245_SRT-A | Breaker | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 797 | 2699.5 | 2620.9 | 338.71 | 328.84 | PECO_P1-2_5012_SRT-A | Single | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 814 | 2520.8 | 2451.7 | 309.68 | 301.19 | PECO_P1-2_5012_SRT-A | Single | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 563 | 1350 | 1342.1 | 239.79 | 238.38 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | Breaker | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 563 | 1348.1 | 1342.1 | 239.45 | 238.38 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | Breaker | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 563 | 1348.2 | 1338.6 | 239.47 | 237.76 | PECO_P4_PEACH235_SRT-A | Breaker | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 563 | 1346.3 | 1338.6 | 239.13 | 237.76 | PECO_P4_PEACH235_SRT-A | Breaker | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 563 | 1345.7 | 1338 | 239.03 | 237.66 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | Breaker | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 563 | 1347.7 | 1338 | 239.37 | 237.66 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | Breaker | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 797 | 1889.7 | 1863.6 | 237.1 | 233.83 | PJM_500_BG_P4_5_CNSTN_15_SRT-A | Breaker | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 578 | 1333.1 | 1328.2 | 230.63 | 229.79 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | Breaker | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 578 | 1331.3 | 1324.7 | 230.32 | 229.18 | PECO_P4_PEACH235_SRT-A | Breaker | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 578 | 1330.7 | 1324.1 | 230.22 | 229.09 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | Breaker | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 578 | 1298.2 | 1297.6 | 224.61 | 224.5 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | Breaker | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 578 | 1296.4 | 1294 | 224.3 | 223.88 | PECO_P4_PEACH235_SRT-A | Breaker | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 578 | 1295.9 | 1293.5 | 224.2 | 223.78 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | Breaker | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 563 | 1266.9 | 1258 | 225.03 | 223.44 | PECO_P4_PEACH245_SRT-A | Breaker | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 563 | 1265 | 1258 | 224.68 | 223.44 | PECO_P4_PEACH245_SRT-A | Breaker | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 797 | 1779.3 | 1750 | 223.26 | 219.58 | BG_P7_GRCTN_CNSTN_SRT-A | Tower | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 578 | 1249.9 | 1244 | 216.25 | 215.22 | PECO_P4_PEACH245_SRT-A | Breaker | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 797 | 1732.9 | 1710.4 | 217.43 | 214.6 | PECO_P2-2_NOTT230B_SRT-A | Bus | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 578 | 1215.1 | 1213.1 | 210.23 | 209.87 | PECO_P4_PEACH245_SRT-A | Breaker | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 814 | 1706.5 | 1688 | 209.65 | 207.38 | PJM_500_BG_P4_5_CNSTN_15_SRT-A | Breaker | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 797 | 1594.7 | 1614.9 | 200.09 | 202.63 | PJM_500_BG_P1_5011_SRT-A | Single | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 797 | 1631.4 | 1607.6 | 204.69 | 201.71 | PJM_500_BG_P2_CNSTN_230-S_SRT-A | Bus | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 797 | 1630.9 | 1607.1 | 204.63 | 201.65 | PJM_500_BG_P2_CNSTN_230-N_SRT-A | Bus | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200065 | PCHBTM2S | 200064 | PCHBTM1S | Z1 | 500 | 230 | 2860 | 5835.6 | 5693.5 | 204.04 | 199.07 | PECO_P4_PEACH255_SRT-A | Breaker | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 1333.6 | 1316.7 | 200.24 | 197.71 | Base Case | Single | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 563 | 1116.8 | 1106.9 | 198.37 | 196.61 | PECO_P1-2_5012_SRT-A | Single | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 563 | 1114.9 | 1106.9 | 198.02 | 196.61 | PECO_P1-2_5012_SRT-A | Single | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200004 | CNASTONE | 1 | 500 | 232/230 | 3526 | 7015.3 | 6873.9 | 198.96 | 194.95 | PL_05_P71_000906_SRT-A | Tower | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200004 | CNASTONE | 1 | 500 | 232/230 | 3526 | 6983 | 6839.9 | 198.04 | 193.98 | PL_04_P42_000557_SRT-A | Breaker | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 814 | 1599.1 | 1577.4 | 196.45 | 193.79 | BG_P7_GRCTN_CNSTN_SRT-A | Tower | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 797 | 1562.1 | 1540.6 | 196 | 193.3 | PECO_P1-2_220-08_SRT-A | Single | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 797 | 1563 | 1539.4 | 196.12 | 193.15 | BG_P1_CNSTN_500-4_SRT-A | Single | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 797 | 1562.5 | 1538.9 | 196.05 | 193.09 | BG_P1_CNSTN_500-2_SRT-A | Single | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200004 | CNASTONE | 1 | 500 | 232/230 | 3526 | 6950 | 6800.7 | 197.11 | 192.87 | PECO_P2-2_NOTT230B_SRT-A | Bus | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200004 | CNASTONE | 1 | 500 | 232/230 | 3526 | 6942 | 6798.7 | 196.88 | 192.82 | PL_04_P42_000561_SRT-A | Breaker | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200004 | CNASTONE | 1 | 500 | 232/230 | 3526 | 6918.9 | 6779.4 | 196.23 | 192.27 | BG_P4_5_GRCTN_2T_SRT-A | Breaker | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200004 | CNASTONE | 1 | 500 | 232/230 | 3526 | 6920.7 | 6777.8 | 196.28 | 192.22 | PL_05_P22_000674_SRT-A | Bus | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200004 | CNASTONE | 1 | 500 | 232/230 | 3526 | 6926.4 | 6768.5 | 196.44 | 191.96 | PJM_500_BG_P4_5_CNSTN_M_SRT-A | Breaker | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 814 | 1575.6 | 1562.1 | 193.56 | 191.9 | PECO_P2-2_NOTT230B_SRT-A | Bus | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200004 | CNASTONE | 1 | 500 | 232/230 | 2828 | 5545 | 5399.2 | 196.08 | 190.92 | Base Case | Single | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200004 | CNASTONE | 1 | 500 | 232/230 | 3526 | 6854.5 | 6704.6 | 194.4 | 190.15 | PL_04_P71_001014_SRT-A | Tower | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 578 | 1099.8 | 1093.1 | 190.28 | 189.11 | PECO_P1-2_5012_SRT-A | Single | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 797 | 1519.1 | 1502 | 190.6 | 188.45 | AP_P7-1_PE-138-022T_SRT-A | Tower | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 797 | 1519.1 | 1502 | 190.6 | 188.45 | AP_P2-2_PE-138-073_SRT-A | Bus | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 801 | 1518.8 | 1509.4 | 189.61 | 188.44 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | Breaker | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 801 | 1518.5 | 1509.2 | 189.58 | 188.41 | PECO_P4_PEACH235_SRT-A | Breaker | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200004 | CNASTONE | 1 | 500 | 232/230 | 3526 | 6790.8 | 6640 | 192.59 | 188.32 | DVP_P4-3: H1TH3_SRT-SW | Breaker | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200004 | CNASTONE | 1 | 500 | 232/230 | 3526 | 6785.5 | 6639.9 | 192.44 | 188.31 | PL_04_P22_102817_SRT-A | Bus | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200004 | CNASTONE | 1 | 500 | 232/230 | 3526 | 6783.3 | 6637.7 | 192.38 | 188.25 | PL_04_P71_000904_SRT-A | Tower | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 797 | 1516.3 | 1500.1 | 190.25 | 188.22 | AP_P2-2_PE-138-003_SRT-A | Bus | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200004 | CNASTONE | 1 | 500 | 232/230 | 3526 | 6781.9 | 6636.5 | 192.34 | 188.22 | PL_04_P71_001822_SRT-A | Tower | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200004 | CNASTONE | 1 | 500 | 232/230 | 3526 | 6695.3 | 6569.2 | 189.88 | 186.31 | BG_P7_GRCTN_RAPHEL_SRT-A | Tower | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200004 | CNASTONE | 1 | 500 | 232/230 | 3526 | 6710.4 | 6566.2 | 190.31 | 186.22 | PL_04_P22_102818_SRT-A | Bus | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200004 | CNASTONE | 1 | 500 | 232/230 | 3526 | 6686 | 6537.2 | 189.62 | 185.4 | PL_04_P22_102291_SRT-A | Bus | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200003 | BRIGHTON | 1 | 500 | 233/232 | 2815 | 5256.7 | 5212.2 | 186.74 | 185.16 | BG_P7_CNSTN_NWEST2_SRT-A | Tower | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200003 | BRIGHTON | 1 | 500 | 233/232 | 2815 | 5218.5 | 5185.1 | 185.38 | 184.2 | BG_P7_GRCTN_RAPHEL_SRT-A | Tower | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 578 | 1065 | 1062.4 | 184.26 | 183.8 | PECO_P1-2_5012_SRT-A | Single | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200003 | BRIGHTON | 1 | 500 | 233/232 | 2815 | 5184.8 | 5151.6 | 184.19 | 183.01 | BG_P7_NEAST_RPHLRD_SRT-A | Tower | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200065 | PCHBTM2S | 200064 | PCHBTM1S | Z2 | 500 | 230 | 2860 | 5324.2 | 5224 | 186.16 | 182.66 | PECO_P4_PEACH025_SRT-A | Breaker | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 801 | 1456.9 | 1446.3 | 181.88 | 180.56 | PECO_P4_PEACH245_SRT-A | Breaker | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 801 | 1442.8 | 1436.3 | 180.13 | 179.31 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | Breaker | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 814 | 1412.5 | 1449 | 173.52 | 178 | PJM_500_BG_P1_5011_SRT-A | Single | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 797 | 1424.6 | 1407.5 | 178.74 | 176.6 | PL_04_P71_100954_SRT-A | Tower | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 814 | 1452.9 | 1437.5 | 178.49 | 176.59 | PJM_500_BG_P2_CNSTN_230-S_SRT-A | Bus | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 814 | 1452.4 | 1436.9 | 178.43 | 176.53 | PJM_500_BG_P2_CNSTN_230-N_SRT-A | Bus | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200065 | PCHBTM2S | 200064 | PCHBTM1S | Z1 | 500 | 230 | 2860 | 5125.6 | 5012.4 | 179.22 | 175.26 | PECO_P4_PEACH055_SRT-A | Breaker | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 797 | 1410.6 | 1395.1 | 176.99 | 175.05 | DVP_P7-1: LN 2114-535_SRT-SW | Tower | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 797 | 1407.8 | 1392.5 | 176.63 | 174.71 | DVP_P7-1: LN 2222-535_SRT-A | Tower | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200003 | BRIGHTON | 1 | 500 | 233/232 | 2815 | 4975.1 | 4917.3 | 176.74 | 174.68 | PJM_500_BG_P4_5_CNSTN_13_SRT-A | Breaker | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200003 | BRIGHTON | 1 | 500 | 233/232 | 2815 | 4972.6 | 4915 | 176.65 | 174.6 | PJM_500_BG_P4_5_CNSTN_6_SRT-A | Breaker | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208078 | SAKR | 208030 | MLWD TR1 | 1 | 230 | 229 | 801 | 1394.2 | 1389.7 | 174.06 | 173.5 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | Breaker | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208078 | SAKR | 208030 | MLWD TR1 | 1 | 230 | 229 | 801 | 1391.1 | 1384.7 | 173.67 | 172.87 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | Breaker | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208078 | SAKR | 208030 | MLWD TR1 | 1 | 230 | 229 | 801 | 1391 | 1384.6 | 173.66 | 172.86 | PECO_P4_PEACH235_SRT-A | Breaker | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 814 | 1398 | 1385.3 | 171.75 | 170.18 | PECO_P1-2_220-08_SRT-A | Single | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200003 | BRIGHTON | 1 | 500 | 233/232 | 2815 | 4821.9 | 4786.9 | 171.29 | 170.05 | AP_P2-3_PE-500-015_SRT-A | Breaker | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 814 | 1391.5 | 1378.7 | 170.95 | 169.38 | PECO_P1-2_220-93_SRT-A | Single | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200003 | BRIGHTON | 1 | 500 | 233/232 | 2815 | 4797.4 | 4767.6 | 170.42 | 169.36 | AP_P2-3_PE-500-016_SRT-SL | Breaker | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200003 | BRIGHTON | 1 | 500 | 233/232 | 2815 | 4798.2 | 4767.4 | 170.45 | 169.36 | AP_P2-3_PE-500-018C_SRT-SL | Breaker | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200065 | PCHBTM2S | 200064 | PCHBTM1S | Z1 | 500 | 230 | 2860 | 4912.8 | 4836.1 | 171.78 | 169.09 | PECO_P4_PEACH045_SRT-A | Breaker | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200003 | BRIGHTON | 1 | 500 | 233/232 | 2815 | 4817.2 | 4754.7 | 171.13 | 168.9 | BG_P7_GRNITE_HIRDG_SRT-A | Tower | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200004 | CNASTONE | 1 | 500 | 232/230 | 3526 | 6105.1 | 5945.4 | 173.14 | 168.61 | PJM_500_BG_P1_5013_SRT-A | Single | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200003 | BRIGHTON | 1 | 500 | 233/232 | 2815 | 4791.3 | 4731.2 | 170.21 | 168.07 | BG_P7_NWEST_GRNITE_SRT-A | Tower | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 814 | 1381.9 | 1366.5 | 169.76 | 167.88 | BG_P1_CNSTN_500-4_SRT-A | Single | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200003 | BRIGHTON | 1 | 500 | 233/232 | 2815 | 4769.4 | 4707 | 169.43 | 167.21 | PJM_500_BG_P2_CNSTN_230-S_SRT-A | Bus | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200003 | BRIGHTON | 1 | 500 | 233/232 | 2815 | 4768.5 | 4706.2 | 169.4 | 167.18 | PJM_500_BG_P2_CNSTN_230-N_SRT-A | Bus | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208020 | MANO TR3 | 208019 | MANO | 1 | 230 | 229 | 731 | 1213 | 1221.3 | 165.93 | 167.08 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | Breaker | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 801 | 1344.3 | 1336.4 | 167.82 | 166.84 | PECO_P1-2_5012_SRT-A | Single | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208020 | MANO TR3 | 208019 | MANO | 1 | 230 | 229 | 731 | 1210.5 | 1216.8 | 165.59 | 166.46 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | Breaker | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208020 | MANO TR3 | 208019 | MANO | 1 | 230 | 229 | 731 | 1210.4 | 1216.7 | 165.58 | 166.44 | PECO_P4_PEACH235_SRT-A | Breaker | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200004 | CNASTONE | 1 | 500 | 232/230 | 3526 | 5978.8 | 5833.8 | 169.56 | 165.45 | PL_04_P12_000257_SRT-A | Single | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200004 | CNASTONE | 1 | 500 | 232/230 | 3526 | 5958.4 | 5808 | 168.99 | 164.72 | PECO_P1-2_220-08_SRT-A | Single | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 1193.5 | 1186.9 | 165.54 | 164.61 | Base Case | Single | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200003 | BRIGHTON | 1 | 500 | 233/232 | 2815 | 4685.7 | 4620.4 | 166.45 | 164.14 | AP_P2-2_WP-500-DRT16_SRT-SL | Bus | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 814 | 1339.5 | 1332.5 | 164.56 | 163.7 | AP_P7-1_PE-138-022T_SRT-A | Tower | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 814 | 1339.5 | 1332.5 | 164.56 | 163.7 | AP_P2-2_PE-138-073_SRT-A | Bus | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208078 | SAKR | 208030 | MLWD TR1 | 1 | 230 | 229 | 801 | 1317.6 | 1309.9 | 164.5 | 163.54 | PECO_P4_PEACH245_SRT-A | Breaker | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 814 | 1336.7 | 1330.7 | 164.22 | 163.47 | AP_P2-2_PE-138-003_SRT-A | Bus | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200004 | CNASTONE | 1 | 500 | 232/230 | 3526 | 5893.3 | 5721.2 | 167.14 | 162.26 | PN_P1-2_PN-500-010T_SRT-A | Single | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200003 | BRIGHTON | 1 | 500 | 233/232 | 2815 | 4620.1 | 4558 | 164.13 | 161.92 | AP_P2-2_PE-138-073_SRT-A | Bus | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200003 | BRIGHTON | 1 | 500 | 233/232 | 2815 | 4619.8 | 4557.3 | 164.11 | 161.89 | ME_P2-2_ME-115-003_SRT-A | Bus | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200004 | CNASTONE | 1 | 500 | 232/230 | 3526 | 5841.8 | 5693.5 | 165.68 | 161.47 | DVP_P1-2: LN 596_SRT-SW | Single | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208031 | MLWD TR2 | 1 | 230 | 229 | 814 | 1303.4 | 1304.8 | 160.12 | 160.3 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | Breaker | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208031 | MLWD TR2 | 1 | 230 | 229 | 814 | 1300.7 | 1300.2 | 159.79 | 159.73 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | Breaker | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208031 | MLWD TR2 | 1 | 230 | 229 | 814 | 1300.6 | 1300.1 | 159.78 | 159.72 | PECO_P4_PEACH235_SRT-A | Breaker | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200065 | PCHBTM2S | 200064 | PCHBTM1S | Z2 | 500 | 230 | 2860 | 4572.2 | 4541.4 | 159.87 | 158.79 | PECO_P4_PEACH015_SRT-A | Breaker | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200065 | PCHBTM2S | 200064 | PCHBTM1S | Z1 | 500 | 230 | 2860 | 4570.6 | 4540.4 | 159.81 | 158.75 | PECO_P4_PEACH225_SRT-A | Breaker | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1417 | 2234.7 | 2242.3 | 157.71 | 158.24 | DVP_P4-2: 514T595_SRT-SW | Breaker | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 814 | 1285.7 | 1278.5 | 157.95 | 157.07 | PL_04_P71_100954_SRT-A | Tower | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208020 | MANO TR3 | 208019 | MANO | 1 | 230 | 229 | 731 | 1142.3 | 1145.7 | 156.27 | 156.73 | PECO_P4_PEACH245_SRT-A | Breaker | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1417 | 2205.2 | 2216.9 | 155.62 | 156.45 | DVP_P4-2: 51482_SRT-A | Breaker | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 814 | 1267.8 | 1261.6 | 155.75 | 154.99 | PL_04_P71_100955_SRT-A | Tower | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 814 | 1266.9 | 1260.3 | 155.64 | 154.83 | PL_04_P71_100956_SRT-A | Tower | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200003 | BRIGHTON | 1 | 500 | 233/232 | 2490 | 3915.2 | 3849.2 | 157.24 | 154.59 | Base Case | Single | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200065 | PCHBTM2S | 200064 | PCHBTM1S | Z2 | 500 | 230 | 2860 | 4492.1 | 4409.7 | 157.07 | 154.18 | PECO_P4_PEACH205_SRT-A | Breaker | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208031 | MLWD TR2 | 208020 | MANO TR3 | 1 | 230 | 229 | 801 | 1223.9 | 1229.3 | 152.8 | 153.47 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | Breaker | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208031 | MLWD TR2 | 208020 | MANO TR3 | 1 | 230 | 229 | 801 | 1220.8 | 1224.2 | 152.41 | 152.83 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | Breaker | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208031 | MLWD TR2 | 208020 | MANO TR3 | 1 | 230 | 229 | 801 | 1220.7 | 1224.1 | 152.4 | 152.82 | PECO_P4_PEACH235_SRT-A | Breaker | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 220980 | RAPHAEL | 220965 | NEAST339 | 1 | 230 | 232 | 1283 | 1957 | 1949.2 | 152.53 | 151.92 | BG_P4_5_NEAST_17_SRT-A | Breaker | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 220980 | RAPHAEL | 220965 | NEAST339 | 1 | 230 | 232 | 1283 | 1957.9 | 1949.2 | 152.6 | 151.92 | BG_P4_5_NEAST_15_SRT-A | Breaker | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208031 | MLWD TR2 | 1 | 230 | 229 | 814 | 1230.2 | 1227.9 | 151.14 | 150.85 | PECO_P4_PEACH245_SRT-A | Breaker | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 220980 | RAPHAEL | 220979 | NEAST317 | 1 | 230 | 232 | 1283 | 1941.9 | 1933.5 | 151.36 | 150.7 | BG_P4_5_NEAST_39_SRT-A | Breaker | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 220980 | RAPHAEL | 220979 | NEAST317 | 1 | 230 | 232 | 1283 | 1941.9 | 1933.5 | 151.36 | 150.7 | BG_P4_5_NEAST_37_SRT-A | Breaker | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208078 | SAKR | 208030 | MLWD TR1 | 1 | 230 | 229 | 801 | 1211.2 | 1205.5 | 151.21 | 150.5 | PECO_P1-2_5012_SRT-A | Single | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 221090 | GLENARM2 | 221089 | WINDYED1 | 1 | 115 | 232 | 192 | 285.9 | 287.7 | 148.89 | 149.82 | BG_P7_GRCTN_RAPHEL_SRT-A | Tower | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200003 | BRIGHTON | 1 | 500 | 233/232 | 2815 | 4235.3 | 4203.9 | 150.46 | 149.34 | AP_P1-2_PE-500-001_SRT-SL | Single | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200003 | BRIGHTON | 1 | 500 | 233/232 | 2815 | 4235.3 | 4203.9 | 150.46 | 149.34 | AP_P1-2_WP-500-DRT17_SRT-SL | Single | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 235463 | 01TANEY | 1 | 138 | 227/201 | 268 | 404.6 | 399.9 | 150.96 | 149.21 | PJM_500_BG_P4_5_CNSTN_J_SRT-A | Breaker | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 235463 | 01TANEY | 1 | 138 | 227/201 | 268 | 403.8 | 399.2 | 150.68 | 148.94 | PEPCO_P4_PP40_SRT-A | Breaker | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200003 | BRIGHTON | 1 | 500 | 233/232 | 2815 | 4225 | 4186 | 150.09 | 148.7 | AP_P1-2_PE-500-004_SRT-SL | Single | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200003 | BRIGHTON | 1 | 500 | 233/232 | 2815 | 4225 | 4186 | 150.09 | 148.7 | AP_P1-2_WP-500-006_SRT-A | Single | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1417 | 2084.1 | 2091.9 | 147.08 | 147.63 | AP_P2-3_PE-500-019C_SRT-SL | Breaker | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200003 | BRIGHTON | 1 | 500 | 233/232 | 2815 | 4172.7 | 4108.9 | 148.23 | 145.96 | BG_P1_CNSTN_500-4_SRT-A | Single | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208031 | MLWD TR2 | 208020 | MANO TR3 | 1 | 230 | 229 | 801 | 1153.3 | 1154.2 | 143.98 | 144.1 | PECO_P4_PEACH245_SRT-A | Breaker | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208020 | MANO TR3 | 208019 | MANO | 1 | 230 | 229 | 731 | 1041.5 | 1049.1 | 142.47 | 143.52 | PECO_P1-2_5012_SRT-A | Single | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200065 | PCHBTM2S | 200064 | PCHBTM1S | Z1 | 500 | 230 | 2860 | 4180.2 | 4089.6 | 146.16 | 142.99 | PECO_P1-2_PBTIE2_SRT-A | Single | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200065 | PCHBTM2S | 200064 | PCHBTM1S | Z2 | 500 | 230 | 2860 | 4180.2 | 4089.5 | 146.16 | 142.99 | PECO_P1-2_PBTIE1_SRT-A | Single | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 205912 | AD1-020 TAP | 204544 | 27LINCOLN | 1 | 115 | 227 | 282 | 403.6 | 402.1 | 143.11 | 142.59 | PJM_500_BG_P4_5_CNSTN_J_SRT-A | Breaker | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 205912 | AD1-020 TAP | 204544 | 27LINCOLN | 1 | 115 | 227 | 282 | 402.9 | 401.4 | 142.87 | 142.35 | PEPCO_P4_PP40_SRT-A | Breaker | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 221092 | FIVE.FOR | 221096 | ROCKRGE1 | 1 | 115 | 232 | 256 | 358.6 | 361.9 | 140.09 | 141.35 | BG_P7_GRCTN_RAPHEL_SRT-A | Tower | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 221090 | GLENARM2 | 221089 | WINDYED1 | 1 | 115 | 232 | 192 | 263.5 | 266.6 | 137.26 | 138.86 | BG_P7_NEAST_RPHLRD_SRT-A | Tower | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208031 | MLWD TR2 | 1 | 230 | 229 | 814 | 1128.4 | 1128.8 | 138.62 | 138.67 | PECO_P1-2_5012_SRT-A | Single | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 223938 | DICKH230 | 223937 | DICK 230 | 2 | 230 | 233 | 680 | 959.5 | 941.7 | 141.1 | 138.49 | PEPCO_P1_PP1_SRT-A | Single | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 223938 | DICKH230 | 223937 | DICK 230 | 1 | 230 | 233 | 680 | 959.5 | 941.7 | 141.1 | 138.49 | PEPCO_P1_PP2_SRT-A | Single | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 220980 | RAPHAEL | 220965 | NEAST339 | 1 | 230 | 232 | 1283 | 1783.3 | 1774.9 | 138.99 | 138.34 | BG_P1_2315_SRT-A | Single | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 220964 | GRACETON | 220999 | BAGLEY2 | 13 | 230 | 232 | 1594 | 2204 | 2191.6 | 138.27 | 137.49 | BG_P4_5_GRCTN_3T_SRT-A | Breaker | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 220980 | RAPHAEL | 220979 | NEAST317 | 1 | 230 | 232 | 1283 | 1770.6 | 1762.5 | 138.01 | 137.37 | BG_P1_2337_SRT-A | Single | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1417 | 1905.9 | 1911.5 | 134.5 | 134.9 | AP_P1-2_PE-500-407T_SRT-SL | Single | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1417 | 1905.9 | 1911.5 | 134.5 | 134.9 | DVP_P1-2: LN 514_SRT-A | Single | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 204538 | 27STRABAN | 1 | 115 | 227 | 313 | 420 | 421.2 | 134.2 | 134.57 | PJM_500_BG_P4_5_CNSTN_J_SRT-A | Breaker | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 204538 | 27STRABAN | 1 | 115 | 227 | 313 | 419.3 | 420.4 | 133.96 | 134.33 | PEPCO_P4_PP40_SRT-A | Breaker | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 235463 | 01TANEY | 1 | 138 | 227/201 | 268 | 365.1 | 359.1 | 136.24 | 134.01 | PJM_500_BG_P1_5011_SRT-A | Single | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 220999 | BAGLEY2 | 220980 | RAPHAEL | 13 | 230 | 232 | 1594 | 2122.8 | 2124.2 | 133.17 | 133.26 | BG_P4_5_GRCTN_3T_SRT-A | Breaker | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 220972 | GRANITE1 | 220953 | HOWARD12 | 1 | 230 | 232 | 728 | 987.1 | 969.4 | 135.59 | 133.16 | PEPCO_P4_PP40_SRT-A | Breaker | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 221092 | FIVE.FOR | 221096 | ROCKRGE1 | 1 | 115 | 232 | 256 | 336.4 | 340.7 | 131.4 | 133.09 | BG_P7_NEAST_RPHLRD_SRT-A | Tower | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 563 | 751.3 | 747.8 | 133.45 | 132.82 | PECO_P4_PEACH205_SRT-A | Breaker | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 563 | 753.3 | 747.8 | 133.79 | 132.82 | PECO_P4_PEACH205_SRT-A | Breaker | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 223938 | DICKH230 | 223937 | DICK 230 | 1 | 230 | 233 | 680 | 905.9 | 900.5 | 133.22 | 132.42 | DVP_P4-2: 514T595_SRT-SW | Breaker | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 223938 | DICKH230 | 223937 | DICK 230 | 2 | 230 | 233 | 680 | 905.9 | 900.5 | 133.22 | 132.42 | DVP_P4-2: 514T595_SRT-SW | Breaker | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 205912 | AD1-020 TAP | 204544 | 27LINCOLN | 1 | 115 | 227 | 282 | 374.6 | 373.2 | 132.83 | 132.33 | PJM_500_BG_P1_5011_SRT-A | Single | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208031 | MLWD TR2 | 208020 | MANO TR3 | 1 | 230 | 229 | 801 | 1054.3 | 1058.8 | 131.63 | 132.19 | PECO_P1-2_5012_SRT-A | Single | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 220972 | GRANITE1 | 220953 | HOWARD12 | 1 | 230 | 232 | 728 | 979.2 | 961.5 | 134.5 | 132.08 | PJM_500_BG_P4_5_CNSTN_J_SRT-A | Breaker | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200099 | LAUS | 208045 | LAUS | 3 | 500/230 | 229 | 1119 | 1469.7 | 1470.2 | 131.34 | 131.38 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | Breaker | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200099 | LAUS | 208045 | LAUS | 3 | 500/230 | 229 | 1119 | 1469.5 | 1470 | 131.32 | 131.37 | PECO_P4_PEACH235_SRT-A | Breaker | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204539 | 27HUNTRSTN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 282 | 371.7 | 370.4 | 131.82 | 131.34 | PJM_500_BG_P4_5_CNSTN_J_SRT-A | Breaker | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204539 | 27HUNTRSTN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 282 | 371.1 | 369.7 | 131.58 | 131.09 | PEPCO_P4_PP40_SRT-A | Breaker | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220972 | GRANITE1 | 1 | 230 | 232 | 728 | 970.6 | 953.2 | 133.33 | 130.93 | PEPCO_P4_PP40_SRT-A | Breaker | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200099 | LAUS | 208045 | LAUS | 3 | 500/230 | 229 | 1119 | 1460.3 | 1461.5 | 130.5 | 130.6 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | Breaker | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220972 | GRANITE1 | 1 | 230 | 232 | 728 | 967 | 949.6 | 132.83 | 130.45 | PJM_500_BG_P4_5_CNSTN_J_SRT-A | Breaker | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 223938 | DICKH230 | 223937 | DICK 230 | 2 | 230 | 233 | 680 | 888.2 | 883.9 | 130.61 | 129.99 | DVP_P4-2: 51482_SRT-A | Breaker | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 223938 | DICKH230 | 223937 | DICK 230 | 1 | 230 | 233 | 680 | 888.2 | 883.9 | 130.61 | 129.99 | DVP_P4-2: 51482_SRT-A | Breaker | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 220980 | RAPHAEL | 220965 | NEAST339 | 1 | 230 | 232 | 1283 | 1671.9 | 1661.6 | 130.31 | 129.51 | PEPCO_P4_PP40_SRT-A | Breaker | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 220980 | RAPHAEL | 220965 | NEAST339 | 1 | 230 | 232 | 1283 | 1670.3 | 1659.6 | 130.19 | 129.35 | PJM_500_BG_P4_5_CNSTN_J_SRT-A | Breaker | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 235118 | 01SOBEND | 200011 | KEYSTONE | 1 | 500 | 226/201 | 2078 | 2296 | 2676.2 | 110.49 | 128.79 | PN_P2-3_PN-500-DRT32_SRT-A | Breaker | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 235118 | 01SOBEND | 200011 | KEYSTONE | 1 | 500 | 226/201 | 2078 | 2296 | 2676.2 | 110.49 | 128.79 | PN_P2-3_PN-500-004-DRT-002_SRT-SL | Breaker | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204538 | 27STRABAN | 204529 | 27GERMANTN | 1 | 115 | 227 | 313 | 400.1 | 402.6 | 127.84 | 128.62 | PJM_500_BG_P4_5_CNSTN_J_SRT-A | Breaker | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204538 | 27STRABAN | 204529 | 27GERMANTN | 1 | 115 | 227 | 313 | 399.4 | 401.8 | 127.6 | 128.37 | PEPCO_P4_PP40_SRT-A | Breaker | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 207923 | BRISREAC | 208132 | WHEM TR1 | 1 | 230 | 229 | 618 | 792.9 | 785.3 | 128.31 | 127.08 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | Breaker | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 207922 | BRIS | 207923 | BRISREAC | RX | 230 | 229 | 618 | 792.9 | 785.3 | 128.31 | 127.08 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | Breaker | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200011 | KEYSTONE | 235118 | 01SOBEND | 1 | 500 | 226/201 | 2078 | 2134.8 | 2635 | 102.73 | 126.81 | PN_P2-3_PN-500-004-DRT-002_SRT-SL | Breaker | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200011 | KEYSTONE | 235118 | 01SOBEND | 1 | 500 | 226/201 | 2078 | 2134.8 | 2635 | 102.73 | 126.81 | PN_P2-3_PN-500-DRT32_SRT-A | Breaker | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 203981 | AD2-062_POI | 235188 | 01GREENE | 1 | 138 | 226/201 | 268 | 341.8 | 337.8 | 127.55 | 126.06 | PJM_500_BG_P4_5_CNSTN_J_SRT-A | Breaker | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 223938 | DICKH230 | 223937 | DICK 230 | 2 | 230 | 233 | 680 | 861.4 | 855 | 126.67 | 125.73 | DVP_P1-2: LN 514_SRT-A | Single | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 223938 | DICKH230 | 223937 | DICK 230 | 1 | 230 | 233 | 680 | 861.4 | 855 | 126.67 | 125.73 | AP_P1-2_PE-500-407T_SRT-SL | Single | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 223938 | DICKH230 | 223937 | DICK 230 | 2 | 230 | 233 | 680 | 861.4 | 855 | 126.67 | 125.73 | AP_P1-2_PE-500-407T_SRT-SL | Single | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 223938 | DICKH230 | 223937 | DICK 230 | 1 | 230 | 233 | 680 | 861.4 | 855 | 126.67 | 125.73 | DVP_P1-2: LN 514_SRT-A | Single | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 203981 | AD2-062_POI | 235188 | 01GREENE | 1 | 138 | 226/201 | 268 | 340.8 | 336.9 | 127.18 | 125.72 | PEPCO_P4_PP40_SRT-A | Breaker | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200099 | LAUS | 208045 | LAUS | 3 | 500/230 | 229 | 1119 | 1398.5 | 1401.8 | 124.98 | 125.27 | PECO_P4_PEACH245_SRT-A | Breaker | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 220980 | RAPHAEL | 220979 | NEAST317 | 1 | 230 | 232 | 1283 | 1614.9 | 1604.9 | 125.87 | 125.09 | PEPCO_P4_PP40_SRT-A | Breaker | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 220980 | RAPHAEL | 220979 | NEAST317 | 1 | 230 | 232 | 1283 | 1613.2 | 1602.9 | 125.74 | 124.93 | PJM_500_BG_P4_5_CNSTN_J_SRT-A | Breaker | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 207923 | BRISREAC | 208132 | WHEM TR1 | 1 | 230 | 229 | 618 | 780.3 | 771.5 | 126.26 | 124.83 | PECO_P1-2_5012_SRT-A | Single | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 207922 | BRIS | 207923 | BRISREAC | RX | 230 | 229 | 618 | 780.3 | 771.5 | 126.26 | 124.83 | PECO_P1-2_5012_SRT-A | Single | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 220973 | GRANITE6 | 220954 | HOWARD32 | 1 | 230 | 232 | 728 | 923.8 | 908.3 | 126.9 | 124.77 | PEPCO_P4_PP40_SRT-A | Breaker | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 207922 | BRIS | 207923 | BRISREAC | RX | 230 | 229 | 618 | 780.1 | 770.9 | 126.23 | 124.74 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | Breaker | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 207923 | BRISREAC | 208132 | WHEM TR1 | 1 | 230 | 229 | 618 | 780.1 | 770.9 | 126.23 | 124.74 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | Breaker | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 207923 | BRISREAC | 208132 | WHEM TR1 | 1 | 230 | 229 | 618 | 780 | 770.8 | 126.22 | 124.72 | PECO_P4_PEACH235_SRT-A | Breaker | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 207922 | BRIS | 207923 | BRISREAC | RX | 230 | 229 | 618 | 780 | 770.8 | 126.22 | 124.72 | PECO_P4_PEACH235_SRT-A | Breaker | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 204538 | 27STRABAN | 1 | 115 | 227 | 313 | 388.8 | 390.2 | 124.22 | 124.67 | PJM_500_BG_P1_5011_SRT-A | Single | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 220973 | GRANITE6 | 220954 | HOWARD32 | 1 | 230 | 232 | 728 | 921.5 | 906 | 126.58 | 124.46 | PJM_500_BG_P4_5_CNSTN_J_SRT-A | Breaker | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 2 | 500/230 | 232 | 1940 | 2359.5 | 2413.7 | 121.62 | 124.42 | PEPCO_P4_PP40_SRT-A | Breaker | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 2 | 500/230 | 232 | 1940 | 2355.4 | 2408.6 | 121.41 | 124.16 | PJM_500_BG_P4_5_CNSTN_J_SRT-A | Breaker | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 1 | 500/230 | 232 | 1941 | 2350.1 | 2403.5 | 121.08 | 123.83 | PEPCO_P4_PP40_SRT-A | Breaker | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 1 | 500/230 | 232 | 1941 | 2350.4 | 2403.5 | 121.09 | 123.83 | PJM_500_BG_P4_5_CNSTN_J_SRT-A | Breaker | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204550 | 27ORRTANNA | 204544 | 27LINCOLN | 1 | 115 | 227 | 160 | 200.1 | 197.7 | 125.09 | 123.59 | ME_P2-3_ME-115-013B_SRT-A | Breaker | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200065 | PCHBTM2S | 200066 | PCHBTM1N | 2 | 500 | 230 | 2860 | 3611 | 3529.4 | 126.26 | 123.41 | PECO_P4_PEACH235_SRT-A | Breaker | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204539 | 27HUNTRSTN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 282 | 349 | 347.8 | 123.76 | 123.32 | PJM_500_BG_P1_5011_SRT-A | Single | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204550 | 27ORRTANNA | 204544 | 27LINCOLN | 1 | 115 | 227 | 160 | 199.5 | 197.1 | 124.68 | 123.17 | ME_P2-3_ME-115-013A_SRT-A | Breaker | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 208070 | SAHA12TP | 1 | 230 | 229 | 628 | 772.2 | 768.9 | 122.96 | 122.44 | BG_P7_GRCTN_CNSTN_SRT-A | Tower | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 207922 | BRIS | 204515 | 27YORKANA | 1 | 230 | 227/229 | 869 | 1073.2 | 1063.5 | 123.5 | 122.38 | PECO_P1-2_5012_SRT-A | Single | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 578 | 707.8 | 704.9 | 122.45 | 121.96 | PECO_P4_PEACH205_SRT-A | Breaker | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 207922 | BRIS | 204515 | 27YORKANA | 1 | 230 | 227/229 | 869 | 1069.6 | 1058.9 | 123.09 | 121.85 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | Breaker | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 207922 | BRIS | 204515 | 27YORKANA | 1 | 230 | 227/229 | 869 | 1069.5 | 1058.8 | 123.08 | 121.84 | PECO_P4_PEACH235_SRT-A | Breaker | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204550 | 27ORRTANNA | 204544 | 27LINCOLN | 1 | 115 | 227 | 160 | 196.2 | 194.8 | 122.65 | 121.77 | ME_P2-3_ME-115-035A_SRT-A | Breaker | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 223938 | DICKH230 | 223937 | DICK 230 | 1 | 230 | 233 | 680 | 838.5 | 827.2 | 123.31 | 121.64 | PEPCO_P4_PP19_SRT-A | Breaker | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 221051 | CHESTN8A | 221049 | FRED.RD8 | 1 | 115 | 232 | 189 | 225 | 229.3 | 119.06 | 121.32 | BG_P7_GRCTN_RAPHEL_SRT-A | Tower | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 242524 | 05CLOVRD | 242519 | 05CLOVRD | 16 | 345/500 | 205 | 1758 | 2122.4 | 2121.3 | 120.73 | 120.67 | AEP_P4_#7423_05CLOVRD 500_GG_SRT-A | Breaker | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 207922 | BRIS | 204515 | 27YORKANA | 1 | 230 | 227/229 | 869 | 1050.4 | 1040.8 | 120.88 | 119.77 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | Breaker | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200099 | LAUS | 208045 | LAUS | 3 | 500/230 | 229 | 1119 | 1332.8 | 1334.3 | 119.11 | 119.24 | PECO_P1-2_5012_SRT-A | Single | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204550 | 27ORRTANNA | 204544 | 27LINCOLN | 1 | 115 | 227 | 160 | 192.3 | 190 | 120.22 | 118.77 | ME_P1-2_ME-115-068_SRT-A | Single | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204538 | 27STRABAN | 204529 | 27GERMANTN | 1 | 115 | 227 | 313 | 368.9 | 371.6 | 117.86 | 118.73 | PJM_500_BG_P1_5011_SRT-A | Single | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204550 | 27ORRTANNA | 204544 | 27LINCOLN | 1 | 115 | 227 | 160 | 191.3 | 189.8 | 119.54 | 118.61 | ME_P2-3_ME-115-035B_SRT-A | Breaker | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 220963 | CONASTON | 220962 | NWEST311 | 1 | 230 | 232 | 1364 | 1603.5 | 1613.6 | 117.56 | 118.3 | PEPCO_P4_PP40_SRT-A | Breaker | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 205912 | AD1-020 TAP | 204544 | 27LINCOLN | 1 | 115 | 227 | 282 | 336.9 | 332.7 | 119.48 | 117.97 | ME_P2-3_ME-115-019A-A_SRT-A | Breaker | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 220963 | CONASTON | 220962 | NWEST311 | 1 | 230 | 232 | 1364 | 1598.9 | 1608.3 | 117.22 | 117.91 | PJM_500_BG_P4_5_CNSTN_J_SRT-A | Breaker | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 220963 | CONASTON | 220961 | NWEST326 | 1 | 230 | 232 | 1364 | 1597.7 | 1607.9 | 117.13 | 117.88 | PEPCO_P4_PP40_SRT-A | Breaker | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 220963 | CONASTON | 220961 | NWEST326 | 1 | 230 | 232 | 1364 | 1592.7 | 1602.3 | 116.77 | 117.47 | PJM_500_BG_P4_5_CNSTN_J_SRT-A | Breaker | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 207923 | BRISREAC | 208132 | WHEM TR1 | 1 | 230 | 229 | 618 | 736.6 | 725.2 | 119.19 | 117.35 | PECO_P4_PEACH245_SRT-A | Breaker | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 207922 | BRIS | 207923 | BRISREAC | RX | 230 | 229 | 618 | 736.6 | 725.2 | 119.19 | 117.35 | PECO_P4_PEACH245_SRT-A | Breaker | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 207922 | BRIS | 204515 | 27YORKANA | 1 | 230 | 227/229 | 869 | 1029.6 | 1016.2 | 118.48 | 116.94 | PECO_P4_PEACH245_SRT-A | Breaker | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 203981 | AD2-062_POI | 235188 | 01GREENE | 1 | 138 | 226/201 | 268 | 320.7 | 312.7 | 119.67 | 116.67 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | Breaker | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 203981 | AD2-062_POI | 235188 | 01GREENE | 1 | 138 | 226/201 | 268 | 320.7 | 312.7 | 119.66 | 116.67 | PECO_P4_PEACH235_SRT-A | Breaker | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 205912 | AD1-020 TAP | 204544 | 27LINCOLN | 1 | 115 | 227 | 282 | 337.2 | 328.7 | 119.57 | 116.57 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | Breaker | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 205912 | AD1-020 TAP | 204544 | 27LINCOLN | 1 | 115 | 227 | 282 | 337.2 | 328.7 | 119.56 | 116.56 | PECO_P4_PEACH235_SRT-A | Breaker | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 578 | 673 | 673 | 116.43 | 116.43 | PECO_P4_PEACH205_SRT-A | Breaker | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 220980 | RAPHAEL | 220965 | NEAST339 | 1 | 230 | 232 | 1283 | 1500.5 | 1490 | 116.95 | 116.13 | PJM_500_BG_P1_5011_SRT-A | Single | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 221092 | FIVE.FOR | 221096 | ROCKRGE1 | 1 | 115 | 232 | 256 | 290.9 | 297 | 113.62 | 116.03 | BG_P1_110512_SRT-A | Single | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 203981 | AD2-062_POI | 235188 | 01GREENE | 1 | 138 | 226/201 | 268 | 319 | 310.8 | 119.03 | 115.96 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | Breaker | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220973 | GRANITE6 | 1 | 230 | 232 | 728 | 860 | 843.5 | 118.13 | 115.87 | PEPCO_P4_PP40_SRT-A | Breaker | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208131 | WHEM | 208133 | WHEM TR2 | 1 | 230 | 229 | 618 | 647.4 | 646 | 104.76 | 104.52 | PECO_P1-2_5012_SRT-A | Single | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208131 | WHEM | 208133 | WHEM TR2 | 1 | 230 | 229 | 618 | 647.2 | 645.4 | 104.73 | 104.43 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | Breaker | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 204538 | 27STRABAN | 1 | 115 | 227 | 313 | 326.5 | 326.8 | 104.31 | 104.42 | BG_P7_GRCTN_RAPHEL_SRT-A | Tower | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208131 | WHEM | 208133 | WHEM TR2 | 1 | 230 | 229 | 618 | 647.1 | 645.3 | 104.72 | 104.42 | PECO_P4_PEACH235_SRT-A | Breaker | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 204538 | 27STRABAN | 1 | 115 | 227 | 313 | 333.1 | 326.4 | 106.41 | 104.27 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | Breaker | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 204538 | 27STRABAN | 1 | 115 | 227 | 313 | 333.1 | 326.3 | 106.41 | 104.26 | PECO_P4_PEACH235_SRT-A | Breaker | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 220960 | BRANDN.S | 220955 | W.CHAPEL | 43 | 230 | 232 | 945 | 980.1 | 981.9 | 103.72 | 103.91 | PJM_500_BG_P4_5_CNSTN_J_SRT-A | Breaker | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208133 | WHEM TR2 | 208021 | MANO TR4 | 2 | 230 | 229 | 531 | 551.4 | 551.5 | 103.84 | 103.86 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | Breaker | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208133 | WHEM TR2 | 208021 | MANO TR4 | 2 | 230 | 229 | 531 | 551.3 | 551.4 | 103.83 | 103.85 | PECO_P4_PEACH235_SRT-A | Breaker | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200011 | KEYSTONE | 200005 | CONEM-GH | 1 | 500 | 226 | 2771 | 2885.6 | 2876.8 | 104.14 | 103.82 | PN_P2-3_PN-500-004-DRT-008_SRT-SL | Breaker | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 220960 | BRANDN.S | 220955 | W.CHAPEL | 43 | 230 | 232 | 945 | 978.9 | 980.1 | 103.59 | 103.72 | PEPCO_P4_PP40_SRT-A | Breaker | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 204538 | 27STRABAN | 1 | 115 | 227 | 313 | 331.4 | 324.4 | 105.88 | 103.64 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | Breaker | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 221090 | GLENARM2 | 221089 | WINDYED1 | 1 | 115 | 232 | 192 | 191.8 | 199 | 99.91 | 103.63 | BG_P4_5_WE_NORTH_TIE_SRT-A/* WINDY EDGE #1(NORTH) BUS BLACK-RED BUS TIE BREAKER 221089 | Breaker | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 235463 | 01TANEY | 1 | 138 | 227/201 | 268 | 279.1 | 277.4 | 104.13 | 103.51 | AP_P2-2_WP-138-074_SRT-A | Bus | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 235463 | 01TANEY | 1 | 138 | 227/201 | 221 | 231.3 | 228.7 | 104.68 | 103.5 | Base Case | Single | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 221090 | GLENARM2 | 221089 | WINDYED1 | 1 | 115 | 232 | 192 | 191.4 | 198.7 | 99.66 | 103.47 | BG_P4_5_WE504_SRT-A | Breaker | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 221058 | DOLFD T1 | 221055 | HARRIS1A | 1 | 115 | 232 | 189 | 197.3 | 195.2 | 104.39 | 103.3 | BG_P7_NWEST_GRNITE_SRT-A | Tower | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 221090 | GLENARM2 | 221089 | WINDYED1 | 1 | 115 | 232 | 192 | 191 | 198.2 | 99.47 | 103.24 | BG_P2_WE_115-N-RED_SRT-A | Bus | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204529 | 27GERMANTN | 204530 | 27GERMANTN | 1 | 115/138 | 227 | 345 | 349.6 | 356.1 | 101.32 | 103.21 | PJM_500_BG_P1_5011_SRT-A | Single | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 207922 | BRIS | 207923 | BRISREAC | RX | 230 | 229 | 618 | 651.2 | 636.9 | 105.38 | 103.06 | ME_P2-3_ME-230-019CT_SRT-A | Breaker | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 207923 | BRISREAC | 208132 | WHEM TR1 | 1 | 230 | 229 | 618 | 651.2 | 636.9 | 105.38 | 103.06 | ME_P2-3_ME-230-019CT_SRT-A | Breaker | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 221090 | GLENARM2 | 221089 | WINDYED1 | 1 | 115 | 232 | 192 | 193.9 | 197.7 | 100.98 | 102.96 | BG_P7_CNSTN_NWEST2_SRT-A | Tower | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 205912 | AD1-020 TAP | 204544 | 27LINCOLN | 1 | 115 | 227 | 282 | 294.1 | 290.2 | 104.29 | 102.9 | PL_05_P22_000674_SRT-A | Bus | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 205912 | AD1-020 TAP | 204544 | 27LINCOLN | 1 | 115 | 227 | 282 | 293.9 | 290 | 104.24 | 102.84 | PL_05_P71_000906_SRT-A | Tower | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 235463 | 01TANEY | 1 | 138 | 227/201 | 268 | 276.6 | 275.4 | 103.22 | 102.76 | BG_P7_NWEST_GRNITE_SRT-A | Tower | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 563 | 581.4 | 578.2 | 103.26 | 102.7 | PL_05_P71_000906_SRT-A | Tower | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 563 | 583.3 | 578.2 | 103.6 | 102.7 | PL_05_P71_000906_SRT-A | Tower | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204539 | 27HUNTRSTN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 282 | 292.4 | 289.5 | 103.69 | 102.66 | ME_P2-3_ME-115-019A-A_SRT-A | Breaker | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204550 | 27ORRTANNA | 204544 | 27LINCOLN | 1 | 115 | 227 | 160 | 167.4 | 164.2 | 104.6 | 102.62 | ME_P1-2_ME-115-067_SRT-A | Single | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 221092 | FIVE.FOR | 221096 | ROCKRGE1 | 1 | 115 | 232 | 256 | 261.5 | 268.5 | 102.14 | 104.89 | BG_P4_5_WE518_SRT-A | Breaker | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 221092 | FIVE.FOR | 221096 | ROCKRGE1 | 1 | 115 | 232 | 256 | 261.5 | 268.5 | 102.14 | 104.89 | BG_P2_WE_115-E-BLK_SRT-A | Bus | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 304070 | 6PERSON230 T | 316281 | AC2-100 TAP | 1 | 230 | 340/345 | 718 | 750.2 | 752.6 | 104.49 | 104.82 | DVP_P4-2: 509T570_SRT-SW | Breaker | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208394 | PPL-BGE TIE | 221092 | FIVE.FOR | 1 | 115 | 229/232 | 247 | 259.6 | 258.9 | 105.09 | 104.81 | PL_05_P71_000906_SRT-A | Tower | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208395 | FARO FF | 208393 | FARO DC TIE | 1 | 69/115 | 229 | 114 | 121.5 | 119.2 | 106.59 | 104.59 | BG_P4_5_GRCTN_2T_SRT-A | Breaker | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200051 | ROCKSPGS | 200065 | PCHBTM2S | 1 | 500 | 235/230 | 2860 | 2960.7 | 2990.8 | 103.52 | 104.57 | PECO_P4_CHICH435_SRT-A | Breaker | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200051 | ROCKSPGS | 200065 | PCHBTM2S | 1 | 500 | 235/230 | 2860 | 2960.7 | 2990.8 | 103.52 | 104.57 | PECO_P4_CHICH195_SRT-A | Breaker | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200051 | ROCKSPGS | 200065 | PCHBTM2S | 1 | 500 | 235/230 | 2860 | 2960.4 | 2990.8 | 103.51 | 104.57 | PECO_P2-2_CHI230B1_SRT-A | Bus | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200051 | ROCKSPGS | 200065 | PCHBTM2S | 1 | 500 | 235/230 | 2860 | 2960.7 | 2990.7 | 103.52 | 104.57 | PECO_P4_CHICH045_SRT-A | Breaker | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 203981 | AD2-062_POI | 235188 | 01GREENE | 1 | 138 | 226/201 | 268 | 298.2 | 293.9 | 111.29 | 109.66 | PJM_500_BG_P1_5011_SRT-A | Single | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208396 | FARO | 208395 | FARO FF | 1 | 69 | 229 | 240 | 262.1 | 263.1 | 109.2 | 109.63 | PL_05_P71_000906_SRT-A | Tower | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 205912 | AD1-020 TAP | 204544 | 27LINCOLN | 1 | 115 | 227 | 282 | 313.2 | 309 | 111.07 | 109.57 | ME_P1-2_ME-115-061_SRT-A | Single | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 205912 | AD1-020 TAP | 204544 | 27LINCOLN | 1 | 115 | 227 | 282 | 310.7 | 308.6 | 110.19 | 109.44 | BG_P7_NEAST_RPHLRD_SRT-A | Tower | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204693 | 27BOONETOWN | 204512 | 27S.RDG | 1 | 230 | 227 | 531 | 580.9 | 580.8 | 109.4 | 109.37 | PL_04_P42_101307_SRT-A | Breaker | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204693 | 27BOONETOWN | 204512 | 27S.RDG | 1 | 230 | 227 | 531 | 581 | 580.5 | 109.42 | 109.32 | PL_24_P42_102306_SRT-A | Breaker | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 205912 | AD1-020 TAP | 204544 | 27LINCOLN | 1 | 115 | 227 | 282 | 311 | 308.1 | 110.28 | 109.25 | BG_P7_CNSTN_NWEST2_SRT-A | Tower | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 220964 | GRACETON | 221000 | BAGLEY | 5 | 230 | 232 | 1594 | 1736.6 | 1736 | 108.95 | 108.91 | PEPCO_P4_PP40_SRT-A | Breaker | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 220964 | GRACETON | 221000 | BAGLEY | 5 | 230 | 232 | 1594 | 1735 | 1733.9 | 108.84 | 108.78 | PJM_500_BG_P4_5_CNSTN_J_SRT-A | Breaker | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 220964 | GRACETON | 220999 | BAGLEY2 | 13 | 230 | 232 | 1594 | 1734.4 | 1733.8 | 108.81 | 108.77 | PEPCO_P4_PP40_SRT-A | Breaker | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220973 | GRANITE6 | 1 | 230 | 232 | 728 | 809.8 | 791.2 | 111.24 | 108.69 | PJM_500_BG_P1_5011_SRT-A | Single | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 221010 | COLUMB12 | 220941 | H.RDGE16 | 1 | 230 | 232 | 777 | 859.2 | 844.5 | 110.58 | 108.69 | PEPCO_P4_PP40_SRT-A | Breaker | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 205912 | AD1-020 TAP | 204544 | 27LINCOLN | 1 | 115 | 227 | 282 | 314.7 | 306.5 | 111.6 | 108.67 | PECO_P1-2_5012_SRT-A | Single | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 220964 | GRACETON | 220999 | BAGLEY2 | 13 | 230 | 232 | 1594 | 1732.7 | 1731.7 | 108.7 | 108.64 | PJM_500_BG_P4_5_CNSTN_J_SRT-A | Breaker | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 205912 | AD1-020 TAP | 204544 | 27LINCOLN | 1 | 115 | 227 | 282 | 312.5 | 306 | 110.83 | 108.53 | PJM_500_BG_P1_5013_SRT-A | Single | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 205912 | AD1-020 TAP | 204544 | 27LINCOLN | 1 | 115 | 227 | 282 | 307.9 | 305.7 | 109.19 | 108.41 | AP_P1-2_PE-500-001_SRT-SL | Single | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 220963 | CONASTON | 220962 | NWEST311 | 1 | 230 | 232 | 1364 | 1465.2 | 1476.1 | 107.42 | 108.22 | PJM_500_BG_P1_5011_SRT-A | Single | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 220999 | BAGLEY2 | 220980 | RAPHAEL | 13 | 230 | 232 | 1594 | 1721 | 1723 | 107.97 | 108.09 | BG_P1_2305_SRT-A | Single | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 221000 | BAGLEY | 220980 | RAPHAEL | 5 | 230 | 232 | 1594 | 1721 | 1723 | 107.97 | 108.09 | BG_P1_2313_SRT-A | Single | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 221054 | CHESTN7A | 221050 | FRED.RD7 | 1 | 115 | 232 | 189 | 199.9 | 204 | 105.79 | 107.95 | BG_P7_NEAST_RPHLRD_SRT-A | Tower | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 221010 | COLUMB12 | 220941 | H.RDGE16 | 1 | 230 | 232 | 777 | 853.1 | 838.6 | 109.79 | 107.92 | PJM_500_BG_P4_5_CNSTN_J_SRT-A | Breaker | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204514 | 27TMI | 204502 | 27JACKSON | 1 | 230 | 227 | 659 | 709.6 | 711 | 107.67 | 107.9 | PECO_P1-2_5012_SRT-A | Single | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200011 | KEYSTONE | 235104 | 01CABOT | 1 | 500 | 226/201 | 2844 | 3108.4 | 3067.1 | 109.3 | 107.85 | AP_P2-3_WP-500-DRT45_SRT-SL | Breaker | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 220963 | CONASTON | 220961 | NWEST326 | 1 | 230 | 232 | 1364 | 1459.8 | 1470.9 | 107.03 | 107.84 | PJM_500_BG_P1_5011_SRT-A | Single | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208070 | SAHA12TP | 208019 | MANO | 1 | 230 | 229 | 814 | 876.5 | 876.7 | 107.67 | 107.71 | BG_P7_GRCTN_CNSTN_SRT-A | Tower | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 801 | 881.6 | 861.8 | 110.06 | 107.59 | PJM_500_BG_P4_5_CNSTN_L_SRT-A | Breaker | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 221094 | GRACE.-1 | 221092 | FIVE.FOR | 1 | 115 | 232 | 437 | 468.6 | 469.4 | 107.24 | 107.41 | BG_P7_GRCTN_RAPHEL_SRT-A | Tower | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 220973 | GRANITE6 | 220954 | HOWARD32 | 1 | 230 | 232 | 728 | 798.5 | 780.8 | 109.69 | 107.25 | PJM_500_BG_P1_5011_SRT-A | Single | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 220999 | BAGLEY2 | 220980 | RAPHAEL | 13 | 230 | 232 | 1594 | 1698 | 1704.6 | 106.52 | 106.94 | PEPCO_P4_PP40_SRT-A | Breaker | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 220999 | BAGLEY2 | 220980 | RAPHAEL | 13 | 230 | 232 | 1594 | 1696.3 | 1702.5 | 106.42 | 106.81 | PJM_500_BG_P4_5_CNSTN_J_SRT-A | Breaker | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208131 | WHEM | 208133 | WHEM TR2 | 1 | 230 | 229 | 618 | 659.4 | 659.2 | 106.71 | 106.67 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | Breaker | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200018 | CHALK PT | 200301 | X4-035 TAP | 1 | 500 | 233 | 1732 | 1844.7 | 1847.1 | 106.51 | 106.65 | PEPCO_P4_PP41_SRT-A | Breaker | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 221000 | BAGLEY | 220980 | RAPHAEL | 5 | 230 | 232 | 1594 | 1692 | 1698.8 | 106.15 | 106.58 | PEPCO_P4_PP40_SRT-A | Breaker | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 221000 | BAGLEY | 220980 | RAPHAEL | 5 | 230 | 232 | 1594 | 1690.3 | 1696.7 | 106.04 | 106.44 | PJM_500_BG_P4_5_CNSTN_J_SRT-A | Breaker | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204693 | 27BOONETOWN | 204512 | 27S.RDG | 1 | 230 | 227 | 531 | 557.5 | 564.7 | 104.98 | 106.34 | PECO_P1-2_5012_SRT-A | Single | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 220954 | HOWARD32 | 220941 | H.RDGE16 | 1 | 230 | 232 | 913 | 989.7 | 970.2 | 108.4 | 106.27 | PEPCO_P4_PP40_SRT-A | Breaker | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 221092 | FIVE.FOR | 221096 | ROCKRGE1 | 1 | 115 | 232 | 256 | 267.8 | 272 | 104.62 | 106.27 | BG_P7_CNSTN_NWEST2_SRT-A | Tower | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 208070 | SAHA12TP | 1 | 230 | 229 | 628 | 668.2 | 666.1 | 106.41 | 106.07 | PJM_500_BG_P4_5_CNSTN_15_SRT-A | Breaker | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208132 | WHEM TR1 | 208131 | WHEM | 1 | 230 | 229 | 618 | 657 | 654.1 | 106.31 | 105.85 | PECO_P4_PEACH245_SRT-A | Breaker | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200532 | 26ROXBURY | 203981 | AD2-062_POI | 1 | 138 | 226 | 268 | 287.1 | 283.3 | 107.12 | 105.72 | PJM_500_BG_P4_5_CNSTN_J_SRT-A | Breaker | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 235463 | 01TANEY | 1 | 138 | 227/201 | 268 | 284.7 | 283.3 | 106.24 | 105.72 | PL_05_P22_000674_SRT-A | Bus | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 223938 | DICKH230 | 223937 | DICK 230 | 2 | 230 | 233 | 680 | 731.1 | 718.3 | 107.52 | 105.64 | PEPCO_P7_2PEPCO_SRT-A | Tower | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 223938 | DICKH230 | 223937 | DICK 230 | 1 | 230 | 233 | 680 | 731.1 | 718.3 | 107.52 | 105.64 | PEPCO_P7_2PEPCO_SRT-A | Tower | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208395 | FARO FF | 208393 | FARO DC TIE | 2 | 69/115 | 229 | 120 | 130 | 126.7 | 108.34 | 105.61 | PL_05_P71_000906_SRT-A | Tower | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 221092 | FIVE.FOR | 221095 | ROCKRGE2 | 1 | 115 | 232 | 300 | 313.7 | 316.8 | 104.55 | 105.61 | BG_P7_NEAST_RPHLRD_SRT-A | Tower | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 235463 | 01TANEY | 1 | 138 | 227/201 | 268 | 284.5 | 283 | 106.15 | 105.6 | PL_05_P71_000906_SRT-A | Tower | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 221092 | FIVE.FOR | 221096 | ROCKRGE1 | 1 | 115 | 232 | 256 | 262.8 | 269.9 | 102.65 | 105.42 | BG_P4_5_WE_EAST_TIE_SRT-A | Breaker | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200532 | 26ROXBURY | 203981 | AD2-062_POI | 1 | 138 | 226 | 268 | 286.1 | 282.4 | 106.75 | 105.38 | PEPCO_P4_PP40_SRT-A | Breaker | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 220954 | HOWARD32 | 220941 | H.RDGE16 | 1 | 230 | 232 | 913 | 980.3 | 960.9 | 107.37 | 105.24 | PJM_500_BG_P4_5_CNSTN_J_SRT-A | Breaker | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 220965 | NEAST339 | 220977 | RIV2339 | 1 | 230 | 232 | 857 | 906.2 | 901.3 | 105.74 | 105.17 | PJM_500_BG_P1_5011_SRT-A | Single | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 235463 | 01TANEY | 1 | 138 | 227/201 | 268 | 303.8 | 302.5 | 113.34 | 112.87 | BG_P7_CNSTN_NWEST2_SRT-A | Tower | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200066 | PCHBTM1N | 200016 | 3 MILE I | 1 | 500 | 227/230 | 3016 | 3465.3 | 3402 | 114.9 | 112.8 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | Breaker | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200066 | PCHBTM1N | 200016 | 3 MILE I | 1 | 500 | 227/230 | 3016 | 3464.9 | 3400.6 | 114.88 | 112.75 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | Breaker | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 221092 | FIVE.FOR | 221095 | ROCKRGE2 | 1 | 115 | 232 | 300 | 336 | 338 | 112 | 112.65 | BG_P7_GRCTN_RAPHEL_SRT-A | Tower | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200066 | PCHBTM1N | 200016 | 3 MILE I | 1 | 500 | 227/230 | 3016 | 3460.5 | 3397.3 | 114.74 | 112.64 | PECO_P4_PEACH235_SRT-A | Breaker | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 220980 | RAPHAEL | 220979 | NEAST317 | 1 | 230 | 232 | 1283 | 1454.7 | 1444.6 | 113.38 | 112.59 | PJM_500_BG_P1_5011_SRT-A | Single | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 220972 | GRANITE1 | 220953 | HOWARD12 | 1 | 230 | 232 | 728 | 838.7 | 818.8 | 115.2 | 112.47 | PJM_500_BG_P1_5011_SRT-A | Single | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 220964 | GRACETON | 221000 | BAGLEY | 5 | 230 | 232 | 1594 | 1802.5 | 1790.1 | 113.08 | 112.3 | BG_P1_2313_SRT-A | Single | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 220964 | GRACETON | 220999 | BAGLEY2 | 13 | 230 | 232 | 1594 | 1802.5 | 1790.1 | 113.08 | 112.3 | BG_P1_2305_SRT-A | Single | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 205912 | AD1-020 TAP | 204544 | 27LINCOLN | 1 | 115 | 227 | 282 | 320.6 | 316 | 113.68 | 112.07 | ME_P2-2_ME-115-0102A-8_SRT-A | Bus | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 205912 | AD1-020 TAP | 204544 | 27LINCOLN | 1 | 115 | 227 | 282 | 317.2 | 314.9 | 112.48 | 111.67 | BG_P7_GRCTN_RAPHEL_SRT-A | Tower | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204693 | 27BOONETOWN | 204512 | 27S.RDG | 1 | 230 | 227 | 531 | 593.9 | 592.6 | 111.84 | 111.6 | PL_04_P13_101211_SRT-A | Single | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1417 | 1556.3 | 1581.1 | 109.83 | 111.58 | DVP_P4-2: H1T560_SRT-A | Breaker | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208395 | FARO FF | 208393 | FARO DC TIE | 1 | 69/115 | 229 | 114 | 130 | 126.7 | 114.04 | 111.17 | PL_05_P71_000906_SRT-A | Tower | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204693 | 27BOONETOWN | 204512 | 27S.RDG | 1 | 230 | 227 | 531 | 589.9 | 588.8 | 111.09 | 110.89 | PL_04_P43_102301_SRT-A | Breaker | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204693 | 27BOONETOWN | 204512 | 27S.RDG | 1 | 230 | 227 | 531 | 589.9 | 588.8 | 111.09 | 110.89 | PL_04_P22_102291_SRT-A | Bus | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204693 | 27BOONETOWN | 204512 | 27S.RDG | 1 | 230 | 227 | 531 | 589.9 | 588.6 | 111.09 | 110.85 | PL_04_P22_102290_SRT-A | Bus | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204693 | 27BOONETOWN | 204512 | 27S.RDG | 1 | 230 | 227 | 531 | 589.9 | 588.6 | 111.09 | 110.85 | PL_04_P43_102300_SRT-A | Breaker | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204693 | 27BOONETOWN | 204512 | 27S.RDG | 1 | 230 | 227 | 531 | 587.5 | 586.6 | 110.63 | 110.48 | PL_04_P42_101309_SRT-A | Breaker | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204514 | 27TMI | 204502 | 27JACKSON | 1 | 230 | 227 | 659 | 727.5 | 727.5 | 110.4 | 110.4 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | Breaker | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204514 | 27TMI | 204502 | 27JACKSON | 1 | 230 | 227 | 659 | 727.5 | 727.5 | 110.39 | 110.39 | PECO_P4_PEACH235_SRT-A | Breaker | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204514 | 27TMI | 204502 | 27JACKSON | 1 | 230 | 227 | 659 | 724.4 | 723.9 | 109.92 | 109.85 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | Breaker | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 235463 | 01TANEY | 1 | 138 | 227/201 | 268 | 311 | 310.3 | 116.04 | 115.78 | BG_P7_GRCTN_RAPHEL_SRT-A | Tower | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 235463 | 01TANEY | 1 | 138 | 227/201 | 268 | 312.6 | 310.1 | 116.65 | 115.7 | AP_P2-3_PE-500-015_SRT-A | Breaker | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220972 | GRANITE1 | 1 | 230 | 232 | 728 | 860.7 | 841 | 118.23 | 115.53 | PJM_500_BG_P1_5011_SRT-A | Single | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 221054 | CHESTN7A | 221050 | FRED.RD7 | 1 | 115 | 232 | 189 | 214 | 218.1 | 113.22 | 115.42 | BG_P7_GRCTN_RAPHEL_SRT-A | Tower | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208132 | WHEM TR1 | 208131 | WHEM | 1 | 230 | 229 | 618 | 711.3 | 712.4 | 115.09 | 115.27 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | Breaker | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220973 | GRANITE6 | 1 | 230 | 232 | 728 | 855 | 838.7 | 117.45 | 115.21 | PJM_500_BG_P4_5_CNSTN_J_SRT-A | Breaker | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 220965 | NEAST339 | 220977 | RIV2339 | 1 | 230 | 232 | 857 | 992.1 | 987.2 | 115.76 | 115.19 | PEPCO_P4_PP40_SRT-A | Breaker | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 235463 | 01TANEY | 1 | 138 | 227/201 | 268 | 317.7 | 308.5 | 118.53 | 115.1 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | Breaker | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 235463 | 01TANEY | 1 | 138 | 227/201 | 268 | 317.6 | 308.5 | 118.52 | 115.1 | PECO_P4_PEACH235_SRT-A | Breaker | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 220965 | NEAST339 | 220977 | RIV2339 | 1 | 230 | 232 | 857 | 991.4 | 986.2 | 115.68 | 115.08 | PJM_500_BG_P4_5_CNSTN_J_SRT-A | Breaker | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200009 | JUNI | 208004 | JUNI | 2 | 500/230 | 229 | 1010 | 1180.2 | 1161.7 | 116.85 | 115.02 | PL_10_P42_000140_SRT-A | Breaker | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204529 | 27GERMANTN | 204530 | 27GERMANTN | 1 | 115/138 | 227 | 345 | 389 | 395.2 | 112.75 | 114.55 | PJM_500_BG_P4_5_CNSTN_J_SRT-A | Breaker | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 221092 | FIVE.FOR | 221096 | ROCKRGE1 | 1 | 115 | 232 | 256 | 286.8 | 293.2 | 112.04 | 114.54 | BG_P4_5_WE512_SRT-A | Breaker | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204529 | 27GERMANTN | 204530 | 27GERMANTN | 1 | 115/138 | 227 | 345 | 388.2 | 394.4 | 112.53 | 114.32 | PEPCO_P4_PP40_SRT-A | Breaker | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 205912 | AD1-020 TAP | 204544 | 27LINCOLN | 1 | 115 | 227 | 232 | 269.6 | 265.2 | 116.21 | 114.31 | Base Case | Single | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 2 | 500/230 | 232 | 1940 | 2164.2 | 2217.6 | 111.56 | 114.31 | PJM_500_BG_P1_5011_SRT-A | Single | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 223938 | DICKH230 | 223937 | DICK 230 | 2 | 230 | 233 | 680 | 781.4 | 775.4 | 114.91 | 114.02 | AP_P2-3_PE-500-019C_SRT-SL | Breaker | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 223938 | DICKH230 | 223937 | DICK 230 | 1 | 230 | 233 | 680 | 781.4 | 775.4 | 114.91 | 114.02 | AP_P2-3_PE-500-019C_SRT-SL | Breaker | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200066 | PCHBTM1N | 200065 | PCHBTM2S | 2 | 500 | 230 | 2860 | 3284.7 | 3260.8 | 114.85 | 114.01 | PECO_P4_PEACH205_SRT-A | Breaker | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 1 | 500/230 | 232 | 1941 | 2159.7 | 2212.9 | 111.27 | 114.01 | PJM_500_BG_P1_5011_SRT-A | Single | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 220960 | BRANDN.S | 220955 | W.CHAPEL | 42 | 230 | 232 | 857 | 974.6 | 976.4 | 113.72 | 113.93 | PJM_500_BG_P4_5_CNSTN_J_SRT-A | Breaker | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 221051 | CHESTN8A | 221049 | FRED.RD8 | 1 | 115 | 232 | 189 | 211 | 215.1 | 111.63 | 113.83 | BG_P7_NEAST_RPHLRD_SRT-A | Tower | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 220960 | BRANDN.S | 220955 | W.CHAPEL | 42 | 230 | 232 | 857 | 973.4 | 974.6 | 113.58 | 113.72 | PEPCO_P4_PP40_SRT-A | Breaker | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 235463 | 01TANEY | 1 | 138 | 227/201 | 268 | 303.7 | 303.5 | 113.32 | 113.24 | BG_P7_NEAST_RPHLRD_SRT-A | Tower | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1417 | 1582 | 1603.6 | 111.65 | 113.17 | DVP_P4-2: GOOSE H1T558_SRT-A | Breaker | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208132 | WHEM TR1 | 208131 | WHEM | 1 | 230 | 229 | 618 | 699.2 | 699 | 113.14 | 113.11 | PECO_P1-2_5012_SRT-A | Single | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208132 | WHEM TR1 | 208131 | WHEM | 1 | 230 | 229 | 618 | 699 | 698.5 | 113.11 | 113.02 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | Breaker | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208132 | WHEM TR1 | 208131 | WHEM | 1 | 230 | 229 | 618 | 698.9 | 698.4 | 113.1 | 113.01 | PECO_P4_PEACH235_SRT-A | Breaker | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 235463 | 01TANEY | 1 | 138 | 227/201 | 268 | 276.8 | 274.3 | 103.27 | 102.37 | AP_P1-2_PE-500-001_SRT-SL | Single | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 235463 | 01TANEY | 1 | 138 | 227/201 | 268 | 276.8 | 274.3 | 103.27 | 102.37 | AP_P1-2_WP-500-DRT17_SRT-SL | Single | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208396 | FARO | 208395 | FARO FF | 1 | 69 | 229 | 240 | 243.3 | 245.6 | 101.38 | 102.33 | BG_P4_5_GRCTN_2T_SRT-A | Breaker | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 242563 | 05BOXWD | 242603 | 05CLIFFR | 1 | 138 | 205 | 167 | 171.7 | 170.8 | 102.84 | 102.3 | DVP_P4-2: 547T566_SRT-SW | Breaker | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 221092 | FIVE.FOR | 221096 | ROCKRGE1 | 1 | 115 | 232 | 256 | 253.4 | 260.7 | 98.99 | 101.82 | BG_P4_5_WE502_SRT-A | Breaker | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208395 | FARO FF | 208393 | FARO DC TIE | 1 | 69/115 | 229 | 114 | 117.2 | 116.1 | 102.81 | 101.81 | BG_P7_GRCTN_RAPHEL_SRT-A | Tower | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 235463 | 01TANEY | 1 | 138 | 227/201 | 268 | 274.5 | 272.7 | 102.41 | 101.75 | AP_P2-2_PE-500-004_SRT-SL | Bus | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208395 | FARO FF | 208393 | FARO DC TIE | 1 | 69/115 | 229 | 114 | 117.9 | 115.8 | 103.46 | 101.6 | PL_05_P22_000674_SRT-A | Bus | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 235463 | 01TANEY | 1 | 138 | 227/201 | 268 | 275.7 | 272.2 | 102.88 | 101.57 | AP_P1-2_PE-500-004_SRT-SL | Single | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 235463 | 01TANEY | 1 | 138 | 227/201 | 268 | 275.7 | 272.2 | 102.88 | 101.57 | AP_P1-2_WP-500-006_SRT-A | Single | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200051 | ROCKSPGS | 200065 | PCHBTM2S | 1 | 500 | 235/230 | 2860 | 2847.1 | 2904.4 | 99.55 | 101.55 | PECO_P4_LINWO125_SRT-A | Breaker | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200051 | ROCKSPGS | 200065 | PCHBTM2S | 1 | 500 | 235/230 | 2860 | 2847.1 | 2904.4 | 99.55 | 101.55 | DPL_P7_1_DBL_6NC_SRT-A | Tower | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200051 | ROCKSPGS | 200065 | PCHBTM2S | 1 | 500 | 235/230 | 2860 | 2847.1 | 2904.4 | 99.55 | 101.55 | PECO_P4_LINWO125/* $ DELCO $ LINWO125 $ STBK_SRT-A | Breaker | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 235463 | 01TANEY | 1 | 138 | 227/201 | 268 | 273.9 | 272.1 | 102.2 | 101.54 | AP_P2-2_PE-500-005_SRT-SL | Bus | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 235463 | 01TANEY | 1 | 138 | 227/201 | 268 | 273.6 | 272.1 | 102.09 | 101.53 | AP_P2-2_PE-138-072_SRT-A | Bus | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204550 | 27ORRTANNA | 204544 | 27LINCOLN | 1 | 115 | 227 | 160 | 165.2 | 162.2 | 103.25 | 101.37 | ME_P2-3_ME-115-0102-A_SRT-A | Breaker | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204550 | 27ORRTANNA | 204544 | 27LINCOLN | 1 | 115 | 227 | 160 | 165.2 | 162.2 | 103.25 | 101.37 | ME_P2-2_ME-115-0102-4_SRT-A | Bus | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208133 | WHEM TR2 | 208021 | MANO TR4 | 2 | 230 | 229 | 531 | 536.4 | 538.1 | 101.02 | 101.35 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | Breaker | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 2 | 500/230 | 232 | 1940 | 1932.5 | 1965.7 | 99.61 | 101.32 | PJM_500_BG_P4_5_CNSTN_15_SRT-A | Breaker | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 221092 | FIVE.FOR | 221096 | ROCKRGE1 | 1 | 115 | 232 | 256 | 252.1 | 259.4 | 98.49 | 101.32 | BG_P4_5_WE505_SRT-A | Breaker | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 232004 | MILF_230 | 232001 | COOLSPRS | 1 | 230 | 235 | 682 | 678.3 | 690.8 | 99.46 | 101.29 | DPL_P4-2_DP3_SRT-A | Breaker | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204514 | 27TMI | 204502 | 27JACKSON | 1 | 230 | 227 | 659 | 668.1 | 667.3 | 101.39 | 101.26 | PECO_P4_PEACH245_SRT-A | Breaker | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208021 | MANO TR4 | 208019 | MANO | 1 | 230 | 229 | 533 | 537 | 539.2 | 100.75 | 101.16 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | Breaker | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200011 | KEYSTONE | 200005 | CONEM-GH | 1 | 500 | 226 | 2844 | 2885.6 | 2876.8 | 101.46 | 101.15 | PN_P2-3_PN-500-DRT31_SRT-SL | Breaker | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208021 | MANO TR4 | 208019 | MANO | 1 | 230 | 229 | 533 | 536.9 | 539.1 | 100.74 | 101.15 | PECO_P4_PEACH235_SRT-A | Breaker | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 208070 | SAHA12TP | 1 | 230 | 229 | 628 | 639.4 | 635.1 | 101.81 | 101.13 | PL_14_P42_000575_SRT-A | Breaker | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 205912 | AD1-020 TAP | 204544 | 27LINCOLN | 1 | 115 | 227 | 282 | 289.1 | 284.7 | 102.51 | 100.95 | AP_P2-2_WP-138-074_SRT-A | Bus | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 563 | 571.7 | 568.1 | 101.54 | 100.9 | PL_05_P22_000674_SRT-A | Bus | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 563 | 573.6 | 568.1 | 101.89 | 100.9 | PL_05_P22_000674_SRT-A | Bus | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208395 | FARO FF | 208393 | FARO DC TIE | 1 | 69/115 | 229 | 77 | 77.3 | 77.6 | 100.4 | 100.81 | Base Case | Single | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208395 | FARO FF | 208393 | FARO DC TIE | 2 | 69/115 | 229 | 77 | 77.3 | 77.6 | 100.4 | 100.81 | Base Case | Single | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 203981 | AD2-062_POI | 235188 | 01GREENE | 1 | 138 | 226/201 | 268 | 270.8 | 270 | 101.03 | 100.76 | BG_P7_GRCTN_RAPHEL_SRT-A | Tower | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204539 | 27HUNTRSTN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 282 | 285.3 | 284 | 101.16 | 100.7 | BG_P7_GRCTN_RAPHEL_SRT-A | Tower | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 221092 | FIVE.FOR | 221096 | ROCKRGE1 | 1 | 115 | 232 | 256 | 252.8 | 257.7 | 98.77 | 100.66 | PJM_500_BG_P1_5011_SRT-A | Single | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 203981 | AD2-062_POI | 235188 | 01GREENE | 1 | 138 | 226/201 | 268 | 277.7 | 269.7 | 103.61 | 100.65 | PECO_P1-2_5012_SRT-A | Single | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 242563 | 05BOXWD | 242603 | 05CLIFFR | 1 | 138 | 205 | 167 | 169.3 | 167.9 | 101.4 | 100.54 | DVP_P4-2: 56602_SRT-SW | Breaker | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 205912 | AD1-020 TAP | 204544 | 27LINCOLN | 1 | 115 | 227 | 282 | 287.7 | 283.5 | 102.01 | 100.53 | AP_P7-1_PE-230-001_SRT-A | Tower | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 223938 | DICKH230 | 223937 | DICK 230 | 2 | 230 | 233 | 680 | 696.5 | 683.2 | 102.43 | 100.47 | PP7_SRT-A | Bus | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 223938 | DICKH230 | 223937 | DICK 230 | 2 | 230 | 233 | 680 | 696.5 | 683.2 | 102.43 | 100.47 | PEPCO_P4_PP16_SRT-A | Breaker | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204539 | 27HUNTRSTN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 282 | 291.4 | 283 | 103.34 | 100.35 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | Breaker | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204539 | 27HUNTRSTN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 282 | 291.4 | 283 | 103.34 | 100.34 | PECO_P4_PEACH235_SRT-A | Breaker | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 242563 | 05BOXWD | 242603 | 05CLIFFR | 1 | 138 | 205 | 167 | 169 | 167.6 | 101.18 | 100.34 | AEP_P4_#7422_05CLOVRD 500_EE2_SRT-A | Breaker | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 221094 | GRACE.-1 | 221092 | FIVE.FOR | 1 | 115 | 232 | 437 | 435.3 | 438.4 | 99.62 | 100.32 | BG_P7_NEAST_RPHLRD_SRT-A | Tower | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 563 | 568.6 | 564.7 | 100.99 | 100.3 | PECO_P1-2_5014_SRT-A | Single | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 563 | 570.5 | 564.7 | 101.34 | 100.3 | PECO_P1-2_5014_SRT-A | Single | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208396 | FARO | 208395 | FARO FF | 1 | 69 | 229 | 240 | 234.6 | 240.4 | 97.75 | 100.19 | BG_P7_GRCTN_RAPHEL_SRT-A | Tower | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204693 | 27BOONETOWN | 204512 | 27S.RDG | 1 | 230 | 227 | 445 | 447.7 | 445.6 | 100.62 | 100.14 | Base Case | Single | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200051 | ROCKSPGS | 200065 | PCHBTM2S | 1 | 500 | 235/230 | 2860 | 2813.6 | 2863.1 | 98.38 | 100.11 | DPL_P7_1_DBL_5NC_SRT-A | Tower | N/A | No | Related to 2022 Window 3, pending window outcome
2023W1-GD-S791 | 243211 | 05ALLEN | 242933 | 05RPMONE | 1 | 345 | 205 | 897 | 918.8 | 936.7 | 102.43 | 104.42 | AEP_P4_#7445_05MARYSV 765_B_SRT-A | Breaker |  | No |  | Addressed by network upgrade N8169.1
2023W1-GD-S872 | 290623 | 05KAMMER_RG | 242925 | 05KAMMER | Z1 | 765 | 205 | 4142 | 4146.6 | 4186.1 | 100.11 | 101.06 | AEP_P4_#2942_05KAMMER 765_PP_SRT-A | Breaker |  | No |  | Due to suspended project AB1-087, AB1-088, and AB1-089.
2023W1-GD-S712 | 238569 | 02BEAVER | 239725 | 02LAKEAVE | 2 | 345 | 202 | 1900 | 2058.3 | 2055.8 | 108.33 | 108.2 | ATSI_P2-3_OEC-345-002_SRT-A | Breaker | 1560/1900/2146 (SN/SE/SLD) | No |  | Due to suspended project AB1-107 and AB1-089.
2023W1-GD-S729 | 238654 | 02DAV-BE | 239289 | 02HAYES | 1 | 345 | 202 | 1683 | 1800.3 | 1806.4 | 106.97 | 107.33 | ATSI_P2-3_OEC-345-005_SRT-A | Breaker | 1560/1900/2146 (SN/SE/SLD) | No |  | Due to suspended project AB1-107 and AB1-089.
2023W1-GD-S1406 | 238768 | 02GRNFLD | 238981 | 02NASA | 1 | 138 | 202 | 192 | 199.1 | 202.5 | 103.71 | 105.45 | ATSI_P7-1_TE-345-030_SRT-A | Tower | 160/192/217 (SN/SE/SLD) | No |  | Due to suspended project AB1-107 and AB1-089.
2023W1-GD-S799 | 241877 | AC2-103 TAP | 238569 | 02BEAVER | 1 | 345 | 202 | 1499 | 1557.3 | 1562.4 | 103.89 | 104.23 | ATSI_P2-3_OEC-345-009_SRT-SL | Breaker | 1542/1878/2120 (SN/SE/SLD) | No |  | Due to suspended project AB1-107 and AB1-089.
2023W1-GD-S1412 | 238981 | 02NASA | 238570 | 02BEAVER | 1 | 138 | 202 | 192 | 195.6 | 199.7 | 101.87 | 104.03 | ATSI_P7-1_TE-345-030_SRT-A | Tower | 160/192/217 (SN/SE/SLD) | No |  | Due to suspended project AB1-107 and AB1-089.
2023W1-GD-S804 | 238654 | 02DAV-BE | 239289 | 02HAYES | 1 | 345 | 202 | 1683 | 1743.9 | 1749.6 | 103.62 | 103.95 | ATSI_P2-3_OEC-345-006_SRT-SL | Breaker | 1560/1900/2146 (SN/SE/SLD) | No |  | Due to suspended project AB1-107 and AB1-089.
2023W1-GD-S1414 | 238768 | 02GRNFLD | 238981 | 02NASA | 1 | 138 | 202 | 192 | 196 | 199.2 | 102.11 | 103.74 | ATSI_P7-1_TE-345-031_SRT-A | Tower | 160/192/217 (SN/SE/SLD) | No |  | Due to suspended project AB1-107 and AB1-089.
2023W1-GD-S821 | 238563 | 02BAY SH | 238654 | 02DAV-BE | 1 | 345 | 202 | 1683 | 1746.4 | 1743 | 103.77 | 103.56 | ATSI_P2-3_TE-345-008B_SRT-SL | Breaker | 1542/1878/2120 (SN/SE/SLD) | No |  | Due to suspended project AB1-107 and AB1-089.
2023W1-GD-S1423 | 238981 | 02NASA | 238570 | 02BEAVER | 1 | 138 | 202 | 192 | 192.5 | 196.5 | 100.26 | 102.32 | ATSI_P7-1_TE-345-031_SRT-A | Tower | 160/192/217 (SN/SE/SLD) | No |  | Due to suspended project AB1-107 and AB1-089.
2023W1-GD-S1425 | 238974 | 02N DEPT | 238590 | 02BRWELL | 1 | 138 | 202 | 230 | 229.1 | 234.4 | 99.62 | 101.93 | ATSI_P7-1_TE-345-030_SRT-A | Tower | 189/230/261 (SN/SE/SLD) | No |  | Due to suspended project AB1-107 and AB1-089.
2023W1-GD-S1428 | 238874 | 02LAKVEW | 238768 | 02GRNFLD | 1 | 138 | 202 | 385 | 387.3 | 390.7 | 100.59 | 101.49 | ATSI_P7-1_TE-345-027A_SRT-A | Tower | 320/385/433 (SN/SE/SLD) | No |  | Due to suspended project AB1-107 and AB1-089.
2023W1-GD-S880 | 241877 | AC2-103 TAP | 238569 | 02BEAVER | 1 | 345 | 202 | 1646 | 1658.6 | 1661.6 | 100.76 | 100.95 | ATSI_P2-3_OEC-345-1152-12_SRT-A | Breaker | 1542/1878/2120 (SN/SE/SLD) | No |  | Due to suspended project AB1-107 and AB1-089.
2023W1-GD-S879 | 241877 | AC2-103 TAP | 238569 | 02BEAVER | 1 | 345 | 202 | 1646 | 1658.6 | 1661.6 | 100.76 | 100.95 | ATSI_P2-3_OEC-345-1152-F1_SRT-A | Breaker | 1542/1878/2120 (SN/SE/SLD) | No |  | Due to suspended project AB1-107 and AB1-089.
2023W1-GD-S1431 | 238590 | 02BRWELL | 238728 | 02FORD | 1 | 138 | 202 | 230 | 227 | 231.9 | 98.69 | 100.82 | ATSI_P7-1_TE-345-030_SRT-A | Tower | 189/230/261 (SN/SE/SLD) | No |  | Due to suspended project AB1-107 and AB1-089.

## Summer IPD
| Note | APS and Dominion zones as a whole are quarantined pending Window 3 outcome and are not included in above results
Related to 2022 Window 3, pending window outcome
Flowgate can be addressed by existing M-3 solution or network upgrade
2028 RTEP PJM Individual Plant Deliverability Result (Summer)
FG # | Fr Bus | Fr Name | To Bus | To Name | CKT | kVs | Areas | Rate Cont (MVA) | Cont Flow (MVA) | FN DC % | FN AC % | Plant | Cont Type | Conductor/Transformer Rating (MVA) | PJM Accepting Proposals | Reason For Exclusion | Comments
2023W1-IPD-S1 | 232002 | CEDAR CK | 232013 | SILVER RUN | 1 | 230 | 235/231 | 805 | 825.4 | 100 | 102.53 | AB2-036 | DPL_P4-2_DP6_SRT-A | 653/808 (SN/SE) | Yes
2023W1-IPD-S2 | 232002 | CEDAR CK | 232013 | SILVER RUN | 1 | 230 | 235/231 | 805 | 822.3 | 99.6 | 102.15 | AB2-037 | DPL_P4-2_DP6_SRT-A | 653/808 (SN/SE) | Yes
2023W1-IPD-S3 | 232002 | CEDAR CK | 232013 | SILVER RUN | 1 | 230 | 235/231 | 805 | 834.8 | 101.09 | 103.7 | AB2-133 | DPL_P4-2_DP6_SRT-A | 653/808 (SN/SE) | Yes
2023W1-IPD-S4 | 232002 | CEDAR CK | 232013 | SILVER RUN | 1 | 230 | 235/231 | 805 | 830.6 | 100.63 | 103.19 | AB2-135 | DPL_P4-2_DP6_SRT-A | 653/808 (SN/SE) | Yes
2023W1-IPD-S5 | 232002 | CEDAR CK | 232013 | SILVER RUN | 1 | 230 | 235/231 | 805 | 829.3 | 100.59 | 103.01 | AB2-136 | DPL_P4-2_DP6_SRT-A | 653/808 (SN/SE) | Yes
2023W1-IPD-S6 | 232002 | CEDAR CK | 232013 | SILVER RUN | 1 | 230 | 235/231 | 805 | 828.3 | 100.47 | 102.9 | AB2-172 | DPL_P4-2_DP6_SRT-A | 653/808 (SN/SE) | Yes
2023W1-IPD-S7 | 232002 | CEDAR CK | 232013 | SILVER RUN | 1 | 230 | 235/231 | 805 | 831.1 | 100.65 | 103.24 | AC1-091 | DPL_P4-2_DP6_SRT-A | 653/808 (SN/SE) | Yes
2023W1-IPD-S8 | 232002 | CEDAR CK | 232013 | SILVER RUN | 1 | 230 | 235/231 | 805 | 831.1 | 100.65 | 103.24 | AC1-092 | DPL_P4-2_DP6_SRT-A | 653/808 (SN/SE) | Yes
2023W1-IPD-S9 | 232002 | CEDAR CK | 232013 | SILVER RUN | 1 | 230 | 235/231 | 805 | 831.6 | 100.71 | 103.31 | AC1-093 | DPL_P4-2_DP6_SRT-A | 653/808 (SN/SE) | Yes
2023W1-IPD-S10 | 232002 | CEDAR CK | 232013 | SILVER RUN | 1 | 230 | 235/231 | 805 | 833.2 | 100.9 | 103.5 | AC1-094 | DPL_P4-2_DP6_SRT-A | 653/808 (SN/SE) | Yes
2023W1-IPD-S11 | 232002 | CEDAR CK | 232013 | SILVER RUN | 1 | 230 | 235/231 | 805 | 830.4 | 100.71 | 103.16 | AC2-023 | DPL_P4-2_DP6_SRT-A | 653/808 (SN/SE) | Yes
2023W1-IPD-S12 | 232002 | CEDAR CK | 232013 | SILVER RUN | 1 | 230 | 235/231 | 805 | 820.2 | 99.35 | 101.89 | AC2-185 | DPL_P4-2_DP6_SRT-A | 653/808 (SN/SE) | Yes
2023W1-IPD-S13 | 232002 | CEDAR CK | 232013 | SILVER RUN | 1 | 230 | 235/231 | 805 | 832.7 | 100.94 | 103.44 | AC2-187 | DPL_P4-2_DP6_SRT-A | 653/808 (SN/SE) | Yes
2023W1-IPD-S14 | 232002 | CEDAR CK | 232013 | SILVER RUN | 1 | 230 | 235/231 | 805 | 832.7 | 100.94 | 103.45 | AC2-188 | DPL_P4-2_DP6_SRT-A | 653/808 (SN/SE) | Yes
2023W1-IPD-S15 | 232002 | CEDAR CK | 232013 | SILVER RUN | 1 | 230 | 235/231 | 805 | 836.2 | 101.27 | 103.88 | AD2-076 | DPL_P4-2_DP6_SRT-A | 653/808 (SN/SE) | Yes
2023W1-IPD-S16 | 232002 | CEDAR CK | 232013 | SILVER RUN | 1 | 230 | 235/231 | 805 | 836.1 | 101.28 | 103.87 | AE2-093 | DPL_P4-2_DP6_SRT-A | 653/808 (SN/SE) | Yes
2023W1-IPD-S17 | 232002 | CEDAR CK | 232013 | SILVER RUN | 1 | 230 | 235/231 | 805 | 835.8 | 101.3 | 103.82 | AG1-397 | DPL_P4-2_DP6_SRT-A | 653/808 (SN/SE) | Yes
2023W1-IPD-S18 | 232002 | CEDAR CK | 232013 | SILVER RUN | 1 | 230 | 235/231 | 805 | 833.3 | 101.04 | 103.51 | CHERRYDALE C | DPL_P4-2_DP6_SRT-A | 653/808 (SN/SE) | Yes
2023W1-IPD-S19 | 232002 | CEDAR CK | 232013 | SILVER RUN | 1 | 230 | 235/231 | 805 | 834.6 | 101.17 | 103.68 | DUP-SFR1 | DPL_P4-2_DP6_SRT-A | 653/808 (SN/SE) | Yes
2023W1-IPD-S20 | 200677 | 26NO MESHO | 200698 | 26MEHOOPNY | 2 | 115 | 226 | 160 | 162.9 | 98.2 | 101.8 | P28 | PN_P2-3_PN-115-43B_SRT-A | 133/160/180 (SN/SE/SLD) | Yes
2023W1-IPD-S21 | 200677 | 26NO MESHO | 200698 | 26MEHOOPNY | 2 | 115 | 226 | 160 | 162.9 | 98.2 | 101.8 | P28 | PN_P1-2_PN-115-041_SRT-A | 133/160/180 (SN/SE/SLD) | Yes
2023W1-IPD-S22 | 200677 | 26NO MESHO | 200699 | 26MEHOP 3 | 1 | 115 | 226 | 160 | 162.8 | 97.6 | 101.77 | P28 | PN_P2-3_PN-115-0272-B_SRT-A | 133/160/180 (SN/SE/SLD) | Yes
2023W1-IPD-S23 | 200677 | 26NO MESHO | 200699 | 26MEHOP 3 | 1 | 115 | 226 | 160 | 162.8 | 97.6 | 101.75 | P28 | PN_P1-2_PN-115-042_SRT-A | 133/160/180 (SN/SE/SLD) | Yes
2023W1-IPD-S24 | 200677 | 26NO MESHO | 200698 | 26MEHOOPNY | 2 | 115 | 226 | 160 | 162 | 97.6 | 101.25 | P28 | PN_P2-3_PN-115-0272-18_SRT-A | 133/160/180 (SN/SE/SLD) | Yes
2023W1-IPD-S25 | 200677 | 26NO MESHO | 200699 | 26MEHOP 3 | 1 | 115 | 226 | 160 | 160.2 | 97.6 | 100.14 | P28 | PN_P2-3_PN-115-0272-14_SRT-A | 133/160/180 (SN/SE/SLD) | Yes
2023W1-IPD-S26 | 232002 | CEDAR CK | 232013 | SILVER RUN | 1 | 230 | 235/231 | 805 | 833.1 | 101.01 | 103.49 | W1-003 | DPL_P4-2_DP6_SRT-A | 653/808 | Yes
2023W1-IPD-S27 | 232002 | CEDAR CK | 232013 | SILVER RUN | 1 | 230 | 235/231 | 805 | 833.1 | 101.01 | 103.49 | W1-004 | DPL_P4-2_DP6_SRT-A | 653/808 | Yes
2023W1-IPD-S28 | 232002 | CEDAR CK | 232013 | SILVER RUN | 1 | 230 | 235/231 | 805 | 833.1 | 101.01 | 103.49 | W1-005 | DPL_P4-2_DP6_SRT-A | 653/808 | Yes
2023W1-IPD-S29 | 232002 | CEDAR CK | 232013 | SILVER RUN | 1 | 230 | 235/231 | 805 | 833.1 | 101.01 | 103.49 | W1-006 | DPL_P4-2_DP6_SRT-A | 653/808 | Yes
2023W1-IPD-S30 | 243598 | 05BCKSKI | 253030 | 09GRNFLD | 1 | 69 | 205/209 | 72 | 72 | 155.69 | 159.1 | AC2-060 | AEP_P4_#14130_05BCKSKI 69.0_A_SRT-A | Dayton side conductor rating: 80/98 (SN/SE) AEP side conductor rating 146/165 (SN/SE) | No | Below 200 kV exclusion | Dayton-2023-002 increases the rating to Dayton conductor rating
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 116.84 | 01BACKB | PJM_500_BG_P1_5013_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 116.84 | 01BACKB | PJM_500_BG_P4_5_CNSTN_M_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.19 | 116.95 | 01BACKB | Base Case | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 105.55 | 110.21 | 01BACKB | PN_P1-2_PN-500-010T_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 104.22 | 108.47 | 01BACKB | PJM_500_BG_P4_5_CNSTN_L_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 116.76 | 01CROSSCHOOL | PJM_500_BG_P1_5013_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 116.76 | 01CROSSCHOOL | PJM_500_BG_P4_5_CNSTN_M_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.19 | 116.86 | 01CROSSCHOOL | Base Case | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 106.71 | 108.17 | 01CROSSCHOOL | BG_P7_CNSTN_NWEST2_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 106.17 | 107.28 | 01CROSSCHOOL | BG_P7_GRCTN_RAPHEL_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 105.55 | 110.13 | 01CROSSCHOOL | PN_P1-2_PN-500-010T_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 104.22 | 108.39 | 01CROSSCHOOL | PJM_500_BG_P4_5_CNSTN_L_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 103.32 | 104.41 | 01CROSSCHOOL | BG_P7_NEAST_RPHLRD_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 101.26 | 102.34 | 01CROSSCHOOL | AP_P2-3_PE-500-015_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 100.32 | 102.25 | 01CROSSCHOOL | PJM_500_BG_P4_5_CNSTN_13_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 228.49 | 236.78 | 01GRNGAP | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 224.05 | 231.9 | 01GRNGAP | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 224.05 | 231.9 | 01GRNGAP | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 224.03 | 231.87 | 01GRNGAP | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 209.21 | 215.23 | 01GRNGAP | PECO_P4_PEACH245_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 202.97 | 209.93 | 01GRNGAP | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 198.66 | 205.15 | 01GRNGAP | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 198.66 | 205.15 | 01GRNGAP | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 198.64 | 205.12 | 01GRNGAP | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 183.92 | 188.71 | 01GRNGAP | PECO_P4_PEACH245_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 166.62 | 167.87 | 01GRNGAP | Base Case | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 130.65 | 130.33 | 01GRNGAP | Base Case | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 647 | 801 | 122.17 | 122.22 | 01GRNGAP | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 207923 | BRISREAC | 208132 | WHEM TR1 | 1 | 230 | 229 | 493 | 618 | 117.78 | 118.3 | 01GRNGAP | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 207922 | BRIS | 207923 | BRISREAC | RX | 230 | 229 | 506 | 618 | 117.78 | 118.3 | 01GRNGAP | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 647 | 801 | 117.38 | 117.76 | 01GRNGAP | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 647 | 801 | 117.38 | 117.76 | 01GRNGAP | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 647 | 801 | 117.37 | 117.75 | 01GRNGAP | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 463 | 563 | 115.98 | 116.2 | 01GRNGAP | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 463 | 563 | 115.98 | 115.87 | 01GRNGAP | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 207923 | BRISREAC | 208132 | WHEM TR1 | 1 | 230 | 229 | 493 | 618 | 115.13 | 115.9 | 01GRNGAP | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 207922 | BRIS | 207923 | BRISREAC | RX | 230 | 229 | 506 | 618 | 115.13 | 115.9 | 01GRNGAP | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 207923 | BRISREAC | 208132 | WHEM TR1 | 1 | 230 | 229 | 493 | 618 | 115.13 | 115.9 | 01GRNGAP | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 207922 | BRIS | 207923 | BRISREAC | RX | 230 | 229 | 506 | 618 | 115.13 | 115.9 | 01GRNGAP | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 207922 | BRIS | 207923 | BRISREAC | RX | 230 | 229 | 506 | 618 | 115.12 | 115.88 | 01GRNGAP | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 207923 | BRISREAC | 208132 | WHEM TR1 | 1 | 230 | 229 | 493 | 618 | 115.12 | 115.88 | 01GRNGAP | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 463 | 563 | 113.42 | 113.59 | 01GRNGAP | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 463 | 563 | 113.42 | 113.92 | 01GRNGAP | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 463 | 563 | 113.37 | 113.86 | 01GRNGAP | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 463 | 563 | 113.37 | 113.53 | 01GRNGAP | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 463 | 563 | 113.37 | 113.53 | 01GRNGAP | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 463 | 563 | 113.37 | 113.86 | 01GRNGAP | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 116.01 | 01GRNGAP | PJM_500_BG_P1_5013_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 116.01 | 01GRNGAP | PJM_500_BG_P4_5_CNSTN_M_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.19 | 115.94 | 01GRNGAP | Base Case | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 709 | 869 | 110.18 | 110.57 | 01GRNGAP | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 463 | 578 | 110.56 | 110.26 | 01GRNGAP | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 709 | 869 | 108.55 | 109.07 | 01GRNGAP | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 709 | 869 | 108.55 | 109.07 | 01GRNGAP | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 709 | 869 | 108.54 | 109.06 | 01GRNGAP | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 647 | 801 | 108.33 | 108.81 | 01GRNGAP | PECO_P4_PEACH245_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 207922 | BRIS | 207923 | BRISREAC | RX | 230 | 229 | 506 | 618 | 107.75 | 108.85 | 01GRNGAP | PECO_P4_PEACH245_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 207923 | BRISREAC | 208132 | WHEM TR1 | 1 | 230 | 229 | 493 | 618 | 107.75 | 108.85 | 01GRNGAP | PECO_P4_PEACH245_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 463 | 578 | 108.07 | 108.04 | 01GRNGAP | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 463 | 578 | 108.02 | 107.98 | 01GRNGAP | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 463 | 578 | 108.02 | 107.98 | 01GRNGAP | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 106.71 | 107.33 | 01GRNGAP | BG_P7_CNSTN_NWEST2_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208131 | WHEM | 208132 | WHEM TR1 | 1 | 230 | 229 | 547 | 618 | 106.32 | 105.47 | 01GRNGAP | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 106.17 | 106.44 | 01GRNGAP | BG_P7_GRCTN_RAPHEL_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 105.55 | 109.39 | 01GRNGAP | PN_P1-2_PN-500-010T_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 463 | 578 | 105.24 | 104.23 | 01GRNGAP | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 104.22 | 107.66 | 01GRNGAP | PJM_500_BG_P4_5_CNSTN_L_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208131 | WHEM | 208132 | WHEM TR1 | 1 | 230 | 229 | 547 | 618 | 103.73 | 103.13 | 01GRNGAP | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208131 | WHEM | 208132 | WHEM TR1 | 1 | 230 | 229 | 547 | 618 | 103.73 | 103.13 | 01GRNGAP | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208131 | WHEM | 208132 | WHEM TR1 | 1 | 230 | 229 | 547 | 618 | 103.72 | 103.12 | 01GRNGAP | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 103.32 | 103.57 | 01GRNGAP | BG_P7_NEAST_RPHLRD_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 220964 | GRACETON | 220999 | BAGLEY2 | 13 | 230 | 232 | 1331 | 1594 | 101.97 | 102.23 | 01GRNGAP | BG_P4_5_GRCTN_3T_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 463 | 578 | 102.74 | 102.01 | 01GRNGAP | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 463 | 578 | 102.69 | 101.96 | 01GRNGAP | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 463 | 578 | 102.69 | 101.96 | 01GRNGAP | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 709 | 869 | 101.29 | 102.1 | 01GRNGAP | PECO_P4_PEACH245_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 101.26 | 101.54 | 01GRNGAP | AP_P2-3_PE-500-015_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 116.74 | 05CELAN | PJM_500_BG_P1_5013_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 116.74 | 05CELAN | PJM_500_BG_P4_5_CNSTN_M_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.19 | 116.84 | 05CELAN | Base Case | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 106.71 | 108.16 | 05CELAN | BG_P7_CNSTN_NWEST2_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 106.17 | 107.26 | 05CELAN | BG_P7_GRCTN_RAPHEL_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 105.55 | 110.11 | 05CELAN | PN_P1-2_PN-500-010T_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 104.22 | 108.37 | 05CELAN | PJM_500_BG_P4_5_CNSTN_L_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 103.32 | 104.39 | 05CELAN | BG_P7_NEAST_RPHLRD_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 101.26 | 102.31 | 05CELAN | AP_P2-3_PE-500-015_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 100.32 | 102.24 | 05CELAN | PJM_500_BG_P4_5_CNSTN_13_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 116.85 | 05NTRDAM | PJM_500_BG_P1_5013_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 116.85 | 05NTRDAM | PJM_500_BG_P4_5_CNSTN_M_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.19 | 116.96 | 05NTRDAM | Base Case | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 116.79 | 08HLCRTG | PJM_500_BG_P1_5013_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 116.79 | 08HLCRTG | PJM_500_BG_P4_5_CNSTN_M_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.19 | 116.88 | 08HLCRTG | Base Case | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 106.71 | 108.21 | 08HLCRTG | BG_P7_CNSTN_NWEST2_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 106.17 | 107.32 | 08HLCRTG | BG_P7_GRCTN_RAPHEL_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 105.55 | 110.16 | 08HLCRTG | PN_P1-2_PN-500-010T_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 104.22 | 108.42 | 08HLCRTG | PJM_500_BG_P4_5_CNSTN_L_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 103.32 | 104.45 | 08HLCRTG | BG_P7_NEAST_RPHLRD_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 100.32 | 102.29 | 08HLCRTG | PJM_500_BG_P4_5_CNSTN_13_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 100.27 | 102.23 | 08HLCRTG | PJM_500_BG_P4_5_CNSTN_6_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 228.49 | 239.44 | 09GRNVIL | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 224.05 | 234.63 | 09GRNVIL | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 224.05 | 234.63 | 09GRNVIL | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 224.03 | 234.6 | 09GRNVIL | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 209.21 | 217.92 | 09GRNVIL | PECO_P4_PEACH245_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 202.97 | 212.49 | 09GRNVIL | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 198.66 | 207.78 | 09GRNVIL | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 198.66 | 207.78 | 09GRNVIL | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 198.64 | 207.76 | 09GRNVIL | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 183.92 | 191.3 | 09GRNVIL | PECO_P4_PEACH245_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 117.4 | 09GRNVIL | PJM_500_BG_P1_5013_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 117.4 | 09GRNVIL | PJM_500_BG_P4_5_CNSTN_M_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.19 | 117.74 | 09GRNVIL | Base Case | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 106.71 | 108.81 | 09GRNVIL | BG_P7_CNSTN_NWEST2_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 106.17 | 107.91 | 09GRNVIL | BG_P7_GRCTN_RAPHEL_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 105.55 | 110.75 | 09GRNVIL | PN_P1-2_PN-500-010T_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 104.22 | 109.01 | 09GRNVIL | PJM_500_BG_P4_5_CNSTN_L_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 103.32 | 105.04 | 09GRNVIL | BG_P7_NEAST_RPHLRD_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 101.26 | 102.88 | 09GRNVIL | AP_P2-3_PE-500-015_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 100.32 | 102.86 | 09GRNVIL | PJM_500_BG_P4_5_CNSTN_13_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 94.68 | 94.53 | 15USSILL | AP_P2-3_WP-138-18201_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 94.68 | 94.53 | 15USSILL | AP_P2-3_WP-138-18200_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 94.64 | 94.5 | 15USSILL | AP_P2-3_WP-138-18202_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 116.79 | 1DOMTR10 | PJM_500_BG_P1_5013_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 116.79 | 1DOMTR10 | PJM_500_BG_P4_5_CNSTN_M_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.19 | 116.92 | 1DOMTR10 | Base Case | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 106.71 | 108.19 | 1DOMTR10 | BG_P7_CNSTN_NWEST2_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 106.17 | 107.29 | 1DOMTR10 | BG_P7_GRCTN_RAPHEL_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 105.55 | 110.15 | 1DOMTR10 | PN_P1-2_PN-500-010T_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 104.22 | 108.42 | 1DOMTR10 | PJM_500_BG_P4_5_CNSTN_L_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 103.32 | 104.42 | 1DOMTR10 | BG_P7_NEAST_RPHLRD_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 101.26 | 102.32 | 1DOMTR10 | AP_P2-3_PE-500-015_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 100.32 | 102.27 | 1DOMTR10 | PJM_500_BG_P4_5_CNSTN_13_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 116.83 | 1DOMTR9 | PJM_500_BG_P1_5013_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 116.83 | 1DOMTR9 | PJM_500_BG_P4_5_CNSTN_M_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.19 | 116.96 | 1DOMTR9 | Base Case | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 106.71 | 108.23 | 1DOMTR9 | BG_P7_CNSTN_NWEST2_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 106.17 | 107.33 | 1DOMTR9 | BG_P7_GRCTN_RAPHEL_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 105.55 | 110.19 | 1DOMTR9 | PN_P1-2_PN-500-010T_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 104.22 | 108.45 | 1DOMTR9 | PJM_500_BG_P4_5_CNSTN_L_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 103.32 | 104.46 | 1DOMTR9 | BG_P7_NEAST_RPHLRD_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 101.26 | 102.36 | 1DOMTR9 | AP_P2-3_PE-500-015_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 100.32 | 102.31 | 1DOMTR9 | PJM_500_BG_P4_5_CNSTN_13_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 116.77 | 1EDGECMA | PJM_500_BG_P1_5013_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 116.77 | 1EDGECMA | PJM_500_BG_P4_5_CNSTN_M_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.19 | 116.89 | 1EDGECMA | Base Case | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 106.71 | 108.17 | 1EDGECMA | BG_P7_CNSTN_NWEST2_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 106.17 | 107.28 | 1EDGECMA | BG_P7_GRCTN_RAPHEL_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 105.55 | 110.14 | 1EDGECMA | PN_P1-2_PN-500-010T_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 104.22 | 108.4 | 1EDGECMA | PJM_500_BG_P4_5_CNSTN_L_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 103.32 | 104.4 | 1EDGECMA | BG_P7_NEAST_RPHLRD_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 101.26 | 102.31 | 1EDGECMA | AP_P2-3_PE-500-015_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 100.32 | 102.25 | 1EDGECMA | PJM_500_BG_P4_5_CNSTN_13_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 116.83 | 1STONECA | PJM_500_BG_P1_5013_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 116.83 | 1STONECA | PJM_500_BG_P4_5_CNSTN_M_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.19 | 116.97 | 1STONECA | Base Case | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 106.71 | 108.23 | 1STONECA | BG_P7_CNSTN_NWEST2_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 106.17 | 107.34 | 1STONECA | BG_P7_GRCTN_RAPHEL_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 105.55 | 110.19 | 1STONECA | PN_P1-2_PN-500-010T_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 104.22 | 108.45 | 1STONECA | PJM_500_BG_P4_5_CNSTN_L_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 103.32 | 104.46 | 1STONECA | BG_P7_NEAST_RPHLRD_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 101.26 | 102.36 | 1STONECA | AP_P2-3_PE-500-015_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 100.32 | 102.31 | 1STONECA | PJM_500_BG_P4_5_CNSTN_13_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 106.71 | 108.61 | 26ARMNA MT | BG_P7_CNSTN_NWEST2_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 106.17 | 107.72 | 26ARMNA MT | BG_P7_GRCTN_RAPHEL_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 103.32 | 104.85 | 26ARMNA MT | BG_P7_NEAST_RPHLRD_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 101.26 | 102.72 | 26ARMNA MT | AP_P2-3_PE-500-015_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 100.32 | 102.67 | 26ARMNA MT | PJM_500_BG_P4_5_CNSTN_13_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 117.15 | 28MDLSEXCO | PJM_500_BG_P1_5013_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 117.15 | 28MDLSEXCO | PJM_500_BG_P4_5_CNSTN_M_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.19 | 117.38 | 28MDLSEXCO | Base Case | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 105.55 | 110.51 | 28MDLSEXCO | PN_P1-2_PN-500-010T_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 104.22 | 108.77 | 28MDLSEXCO | PJM_500_BG_P4_5_CNSTN_L_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.19 | 117.36 | 28SIXFLAGS | Base Case | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 116.85 | 3UNCAMP | PJM_500_BG_P1_5013_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 116.85 | 3UNCAMP | PJM_500_BG_P4_5_CNSTN_M_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 105.55 | 110.21 | 3UNCAMP | PN_P1-2_PN-500-010T_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 116.81 | 4E MILL | PJM_500_BG_P1_5013_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 116.81 | 4E MILL | PJM_500_BG_P4_5_CNSTN_M_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.19 | 116.93 | 4E MILL | Base Case | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 106.71 | 108.21 | 4E MILL | BG_P7_CNSTN_NWEST2_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 106.17 | 107.32 | 4E MILL | BG_P7_GRCTN_RAPHEL_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 105.55 | 110.17 | 4E MILL | PN_P1-2_PN-500-010T_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 104.22 | 108.44 | 4E MILL | PJM_500_BG_P4_5_CNSTN_L_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 103.32 | 104.45 | 4E MILL | BG_P7_NEAST_RPHLRD_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 101.26 | 102.35 | 4E MILL | AP_P2-3_PE-500-015_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 100.32 | 102.29 | 4E MILL | PJM_500_BG_P4_5_CNSTN_13_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 116.83 | 6PAPERMILL | PJM_500_BG_P1_5013_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 116.83 | 6PAPERMILL | PJM_500_BG_P4_5_CNSTN_M_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.19 | 116.97 | 6PAPERMILL | Base Case | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 106.71 | 108.23 | 6PAPERMILL | BG_P7_CNSTN_NWEST2_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 106.17 | 107.34 | 6PAPERMILL | BG_P7_GRCTN_RAPHEL_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 105.55 | 110.2 | 6PAPERMILL | PN_P1-2_PN-500-010T_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 104.22 | 108.46 | 6PAPERMILL | PJM_500_BG_P4_5_CNSTN_L_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 103.32 | 104.47 | 6PAPERMILL | BG_P7_NEAST_RPHLRD_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 101.26 | 102.36 | 6PAPERMILL | AP_P2-3_PE-500-015_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 100.32 | 102.31 | 6PAPERMILL | PJM_500_BG_P4_5_CNSTN_13_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 209.21 | 216.47 | AA1-018 | PECO_P4_PEACH245_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 116.64 | AA1-018 | PJM_500_BG_P1_5013_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 116.63 | AA1-018 | PJM_500_BG_P4_5_CNSTN_M_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.19 | 116.67 | AA1-018 | Base Case | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 106.71 | 108.06 | AA1-018 | BG_P7_CNSTN_NWEST2_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 106.17 | 107.17 | AA1-018 | BG_P7_GRCTN_RAPHEL_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 105.55 | 110.01 | AA1-018 | PN_P1-2_PN-500-010T_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 104.22 | 108.27 | AA1-018 | PJM_500_BG_P4_5_CNSTN_L_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 103.32 | 104.3 | AA1-018 | BG_P7_NEAST_RPHLRD_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 101.26 | 102.24 | AA1-018 | AP_P2-3_PE-500-015_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 116.74 | AA1-038 | PJM_500_BG_P1_5013_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 116.74 | AA1-038 | PJM_500_BG_P4_5_CNSTN_M_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.19 | 116.85 | AA1-038 | Base Case | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 106.71 | 108.14 | AA1-038 | BG_P7_CNSTN_NWEST2_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 106.17 | 107.25 | AA1-038 | BG_P7_GRCTN_RAPHEL_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 105.55 | 110.11 | AA1-038 | PN_P1-2_PN-500-010T_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 104.22 | 108.37 | AA1-038 | PJM_500_BG_P4_5_CNSTN_L_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 103.32 | 104.38 | AA1-038 | BG_P7_NEAST_RPHLRD_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 101.26 | 102.29 | AA1-038 | AP_P2-3_PE-500-015_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 100.32 | 102.22 | AA1-038 | PJM_500_BG_P4_5_CNSTN_13_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 117.16 | AA1-060 | PJM_500_BG_P1_5013_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 117.16 | AA1-060 | PJM_500_BG_P4_5_CNSTN_M_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.19 | 117.39 | AA1-060 | Base Case | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 105.55 | 110.52 | AA1-060 | PN_P1-2_PN-500-010T_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 104.22 | 108.78 | AA1-060 | PJM_500_BG_P4_5_CNSTN_L_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 228.49 | 239.93 | AA1-102 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 224.05 | 235.15 | AA1-102 | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 224.05 | 235.14 | AA1-102 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 224.03 | 235.12 | AA1-102 | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 209.21 | 218.46 | AA1-102 | PECO_P4_PEACH245_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 202.97 | 212.99 | AA1-102 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 198.66 | 208.31 | AA1-102 | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 198.66 | 208.31 | AA1-102 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 198.64 | 208.28 | AA1-102 | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 183.92 | 191.85 | AA1-102 | PECO_P4_PEACH245_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 647 | 801 | 122.17 | 123.85 | AA1-102 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 647 | 801 | 117.38 | 119.48 | AA1-102 | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 647 | 801 | 117.38 | 119.48 | AA1-102 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 647 | 801 | 117.37 | 119.46 | AA1-102 | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 463 | 563 | 115.98 | 118.96 | AA1-102 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 463 | 563 | 115.98 | 119.32 | AA1-102 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 463 | 563 | 113.42 | 117.09 | AA1-102 | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 463 | 563 | 113.42 | 116.73 | AA1-102 | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 463 | 563 | 113.37 | 117.03 | AA1-102 | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 463 | 563 | 113.37 | 116.67 | AA1-102 | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 463 | 563 | 113.37 | 117.03 | AA1-102 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 463 | 563 | 113.37 | 116.67 | AA1-102 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 117.91 | AA1-102 | PJM_500_BG_P1_5013_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 117.91 | AA1-102 | PJM_500_BG_P4_5_CNSTN_M_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.19 | 118.45 | AA1-102 | Base Case | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 463 | 578 | 110.56 | 113.28 | AA1-102 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 463 | 578 | 108.07 | 111.1 | AA1-102 | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 463 | 578 | 108.02 | 111.05 | AA1-102 | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 463 | 578 | 108.02 | 111.04 | AA1-102 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 647 | 801 | 108.33 | 110.51 | AA1-102 | PECO_P4_PEACH245_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 106.71 | 109.22 | AA1-102 | BG_P7_CNSTN_NWEST2_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 106.17 | 108.32 | AA1-102 | BG_P7_GRCTN_RAPHEL_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 463 | 578 | 105.24 | 107.25 | AA1-102 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 105.55 | 111.29 | AA1-102 | PN_P1-2_PN-500-010T_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 104.22 | 109.49 | AA1-102 | PJM_500_BG_P4_5_CNSTN_L_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 463 | 578 | 102.74 | 105.08 | AA1-102 | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 463 | 578 | 102.69 | 105.02 | AA1-102 | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 463 | 578 | 102.69 | 105.02 | AA1-102 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 103.32 | 105.44 | AA1-102 | BG_P7_NEAST_RPHLRD_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 220964 | GRACETON | 220999 | BAGLEY2 | 13 | 230 | 232 | 1331 | 1594 | 101.97 | 103.14 | AA1-102 | BG_P4_5_GRCTN_3T_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 101.26 | 103.25 | AA1-102 | AP_P2-3_PE-500-015_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 100.32 | 103.25 | AA1-102 | PJM_500_BG_P4_5_CNSTN_13_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 463 | 563 | 98.5 | 101.6 | AA1-102 | PECO_P4_PEACH245_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 463 | 563 | 98.5 | 101.96 | AA1-102 | PECO_P4_PEACH245_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 220965 | NEAST339 | 220980 | RAPHAEL | 1 | 230 | 232 | 1098 | 1283 | 99.71 | 100.87 | AA1-102 | BG_P4_5_NEAST_17_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 220965 | NEAST339 | 220980 | RAPHAEL | 1 | 230 | 232 | 1098 | 1283 | 99.71 | 100.94 | AA1-102 | BG_P4_5_NEAST_15_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 116.8 | AA1-139 | PJM_500_BG_P1_5013_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 116.8 | AA1-139 | PJM_500_BG_P4_5_CNSTN_M_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.19 | 116.93 | AA1-139 | Base Case | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 106.71 | 108.2 | AA1-139 | BG_P7_CNSTN_NWEST2_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 106.17 | 107.3 | AA1-139 | BG_P7_GRCTN_RAPHEL_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 105.55 | 110.17 | AA1-139 | PN_P1-2_PN-500-010T_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 104.22 | 108.43 | AA1-139 | PJM_500_BG_P4_5_CNSTN_L_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 103.32 | 104.43 | AA1-139 | BG_P7_NEAST_RPHLRD_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 101.26 | 102.33 | AA1-139 | AP_P2-3_PE-500-015_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 100.32 | 102.28 | AA1-139 | PJM_500_BG_P4_5_CNSTN_13_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 116.74 | AA2-088 | PJM_500_BG_P1_5013_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 116.74 | AA2-088 | PJM_500_BG_P4_5_CNSTN_M_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.19 | 116.86 | AA2-088 | Base Case | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 106.71 | 108.13 | AA2-088 | BG_P7_CNSTN_NWEST2_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 106.17 | 107.24 | AA2-088 | BG_P7_GRCTN_RAPHEL_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 105.55 | 110.11 | AA2-088 | PN_P1-2_PN-500-010T_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 104.22 | 108.37 | AA2-088 | PJM_500_BG_P4_5_CNSTN_L_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 103.32 | 104.37 | AA2-088 | BG_P7_NEAST_RPHLRD_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 101.26 | 102.27 | AA2-088 | AP_P2-3_PE-500-015_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 100.32 | 102.22 | AA2-088 | PJM_500_BG_P4_5_CNSTN_13_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 228.49 | 237.82 | AB1-006 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 224.05 | 232.95 | AB1-006 | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 224.05 | 232.95 | AB1-006 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 224.03 | 232.93 | AB1-006 | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 209.21 | 216.28 | AB1-006 | PECO_P4_PEACH245_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 202.97 | 210.93 | AB1-006 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 198.66 | 206.17 | AB1-006 | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 198.66 | 206.17 | AB1-006 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 198.64 | 206.14 | AB1-006 | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 183.92 | 189.72 | AB1-006 | PECO_P4_PEACH245_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 116.53 | AB1-006 | PJM_500_BG_P1_5013_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 116.53 | AB1-006 | PJM_500_BG_P4_5_CNSTN_M_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.19 | 116.53 | AB1-006 | Base Case | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 106.71 | 107.96 | AB1-006 | BG_P7_CNSTN_NWEST2_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 106.17 | 107.07 | AB1-006 | BG_P7_GRCTN_RAPHEL_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 105.55 | 109.91 | AB1-006 | PN_P1-2_PN-500-010T_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 104.22 | 108.17 | AB1-006 | PJM_500_BG_P4_5_CNSTN_L_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 103.32 | 104.2 | AB1-006 | BG_P7_NEAST_RPHLRD_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 101.26 | 102.16 | AB1-006 | AP_P2-3_PE-500-015_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 228.49 | 241 | AB1-056 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 224.05 | 236.26 | AB1-056 | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 224.05 | 236.26 | AB1-056 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 224.03 | 236.23 | AB1-056 | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 209.21 | 219.59 | AB1-056 | PECO_P4_PEACH245_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 202.97 | 214.05 | AB1-056 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 198.66 | 209.41 | AB1-056 | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 198.66 | 209.41 | AB1-056 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 198.64 | 209.38 | AB1-056 | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 183.92 | 192.97 | AB1-056 | PECO_P4_PEACH245_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 647 | 801 | 122.17 | 124.4 | AB1-056 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 463 | 563 | 115.98 | 120.45 | AB1-056 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 463 | 563 | 115.98 | 120.82 | AB1-056 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 207922 | BRIS | 207923 | BRISREAC | RX | 230 | 229 | 506 | 618 | 117.78 | 120.06 | AB1-056 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 207923 | BRISREAC | 208132 | WHEM TR1 | 1 | 230 | 229 | 493 | 618 | 117.78 | 120.06 | AB1-056 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 647 | 801 | 117.38 | 120.07 | AB1-056 | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 647 | 801 | 117.38 | 120.07 | AB1-056 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 647 | 801 | 117.37 | 120.06 | AB1-056 | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 463 | 563 | 113.42 | 118.24 | AB1-056 | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 463 | 563 | 113.42 | 118.61 | AB1-056 | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 463 | 563 | 113.37 | 118.18 | AB1-056 | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 463 | 563 | 113.37 | 118.55 | AB1-056 | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 463 | 563 | 113.37 | 118.18 | AB1-056 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 463 | 563 | 113.37 | 118.55 | AB1-056 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 207922 | BRIS | 207923 | BRISREAC | RX | 230 | 229 | 506 | 618 | 115.13 | 117.73 | AB1-056 | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 207923 | BRISREAC | 208132 | WHEM TR1 | 1 | 230 | 229 | 493 | 618 | 115.13 | 117.73 | AB1-056 | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 207922 | BRIS | 207923 | BRISREAC | RX | 230 | 229 | 506 | 618 | 115.13 | 117.73 | AB1-056 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 207923 | BRISREAC | 208132 | WHEM TR1 | 1 | 230 | 229 | 493 | 618 | 115.13 | 117.73 | AB1-056 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 207922 | BRIS | 207923 | BRISREAC | RX | 230 | 229 | 506 | 618 | 115.12 | 117.72 | AB1-056 | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 207923 | BRISREAC | 208132 | WHEM TR1 | 1 | 230 | 229 | 493 | 618 | 115.12 | 117.72 | AB1-056 | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.19 | 119.59 | AB1-056 | Base Case | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 118.71 | AB1-056 | PJM_500_BG_P1_5013_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 118.71 | AB1-056 | PJM_500_BG_P4_5_CNSTN_M_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 463 | 578 | 110.56 | 114.72 | AB1-056 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 463 | 578 | 108.07 | 112.57 | AB1-056 | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 463 | 578 | 108.02 | 112.51 | AB1-056 | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 463 | 578 | 108.02 | 112.51 | AB1-056 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 709 | 869 | 110.18 | 112.37 | AB1-056 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 709 | 869 | 108.55 | 110.91 | AB1-056 | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 709 | 869 | 108.55 | 110.91 | AB1-056 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 709 | 869 | 108.54 | 110.9 | AB1-056 | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 647 | 801 | 108.33 | 111.11 | AB1-056 | PECO_P4_PEACH245_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 207923 | BRISREAC | 208132 | WHEM TR1 | 1 | 230 | 229 | 493 | 618 | 107.75 | 110.68 | AB1-056 | PECO_P4_PEACH245_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 207922 | BRIS | 207923 | BRISREAC | RX | 230 | 229 | 506 | 618 | 107.75 | 110.68 | AB1-056 | PECO_P4_PEACH245_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 463 | 578 | 105.24 | 108.7 | AB1-056 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 106.71 | 109.91 | AB1-056 | BG_P7_CNSTN_NWEST2_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 106.17 | 109 | AB1-056 | BG_P7_GRCTN_RAPHEL_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208131 | WHEM | 208132 | WHEM TR1 | 1 | 230 | 229 | 547 | 618 | 106.32 | 107.16 | AB1-056 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 105.55 | 112.1 | AB1-056 | PN_P1-2_PN-500-010T_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 559 | 680 | 105.77 | 108.17 | AB1-056 | PEPCO_P4_PP19_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 463 | 578 | 102.74 | 106.55 | AB1-056 | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 463 | 578 | 102.69 | 106.49 | AB1-056 | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 463 | 578 | 102.69 | 106.49 | AB1-056 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 104.22 | 110.26 | AB1-056 | PJM_500_BG_P4_5_CNSTN_L_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 103.32 | 106.13 | AB1-056 | BG_P7_NEAST_RPHLRD_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208131 | WHEM | 208132 | WHEM TR1 | 1 | 230 | 229 | 547 | 618 | 103.73 | 104.89 | AB1-056 | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208131 | WHEM | 208132 | WHEM TR1 | 1 | 230 | 229 | 547 | 618 | 103.73 | 104.89 | AB1-056 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208131 | WHEM | 208132 | WHEM TR1 | 1 | 230 | 229 | 547 | 618 | 103.72 | 104.88 | AB1-056 | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 220964 | GRACETON | 220999 | BAGLEY2 | 13 | 230 | 232 | 1331 | 1594 | 101.97 | 103.47 | AB1-056 | BG_P4_5_GRCTN_3T_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 101.26 | 103.85 | AB1-056 | AP_P2-3_PE-500-015_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 709 | 869 | 101.29 | 103.94 | AB1-056 | PECO_P4_PEACH245_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 100.32 | 103.92 | AB1-056 | PJM_500_BG_P4_5_CNSTN_13_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 463 | 563 | 98.5 | 103.12 | AB1-056 | PECO_P4_PEACH245_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 463 | 563 | 98.5 | 103.49 | AB1-056 | PECO_P4_PEACH245_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 220965 | NEAST339 | 220980 | RAPHAEL | 1 | 230 | 232 | 1098 | 1283 | 99.71 | 101.26 | AB1-056 | BG_P4_5_NEAST_17_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 220965 | NEAST339 | 220980 | RAPHAEL | 1 | 230 | 232 | 1098 | 1283 | 99.71 | 101.33 | AB1-056 | BG_P4_5_NEAST_15_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208078 | SAKR | 1 | 230 | 229 | 647 | 801 | 98.95 | 100.99 | AB1-056 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 220965 | NEAST339 | 220980 | RAPHAEL | 1 | 230 | 232 | 1098 | 1283 | 99.42 | 101.07 | AB1-056 | BG_P1_2315_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 98.57 | 102.77 | AB1-056 | Base Case | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 220979 | NEAST317 | 220980 | RAPHAEL | 1 | 230 | 232 | 1098 | 1283 | 99.26 | 100.85 | AB1-056 | BG_P4_5_NEAST_39_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 220979 | NEAST317 | 220980 | RAPHAEL | 1 | 230 | 232 | 1098 | 1283 | 99.26 | 100.85 | AB1-056 | BG_P4_5_NEAST_37_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213775 | MACDADE | 213925 | RIDLEY | 1 | 230 | 230 | 927 | 927 | 99.07 | 101.43 | AB1-056 | PECO_P1-2_220-23_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 116.83 | AB1-132 | PJM_500_BG_P1_5013_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 116.83 | AB1-132 | PJM_500_BG_P4_5_CNSTN_M_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.19 | 116.97 | AB1-132 | Base Case | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 106.71 | 108.24 | AB1-132 | BG_P7_CNSTN_NWEST2_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 106.17 | 107.34 | AB1-132 | BG_P7_GRCTN_RAPHEL_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 105.55 | 110.2 | AB1-132 | PN_P1-2_PN-500-010T_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 104.22 | 108.46 | AB1-132 | PJM_500_BG_P4_5_CNSTN_L_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 103.32 | 104.47 | AB1-132 | BG_P7_NEAST_RPHLRD_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 101.26 | 102.37 | AB1-132 | AP_P2-3_PE-500-015_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 228.49 | 239.79 | AB2-036 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 224.05 | 235 | AB2-036 | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 224.05 | 235 | AB2-036 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 224.03 | 234.98 | AB2-036 | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 209.21 | 218.32 | AB2-036 | PECO_P4_PEACH245_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 202.97 | 212.86 | AB2-036 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 198.66 | 208.17 | AB2-036 | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 198.66 | 208.17 | AB2-036 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 198.64 | 208.14 | AB2-036 | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 183.92 | 191.71 | AB2-036 | PECO_P4_PEACH245_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 463 | 563 | 115.98 | 119.28 | AB2-036 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 463 | 563 | 115.98 | 118.92 | AB2-036 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 463 | 563 | 113.42 | 117.05 | AB2-036 | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 463 | 563 | 113.42 | 116.69 | AB2-036 | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 463 | 563 | 113.37 | 116.99 | AB2-036 | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 463 | 563 | 113.37 | 116.63 | AB2-036 | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 463 | 563 | 113.37 | 116.99 | AB2-036 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 463 | 563 | 113.37 | 116.63 | AB2-036 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 117.83 | AB2-036 | PJM_500_BG_P1_5013_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 117.83 | AB2-036 | PJM_500_BG_P4_5_CNSTN_M_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.19 | 118.34 | AB2-036 | Base Case | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 463 | 578 | 110.56 | 113.24 | AB2-036 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 463 | 578 | 108.07 | 111.06 | AB2-036 | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 463 | 578 | 108.02 | 111 | AB2-036 | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 463 | 578 | 108.02 | 111 | AB2-036 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 106.71 | 109.15 | AB2-036 | BG_P7_CNSTN_NWEST2_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 106.17 | 108.25 | AB2-036 | BG_P7_GRCTN_RAPHEL_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 463 | 578 | 105.24 | 107.21 | AB2-036 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 105.55 | 111.21 | AB2-036 | PN_P1-2_PN-500-010T_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 104.22 | 109.42 | AB2-036 | PJM_500_BG_P4_5_CNSTN_L_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 463 | 578 | 102.74 | 105.03 | AB2-036 | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 463 | 578 | 102.69 | 104.98 | AB2-036 | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 463 | 578 | 102.69 | 104.98 | AB2-036 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 103.32 | 105.38 | AB2-036 | BG_P7_NEAST_RPHLRD_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 220964 | GRACETON | 220999 | BAGLEY2 | 13 | 230 | 232 | 1331 | 1594 | 101.97 | 103.11 | AB2-036 | BG_P4_5_GRCTN_3T_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 101.26 | 103.19 | AB2-036 | AP_P2-3_PE-500-015_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 100.32 | 103.19 | AB2-036 | PJM_500_BG_P4_5_CNSTN_13_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 463 | 563 | 98.5 | 101.56 | AB2-036 | PECO_P4_PEACH245_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 463 | 563 | 98.5 | 101.92 | AB2-036 | PECO_P4_PEACH245_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 220965 | NEAST339 | 220980 | RAPHAEL | 1 | 230 | 232 | 1098 | 1283 | 99.71 | 100.84 | AB2-036 | BG_P4_5_NEAST_17_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 220965 | NEAST339 | 220980 | RAPHAEL | 1 | 230 | 232 | 1098 | 1283 | 99.71 | 100.91 | AB2-036 | BG_P4_5_NEAST_15_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 228.49 | 240.33 | AB2-037 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 224.05 | 235.56 | AB2-037 | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 224.05 | 235.56 | AB2-037 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 224.03 | 235.53 | AB2-037 | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 209.21 | 218.88 | AB2-037 | PECO_P4_PEACH245_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 202.97 | 213.39 | AB2-037 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 198.66 | 208.72 | AB2-037 | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 198.66 | 208.72 | AB2-037 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 198.64 | 208.69 | AB2-037 | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 183.92 | 192.27 | AB2-037 | PECO_P4_PEACH245_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 647 | 801 | 122.17 | 124.06 | AB2-037 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 463 | 563 | 115.98 | 119.57 | AB2-037 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 463 | 563 | 115.98 | 119.93 | AB2-037 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 647 | 801 | 117.38 | 119.7 | AB2-037 | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 647 | 801 | 117.38 | 119.7 | AB2-037 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 647 | 801 | 117.37 | 119.69 | AB2-037 | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 463 | 563 | 113.42 | 117.71 | AB2-037 | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 463 | 563 | 113.42 | 117.34 | AB2-037 | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 463 | 563 | 113.37 | 117.65 | AB2-037 | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 463 | 563 | 113.37 | 117.29 | AB2-037 | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 463 | 563 | 113.37 | 117.65 | AB2-037 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 463 | 563 | 113.37 | 117.28 | AB2-037 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.19 | 118.89 | AB2-037 | Base Case | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 118.22 | AB2-037 | PJM_500_BG_P1_5013_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 118.22 | AB2-037 | PJM_500_BG_P4_5_CNSTN_M_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 463 | 578 | 110.56 | 113.86 | AB2-037 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 709 | 869 | 110.18 | 112.08 | AB2-037 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 463 | 578 | 108.07 | 111.7 | AB2-037 | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 463 | 578 | 108.02 | 111.64 | AB2-037 | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 463 | 578 | 108.02 | 111.64 | AB2-037 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 709 | 869 | 108.55 | 110.61 | AB2-037 | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 709 | 869 | 108.55 | 110.61 | AB2-037 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 709 | 869 | 108.54 | 110.6 | AB2-037 | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 647 | 801 | 108.33 | 110.74 | AB2-037 | PECO_P4_PEACH245_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 106.71 | 109.48 | AB2-037 | BG_P7_CNSTN_NWEST2_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 463 | 578 | 105.24 | 107.84 | AB2-037 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 106.17 | 108.58 | AB2-037 | BG_P7_GRCTN_RAPHEL_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 105.55 | 111.6 | AB2-037 | PN_P1-2_PN-500-010T_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 104.22 | 109.79 | AB2-037 | PJM_500_BG_P4_5_CNSTN_L_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 463 | 578 | 102.74 | 105.67 | AB2-037 | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 463 | 578 | 102.69 | 105.61 | AB2-037 | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 463 | 578 | 102.69 | 105.61 | AB2-037 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 103.32 | 105.71 | AB2-037 | BG_P7_NEAST_RPHLRD_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 220964 | GRACETON | 220999 | BAGLEY2 | 13 | 230 | 232 | 1331 | 1594 | 101.97 | 103.27 | AB2-037 | BG_P4_5_GRCTN_3T_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 101.26 | 103.48 | AB2-037 | AP_P2-3_PE-500-015_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 709 | 869 | 101.29 | 103.64 | AB2-037 | PECO_P4_PEACH245_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 100.32 | 103.51 | AB2-037 | PJM_500_BG_P4_5_CNSTN_13_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 463 | 563 | 98.5 | 102.22 | AB2-037 | PECO_P4_PEACH245_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 463 | 563 | 98.5 | 102.58 | AB2-037 | PECO_P4_PEACH245_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 220965 | NEAST339 | 220980 | RAPHAEL | 1 | 230 | 232 | 1098 | 1283 | 99.71 | 101.02 | AB2-037 | BG_P4_5_NEAST_17_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 220965 | NEAST339 | 220980 | RAPHAEL | 1 | 230 | 232 | 1098 | 1283 | 99.71 | 101.09 | AB2-037 | BG_P4_5_NEAST_15_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 220965 | NEAST339 | 220980 | RAPHAEL | 1 | 230 | 232 | 1098 | 1283 | 99.42 | 100.83 | AB2-037 | BG_P1_2315_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208078 | SAKR | 1 | 230 | 229 | 647 | 801 | 98.95 | 100.57 | AB2-037 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 116.72 | AB2-040 | PJM_500_BG_P1_5013_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 116.72 | AB2-040 | PJM_500_BG_P4_5_CNSTN_M_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.19 | 116.83 | AB2-040 | Base Case | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 106.71 | 108.11 | AB2-040 | BG_P7_CNSTN_NWEST2_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 106.17 | 107.22 | AB2-040 | BG_P7_GRCTN_RAPHEL_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 105.55 | 110.08 | AB2-040 | PN_P1-2_PN-500-010T_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 104.22 | 108.35 | AB2-040 | PJM_500_BG_P4_5_CNSTN_L_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 103.32 | 104.34 | AB2-040 | BG_P7_NEAST_RPHLRD_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 101.26 | 102.25 | AB2-040 | AP_P2-3_PE-500-015_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 100.32 | 102.19 | AB2-040 | PJM_500_BG_P4_5_CNSTN_13_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 228.49 | 237.6 | AB2-047 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 224.05 | 232.73 | AB2-047 | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 224.05 | 232.73 | AB2-047 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 224.03 | 232.7 | AB2-047 | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 209.21 | 216.06 | AB2-047 | PECO_P4_PEACH245_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 202.97 | 210.73 | AB2-047 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 198.66 | 205.96 | AB2-047 | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 198.66 | 205.96 | AB2-047 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 198.64 | 205.93 | AB2-047 | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 183.92 | 189.51 | AB2-047 | PECO_P4_PEACH245_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 463 | 563 | 115.98 | 116.68 | AB2-047 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 463 | 563 | 115.98 | 116.35 | AB2-047 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 463 | 563 | 113.42 | 114.41 | AB2-047 | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 463 | 563 | 113.42 | 114.07 | AB2-047 | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 463 | 563 | 113.37 | 114.01 | AB2-047 | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 463 | 563 | 113.37 | 114.35 | AB2-047 | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 463 | 563 | 113.37 | 114.35 | AB2-047 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 463 | 563 | 113.37 | 114.01 | AB2-047 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 116.42 | AB2-047 | PJM_500_BG_P1_5013_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 116.42 | AB2-047 | PJM_500_BG_P4_5_CNSTN_M_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.19 | 116.37 | AB2-047 | Base Case | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 463 | 578 | 110.56 | 110.73 | AB2-047 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 463 | 578 | 108.07 | 108.51 | AB2-047 | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 463 | 578 | 108.02 | 108.45 | AB2-047 | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 463 | 578 | 108.02 | 108.45 | AB2-047 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 106.71 | 107.85 | AB2-047 | BG_P7_CNSTN_NWEST2_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 106.17 | 106.96 | AB2-047 | BG_P7_GRCTN_RAPHEL_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 105.55 | 109.8 | AB2-047 | PN_P1-2_PN-500-010T_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 463 | 578 | 105.24 | 104.7 | AB2-047 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 104.22 | 108.06 | AB2-047 | PJM_500_BG_P4_5_CNSTN_L_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 103.32 | 104.09 | AB2-047 | BG_P7_NEAST_RPHLRD_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 463 | 578 | 102.74 | 102.49 | AB2-047 | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 463 | 578 | 102.69 | 102.43 | AB2-047 | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 463 | 578 | 102.69 | 102.43 | AB2-047 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 101.26 | 102.05 | AB2-047 | AP_P2-3_PE-500-015_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 116.82 | AB2-060 | PJM_500_BG_P1_5013_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 116.82 | AB2-060 | PJM_500_BG_P4_5_CNSTN_M_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.19 | 116.95 | AB2-060 | Base Case | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 106.71 | 108.22 | AB2-060 | BG_P7_CNSTN_NWEST2_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 106.17 | 107.33 | AB2-060 | BG_P7_GRCTN_RAPHEL_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 105.55 | 110.19 | AB2-060 | PN_P1-2_PN-500-010T_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 104.22 | 108.45 | AB2-060 | PJM_500_BG_P4_5_CNSTN_L_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 103.32 | 104.46 | AB2-060 | BG_P7_NEAST_RPHLRD_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 101.26 | 102.36 | AB2-060 | AP_P2-3_PE-500-015_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 100.32 | 102.3 | AB2-060 | PJM_500_BG_P4_5_CNSTN_13_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 228.49 | 237.88 | AB2-070 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 224.05 | 233.01 | AB2-070 | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 224.05 | 233.01 | AB2-070 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 224.03 | 232.98 | AB2-070 | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 209.21 | 216.34 | AB2-070 | PECO_P4_PEACH245_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 202.97 | 210.99 | AB2-070 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 198.66 | 206.23 | AB2-070 | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 198.66 | 206.23 | AB2-070 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 198.64 | 206.2 | AB2-070 | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 183.92 | 189.78 | AB2-070 | PECO_P4_PEACH245_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 116.57 | AB2-070 | PJM_500_BG_P1_5013_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 116.56 | AB2-070 | PJM_500_BG_P4_5_CNSTN_M_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.19 | 116.57 | AB2-070 | Base Case | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 106.71 | 107.99 | AB2-070 | BG_P7_CNSTN_NWEST2_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 106.17 | 107.1 | AB2-070 | BG_P7_GRCTN_RAPHEL_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 105.55 | 109.94 | AB2-070 | PN_P1-2_PN-500-010T_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 104.22 | 108.2 | AB2-070 | PJM_500_BG_P4_5_CNSTN_L_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 103.32 | 104.23 | AB2-070 | BG_P7_NEAST_RPHLRD_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 101.26 | 102.18 | AB2-070 | AP_P2-3_PE-500-015_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 116.79 | AB2-085 | PJM_500_BG_P1_5013_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 116.79 | AB2-085 | PJM_500_BG_P4_5_CNSTN_M_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.19 | 116.88 | AB2-085 | Base Case | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 106.71 | 108.21 | AB2-085 | BG_P7_CNSTN_NWEST2_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 106.17 | 107.32 | AB2-085 | BG_P7_GRCTN_RAPHEL_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 105.55 | 110.16 | AB2-085 | PN_P1-2_PN-500-010T_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 104.22 | 108.42 | AB2-085 | PJM_500_BG_P4_5_CNSTN_L_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 103.32 | 104.45 | AB2-085 | BG_P7_NEAST_RPHLRD_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 100.32 | 102.29 | AB2-085 | PJM_500_BG_P4_5_CNSTN_13_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 100.27 | 102.24 | AB2-085 | PJM_500_BG_P4_5_CNSTN_6_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 116.85 | AB2-100 | PJM_500_BG_P1_5013_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 116.85 | AB2-100 | PJM_500_BG_P4_5_CNSTN_M_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.19 | 116.98 | AB2-100 | Base Case | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 105.55 | 110.21 | AB2-100 | PN_P1-2_PN-500-010T_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 104.22 | 108.47 | AB2-100 | PJM_500_BG_P4_5_CNSTN_L_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 117.29 | AB2-133 | PJM_500_BG_P1_5013_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 117.28 | AB2-133 | PJM_500_BG_P4_5_CNSTN_M_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.19 | 117.57 | AB2-133 | Base Case | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 106.71 | 108.67 | AB2-133 | BG_P7_CNSTN_NWEST2_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 106.17 | 107.78 | AB2-133 | BG_P7_GRCTN_RAPHEL_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 105.55 | 110.65 | AB2-133 | PN_P1-2_PN-500-010T_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 104.22 | 108.9 | AB2-133 | PJM_500_BG_P4_5_CNSTN_L_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 103.32 | 104.91 | AB2-133 | BG_P7_NEAST_RPHLRD_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 101.26 | 102.77 | AB2-133 | AP_P2-3_PE-500-015_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 100.32 | 102.73 | AB2-133 | PJM_500_BG_P4_5_CNSTN_13_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 116.69 | AB2-134 | PJM_500_BG_P1_5013_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 116.69 | AB2-134 | PJM_500_BG_P4_5_CNSTN_M_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.19 | 116.8 | AB2-134 | Base Case | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 106.71 | 108.07 | AB2-134 | BG_P7_CNSTN_NWEST2_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 106.17 | 107.18 | AB2-134 | BG_P7_GRCTN_RAPHEL_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 105.55 | 110.06 | AB2-134 | PN_P1-2_PN-500-010T_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 104.22 | 108.32 | AB2-134 | PJM_500_BG_P4_5_CNSTN_L_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 103.32 | 104.31 | AB2-134 | BG_P7_NEAST_RPHLRD_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 101.26 | 102.22 | AB2-134 | AP_P2-3_PE-500-015_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 117.31 | AB2-135 | PJM_500_BG_P1_5013_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 117.3 | AB2-135 | PJM_500_BG_P4_5_CNSTN_M_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.19 | 117.6 | AB2-135 | Base Case | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 106.71 | 108.69 | AB2-135 | BG_P7_CNSTN_NWEST2_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 106.17 | 107.8 | AB2-135 | BG_P7_GRCTN_RAPHEL_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 105.55 | 110.67 | AB2-135 | PN_P1-2_PN-500-010T_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 104.22 | 108.91 | AB2-135 | PJM_500_BG_P4_5_CNSTN_L_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 103.32 | 104.92 | AB2-135 | BG_P7_NEAST_RPHLRD_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 101.26 | 102.78 | AB2-135 | AP_P2-3_PE-500-015_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 100.32 | 102.75 | AB2-135 | PJM_500_BG_P4_5_CNSTN_13_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 117.25 | AB2-136 | PJM_500_BG_P1_5013_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 117.25 | AB2-136 | PJM_500_BG_P4_5_CNSTN_M_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.19 | 117.53 | AB2-136 | Base Case | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 106.71 | 108.64 | AB2-136 | BG_P7_CNSTN_NWEST2_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 106.17 | 107.75 | AB2-136 | BG_P7_GRCTN_RAPHEL_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 105.55 | 110.62 | AB2-136 | PN_P1-2_PN-500-010T_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 104.22 | 108.86 | AB2-136 | PJM_500_BG_P4_5_CNSTN_L_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 103.32 | 104.87 | AB2-136 | BG_P7_NEAST_RPHLRD_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 101.26 | 102.74 | AB2-136 | AP_P2-3_PE-500-015_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 100.32 | 102.7 | AB2-136 | PJM_500_BG_P4_5_CNSTN_13_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 116.84 | AB2-158 | PJM_500_BG_P1_5013_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 116.84 | AB2-158 | PJM_500_BG_P4_5_CNSTN_M_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.19 | 116.98 | AB2-158 | Base Case | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 106.71 | 108.24 | AB2-158 | BG_P7_CNSTN_NWEST2_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 106.17 | 107.34 | AB2-158 | BG_P7_GRCTN_RAPHEL_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 105.55 | 110.2 | AB2-158 | PN_P1-2_PN-500-010T_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 104.22 | 108.47 | AB2-158 | PJM_500_BG_P4_5_CNSTN_L_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 103.32 | 104.47 | AB2-158 | BG_P7_NEAST_RPHLRD_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 101.26 | 102.37 | AB2-158 | AP_P2-3_PE-500-015_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 228.49 | 237.98 | AB2-160 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 224.05 | 233.13 | AB2-160 | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 224.05 | 233.13 | AB2-160 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 224.03 | 233.11 | AB2-160 | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 209.21 | 216.45 | AB2-160 | PECO_P4_PEACH245_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 202.97 | 211.09 | AB2-160 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 198.66 | 206.34 | AB2-160 | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 198.66 | 206.34 | AB2-160 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 198.64 | 206.31 | AB2-160 | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 183.92 | 189.88 | AB2-160 | PECO_P4_PEACH245_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 116.65 | AB2-160 | PJM_500_BG_P1_5013_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 116.65 | AB2-160 | PJM_500_BG_P4_5_CNSTN_M_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.19 | 116.75 | AB2-160 | Base Case | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 106.71 | 108.03 | AB2-160 | BG_P7_CNSTN_NWEST2_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 106.17 | 107.13 | AB2-160 | BG_P7_GRCTN_RAPHEL_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 105.55 | 110.01 | AB2-160 | PN_P1-2_PN-500-010T_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 104.22 | 108.28 | AB2-160 | PJM_500_BG_P4_5_CNSTN_L_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 103.32 | 104.26 | AB2-160 | BG_P7_NEAST_RPHLRD_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 101.26 | 102.17 | AB2-160 | AP_P2-3_PE-500-015_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 117.3 | AB2-172 | PJM_500_BG_P1_5013_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 117.3 | AB2-172 | PJM_500_BG_P4_5_CNSTN_M_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.19 | 117.59 | AB2-172 | Base Case | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 106.71 | 108.68 | AB2-172 | BG_P7_CNSTN_NWEST2_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 106.17 | 107.79 | AB2-172 | BG_P7_GRCTN_RAPHEL_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 105.55 | 110.67 | AB2-172 | PN_P1-2_PN-500-010T_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 104.22 | 108.91 | AB2-172 | PJM_500_BG_P4_5_CNSTN_L_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 103.32 | 104.91 | AB2-172 | BG_P7_NEAST_RPHLRD_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 101.26 | 102.78 | AB2-172 | AP_P2-3_PE-500-015_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 100.32 | 102.74 | AB2-172 | PJM_500_BG_P4_5_CNSTN_13_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 116.84 | AB2-174 | PJM_500_BG_P1_5013_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 116.84 | AB2-174 | PJM_500_BG_P4_5_CNSTN_M_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.19 | 116.98 | AB2-174 | Base Case | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 105.55 | 110.21 | AB2-174 | PN_P1-2_PN-500-010T_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 104.22 | 108.47 | AB2-174 | PJM_500_BG_P4_5_CNSTN_L_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 117.15 | AB2-179 | PJM_500_BG_P1_5013_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 117.15 | AB2-179 | PJM_500_BG_P4_5_CNSTN_M_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.19 | 117.39 | AB2-179 | Base Case | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 105.55 | 110.52 | AB2-179 | PN_P1-2_PN-500-010T_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 104.22 | 108.77 | AB2-179 | PJM_500_BG_P4_5_CNSTN_L_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 228.49 | 237.97 | AB2-190 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 224.05 | 233.12 | AB2-190 | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 224.05 | 233.12 | AB2-190 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 224.03 | 233.09 | AB2-190 | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 209.21 | 216.43 | AB2-190 | PECO_P4_PEACH245_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 202.97 | 211.07 | AB2-190 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 198.66 | 206.33 | AB2-190 | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 198.66 | 206.32 | AB2-190 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 198.64 | 206.3 | AB2-190 | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 183.92 | 189.87 | AB2-190 | PECO_P4_PEACH245_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 116.64 | AB2-190 | PJM_500_BG_P1_5013_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 116.64 | AB2-190 | PJM_500_BG_P4_5_CNSTN_M_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.19 | 116.74 | AB2-190 | Base Case | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 106.71 | 108.02 | AB2-190 | BG_P7_CNSTN_NWEST2_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 106.17 | 107.13 | AB2-190 | BG_P7_GRCTN_RAPHEL_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 105.55 | 110.01 | AB2-190 | PN_P1-2_PN-500-010T_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 104.22 | 108.27 | AB2-190 | PJM_500_BG_P4_5_CNSTN_L_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 103.32 | 104.25 | AB2-190 | BG_P7_NEAST_RPHLRD_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 101.26 | 102.16 | AB2-190 | AP_P2-3_PE-500-015_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 116.77 | AC1-033 | PJM_500_BG_P1_5013_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 116.77 | AC1-033 | PJM_500_BG_P4_5_CNSTN_M_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.19 | 116.85 | AC1-033 | Base Case | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 106.71 | 108.2 | AC1-033 | BG_P7_CNSTN_NWEST2_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 106.17 | 107.3 | AC1-033 | BG_P7_GRCTN_RAPHEL_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 105.55 | 110.14 | AC1-033 | PN_P1-2_PN-500-010T_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 104.22 | 108.4 | AC1-033 | PJM_500_BG_P4_5_CNSTN_L_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 103.32 | 104.43 | AC1-033 | BG_P7_NEAST_RPHLRD_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 101.26 | 102.35 | AC1-033 | AP_P2-3_PE-500-015_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 100.32 | 102.27 | AC1-033 | PJM_500_BG_P4_5_CNSTN_13_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 228.49 | 237.72 | AC1-043 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 224.05 | 232.86 | AC1-043 | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 224.05 | 232.86 | AC1-043 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 224.03 | 232.84 | AC1-043 | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 209.21 | 216.18 | AC1-043 | PECO_P4_PEACH245_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 202.97 | 210.83 | AC1-043 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 198.66 | 206.08 | AC1-043 | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 198.66 | 206.08 | AC1-043 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 198.64 | 206.05 | AC1-043 | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 183.92 | 189.62 | AC1-043 | PECO_P4_PEACH245_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 2 | 230 | 233 | 559 | 680 | 129.8 | 131.54 | AC1-043 | PEPCO_P1_PP1_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 559 | 680 | 129.8 | 131.54 | AC1-043 | PEPCO_P1_PP2_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 2 | 230 | 233 | 559 | 680 | 122.19 | 122.09 | AC1-043 | DVP_P4-2: 514T595_SRT-SW | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 559 | 680 | 122.19 | 122.09 | AC1-043 | DVP_P4-2: 514T595_SRT-SW | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 2 | 230 | 233 | 559 | 680 | 119.41 | 119.12 | AC1-043 | DVP_P4-2: 51482_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 559 | 680 | 119.41 | 119.12 | AC1-043 | DVP_P4-2: 51482_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 2 | 230 | 233 | 559 | 680 | 119.12 | 119.12 | AC1-043 | AP_P1-2_PE-500-407T_SRT-SL | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 559 | 680 | 119.12 | 119.12 | AC1-043 | DVP_P1-2: LN 514_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 559 | 680 | 119.12 | 119.12 | AC1-043 | AP_P1-2_PE-500-407T_SRT-SL | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 2 | 230 | 233 | 559 | 680 | 119.12 | 119.12 | AC1-043 | DVP_P1-2: LN 514_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 116.51 | AC1-043 | PJM_500_BG_P1_5013_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 116.51 | AC1-043 | PJM_500_BG_P4_5_CNSTN_M_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.19 | 116.61 | AC1-043 | Base Case | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 106.71 | 107.87 | AC1-043 | BG_P7_CNSTN_NWEST2_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 106.17 | 106.98 | AC1-043 | BG_P7_GRCTN_RAPHEL_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 105.55 | 109.88 | AC1-043 | PN_P1-2_PN-500-010T_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 104.22 | 108.15 | AC1-043 | PJM_500_BG_P4_5_CNSTN_L_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 103.32 | 104.11 | AC1-043 | BG_P7_NEAST_RPHLRD_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 101.26 | 102.01 | AC1-043 | AP_P2-3_PE-500-015_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 143.84 | 146.96 | AC1-048 | AP_P1-2_WP-138-341T_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 143.74 | 146.85 | AC1-048 | AP_P2-2_PE-138-073_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 143.74 | 146.85 | AC1-048 | AP_P7-1_PE-138-022T_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 143.74 | 146.85 | AC1-048 | ME_P1-2_ME-115-240T_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 143.57 | 146.55 | AC1-048 | AP_P2-3_PE-138-071_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 120.22 | 121.97 | AC1-048 | AP_P1-2_WP-138-341T_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 120.12 | 121.86 | AC1-048 | AP_P2-2_PE-138-073_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 120.12 | 121.86 | AC1-048 | AP_P7-1_PE-138-022T_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 120.12 | 121.86 | AC1-048 | ME_P1-2_ME-115-240T_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 119.95 | 121.56 | AC1-048 | AP_P2-3_PE-138-071_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 235463 | 01TANEY | 1 | 138 | 227/201 | 221 | 268 | 110.75 | 119.04 | AC1-048 | PJM_500_BG_P4_5_CNSTN_J_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 235463 | 01TANEY | 1 | 138 | 227/201 | 221 | 268 | 110.75 | 119.04 | AC1-048 | PJM_500_BG_P1_5011_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 235463 | 01TANEY | 1 | 138 | 227/201 | 221 | 268 | 110.45 | 118.73 | AC1-048 | PEPCO_P4_PP40_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 232 | 282 | 116.72 | 108.39 | AC1-048 | PJM_500_BG_P4_5_CNSTN_J_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 232 | 282 | 116.72 | 108.39 | AC1-048 | PJM_500_BG_P1_5011_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 232 | 282 | 116.46 | 108.13 | AC1-048 | PEPCO_P4_PP40_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 105.55 | 110.21 | AC1-048 | PN_P1-2_PN-500-010T_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 228.49 | 237.82 | AC1-053 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 224.05 | 232.95 | AC1-053 | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 224.05 | 232.95 | AC1-053 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 224.03 | 232.92 | AC1-053 | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 209.21 | 216.28 | AC1-053 | PECO_P4_PEACH245_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 202.97 | 210.93 | AC1-053 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 198.66 | 206.17 | AC1-053 | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 198.66 | 206.17 | AC1-053 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 198.64 | 206.14 | AC1-053 | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 183.92 | 189.72 | AC1-053 | PECO_P4_PEACH245_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 116.53 | AC1-053 | PJM_500_BG_P1_5013_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 116.53 | AC1-053 | PJM_500_BG_P4_5_CNSTN_M_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.19 | 116.53 | AC1-053 | Base Case | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 106.71 | 107.96 | AC1-053 | BG_P7_CNSTN_NWEST2_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 106.17 | 107.07 | AC1-053 | BG_P7_GRCTN_RAPHEL_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 105.55 | 109.91 | AC1-053 | PN_P1-2_PN-500-010T_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 104.22 | 108.17 | AC1-053 | PJM_500_BG_P4_5_CNSTN_L_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 103.32 | 104.2 | AC1-053 | BG_P7_NEAST_RPHLRD_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 101.26 | 102.15 | AC1-053 | AP_P2-3_PE-500-015_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 228.49 | 237.87 | AC1-065 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 224.05 | 233.02 | AC1-065 | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 224.05 | 233.01 | AC1-065 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 224.03 | 232.99 | AC1-065 | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 209.21 | 216.33 | AC1-065 | PECO_P4_PEACH245_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 202.97 | 210.97 | AC1-065 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 198.66 | 206.22 | AC1-065 | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 198.66 | 206.22 | AC1-065 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 198.64 | 206.2 | AC1-065 | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 183.92 | 189.77 | AC1-065 | PECO_P4_PEACH245_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 116.59 | AC1-065 | PJM_500_BG_P1_5013_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 116.59 | AC1-065 | PJM_500_BG_P4_5_CNSTN_M_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.19 | 116.68 | AC1-065 | Base Case | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 106.71 | 107.96 | AC1-065 | BG_P7_CNSTN_NWEST2_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 106.17 | 107.07 | AC1-065 | BG_P7_GRCTN_RAPHEL_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 105.55 | 109.96 | AC1-065 | PN_P1-2_PN-500-010T_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 104.22 | 108.22 | AC1-065 | PJM_500_BG_P4_5_CNSTN_L_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 103.32 | 104.2 | AC1-065 | BG_P7_NEAST_RPHLRD_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 101.26 | 102.11 | AC1-065 | AP_P2-3_PE-500-015_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 116.84 | AC1-075 and AC1-080 | PJM_500_BG_P1_5013_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 116.84 | AC1-075 and AC1-080 | PJM_500_BG_P4_5_CNSTN_M_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.19 | 116.98 | AC1-075 and AC1-080 | Base Case | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 105.55 | 110.21 | AC1-075 and AC1-080 | PN_P1-2_PN-500-010T_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 104.22 | 108.47 | AC1-075 and AC1-080 | PJM_500_BG_P4_5_CNSTN_L_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 116.81 | AC1-076 | PJM_500_BG_P1_5013_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 116.81 | AC1-076 | PJM_500_BG_P4_5_CNSTN_M_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.19 | 116.95 | AC1-076 | Base Case | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 106.71 | 108.2 | AC1-076 | BG_P7_CNSTN_NWEST2_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 106.17 | 107.31 | AC1-076 | BG_P7_GRCTN_RAPHEL_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 105.55 | 110.17 | AC1-076 | PN_P1-2_PN-500-010T_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 104.22 | 108.44 | AC1-076 | PJM_500_BG_P4_5_CNSTN_L_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 103.32 | 104.44 | AC1-076 | BG_P7_NEAST_RPHLRD_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 101.26 | 102.34 | AC1-076 | AP_P2-3_PE-500-015_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 100.32 | 102.28 | AC1-076 | PJM_500_BG_P4_5_CNSTN_13_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 116.7 | AC1-078 | PJM_500_BG_P1_5013_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 116.7 | AC1-078 | PJM_500_BG_P4_5_CNSTN_M_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.19 | 116.76 | AC1-078 | Base Case | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 106.71 | 108.14 | AC1-078 | BG_P7_CNSTN_NWEST2_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 106.17 | 107.24 | AC1-078 | BG_P7_GRCTN_RAPHEL_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 105.55 | 110.07 | AC1-078 | PN_P1-2_PN-500-010T_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 104.22 | 108.34 | AC1-078 | PJM_500_BG_P4_5_CNSTN_L_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 103.32 | 104.37 | AC1-078 | BG_P7_NEAST_RPHLRD_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 101.26 | 102.3 | AC1-078 | AP_P2-3_PE-500-015_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 100.32 | 102.22 | AC1-078 | PJM_500_BG_P4_5_CNSTN_13_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.19 | 116.98 | AC1-082 | Base Case | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 116.74 | AC1-083 | PJM_500_BG_P1_5013_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 116.74 | AC1-083 | PJM_500_BG_P4_5_CNSTN_M_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.19 | 116.84 | AC1-083 | Base Case | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 106.71 | 108.15 | AC1-083 | BG_P7_CNSTN_NWEST2_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 106.17 | 107.25 | AC1-083 | BG_P7_GRCTN_RAPHEL_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 105.55 | 110.11 | AC1-083 | PN_P1-2_PN-500-010T_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 104.22 | 108.37 | AC1-083 | PJM_500_BG_P4_5_CNSTN_L_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 103.32 | 104.38 | AC1-083 | BG_P7_NEAST_RPHLRD_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 101.26 | 102.3 | AC1-083 | AP_P2-3_PE-500-015_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 100.32 | 102.23 | AC1-083 | PJM_500_BG_P4_5_CNSTN_13_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 228.49 | 237.48 | AC1-085 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 224.05 | 232.6 | AC1-085 | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 224.05 | 232.6 | AC1-085 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 224.03 | 232.58 | AC1-085 | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 209.21 | 215.94 | AC1-085 | PECO_P4_PEACH245_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 202.97 | 210.61 | AC1-085 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 198.66 | 205.83 | AC1-085 | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 198.66 | 205.83 | AC1-085 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 198.64 | 205.81 | AC1-085 | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 183.92 | 189.4 | AC1-085 | PECO_P4_PEACH245_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 647 | 801 | 117.38 | 118.15 | AC1-085 | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 647 | 801 | 117.38 | 118.15 | AC1-085 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 647 | 801 | 117.37 | 118.14 | AC1-085 | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 463 | 563 | 115.98 | 116.57 | AC1-085 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 463 | 563 | 115.98 | 116.24 | AC1-085 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 463 | 563 | 113.42 | 113.96 | AC1-085 | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 463 | 563 | 113.42 | 114.3 | AC1-085 | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 463 | 563 | 113.37 | 114.24 | AC1-085 | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 463 | 563 | 113.37 | 113.9 | AC1-085 | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 463 | 563 | 113.37 | 113.9 | AC1-085 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 463 | 563 | 113.37 | 114.24 | AC1-085 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 116.35 | AC1-085 | PJM_500_BG_P1_5013_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 116.35 | AC1-085 | PJM_500_BG_P4_5_CNSTN_M_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.19 | 116.27 | AC1-085 | Base Case | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 463 | 578 | 110.56 | 110.62 | AC1-085 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 463 | 578 | 108.07 | 108.4 | AC1-085 | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 463 | 578 | 108.02 | 108.34 | AC1-085 | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 463 | 578 | 108.02 | 108.34 | AC1-085 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 106.71 | 107.79 | AC1-085 | BG_P7_CNSTN_NWEST2_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 106.17 | 106.9 | AC1-085 | BG_P7_GRCTN_RAPHEL_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 105.55 | 109.73 | AC1-085 | PN_P1-2_PN-500-010T_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 463 | 578 | 105.24 | 104.6 | AC1-085 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 104.22 | 107.99 | AC1-085 | PJM_500_BG_P4_5_CNSTN_L_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 103.32 | 104.02 | AC1-085 | BG_P7_NEAST_RPHLRD_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 463 | 578 | 102.74 | 102.38 | AC1-085 | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 463 | 578 | 102.69 | 102.32 | AC1-085 | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 463 | 578 | 102.69 | 102.32 | AC1-085 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 101.26 | 102 | AC1-085 | AP_P2-3_PE-500-015_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 116.75 | AC1-086 | PJM_500_BG_P1_5013_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 116.75 | AC1-086 | PJM_500_BG_P4_5_CNSTN_M_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.19 | 116.87 | AC1-086 | Base Case | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 106.71 | 108.15 | AC1-086 | BG_P7_CNSTN_NWEST2_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 106.17 | 107.25 | AC1-086 | BG_P7_GRCTN_RAPHEL_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 105.55 | 110.12 | AC1-086 | PN_P1-2_PN-500-010T_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 104.22 | 108.38 | AC1-086 | PJM_500_BG_P4_5_CNSTN_L_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 103.32 | 104.38 | AC1-086 | BG_P7_NEAST_RPHLRD_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 101.26 | 102.29 | AC1-086 | AP_P2-3_PE-500-015_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 100.32 | 102.23 | AC1-086 | PJM_500_BG_P4_5_CNSTN_13_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 116.75 | AC1-089 | PJM_500_BG_P1_5013_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 116.75 | AC1-089 | PJM_500_BG_P4_5_CNSTN_M_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.19 | 116.83 | AC1-089 | Base Case | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 106.71 | 108.18 | AC1-089 | BG_P7_CNSTN_NWEST2_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 106.17 | 107.29 | AC1-089 | BG_P7_GRCTN_RAPHEL_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 105.55 | 110.12 | AC1-089 | PN_P1-2_PN-500-010T_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 104.22 | 108.38 | AC1-089 | PJM_500_BG_P4_5_CNSTN_L_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 103.32 | 104.41 | AC1-089 | BG_P7_NEAST_RPHLRD_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 101.26 | 102.34 | AC1-089 | AP_P2-3_PE-500-015_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 100.32 | 102.26 | AC1-089 | PJM_500_BG_P4_5_CNSTN_13_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 116.71 | AC1-120 | PJM_500_BG_P1_5013_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 116.71 | AC1-120 | PJM_500_BG_P4_5_CNSTN_M_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.19 | 116.83 | AC1-120 | Base Case | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 106.71 | 108.09 | AC1-120 | BG_P7_CNSTN_NWEST2_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 106.17 | 107.2 | AC1-120 | BG_P7_GRCTN_RAPHEL_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 105.55 | 110.08 | AC1-120 | PN_P1-2_PN-500-010T_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 104.22 | 108.34 | AC1-120 | PJM_500_BG_P4_5_CNSTN_L_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 103.32 | 104.33 | AC1-120 | BG_P7_NEAST_RPHLRD_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 101.26 | 102.23 | AC1-120 | AP_P2-3_PE-500-015_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 100.32 | 102.18 | AC1-120 | PJM_500_BG_P4_5_CNSTN_13_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 228.49 | 235.32 | AC1-158 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 224.05 | 230.42 | AC1-158 | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 224.05 | 230.42 | AC1-158 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 224.03 | 230.4 | AC1-158 | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 209.21 | 213.77 | AC1-158 | PECO_P4_PEACH245_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 202.97 | 208.51 | AC1-158 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 198.66 | 203.71 | AC1-158 | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 198.66 | 203.71 | AC1-158 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 198.64 | 203.68 | AC1-158 | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 183.92 | 187.28 | AC1-158 | PECO_P4_PEACH245_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 166.62 | 166.8 | AC1-158 | Base Case | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 130.65 | 129.35 | AC1-158 | Base Case | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 559 | 680 | 129.8 | 129.88 | AC1-158 | PEPCO_P1_PP2_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 2 | 230 | 233 | 559 | 680 | 129.8 | 129.88 | AC1-158 | PEPCO_P1_PP1_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 647 | 801 | 122.17 | 121.44 | AC1-158 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 559 | 680 | 122.19 | 120.11 | AC1-158 | DVP_P4-2: 514T595_SRT-SW | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 2 | 230 | 233 | 559 | 680 | 122.19 | 120.11 | AC1-158 | DVP_P4-2: 514T595_SRT-SW | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 559 | 680 | 119.41 | 117.09 | AC1-158 | DVP_P4-2: 51482_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 2 | 230 | 233 | 559 | 680 | 119.41 | 117.09 | AC1-158 | DVP_P4-2: 51482_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 207923 | BRISREAC | 208132 | WHEM TR1 | 1 | 230 | 229 | 493 | 618 | 117.78 | 117.68 | AC1-158 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 207922 | BRIS | 207923 | BRISREAC | RX | 230 | 229 | 506 | 618 | 117.78 | 117.68 | AC1-158 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 559 | 680 | 119.12 | 117.09 | AC1-158 | AP_P1-2_PE-500-407T_SRT-SL | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 2 | 230 | 233 | 559 | 680 | 119.12 | 117.09 | AC1-158 | AP_P1-2_PE-500-407T_SRT-SL | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 2 | 230 | 233 | 559 | 680 | 119.12 | 117.09 | AC1-158 | DVP_P1-2: LN 514_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 559 | 680 | 119.12 | 117.09 | AC1-158 | DVP_P1-2: LN 514_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 647 | 801 | 117.38 | 116.96 | AC1-158 | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 647 | 801 | 117.38 | 116.96 | AC1-158 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 647 | 801 | 117.37 | 116.95 | AC1-158 | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 232 | 282 | 116.72 | 115.11 | AC1-158 | PJM_500_BG_P4_5_CNSTN_J_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 232 | 282 | 116.72 | 115.11 | AC1-158 | PJM_500_BG_P1_5011_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 232 | 282 | 116.46 | 114.85 | AC1-158 | PEPCO_P4_PP40_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 463 | 563 | 115.98 | 115.32 | AC1-158 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 463 | 563 | 115.98 | 115 | AC1-158 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 207923 | BRISREAC | 208132 | WHEM TR1 | 1 | 230 | 229 | 493 | 618 | 115.13 | 115.27 | AC1-158 | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 207922 | BRIS | 207923 | BRISREAC | RX | 230 | 229 | 506 | 618 | 115.13 | 115.27 | AC1-158 | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 207923 | BRISREAC | 208132 | WHEM TR1 | 1 | 230 | 229 | 493 | 618 | 115.13 | 115.27 | AC1-158 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 207922 | BRIS | 207923 | BRISREAC | RX | 230 | 229 | 506 | 618 | 115.13 | 115.27 | AC1-158 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 207923 | BRISREAC | 208132 | WHEM TR1 | 1 | 230 | 229 | 493 | 618 | 115.12 | 115.26 | AC1-158 | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 207922 | BRIS | 207923 | BRISREAC | RX | 230 | 229 | 506 | 618 | 115.12 | 115.26 | AC1-158 | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 463 | 563 | 113.42 | 113.04 | AC1-158 | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 463 | 563 | 113.42 | 112.71 | AC1-158 | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 463 | 563 | 113.37 | 112.98 | AC1-158 | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 463 | 563 | 113.37 | 112.65 | AC1-158 | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 463 | 563 | 113.37 | 112.98 | AC1-158 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 463 | 563 | 113.37 | 112.65 | AC1-158 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 115.32 | AC1-158 | PJM_500_BG_P1_5013_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 115.32 | AC1-158 | PJM_500_BG_P4_5_CNSTN_M_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.19 | 115.2 | AC1-158 | Base Case | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 709 | 869 | 110.18 | 110.01 | AC1-158 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200009 | JUNI | 208004 | JUNI | 2 | 500/230 | 229 | 776 | 1010 | 108.85 | 110.16 | AC1-158 | PL_10_P42_000140_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 235463 | 01TANEY | 1 | 138 | 227/201 | 221 | 268 | 110.75 | 109.93 | AC1-158 | PJM_500_BG_P4_5_CNSTN_J_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 235463 | 01TANEY | 1 | 138 | 227/201 | 221 | 268 | 110.75 | 109.93 | AC1-158 | PJM_500_BG_P1_5011_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 463 | 578 | 110.56 | 109.41 | AC1-158 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 235463 | 01TANEY | 1 | 138 | 227/201 | 221 | 268 | 110.45 | 109.62 | AC1-158 | PEPCO_P4_PP40_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 709 | 869 | 108.55 | 108.51 | AC1-158 | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 709 | 869 | 108.55 | 108.51 | AC1-158 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 709 | 869 | 108.54 | 108.5 | AC1-158 | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 647 | 801 | 108.33 | 108.01 | AC1-158 | PECO_P4_PEACH245_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 207923 | BRISREAC | 208132 | WHEM TR1 | 1 | 230 | 229 | 493 | 618 | 107.75 | 108.22 | AC1-158 | PECO_P4_PEACH245_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 207922 | BRIS | 207923 | BRISREAC | RX | 230 | 229 | 506 | 618 | 107.75 | 108.22 | AC1-158 | PECO_P4_PEACH245_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 463 | 578 | 108.07 | 107.18 | AC1-158 | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 463 | 578 | 108.02 | 107.13 | AC1-158 | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 463 | 578 | 108.02 | 107.13 | AC1-158 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208131 | WHEM | 208132 | WHEM TR1 | 1 | 230 | 229 | 547 | 618 | 106.32 | 104.88 | AC1-158 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 106.71 | 106.52 | AC1-158 | BG_P7_CNSTN_NWEST2_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 106.17 | 105.63 | AC1-158 | BG_P7_GRCTN_RAPHEL_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 105.55 | 108.7 | AC1-158 | PN_P1-2_PN-500-010T_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 463 | 578 | 105.24 | 103.39 | AC1-158 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 104.22 | 106.99 | AC1-158 | PJM_500_BG_P4_5_CNSTN_L_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208131 | WHEM | 208132 | WHEM TR1 | 1 | 230 | 229 | 547 | 618 | 103.73 | 102.53 | AC1-158 | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208131 | WHEM | 208132 | WHEM TR1 | 1 | 230 | 229 | 547 | 618 | 103.73 | 102.53 | AC1-158 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208131 | WHEM | 208132 | WHEM TR1 | 1 | 230 | 229 | 547 | 618 | 103.72 | 102.52 | AC1-158 | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 103.32 | 102.76 | AC1-158 | BG_P7_NEAST_RPHLRD_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 220964 | GRACETON | 220999 | BAGLEY2 | 13 | 230 | 232 | 1331 | 1594 | 101.97 | 101.76 | AC1-158 | BG_P4_5_GRCTN_3T_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204538 | 27STRABAN | 204544 | 27LINCOLN | 1 | 115 | 227 | 257 | 313 | 102.73 | 100.13 | AC1-158 | PJM_500_BG_P4_5_CNSTN_J_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204538 | 27STRABAN | 204544 | 27LINCOLN | 1 | 115 | 227 | 257 | 313 | 102.73 | 100.13 | AC1-158 | PJM_500_BG_P1_5011_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 463 | 578 | 102.74 | 101.16 | AC1-158 | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 463 | 578 | 102.69 | 101.11 | AC1-158 | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 463 | 578 | 102.69 | 101.11 | AC1-158 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204538 | 27STRABAN | 204544 | 27LINCOLN | 1 | 115 | 227 | 257 | 313 | 102.46 | 99.87 | AC1-158 | PEPCO_P4_PP40_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 228.49 | 237.98 | AC1-161 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 224.05 | 233.13 | AC1-161 | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 224.05 | 233.13 | AC1-161 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 224.03 | 233.1 | AC1-161 | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 209.21 | 216.44 | AC1-161 | PECO_P4_PEACH245_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 202.97 | 211.08 | AC1-161 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 198.66 | 206.33 | AC1-161 | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 198.66 | 206.33 | AC1-161 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 198.64 | 206.3 | AC1-161 | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 183.92 | 189.87 | AC1-161 | PECO_P4_PEACH245_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 116.64 | AC1-161 | PJM_500_BG_P1_5013_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 116.64 | AC1-161 | PJM_500_BG_P4_5_CNSTN_M_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.19 | 116.74 | AC1-161 | Base Case | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 106.71 | 108.02 | AC1-161 | BG_P7_CNSTN_NWEST2_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 106.17 | 107.13 | AC1-161 | BG_P7_GRCTN_RAPHEL_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 105.55 | 110.01 | AC1-161 | PN_P1-2_PN-500-010T_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 104.22 | 108.27 | AC1-161 | PJM_500_BG_P4_5_CNSTN_L_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 103.32 | 104.26 | AC1-161 | BG_P7_NEAST_RPHLRD_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 101.26 | 102.17 | AC1-161 | AP_P2-3_PE-500-015_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 228.49 | 237.41 | AC1-164 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 224.05 | 232.55 | AC1-164 | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 224.05 | 232.55 | AC1-164 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 224.03 | 232.52 | AC1-164 | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 209.21 | 215.87 | AC1-164 | PECO_P4_PEACH245_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 202.97 | 210.53 | AC1-164 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 198.66 | 205.78 | AC1-164 | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 198.66 | 205.77 | AC1-164 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 198.64 | 205.75 | AC1-164 | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 183.92 | 189.32 | AC1-164 | PECO_P4_PEACH245_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 166.62 | 168.21 | AC1-164 | Base Case | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 130.65 | 130.63 | AC1-164 | Base Case | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 559 | 680 | 129.8 | 131.48 | AC1-164 | PEPCO_P1_PP2_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 2 | 230 | 233 | 559 | 680 | 129.8 | 131.48 | AC1-164 | PEPCO_P1_PP1_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 647 | 801 | 122.17 | 122.54 | AC1-164 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 2 | 230 | 233 | 559 | 680 | 122.19 | 122.03 | AC1-164 | DVP_P4-2: 514T595_SRT-SW | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 559 | 680 | 122.19 | 122.03 | AC1-164 | DVP_P4-2: 514T595_SRT-SW | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 559 | 680 | 119.41 | 119.06 | AC1-164 | DVP_P4-2: 51482_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 2 | 230 | 233 | 559 | 680 | 119.41 | 119.06 | AC1-164 | DVP_P4-2: 51482_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 559 | 680 | 119.12 | 119.06 | AC1-164 | DVP_P1-2: LN 514_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 559 | 680 | 119.12 | 119.06 | AC1-164 | AP_P1-2_PE-500-407T_SRT-SL | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 2 | 230 | 233 | 559 | 680 | 119.12 | 119.06 | AC1-164 | AP_P1-2_PE-500-407T_SRT-SL | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 2 | 230 | 233 | 559 | 680 | 119.12 | 119.06 | AC1-164 | DVP_P1-2: LN 514_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 647 | 801 | 117.38 | 118.1 | AC1-164 | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 647 | 801 | 117.38 | 118.1 | AC1-164 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 647 | 801 | 117.37 | 118.08 | AC1-164 | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 463 | 563 | 115.98 | 116.72 | AC1-164 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 463 | 563 | 115.98 | 116.38 | AC1-164 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 463 | 563 | 113.42 | 114.45 | AC1-164 | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 463 | 563 | 113.42 | 114.11 | AC1-164 | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 463 | 563 | 113.37 | 114.05 | AC1-164 | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 463 | 563 | 113.37 | 114.39 | AC1-164 | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 463 | 563 | 113.37 | 114.39 | AC1-164 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 463 | 563 | 113.37 | 114.05 | AC1-164 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 116.36 | AC1-164 | PJM_500_BG_P1_5013_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 116.36 | AC1-164 | PJM_500_BG_P4_5_CNSTN_M_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.19 | 116.41 | AC1-164 | Base Case | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 463 | 578 | 110.56 | 110.76 | AC1-164 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 647 | 801 | 108.33 | 109.13 | AC1-164 | PECO_P4_PEACH245_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 463 | 578 | 108.07 | 108.55 | AC1-164 | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 463 | 578 | 108.02 | 108.49 | AC1-164 | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 463 | 578 | 108.02 | 108.49 | AC1-164 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 106.71 | 107.71 | AC1-164 | BG_P7_CNSTN_NWEST2_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 106.17 | 106.82 | AC1-164 | BG_P7_GRCTN_RAPHEL_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 105.55 | 109.73 | AC1-164 | PN_P1-2_PN-500-010T_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 463 | 578 | 105.24 | 104.74 | AC1-164 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 104.22 | 108 | AC1-164 | PJM_500_BG_P4_5_CNSTN_L_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 103.32 | 103.94 | AC1-164 | BG_P7_NEAST_RPHLRD_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 463 | 578 | 102.74 | 102.53 | AC1-164 | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 463 | 578 | 102.69 | 102.47 | AC1-164 | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 463 | 578 | 102.69 | 102.47 | AC1-164 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 220964 | GRACETON | 220999 | BAGLEY2 | 13 | 230 | 232 | 1331 | 1594 | 101.97 | 102.38 | AC1-164 | BG_P4_5_GRCTN_3T_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 101.26 | 101.86 | AC1-164 | AP_P2-3_PE-500-015_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 116.82 | AC1-168 | PJM_500_BG_P1_5013_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 116.82 | AC1-168 | PJM_500_BG_P4_5_CNSTN_M_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.19 | 116.92 | AC1-168 | Base Case | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 105.55 | 110.19 | AC1-168 | PN_P1-2_PN-500-010T_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 104.22 | 108.45 | AC1-168 | PJM_500_BG_P4_5_CNSTN_L_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 116.83 | AC1-173 GEN | PJM_500_BG_P1_5013_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 116.83 | AC1-173 GEN | PJM_500_BG_P4_5_CNSTN_M_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.19 | 116.94 | AC1-173 GEN | Base Case | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 105.55 | 110.2 | AC1-173 GEN | PN_P1-2_PN-500-010T_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 104.22 | 108.46 | AC1-173 GEN | PJM_500_BG_P4_5_CNSTN_L_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 116.84 | AC1-174 | PJM_500_BG_P1_5013_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 116.84 | AC1-174 | PJM_500_BG_P4_5_CNSTN_M_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.19 | 116.94 | AC1-174 | Base Case | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 105.55 | 110.2 | AC1-174 | PN_P1-2_PN-500-010T_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 104.22 | 108.46 | AC1-174 | PJM_500_BG_P4_5_CNSTN_L_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 116.84 | AC1-175 | PJM_500_BG_P1_5013_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 116.84 | AC1-175 | PJM_500_BG_P4_5_CNSTN_M_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.19 | 116.94 | AC1-175 | Base Case | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 105.55 | 110.2 | AC1-175 | PN_P1-2_PN-500-010T_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 104.22 | 108.46 | AC1-175 | PJM_500_BG_P4_5_CNSTN_L_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 116.68 | AC1-189 | PJM_500_BG_P1_5013_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 116.68 | AC1-189 | PJM_500_BG_P4_5_CNSTN_M_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.19 | 116.78 | AC1-189 | Base Case | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 106.71 | 108.07 | AC1-189 | BG_P7_CNSTN_NWEST2_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 106.17 | 107.18 | AC1-189 | BG_P7_GRCTN_RAPHEL_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 105.55 | 110.05 | AC1-189 | PN_P1-2_PN-500-010T_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 104.22 | 108.31 | AC1-189 | PJM_500_BG_P4_5_CNSTN_L_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 103.32 | 104.3 | AC1-189 | BG_P7_NEAST_RPHLRD_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 101.26 | 102.22 | AC1-189 | AP_P2-3_PE-500-015_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 228.49 | 237.96 | AC1-191 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 224.05 | 233.11 | AC1-191 | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 224.05 | 233.11 | AC1-191 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 224.03 | 233.08 | AC1-191 | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 209.21 | 216.42 | AC1-191 | PECO_P4_PEACH245_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 202.97 | 211.06 | AC1-191 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 198.66 | 206.32 | AC1-191 | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 198.66 | 206.31 | AC1-191 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 198.64 | 206.29 | AC1-191 | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 183.92 | 189.86 | AC1-191 | PECO_P4_PEACH245_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 116.64 | AC1-191 | PJM_500_BG_P1_5013_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 116.63 | AC1-191 | PJM_500_BG_P4_5_CNSTN_M_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.19 | 116.74 | AC1-191 | Base Case | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 106.71 | 108.01 | AC1-191 | BG_P7_CNSTN_NWEST2_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 106.17 | 107.12 | AC1-191 | BG_P7_GRCTN_RAPHEL_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 105.55 | 110 | AC1-191 | PN_P1-2_PN-500-010T_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 104.22 | 108.27 | AC1-191 | PJM_500_BG_P4_5_CNSTN_L_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 103.32 | 104.25 | AC1-191 | BG_P7_NEAST_RPHLRD_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 101.26 | 102.15 | AC1-191 | AP_P2-3_PE-500-015_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 116.8 | AC1-194 | PJM_500_BG_P1_5013_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 116.8 | AC1-194 | PJM_500_BG_P4_5_CNSTN_M_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.19 | 116.89 | AC1-194 | Base Case | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 106.71 | 108.23 | AC1-194 | BG_P7_CNSTN_NWEST2_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 106.17 | 107.33 | AC1-194 | BG_P7_GRCTN_RAPHEL_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 105.55 | 110.17 | AC1-194 | PN_P1-2_PN-500-010T_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 104.22 | 108.43 | AC1-194 | PJM_500_BG_P4_5_CNSTN_L_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 103.32 | 104.46 | AC1-194 | BG_P7_NEAST_RPHLRD_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 100.32 | 102.31 | AC1-194 | PJM_500_BG_P4_5_CNSTN_13_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 100.27 | 102.25 | AC1-194 | PJM_500_BG_P4_5_CNSTN_6_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 116.83 | AC1-214 | PJM_500_BG_P1_5013_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 116.83 | AC1-214 | PJM_500_BG_P4_5_CNSTN_M_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.19 | 116.93 | AC1-214 | Base Case | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 105.55 | 110.19 | AC1-214 | PN_P1-2_PN-500-010T_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 104.22 | 108.46 | AC1-214 | PJM_500_BG_P4_5_CNSTN_L_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 116.81 | AC1-216 | PJM_500_BG_P1_5013_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 116.81 | AC1-216 | PJM_500_BG_P4_5_CNSTN_M_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.19 | 116.94 | AC1-216 | Base Case | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 106.71 | 108.21 | AC1-216 | BG_P7_CNSTN_NWEST2_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 106.17 | 107.31 | AC1-216 | BG_P7_GRCTN_RAPHEL_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 105.55 | 110.17 | AC1-216 | PN_P1-2_PN-500-010T_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 104.22 | 108.44 | AC1-216 | PJM_500_BG_P4_5_CNSTN_L_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 103.32 | 104.44 | AC1-216 | BG_P7_NEAST_RPHLRD_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 101.26 | 102.34 | AC1-216 | AP_P2-3_PE-500-015_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 100.32 | 102.29 | AC1-216 | PJM_500_BG_P4_5_CNSTN_13_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 116.75 | AC1-221 | PJM_500_BG_P1_5013_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 116.75 | AC1-221 | PJM_500_BG_P4_5_CNSTN_M_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.19 | 116.86 | AC1-221 | Base Case | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 106.71 | 108.15 | AC1-221 | BG_P7_CNSTN_NWEST2_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 106.17 | 107.26 | AC1-221 | BG_P7_GRCTN_RAPHEL_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 105.55 | 110.12 | AC1-221 | PN_P1-2_PN-500-010T_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 104.22 | 108.38 | AC1-221 | PJM_500_BG_P4_5_CNSTN_L_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 103.32 | 104.39 | AC1-221 | BG_P7_NEAST_RPHLRD_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 101.26 | 102.3 | AC1-221 | AP_P2-3_PE-500-015_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 100.32 | 102.23 | AC1-221 | PJM_500_BG_P4_5_CNSTN_13_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 116.75 | AC1-222 | PJM_500_BG_P1_5013_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 116.75 | AC1-222 | PJM_500_BG_P4_5_CNSTN_M_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.19 | 116.86 | AC1-222 | Base Case | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 106.71 | 108.15 | AC1-222 | BG_P7_CNSTN_NWEST2_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 106.17 | 107.25 | AC1-222 | BG_P7_GRCTN_RAPHEL_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 105.55 | 110.12 | AC1-222 | PN_P1-2_PN-500-010T_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 104.22 | 108.38 | AC1-222 | PJM_500_BG_P4_5_CNSTN_L_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 103.32 | 104.38 | AC1-222 | BG_P7_NEAST_RPHLRD_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 101.26 | 102.29 | AC1-222 | AP_P2-3_PE-500-015_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 100.32 | 102.23 | AC1-222 | PJM_500_BG_P4_5_CNSTN_13_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 228.49 | 237.77 | AC2-012 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 224.05 | 232.92 | AC2-012 | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 224.05 | 232.92 | AC2-012 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 224.03 | 232.89 | AC2-012 | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 209.21 | 216.23 | AC2-012 | PECO_P4_PEACH245_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 202.97 | 210.88 | AC2-012 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 198.66 | 206.13 | AC2-012 | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 198.66 | 206.13 | AC2-012 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 198.64 | 206.1 | AC2-012 | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 183.92 | 189.67 | AC2-012 | PECO_P4_PEACH245_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 116.54 | AC2-012 | PJM_500_BG_P1_5013_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 116.54 | AC2-012 | PJM_500_BG_P4_5_CNSTN_M_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.19 | 116.62 | AC2-012 | Base Case | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 106.71 | 107.91 | AC2-012 | BG_P7_CNSTN_NWEST2_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 106.17 | 107.02 | AC2-012 | BG_P7_GRCTN_RAPHEL_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 105.55 | 109.91 | AC2-012 | PN_P1-2_PN-500-010T_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 104.22 | 108.17 | AC2-012 | PJM_500_BG_P4_5_CNSTN_L_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 103.32 | 104.14 | AC2-012 | BG_P7_NEAST_RPHLRD_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 101.26 | 102.06 | AC2-012 | AP_P2-3_PE-500-015_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 117.19 | AC2-023 | PJM_500_BG_P1_5013_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 117.19 | AC2-023 | PJM_500_BG_P4_5_CNSTN_M_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.19 | 117.44 | AC2-023 | Base Case | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 105.55 | 110.56 | AC2-023 | PN_P1-2_PN-500-010T_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 104.22 | 108.8 | AC2-023 | PJM_500_BG_P4_5_CNSTN_L_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 116.82 | AC2-059 | PJM_500_BG_P1_5013_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 116.82 | AC2-059 | PJM_500_BG_P4_5_CNSTN_M_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.19 | 116.92 | AC2-059 | Base Case | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 105.55 | 110.19 | AC2-059 | PN_P1-2_PN-500-010T_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 104.22 | 108.45 | AC2-059 | PJM_500_BG_P4_5_CNSTN_L_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 116.83 | AC2-061 | PJM_500_BG_P1_5013_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 116.83 | AC2-061 | PJM_500_BG_P4_5_CNSTN_M_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.19 | 116.94 | AC2-061 | Base Case | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 105.55 | 110.2 | AC2-061 | PN_P1-2_PN-500-010T_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 104.22 | 108.46 | AC2-061 | PJM_500_BG_P4_5_CNSTN_L_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 228.49 | 237.96 | AC2-079 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 224.05 | 233.11 | AC2-079 | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 224.05 | 233.1 | AC2-079 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 224.03 | 233.08 | AC2-079 | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 209.21 | 216.42 | AC2-079 | PECO_P4_PEACH245_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 202.97 | 211.06 | AC2-079 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 198.66 | 206.31 | AC2-079 | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 198.66 | 206.31 | AC2-079 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 198.64 | 206.28 | AC2-079 | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 183.92 | 189.85 | AC2-079 | PECO_P4_PEACH245_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 116.63 | AC2-079 | PJM_500_BG_P1_5013_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 116.63 | AC2-079 | PJM_500_BG_P4_5_CNSTN_M_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.19 | 116.73 | AC2-079 | Base Case | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 106.71 | 108.01 | AC2-079 | BG_P7_CNSTN_NWEST2_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 106.17 | 107.12 | AC2-079 | BG_P7_GRCTN_RAPHEL_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 105.55 | 110 | AC2-079 | PN_P1-2_PN-500-010T_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 104.22 | 108.26 | AC2-079 | PJM_500_BG_P4_5_CNSTN_L_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 103.32 | 104.25 | AC2-079 | BG_P7_NEAST_RPHLRD_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 101.26 | 102.16 | AC2-079 | AP_P2-3_PE-500-015_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 228.49 | 237.74 | AC2-103 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 224.05 | 232.86 | AC2-103 | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 224.05 | 232.86 | AC2-103 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 224.03 | 232.84 | AC2-103 | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 209.21 | 216.2 | AC2-103 | PECO_P4_PEACH245_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 202.97 | 210.86 | AC2-103 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 198.66 | 206.09 | AC2-103 | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 198.66 | 206.09 | AC2-103 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 198.64 | 206.06 | AC2-103 | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 183.92 | 189.65 | AC2-103 | PECO_P4_PEACH245_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 463 | 563 | 115.98 | 116.68 | AC2-103 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 463 | 563 | 115.98 | 116.35 | AC2-103 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 463 | 563 | 113.42 | 114.41 | AC2-103 | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 463 | 563 | 113.42 | 114.07 | AC2-103 | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 463 | 563 | 113.37 | 114.01 | AC2-103 | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 463 | 563 | 113.37 | 114.35 | AC2-103 | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 463 | 563 | 113.37 | 114.35 | AC2-103 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 463 | 563 | 113.37 | 114.01 | AC2-103 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 116.47 | AC2-103 | PJM_500_BG_P1_5013_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 116.47 | AC2-103 | PJM_500_BG_P4_5_CNSTN_M_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.19 | 116.37 | AC2-103 | Base Case | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 463 | 578 | 110.56 | 110.73 | AC2-103 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 463 | 578 | 108.07 | 108.51 | AC2-103 | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 463 | 578 | 108.02 | 108.45 | AC2-103 | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 463 | 578 | 108.02 | 108.45 | AC2-103 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 106.71 | 107.95 | AC2-103 | BG_P7_CNSTN_NWEST2_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 106.17 | 107.06 | AC2-103 | BG_P7_GRCTN_RAPHEL_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 105.55 | 109.85 | AC2-103 | PN_P1-2_PN-500-010T_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 463 | 578 | 105.24 | 104.7 | AC2-103 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 104.22 | 108.11 | AC2-103 | PJM_500_BG_P4_5_CNSTN_L_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 103.32 | 104.19 | AC2-103 | BG_P7_NEAST_RPHLRD_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 463 | 578 | 102.74 | 102.49 | AC2-103 | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 463 | 578 | 102.69 | 102.43 | AC2-103 | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 463 | 578 | 102.69 | 102.43 | AC2-103 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 101.26 | 102.17 | AC2-103 | AP_P2-3_PE-500-015_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.19 | 116.98 | AC2-111 | Base Case | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 116.8 | AC2-112 | PJM_500_BG_P1_5013_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 116.8 | AC2-112 | PJM_500_BG_P4_5_CNSTN_M_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.19 | 116.92 | AC2-112 | Base Case | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 106.71 | 108.2 | AC2-112 | BG_P7_CNSTN_NWEST2_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 106.17 | 107.31 | AC2-112 | BG_P7_GRCTN_RAPHEL_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 105.55 | 110.16 | AC2-112 | PN_P1-2_PN-500-010T_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 104.22 | 108.42 | AC2-112 | PJM_500_BG_P4_5_CNSTN_L_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 103.32 | 104.43 | AC2-112 | BG_P7_NEAST_RPHLRD_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 101.26 | 102.34 | AC2-112 | AP_P2-3_PE-500-015_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 100.32 | 102.28 | AC2-112 | PJM_500_BG_P4_5_CNSTN_13_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 228.49 | 237.83 | AC2-165 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 224.05 | 232.97 | AC2-165 | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 224.05 | 232.97 | AC2-165 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 224.03 | 232.95 | AC2-165 | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 209.21 | 216.29 | AC2-165 | PECO_P4_PEACH245_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 202.97 | 210.93 | AC2-165 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 198.66 | 206.18 | AC2-165 | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 198.66 | 206.18 | AC2-165 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 198.64 | 206.16 | AC2-165 | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 183.92 | 189.73 | AC2-165 | PECO_P4_PEACH245_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 116.57 | AC2-165 | PJM_500_BG_P1_5013_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 116.57 | AC2-165 | PJM_500_BG_P4_5_CNSTN_M_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.19 | 116.65 | AC2-165 | Base Case | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 106.71 | 107.94 | AC2-165 | BG_P7_CNSTN_NWEST2_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 106.17 | 107.05 | AC2-165 | BG_P7_GRCTN_RAPHEL_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 105.55 | 109.93 | AC2-165 | PN_P1-2_PN-500-010T_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 104.22 | 108.2 | AC2-165 | PJM_500_BG_P4_5_CNSTN_L_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 103.32 | 104.17 | AC2-165 | BG_P7_NEAST_RPHLRD_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 101.26 | 102.09 | AC2-165 | AP_P2-3_PE-500-015_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 116.71 | AC2-176 | PJM_500_BG_P1_5013_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 116.71 | AC2-176 | PJM_500_BG_P4_5_CNSTN_M_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.19 | 116.76 | AC2-176 | Base Case | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 106.71 | 108.14 | AC2-176 | BG_P7_CNSTN_NWEST2_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 106.17 | 107.24 | AC2-176 | BG_P7_GRCTN_RAPHEL_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 105.55 | 110.08 | AC2-176 | PN_P1-2_PN-500-010T_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 104.22 | 108.34 | AC2-176 | PJM_500_BG_P4_5_CNSTN_L_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 103.32 | 104.37 | AC2-176 | BG_P7_NEAST_RPHLRD_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 101.26 | 102.3 | AC2-176 | AP_P2-3_PE-500-015_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 100.32 | 102.22 | AC2-176 | PJM_500_BG_P4_5_CNSTN_13_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 117.22 | AC2-185 | PJM_500_BG_P1_5013_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 117.22 | AC2-185 | PJM_500_BG_P4_5_CNSTN_M_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.19 | 117.48 | AC2-185 | Base Case | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 106.71 | 108.61 | AC2-185 | BG_P7_CNSTN_NWEST2_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 106.17 | 107.72 | AC2-185 | BG_P7_GRCTN_RAPHEL_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 105.55 | 110.59 | AC2-185 | PN_P1-2_PN-500-010T_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 104.22 | 108.83 | AC2-185 | PJM_500_BG_P4_5_CNSTN_L_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 103.32 | 104.85 | AC2-185 | BG_P7_NEAST_RPHLRD_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 100.32 | 102.67 | AC2-185 | PJM_500_BG_P4_5_CNSTN_13_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 100.27 | 102.62 | AC2-185 | PJM_500_BG_P4_5_CNSTN_6_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 228.49 | 239.64 | AD1-020 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 224.05 | 234.81 | AD1-020 | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 224.05 | 234.81 | AD1-020 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 224.03 | 234.79 | AD1-020 | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 209.21 | 218.13 | AD1-020 | PECO_P4_PEACH245_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 202.97 | 212.71 | AD1-020 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 198.66 | 207.98 | AD1-020 | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 198.66 | 207.98 | AD1-020 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 198.64 | 207.95 | AD1-020 | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 183.92 | 191.52 | AD1-020 | PECO_P4_PEACH245_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 166.62 | 170.28 | AD1-020 | Base Case | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 130.65 | 132.54 | AD1-020 | Base Case | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 647 | 801 | 122.17 | 124.39 | AD1-020 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 232 | 282 | 116.72 | 121.75 | AD1-020 | PJM_500_BG_P4_5_CNSTN_J_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 232 | 282 | 116.72 | 121.75 | AD1-020 | PJM_500_BG_P1_5011_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 232 | 282 | 116.46 | 121.49 | AD1-020 | PEPCO_P4_PP40_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 647 | 801 | 117.38 | 119.99 | AD1-020 | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 647 | 801 | 117.38 | 119.99 | AD1-020 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 647 | 801 | 117.37 | 119.97 | AD1-020 | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 208070 | SAHA12TP | 1 | 230 | 229 | 513 | 628 | 116.86 | 118.17 | AD1-020 | BG_P7_GRCTN_CNSTN_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 235463 | 01TANEY | 1 | 138 | 227/201 | 221 | 268 | 110.75 | 116.34 | AD1-020 | PJM_500_BG_P4_5_CNSTN_J_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 235463 | 01TANEY | 1 | 138 | 227/201 | 221 | 268 | 110.75 | 116.34 | AD1-020 | PJM_500_BG_P1_5011_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 235463 | 01TANEY | 1 | 138 | 227/201 | 221 | 268 | 110.45 | 116.04 | AD1-020 | PEPCO_P4_PP40_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 709 | 869 | 110.18 | 110.77 | AD1-020 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 647 | 801 | 108.33 | 111.02 | AD1-020 | PECO_P4_PEACH245_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200009 | JUNI | 208004 | JUNI | 2 | 500/230 | 229 | 776 | 1010 | 108.85 | 110.1 | AD1-020 | PL_10_P42_000140_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 709 | 869 | 108.55 | 109.28 | AD1-020 | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 709 | 869 | 108.55 | 109.28 | AD1-020 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 709 | 869 | 108.54 | 109.27 | AD1-020 | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 106.71 | 108.7 | AD1-020 | BG_P7_CNSTN_NWEST2_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 106.17 | 107.81 | AD1-020 | BG_P7_GRCTN_RAPHEL_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204538 | 27STRABAN | 204544 | 27LINCOLN | 1 | 115 | 227 | 257 | 313 | 102.73 | 105.68 | AD1-020 | PJM_500_BG_P4_5_CNSTN_J_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204538 | 27STRABAN | 204544 | 27LINCOLN | 1 | 115 | 227 | 257 | 313 | 102.73 | 105.68 | AD1-020 | PJM_500_BG_P1_5011_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204538 | 27STRABAN | 204544 | 27LINCOLN | 1 | 115 | 227 | 257 | 313 | 102.46 | 105.42 | AD1-020 | PEPCO_P4_PP40_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 105.55 | 110.19 | AD1-020 | PN_P1-2_PN-500-010T_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 204550 | 27ORRTANNA | 1 | 115 | 227 | 133 | 160 | 101.04 | 106.12 | AD1-020 | ME_P1-2_ME-115-068_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 232 | 282 | 99.33 | 106.54 | AD1-020 | Base Case | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 103.32 | 104.94 | AD1-020 | BG_P7_NEAST_RPHLRD_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208070 | SAHA12TP | 1 | 230 | 229 | 721 | 814 | 102.85 | 103.39 | AD1-020 | BG_P7_GRCTN_CNSTN_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 232 | 282 | 97.98 | 103.55 | AD1-020 | AP_P2-3_PE-500-015_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 204550 | 27ORRTANNA | 1 | 115 | 227 | 133 | 160 | 97.89 | 103.01 | AD1-020 | ME_P2-3_ME-115-013B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 101.26 | 102.77 | AD1-020 | AP_P2-3_PE-500-015_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 232 | 282 | 96.88 | 103.43 | AD1-020 | PJM_500_BG_P4_5_CNSTN_M_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 204550 | 27ORRTANNA | 1 | 115 | 227 | 133 | 160 | 97.47 | 102.6 | AD1-020 | ME_P2-3_ME-115-013A_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 709 | 869 | 101.29 | 102.3 | AD1-020 | PECO_P4_PEACH245_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 100.32 | 102.73 | AD1-020 | PJM_500_BG_P4_5_CNSTN_13_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204529 | 27GERMANTN | 204538 | 27STRABAN | 1 | 115 | 227 | 257 | 313 | 96.79 | 99.29 | AD1-020 | PJM_500_BG_P4_5_CNSTN_J_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204529 | 27GERMANTN | 204538 | 27STRABAN | 1 | 115 | 227 | 257 | 313 | 96.79 | 99.29 | AD1-020 | PJM_500_BG_P1_5011_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204529 | 27GERMANTN | 204538 | 27STRABAN | 1 | 115 | 227 | 257 | 313 | 96.52 | 99.02 | AD1-020 | PEPCO_P4_PP40_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 116.74 | AD1-025 | PJM_500_BG_P1_5013_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 116.74 | AD1-025 | PJM_500_BG_P4_5_CNSTN_M_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.19 | 116.86 | AD1-025 | Base Case | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 106.71 | 108.13 | AD1-025 | BG_P7_CNSTN_NWEST2_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 106.17 | 107.24 | AD1-025 | BG_P7_GRCTN_RAPHEL_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 105.55 | 110.11 | AD1-025 | PN_P1-2_PN-500-010T_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 104.22 | 108.37 | AD1-025 | PJM_500_BG_P4_5_CNSTN_L_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 103.32 | 104.37 | AD1-025 | BG_P7_NEAST_RPHLRD_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 101.26 | 102.27 | AD1-025 | AP_P2-3_PE-500-015_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 100.32 | 102.21 | AD1-025 | PJM_500_BG_P4_5_CNSTN_13_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 116.71 | AD1-070 | PJM_500_BG_P1_5013_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 116.71 | AD1-070 | PJM_500_BG_P4_5_CNSTN_M_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.19 | 116.76 | AD1-070 | Base Case | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 106.71 | 108.15 | AD1-070 | BG_P7_CNSTN_NWEST2_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 106.17 | 107.26 | AD1-070 | BG_P7_GRCTN_RAPHEL_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 105.55 | 110.08 | AD1-070 | PN_P1-2_PN-500-010T_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 104.22 | 108.35 | AD1-070 | PJM_500_BG_P4_5_CNSTN_L_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 103.32 | 104.39 | AD1-070 | BG_P7_NEAST_RPHLRD_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 101.26 | 102.32 | AD1-070 | AP_P2-3_PE-500-015_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 100.32 | 102.24 | AD1-070 | PJM_500_BG_P4_5_CNSTN_13_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 228.49 | 237.88 | AD1-083 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 224.05 | 233.02 | AD1-083 | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 224.05 | 233.02 | AD1-083 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 224.03 | 232.99 | AD1-083 | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 209.21 | 216.34 | AD1-083 | PECO_P4_PEACH245_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 202.97 | 210.98 | AD1-083 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 198.66 | 206.23 | AD1-083 | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 198.66 | 206.23 | AD1-083 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 198.64 | 206.2 | AD1-083 | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 183.92 | 189.77 | AD1-083 | PECO_P4_PEACH245_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 116.58 | AD1-083 | PJM_500_BG_P1_5013_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 116.58 | AD1-083 | PJM_500_BG_P4_5_CNSTN_M_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.19 | 116.66 | AD1-083 | Base Case | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 106.71 | 107.96 | AD1-083 | BG_P7_CNSTN_NWEST2_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 106.17 | 107.06 | AD1-083 | BG_P7_GRCTN_RAPHEL_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 105.55 | 109.95 | AD1-083 | PN_P1-2_PN-500-010T_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 104.22 | 108.21 | AD1-083 | PJM_500_BG_P4_5_CNSTN_L_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 103.32 | 104.19 | AD1-083 | BG_P7_NEAST_RPHLRD_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 101.26 | 102.1 | AD1-083 | AP_P2-3_PE-500-015_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 116.84 | AD1-088 | PJM_500_BG_P1_5013_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 116.84 | AD1-088 | PJM_500_BG_P4_5_CNSTN_M_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.19 | 116.98 | AD1-088 | Base Case | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 105.55 | 110.21 | AD1-088 | PN_P1-2_PN-500-010T_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 104.22 | 108.47 | AD1-088 | PJM_500_BG_P4_5_CNSTN_L_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 116.85 | AD1-105 | PJM_500_BG_P1_5013_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 116.85 | AD1-105 | PJM_500_BG_P4_5_CNSTN_M_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 105.55 | 110.21 | AD1-105 | PN_P1-2_PN-500-010T_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 104.22 | 108.47 | AD1-105 | PJM_500_BG_P4_5_CNSTN_L_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 116.76 | AD1-115 | PJM_500_BG_P1_5013_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 116.75 | AD1-115 | PJM_500_BG_P4_5_CNSTN_M_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.19 | 116.89 | AD1-115 | Base Case | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 106.71 | 108.14 | AD1-115 | BG_P7_CNSTN_NWEST2_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 106.17 | 107.25 | AD1-115 | BG_P7_GRCTN_RAPHEL_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 105.55 | 110.12 | AD1-115 | PN_P1-2_PN-500-010T_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 104.22 | 108.38 | AD1-115 | PJM_500_BG_P4_5_CNSTN_L_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 103.32 | 104.38 | AD1-115 | BG_P7_NEAST_RPHLRD_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 101.26 | 102.28 | AD1-115 | AP_P2-3_PE-500-015_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 100.32 | 102.23 | AD1-115 | PJM_500_BG_P4_5_CNSTN_13_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 116.77 | AD1-125 | PJM_500_BG_P1_5013_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 116.77 | AD1-125 | PJM_500_BG_P4_5_CNSTN_M_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.19 | 116.87 | AD1-125 | Base Case | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 106.71 | 108.18 | AD1-125 | BG_P7_CNSTN_NWEST2_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 106.17 | 107.29 | AD1-125 | BG_P7_GRCTN_RAPHEL_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 105.55 | 110.14 | AD1-125 | PN_P1-2_PN-500-010T_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 104.22 | 108.4 | AD1-125 | PJM_500_BG_P4_5_CNSTN_L_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 103.32 | 104.42 | AD1-125 | BG_P7_NEAST_RPHLRD_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 101.26 | 102.34 | AD1-125 | AP_P2-3_PE-500-015_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 100.32 | 102.26 | AD1-125 | PJM_500_BG_P4_5_CNSTN_13_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 116.76 | AD1-128 | PJM_500_BG_P1_5013_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 116.76 | AD1-128 | PJM_500_BG_P4_5_CNSTN_M_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.19 | 116.83 | AD1-128 | Base Case | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 106.71 | 108.18 | AD1-128 | BG_P7_CNSTN_NWEST2_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 106.17 | 107.29 | AD1-128 | BG_P7_GRCTN_RAPHEL_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 105.55 | 110.13 | AD1-128 | PN_P1-2_PN-500-010T_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 104.22 | 108.39 | AD1-128 | PJM_500_BG_P4_5_CNSTN_L_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 103.32 | 104.42 | AD1-128 | BG_P7_NEAST_RPHLRD_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 101.26 | 102.34 | AD1-128 | AP_P2-3_PE-500-015_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 100.32 | 102.26 | AD1-128 | PJM_500_BG_P4_5_CNSTN_13_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 228.49 | 237.86 | AD1-140 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 224.05 | 233 | AD1-140 | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 224.05 | 233 | AD1-140 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 224.03 | 232.97 | AD1-140 | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 209.21 | 216.32 | AD1-140 | PECO_P4_PEACH245_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 202.97 | 210.98 | AD1-140 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 198.66 | 206.21 | AD1-140 | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 198.66 | 206.21 | AD1-140 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 198.64 | 206.19 | AD1-140 | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 183.92 | 189.77 | AD1-140 | PECO_P4_PEACH245_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 116.55 | AD1-140 | PJM_500_BG_P1_5013_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 116.55 | AD1-140 | PJM_500_BG_P4_5_CNSTN_M_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.19 | 116.55 | AD1-140 | Base Case | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 106.71 | 107.99 | AD1-140 | BG_P7_CNSTN_NWEST2_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 106.17 | 107.1 | AD1-140 | BG_P7_GRCTN_RAPHEL_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 105.55 | 109.93 | AD1-140 | PN_P1-2_PN-500-010T_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 104.22 | 108.19 | AD1-140 | PJM_500_BG_P4_5_CNSTN_L_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 103.32 | 104.22 | AD1-140 | BG_P7_NEAST_RPHLRD_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 101.26 | 102.18 | AD1-140 | AP_P2-3_PE-500-015_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 228.49 | 239.82 | AD1-143 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 224.05 | 235.02 | AD1-143 | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 224.05 | 235.02 | AD1-143 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 224.03 | 234.99 | AD1-143 | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 209.21 | 218.33 | AD1-143 | PECO_P4_PEACH245_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 202.97 | 212.89 | AD1-143 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 198.66 | 208.18 | AD1-143 | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 198.66 | 208.18 | AD1-143 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 198.64 | 208.16 | AD1-143 | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 183.92 | 191.73 | AD1-143 | PECO_P4_PEACH245_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 166.62 | 169.81 | AD1-143 | Base Case | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 211061 | PSPA TP1 | 211068 | AD1-143 TAP | 1 | 69 | 229 | 68 | 91 | 0.04 | 131.86 | AD1-143 | Base Case | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 130.65 | 132.1 | AD1-143 | Base Case | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 117.49 | AD1-143 | PJM_500_BG_P1_5013_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 117.49 | AD1-143 | PJM_500_BG_P4_5_CNSTN_M_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.19 | 117.84 | AD1-143 | Base Case | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 106.71 | 108.93 | AD1-143 | BG_P7_CNSTN_NWEST2_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 106.17 | 108.03 | AD1-143 | BG_P7_GRCTN_RAPHEL_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 105.55 | 110.85 | AD1-143 | PN_P1-2_PN-500-010T_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 104.22 | 109.1 | AD1-143 | PJM_500_BG_P4_5_CNSTN_L_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 103.32 | 105.16 | AD1-143 | BG_P7_NEAST_RPHLRD_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 211061 | PSPA TP1 | 211698 | LNFD | 1 | 69 | 229 | 96 | 125 | 8.97 | 101.28 | AD1-143 | Base Case | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 101.26 | 102.99 | AD1-143 | AP_P2-3_PE-500-015_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 100.32 | 102.97 | AD1-143 | PJM_500_BG_P4_5_CNSTN_13_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 116.84 | AD1-155 | PJM_500_BG_P1_5013_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 116.84 | AD1-155 | PJM_500_BG_P4_5_CNSTN_M_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.19 | 116.98 | AD1-155 | Base Case | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 106.71 | 108.24 | AD1-155 | BG_P7_CNSTN_NWEST2_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 106.17 | 107.35 | AD1-155 | BG_P7_GRCTN_RAPHEL_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 105.55 | 110.2 | AD1-155 | PN_P1-2_PN-500-010T_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 104.22 | 108.46 | AD1-155 | PJM_500_BG_P4_5_CNSTN_L_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 103.32 | 104.47 | AD1-155 | BG_P7_NEAST_RPHLRD_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 101.26 | 102.37 | AD1-155 | AP_P2-3_PE-500-015_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 228.49 | 237.68 | AD2-016 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 224.05 | 232.81 | AD2-016 | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 224.05 | 232.81 | AD2-016 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 224.03 | 232.78 | AD2-016 | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 209.21 | 216.14 | AD2-016 | PECO_P4_PEACH245_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 202.97 | 210.8 | AD2-016 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 198.66 | 206.03 | AD2-016 | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 198.66 | 206.03 | AD2-016 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 198.64 | 206 | AD2-016 | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 183.92 | 189.59 | AD2-016 | PECO_P4_PEACH245_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 116.46 | AD2-016 | PJM_500_BG_P1_5013_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 116.46 | AD2-016 | PJM_500_BG_P4_5_CNSTN_M_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.19 | 116.41 | AD2-016 | Base Case | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 106.71 | 107.89 | AD2-016 | BG_P7_CNSTN_NWEST2_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 106.17 | 107 | AD2-016 | BG_P7_GRCTN_RAPHEL_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 105.55 | 109.83 | AD2-016 | PN_P1-2_PN-500-010T_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 104.22 | 108.1 | AD2-016 | PJM_500_BG_P4_5_CNSTN_L_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 103.32 | 104.13 | AD2-016 | BG_P7_NEAST_RPHLRD_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 101.26 | 102.1 | AD2-016 | AP_P2-3_PE-500-015_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 203981 | AD2-062_POI | 235188 | 01GREENE | 1 | 138 | 226/201 | 221 | 268 | 95.88 | 103.9 | AD2-062 | PJM_500_BG_P4_5_CNSTN_J_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 203981 | AD2-062_POI | 235188 | 01GREENE | 1 | 138 | 226/201 | 221 | 268 | 95.88 | 103.9 | AD2-062 | PJM_500_BG_P1_5011_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 203981 | AD2-062_POI | 235188 | 01GREENE | 1 | 138 | 226/201 | 221 | 268 | 95.51 | 103.51 | AD2-062 | PEPCO_P4_PP40_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 116.74 | AD2-072 | PJM_500_BG_P1_5013_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 116.74 | AD2-072 | PJM_500_BG_P4_5_CNSTN_M_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.19 | 116.81 | AD2-072 | Base Case | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 106.71 | 108.16 | AD2-072 | BG_P7_CNSTN_NWEST2_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 106.17 | 107.27 | AD2-072 | BG_P7_GRCTN_RAPHEL_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 105.55 | 110.11 | AD2-072 | PN_P1-2_PN-500-010T_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 104.22 | 108.37 | AD2-072 | PJM_500_BG_P4_5_CNSTN_L_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 103.32 | 104.4 | AD2-072 | BG_P7_NEAST_RPHLRD_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 101.26 | 102.32 | AD2-072 | AP_P2-3_PE-500-015_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 100.32 | 102.24 | AD2-072 | PJM_500_BG_P4_5_CNSTN_13_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 116.75 | AD2-074 | PJM_500_BG_P1_5013_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 116.75 | AD2-074 | PJM_500_BG_P4_5_CNSTN_M_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.19 | 116.87 | AD2-074 | Base Case | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 106.71 | 108.14 | AD2-074 | BG_P7_CNSTN_NWEST2_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 106.17 | 107.25 | AD2-074 | BG_P7_GRCTN_RAPHEL_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 105.55 | 110.12 | AD2-074 | PN_P1-2_PN-500-010T_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 104.22 | 108.38 | AD2-074 | PJM_500_BG_P4_5_CNSTN_L_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 103.32 | 104.38 | AD2-074 | BG_P7_NEAST_RPHLRD_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 101.26 | 102.28 | AD2-074 | AP_P2-3_PE-500-015_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 100.32 | 102.22 | AD2-074 | PJM_500_BG_P4_5_CNSTN_13_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 117.27 | AD2-076 | PJM_500_BG_P1_5013_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 117.27 | AD2-076 | PJM_500_BG_P4_5_CNSTN_M_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.19 | 117.55 | AD2-076 | Base Case | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 106.71 | 108.66 | AD2-076 | BG_P7_CNSTN_NWEST2_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 106.17 | 107.76 | AD2-076 | BG_P7_GRCTN_RAPHEL_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 105.55 | 110.64 | AD2-076 | PN_P1-2_PN-500-010T_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 104.22 | 108.88 | AD2-076 | PJM_500_BG_P4_5_CNSTN_L_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 103.32 | 104.89 | AD2-076 | BG_P7_NEAST_RPHLRD_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 101.26 | 102.75 | AD2-076 | AP_P2-3_PE-500-015_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 100.32 | 102.72 | AD2-076 | PJM_500_BG_P4_5_CNSTN_13_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 116.77 | AD2-093 | PJM_500_BG_P1_5013_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 116.77 | AD2-093 | PJM_500_BG_P4_5_CNSTN_M_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.19 | 116.85 | AD2-093 | Base Case | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 106.71 | 108.2 | AD2-093 | BG_P7_CNSTN_NWEST2_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 106.17 | 107.31 | AD2-093 | BG_P7_GRCTN_RAPHEL_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 105.55 | 110.14 | AD2-093 | PN_P1-2_PN-500-010T_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 104.22 | 108.4 | AD2-093 | PJM_500_BG_P4_5_CNSTN_L_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 103.32 | 104.43 | AD2-093 | BG_P7_NEAST_RPHLRD_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 101.26 | 102.36 | AD2-093 | AP_P2-3_PE-500-015_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 100.32 | 102.28 | AD2-093 | PJM_500_BG_P4_5_CNSTN_13_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200009 | JUNI | 208004 | JUNI | 2 | 500/230 | 229 | 776 | 1010 | 108.85 | 109.99 | AD2-133 | PL_10_P42_000140_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 116.72 | AD2-134 | PJM_500_BG_P1_5013_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 116.72 | AD2-134 | PJM_500_BG_P4_5_CNSTN_M_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.19 | 116.78 | AD2-134 | Base Case | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 106.71 | 108.15 | AD2-134 | BG_P7_CNSTN_NWEST2_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 106.17 | 107.25 | AD2-134 | BG_P7_GRCTN_RAPHEL_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 105.55 | 110.09 | AD2-134 | PN_P1-2_PN-500-010T_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 104.22 | 108.35 | AD2-134 | PJM_500_BG_P4_5_CNSTN_L_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 103.32 | 104.38 | AD2-134 | BG_P7_NEAST_RPHLRD_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 101.26 | 102.31 | AD2-134 | AP_P2-3_PE-500-015_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 100.32 | 102.23 | AD2-134 | PJM_500_BG_P4_5_CNSTN_13_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 228.49 | 238 | AD2-158 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 224.05 | 233.15 | AD2-158 | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 224.05 | 233.15 | AD2-158 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 224.03 | 233.12 | AD2-158 | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 209.21 | 216.46 | AD2-158 | PECO_P4_PEACH245_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 202.97 | 211.1 | AD2-158 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 198.66 | 206.35 | AD2-158 | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 198.66 | 206.35 | AD2-158 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 198.64 | 206.32 | AD2-158 | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 183.92 | 189.89 | AD2-158 | PECO_P4_PEACH245_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 559 | 680 | 129.8 | 133.13 | AD2-158 | PEPCO_P1_PP2_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 2 | 230 | 233 | 559 | 680 | 129.8 | 133.13 | AD2-158 | PEPCO_P1_PP1_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 116.64 | AD2-158 | PJM_500_BG_P1_5013_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 116.63 | AD2-158 | PJM_500_BG_P4_5_CNSTN_M_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.19 | 116.74 | AD2-158 | Base Case | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 106.71 | 108.01 | AD2-158 | BG_P7_CNSTN_NWEST2_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 106.17 | 107.11 | AD2-158 | BG_P7_GRCTN_RAPHEL_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 105.55 | 110 | AD2-158 | PN_P1-2_PN-500-010T_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 104.22 | 108.27 | AD2-158 | PJM_500_BG_P4_5_CNSTN_L_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 103.32 | 104.24 | AD2-158 | BG_P7_NEAST_RPHLRD_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 101.26 | 102.12 | AD2-158 | AP_P2-3_PE-500-015_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 116.84 | AD2-163 | PJM_500_BG_P1_5013_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 116.84 | AD2-163 | PJM_500_BG_P4_5_CNSTN_M_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.19 | 116.95 | AD2-163 | Base Case | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 105.55 | 110.21 | AD2-163 | PN_P1-2_PN-500-010T_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 104.22 | 108.47 | AD2-163 | PJM_500_BG_P4_5_CNSTN_L_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 116.71 | AD2-180 | PJM_500_BG_P1_5013_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 116.71 | AD2-180 | PJM_500_BG_P4_5_CNSTN_M_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.19 | 116.79 | AD2-180 | Base Case | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 106.71 | 108.12 | AD2-180 | BG_P7_CNSTN_NWEST2_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 106.17 | 107.23 | AD2-180 | BG_P7_GRCTN_RAPHEL_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 105.55 | 110.08 | AD2-180 | PN_P1-2_PN-500-010T_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 104.22 | 108.34 | AD2-180 | PJM_500_BG_P4_5_CNSTN_L_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 103.32 | 104.36 | AD2-180 | BG_P7_NEAST_RPHLRD_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 101.26 | 102.29 | AD2-180 | AP_P2-3_PE-500-015_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 100.59 | 101.5 | AD2-180 | AP_P2-3_PE-500-018D_SRT-SL | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 117.15 | AD2-213 | PJM_500_BG_P1_5013_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 117.15 | AD2-213 | PJM_500_BG_P4_5_CNSTN_M_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.19 | 117.38 | AD2-213 | Base Case | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 105.55 | 110.51 | AD2-213 | PN_P1-2_PN-500-010T_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 228.49 | 236.75 | AE1-044 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 224.05 | 231.88 | AE1-044 | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 224.05 | 231.88 | AE1-044 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 224.03 | 231.85 | AE1-044 | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 209.21 | 215.2 | AE1-044 | PECO_P4_PEACH245_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 202.97 | 209.89 | AE1-044 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 198.66 | 205.12 | AE1-044 | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 198.66 | 205.12 | AE1-044 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 198.64 | 205.09 | AE1-044 | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 183.92 | 188.67 | AE1-044 | PECO_P4_PEACH245_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 166.62 | 167.75 | AE1-044 | Base Case | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 130.65 | 130.21 | AE1-044 | Base Case | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 2 | 230 | 233 | 559 | 680 | 129.8 | 130.8 | AE1-044 | PEPCO_P1_PP1_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 559 | 680 | 129.8 | 130.8 | AE1-044 | PEPCO_P1_PP2_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 647 | 801 | 122.17 | 122.18 | AE1-044 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 2 | 230 | 233 | 559 | 680 | 122.19 | 121.19 | AE1-044 | DVP_P4-2: 514T595_SRT-SW | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 559 | 680 | 122.19 | 121.19 | AE1-044 | DVP_P4-2: 514T595_SRT-SW | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 2 | 230 | 233 | 559 | 680 | 119.41 | 118.2 | AE1-044 | DVP_P4-2: 51482_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 559 | 680 | 119.41 | 118.2 | AE1-044 | DVP_P4-2: 51482_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 2 | 230 | 233 | 559 | 680 | 119.12 | 118.2 | AE1-044 | DVP_P1-2: LN 514_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 2 | 230 | 233 | 559 | 680 | 119.12 | 118.2 | AE1-044 | AP_P1-2_PE-500-407T_SRT-SL | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 559 | 680 | 119.12 | 118.2 | AE1-044 | AP_P1-2_PE-500-407T_SRT-SL | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 559 | 680 | 119.12 | 118.2 | AE1-044 | DVP_P1-2: LN 514_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 207922 | BRIS | 207923 | BRISREAC | RX | 230 | 229 | 506 | 618 | 117.78 | 118.28 | AE1-044 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 207923 | BRISREAC | 208132 | WHEM TR1 | 1 | 230 | 229 | 493 | 618 | 117.78 | 118.28 | AE1-044 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 647 | 801 | 117.38 | 117.73 | AE1-044 | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 647 | 801 | 117.38 | 117.73 | AE1-044 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 647 | 801 | 117.37 | 117.72 | AE1-044 | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 463 | 563 | 115.98 | 115.96 | AE1-044 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 463 | 563 | 115.98 | 116.29 | AE1-044 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 207922 | BRIS | 207923 | BRISREAC | RX | 230 | 229 | 506 | 618 | 115.13 | 115.88 | AE1-044 | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 207923 | BRISREAC | 208132 | WHEM TR1 | 1 | 230 | 229 | 493 | 618 | 115.13 | 115.88 | AE1-044 | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 207922 | BRIS | 207923 | BRISREAC | RX | 230 | 229 | 506 | 618 | 115.13 | 115.88 | AE1-044 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 207923 | BRISREAC | 208132 | WHEM TR1 | 1 | 230 | 229 | 493 | 618 | 115.13 | 115.88 | AE1-044 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 207922 | BRIS | 207923 | BRISREAC | RX | 230 | 229 | 506 | 618 | 115.12 | 115.87 | AE1-044 | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 207923 | BRISREAC | 208132 | WHEM TR1 | 1 | 230 | 229 | 493 | 618 | 115.12 | 115.87 | AE1-044 | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 463 | 563 | 113.42 | 114.02 | AE1-044 | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 463 | 563 | 113.42 | 113.68 | AE1-044 | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 463 | 563 | 113.37 | 113.96 | AE1-044 | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 463 | 563 | 113.37 | 113.63 | AE1-044 | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 463 | 563 | 113.37 | 113.96 | AE1-044 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 463 | 563 | 113.37 | 113.62 | AE1-044 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 116.03 | AE1-044 | PJM_500_BG_P1_5013_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 116.03 | AE1-044 | PJM_500_BG_P4_5_CNSTN_M_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.19 | 116.04 | AE1-044 | Base Case | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 709 | 869 | 110.18 | 110.58 | AE1-044 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 463 | 578 | 110.56 | 110.35 | AE1-044 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 709 | 869 | 108.55 | 109.08 | AE1-044 | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 709 | 869 | 108.55 | 109.08 | AE1-044 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 709 | 869 | 108.54 | 109.07 | AE1-044 | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 647 | 801 | 108.33 | 108.77 | AE1-044 | PECO_P4_PEACH245_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 207922 | BRIS | 207923 | BRISREAC | RX | 230 | 229 | 506 | 618 | 107.75 | 108.83 | AE1-044 | PECO_P4_PEACH245_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 207923 | BRISREAC | 208132 | WHEM TR1 | 1 | 230 | 229 | 493 | 618 | 107.75 | 108.83 | AE1-044 | PECO_P4_PEACH245_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 463 | 578 | 108.07 | 108.13 | AE1-044 | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 463 | 578 | 108.02 | 108.08 | AE1-044 | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 463 | 578 | 108.02 | 108.07 | AE1-044 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 106.71 | 107.32 | AE1-044 | BG_P7_CNSTN_NWEST2_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208131 | WHEM | 208132 | WHEM TR1 | 1 | 230 | 229 | 547 | 618 | 106.32 | 105.45 | AE1-044 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 106.17 | 106.43 | AE1-044 | BG_P7_GRCTN_RAPHEL_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 105.55 | 109.41 | AE1-044 | PN_P1-2_PN-500-010T_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 463 | 578 | 105.24 | 104.32 | AE1-044 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 104.22 | 107.68 | AE1-044 | PJM_500_BG_P4_5_CNSTN_L_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208131 | WHEM | 208132 | WHEM TR1 | 1 | 230 | 229 | 547 | 618 | 103.73 | 103.12 | AE1-044 | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208131 | WHEM | 208132 | WHEM TR1 | 1 | 230 | 229 | 547 | 618 | 103.73 | 103.12 | AE1-044 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208131 | WHEM | 208132 | WHEM TR1 | 1 | 230 | 229 | 547 | 618 | 103.72 | 103.1 | AE1-044 | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 103.32 | 103.56 | AE1-044 | BG_P7_NEAST_RPHLRD_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 463 | 578 | 102.74 | 102.11 | AE1-044 | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 220964 | GRACETON | 220999 | BAGLEY2 | 13 | 230 | 232 | 1331 | 1594 | 101.97 | 102.18 | AE1-044 | BG_P4_5_GRCTN_3T_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 463 | 578 | 102.69 | 102.05 | AE1-044 | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 463 | 578 | 102.69 | 102.05 | AE1-044 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 709 | 869 | 101.29 | 102.11 | AE1-044 | PECO_P4_PEACH245_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 101.26 | 101.47 | AE1-044 | AP_P2-3_PE-500-015_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 116.75 | AE1-056 | PJM_500_BG_P1_5013_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 116.75 | AE1-056 | PJM_500_BG_P4_5_CNSTN_M_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.19 | 116.87 | AE1-056 | Base Case | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 106.71 | 108.15 | AE1-056 | BG_P7_CNSTN_NWEST2_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 106.17 | 107.25 | AE1-056 | BG_P7_GRCTN_RAPHEL_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 105.55 | 110.12 | AE1-056 | PN_P1-2_PN-500-010T_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 104.22 | 108.38 | AE1-056 | PJM_500_BG_P4_5_CNSTN_L_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 103.32 | 104.38 | AE1-056 | BG_P7_NEAST_RPHLRD_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 101.26 | 102.29 | AE1-056 | AP_P2-3_PE-500-015_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 100.32 | 102.23 | AE1-056 | PJM_500_BG_P4_5_CNSTN_13_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200009 | JUNI | 208004 | JUNI | 2 | 500/230 | 229 | 776 | 1010 | 108.85 | 110.1 | AE1-071 | PL_10_P42_000140_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 203981 | AD2-062_POI | 235188 | 01GREENE | 1 | 138 | 226/201 | 221 | 268 | 95.88 | 102.82 | AE1-071 | PJM_500_BG_P4_5_CNSTN_J_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 203981 | AD2-062_POI | 235188 | 01GREENE | 1 | 138 | 226/201 | 221 | 268 | 95.88 | 102.81 | AE1-071 | PJM_500_BG_P1_5011_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 203981 | AD2-062_POI | 235188 | 01GREENE | 1 | 138 | 226/201 | 221 | 268 | 95.51 | 102.43 | AE1-071 | PEPCO_P4_PP40_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 116.67 | AE1-084 | PJM_500_BG_P1_5013_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 116.67 | AE1-084 | PJM_500_BG_P4_5_CNSTN_M_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.19 | 116.77 | AE1-084 | Base Case | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 106.71 | 108.06 | AE1-084 | BG_P7_CNSTN_NWEST2_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 106.17 | 107.17 | AE1-084 | BG_P7_GRCTN_RAPHEL_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 105.55 | 110.04 | AE1-084 | PN_P1-2_PN-500-010T_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 104.22 | 108.3 | AE1-084 | PJM_500_BG_P4_5_CNSTN_L_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 103.32 | 104.3 | AE1-084 | BG_P7_NEAST_RPHLRD_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 101.26 | 102.21 | AE1-084 | AP_P2-3_PE-500-015_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 2 | 230 | 233 | 559 | 680 | 129.8 | 133.16 | AE1-101 | PEPCO_P1_PP1_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 559 | 680 | 129.8 | 133.16 | AE1-101 | PEPCO_P1_PP2_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 116.8 | AE1-101 | PJM_500_BG_P1_5013_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 116.8 | AE1-101 | PJM_500_BG_P4_5_CNSTN_M_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.19 | 116.93 | AE1-101 | Base Case | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 106.71 | 108.21 | AE1-101 | BG_P7_CNSTN_NWEST2_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 106.17 | 107.32 | AE1-101 | BG_P7_GRCTN_RAPHEL_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 105.55 | 110.15 | AE1-101 | PN_P1-2_PN-500-010T_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 104.22 | 108.43 | AE1-101 | PJM_500_BG_P4_5_CNSTN_L_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 103.32 | 104.45 | AE1-101 | BG_P7_NEAST_RPHLRD_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 101.26 | 102.32 | AE1-101 | AP_P2-3_PE-500-015_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 100.59 | 101.49 | AE1-101 | AP_P2-3_PE-500-018D_SRT-SL | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 228.49 | 242.61 | AE1-104 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 224.05 | 237.92 | AE1-104 | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 224.05 | 237.92 | AE1-104 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 224.03 | 237.89 | AE1-104 | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 209.21 | 221.26 | AE1-104 | PECO_P4_PEACH245_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 202.97 | 215.64 | AE1-104 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 198.66 | 211.05 | AE1-104 | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 198.66 | 211.05 | AE1-104 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 198.64 | 211.02 | AE1-104 | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 183.92 | 194.62 | AE1-104 | PECO_P4_PEACH245_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 166.62 | 170.65 | AE1-104 | Base Case | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 130.65 | 132.9 | AE1-104 | Base Case | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 559 | 680 | 129.8 | 133.19 | AE1-104 | PEPCO_P1_PP2_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 2 | 230 | 233 | 559 | 680 | 129.8 | 133.19 | AE1-104 | PEPCO_P1_PP1_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 647 | 801 | 122.17 | 125.18 | AE1-104 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 559 | 680 | 122.19 | 123.98 | AE1-104 | DVP_P4-2: 514T595_SRT-SW | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 2 | 230 | 233 | 559 | 680 | 122.19 | 123.98 | AE1-104 | DVP_P4-2: 514T595_SRT-SW | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 463 | 563 | 115.98 | 121.65 | AE1-104 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 463 | 563 | 115.98 | 122.03 | AE1-104 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 2 | 230 | 233 | 559 | 680 | 119.41 | 121.06 | AE1-104 | DVP_P4-2: 51482_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 559 | 680 | 119.41 | 121.06 | AE1-104 | DVP_P4-2: 51482_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 2 | 230 | 233 | 559 | 680 | 119.12 | 121.06 | AE1-104 | DVP_P1-2: LN 514_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 2 | 230 | 233 | 559 | 680 | 119.12 | 121.06 | AE1-104 | AP_P1-2_PE-500-407T_SRT-SL | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 559 | 680 | 119.12 | 121.06 | AE1-104 | AP_P1-2_PE-500-407T_SRT-SL | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 559 | 680 | 119.12 | 121.06 | AE1-104 | DVP_P1-2: LN 514_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 647 | 801 | 117.38 | 120.9 | AE1-104 | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 647 | 801 | 117.38 | 120.9 | AE1-104 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 647 | 801 | 117.37 | 120.88 | AE1-104 | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 207923 | BRISREAC | 208132 | WHEM TR1 | 1 | 230 | 229 | 493 | 618 | 117.78 | 120.7 | AE1-104 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 207922 | BRIS | 207923 | BRISREAC | RX | 230 | 229 | 506 | 618 | 117.78 | 120.7 | AE1-104 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 232 | 282 | 116.72 | 119.55 | AE1-104 | PJM_500_BG_P4_5_CNSTN_J_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 232 | 282 | 116.72 | 119.55 | AE1-104 | PJM_500_BG_P1_5011_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 232 | 282 | 116.46 | 119.29 | AE1-104 | PEPCO_P4_PP40_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 463 | 563 | 113.42 | 119.46 | AE1-104 | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 463 | 563 | 113.42 | 119.85 | AE1-104 | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 463 | 563 | 113.37 | 119.79 | AE1-104 | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 463 | 563 | 113.37 | 119.4 | AE1-104 | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 463 | 563 | 113.37 | 119.4 | AE1-104 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 463 | 563 | 113.37 | 119.79 | AE1-104 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 207922 | BRIS | 207923 | BRISREAC | RX | 230 | 229 | 506 | 618 | 115.13 | 118.39 | AE1-104 | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 207923 | BRISREAC | 208132 | WHEM TR1 | 1 | 230 | 229 | 493 | 618 | 115.13 | 118.39 | AE1-104 | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 207922 | BRIS | 207923 | BRISREAC | RX | 230 | 229 | 506 | 618 | 115.13 | 118.39 | AE1-104 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 207923 | BRISREAC | 208132 | WHEM TR1 | 1 | 230 | 229 | 493 | 618 | 115.13 | 118.39 | AE1-104 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 207922 | BRIS | 207923 | BRISREAC | RX | 230 | 229 | 506 | 618 | 115.12 | 118.38 | AE1-104 | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 207923 | BRISREAC | 208132 | WHEM TR1 | 1 | 230 | 229 | 493 | 618 | 115.12 | 118.38 | AE1-104 | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.19 | 120.63 | AE1-104 | Base Case | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 119.46 | AE1-104 | PJM_500_BG_P1_5013_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 119.46 | AE1-104 | PJM_500_BG_P4_5_CNSTN_M_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 463 | 578 | 110.56 | 115.89 | AE1-104 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 235463 | 01TANEY | 1 | 138 | 227/201 | 221 | 268 | 110.75 | 115.1 | AE1-104 | PJM_500_BG_P4_5_CNSTN_J_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 235463 | 01TANEY | 1 | 138 | 227/201 | 221 | 268 | 110.75 | 115.1 | AE1-104 | PJM_500_BG_P1_5011_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 235463 | 01TANEY | 1 | 138 | 227/201 | 221 | 268 | 110.45 | 114.79 | AE1-104 | PEPCO_P4_PP40_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 463 | 578 | 108.07 | 113.76 | AE1-104 | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 463 | 578 | 108.02 | 113.7 | AE1-104 | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 463 | 578 | 108.02 | 113.7 | AE1-104 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 709 | 869 | 110.18 | 113.02 | AE1-104 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 647 | 801 | 108.33 | 111.94 | AE1-104 | PECO_P4_PEACH245_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 709 | 869 | 108.55 | 111.58 | AE1-104 | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 709 | 869 | 108.55 | 111.57 | AE1-104 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 709 | 869 | 108.54 | 111.57 | AE1-104 | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 463 | 578 | 105.24 | 109.86 | AE1-104 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 207923 | BRISREAC | 208132 | WHEM TR1 | 1 | 230 | 229 | 493 | 618 | 107.75 | 111.34 | AE1-104 | PECO_P4_PEACH245_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 207922 | BRIS | 207923 | BRISREAC | RX | 230 | 229 | 506 | 618 | 107.75 | 111.34 | AE1-104 | PECO_P4_PEACH245_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 106.71 | 110.66 | AE1-104 | BG_P7_CNSTN_NWEST2_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 106.17 | 109.76 | AE1-104 | BG_P7_GRCTN_RAPHEL_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 105.55 | 112.86 | AE1-104 | PN_P1-2_PN-500-010T_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208131 | WHEM | 208132 | WHEM TR1 | 1 | 230 | 229 | 547 | 618 | 106.32 | 107.77 | AE1-104 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 463 | 578 | 102.74 | 107.73 | AE1-104 | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 463 | 578 | 102.69 | 107.68 | AE1-104 | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 463 | 578 | 102.69 | 107.68 | AE1-104 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 104.22 | 110.99 | AE1-104 | PJM_500_BG_P4_5_CNSTN_L_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 103.32 | 106.88 | AE1-104 | BG_P7_NEAST_RPHLRD_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208131 | WHEM | 208132 | WHEM TR1 | 1 | 230 | 229 | 547 | 618 | 103.73 | 105.52 | AE1-104 | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208131 | WHEM | 208132 | WHEM TR1 | 1 | 230 | 229 | 547 | 618 | 103.73 | 105.52 | AE1-104 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208131 | WHEM | 208132 | WHEM TR1 | 1 | 230 | 229 | 547 | 618 | 103.72 | 105.51 | AE1-104 | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204538 | 27STRABAN | 204544 | 27LINCOLN | 1 | 115 | 227 | 257 | 313 | 102.73 | 104.59 | AE1-104 | PJM_500_BG_P4_5_CNSTN_J_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204538 | 27STRABAN | 204544 | 27LINCOLN | 1 | 115 | 227 | 257 | 313 | 102.73 | 104.59 | AE1-104 | PJM_500_BG_P1_5011_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204538 | 27STRABAN | 204544 | 27LINCOLN | 1 | 115 | 227 | 257 | 313 | 102.46 | 104.33 | AE1-104 | PEPCO_P4_PP40_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 101.26 | 104.52 | AE1-104 | AP_P2-3_PE-500-015_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 220964 | GRACETON | 220999 | BAGLEY2 | 13 | 230 | 232 | 1331 | 1594 | 101.97 | 103.89 | AE1-104 | BG_P4_5_GRCTN_3T_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 204550 | 27ORRTANNA | 1 | 115 | 227 | 133 | 160 | 101.04 | 104.37 | AE1-104 | ME_P1-2_ME-115-068_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 709 | 869 | 101.29 | 104.61 | AE1-104 | PECO_P4_PEACH245_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 463 | 563 | 98.5 | 104.74 | AE1-104 | PECO_P4_PEACH245_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 463 | 563 | 98.5 | 104.36 | AE1-104 | PECO_P4_PEACH245_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204512 | 27S.RDG | 204693 | 27BOONETOWN | 1 | 230 | 227 | 445 | 531 | 101.56 | 102.85 | AE1-104 | PL_04_P43_102301_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204512 | 27S.RDG | 204693 | 27BOONETOWN | 1 | 230 | 227 | 445 | 531 | 101.56 | 102.85 | AE1-104 | PL_04_P22_102291_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204512 | 27S.RDG | 204693 | 27BOONETOWN | 1 | 230 | 227 | 445 | 531 | 101.52 | 102.85 | AE1-104 | PL_04_P43_102300_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204512 | 27S.RDG | 204693 | 27BOONETOWN | 1 | 230 | 227 | 445 | 531 | 101.52 | 102.85 | AE1-104 | PL_04_P22_102290_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204512 | 27S.RDG | 204693 | 27BOONETOWN | 1 | 230 | 227 | 445 | 531 | 101.52 | 102.85 | AE1-104 | PL_04_P13_101211_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 100.32 | 104.63 | AE1-104 | PJM_500_BG_P4_5_CNSTN_13_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208078 | SAKR | 1 | 230 | 229 | 647 | 801 | 98.95 | 102 | AE1-104 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 220965 | NEAST339 | 220980 | RAPHAEL | 1 | 230 | 232 | 1098 | 1283 | 99.71 | 101.74 | AE1-104 | BG_P4_5_NEAST_17_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 220965 | NEAST339 | 220980 | RAPHAEL | 1 | 230 | 232 | 1098 | 1283 | 99.71 | 101.82 | AE1-104 | BG_P4_5_NEAST_15_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 98.57 | 103.53 | AE1-104 | Base Case | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 220965 | NEAST339 | 220980 | RAPHAEL | 1 | 230 | 232 | 1098 | 1283 | 99.42 | 101.57 | AE1-104 | BG_P1_2315_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 97.97 | 104.18 | AE1-104 | AP_P2-3_PE-500-015_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 220979 | NEAST317 | 220980 | RAPHAEL | 1 | 230 | 232 | 1098 | 1283 | 99.26 | 101.33 | AE1-104 | BG_P4_5_NEAST_39_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 220979 | NEAST317 | 220980 | RAPHAEL | 1 | 230 | 232 | 1098 | 1283 | 99.26 | 101.33 | AE1-104 | BG_P4_5_NEAST_37_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204539 | 27HUNTRSTN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 232 | 282 | 98.13 | 100.96 | AE1-104 | PJM_500_BG_P4_5_CNSTN_J_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204539 | 27HUNTRSTN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 232 | 282 | 98.13 | 100.96 | AE1-104 | PJM_500_BG_P1_5011_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 220979 | NEAST317 | 220980 | RAPHAEL | 1 | 230 | 232 | 1098 | 1283 | 98.92 | 101.04 | AE1-104 | BG_P1_2337_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204539 | 27HUNTRSTN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 232 | 282 | 97.87 | 100.7 | AE1-104 | PEPCO_P4_PP40_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 204550 | 27ORRTANNA | 1 | 115 | 227 | 133 | 160 | 98.04 | 100.78 | AE1-104 | ME_P2-3_ME-115-035A_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 228.49 | 240.48 | AE1-129 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 224.05 | 235.69 | AE1-129 | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 224.05 | 235.68 | AE1-129 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 224.03 | 235.66 | AE1-129 | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 209.21 | 219 | AE1-129 | PECO_P4_PEACH245_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 202.97 | 213.53 | AE1-129 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 198.66 | 208.84 | AE1-129 | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 198.66 | 208.84 | AE1-129 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 198.64 | 208.81 | AE1-129 | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 183.92 | 192.38 | AE1-129 | PECO_P4_PEACH245_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 166.62 | 171.12 | AE1-129 | Base Case | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 130.65 | 133.31 | AE1-129 | Base Case | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 647 | 801 | 122.17 | 125.1 | AE1-129 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 647 | 801 | 117.38 | 120.72 | AE1-129 | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 647 | 801 | 117.38 | 120.72 | AE1-129 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 647 | 801 | 117.37 | 120.7 | AE1-129 | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 208070 | SAHA12TP | 1 | 230 | 229 | 513 | 628 | 116.86 | 118.43 | AE1-129 | BG_P7_GRCTN_CNSTN_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 647 | 801 | 108.33 | 111.75 | AE1-129 | PECO_P4_PEACH245_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200009 | JUNI | 208004 | JUNI | 2 | 500/230 | 229 | 776 | 1010 | 108.85 | 109.79 | AE1-129 | PL_10_P42_000140_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 106.71 | 108.84 | AE1-129 | BG_P7_CNSTN_NWEST2_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 106.17 | 107.95 | AE1-129 | BG_P7_GRCTN_RAPHEL_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 103.32 | 105.08 | AE1-129 | BG_P7_NEAST_RPHLRD_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208070 | SAHA12TP | 1 | 230 | 229 | 721 | 814 | 102.85 | 103.59 | AE1-129 | BG_P7_GRCTN_CNSTN_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 220964 | GRACETON | 220999 | BAGLEY2 | 13 | 230 | 232 | 1331 | 1594 | 101.97 | 103.12 | AE1-129 | BG_P4_5_GRCTN_3T_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 101.26 | 102.89 | AE1-129 | AP_P2-3_PE-500-015_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 100.32 | 102.85 | AE1-129 | PJM_500_BG_P4_5_CNSTN_13_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 220965 | NEAST339 | 220980 | RAPHAEL | 1 | 230 | 232 | 1098 | 1283 | 99.71 | 100.85 | AE1-129 | BG_P4_5_NEAST_17_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 220965 | NEAST339 | 220980 | RAPHAEL | 1 | 230 | 232 | 1098 | 1283 | 99.71 | 100.92 | AE1-129 | BG_P4_5_NEAST_15_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 209.21 | 216.47 | AE1-143 | PECO_P4_PEACH245_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 183.92 | 189.9 | AE1-143 | PECO_P4_PEACH245_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 116.64 | AE1-143 | PJM_500_BG_P1_5013_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 116.64 | AE1-143 | PJM_500_BG_P4_5_CNSTN_M_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.19 | 116.68 | AE1-143 | Base Case | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 106.71 | 108.06 | AE1-143 | BG_P7_CNSTN_NWEST2_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 106.17 | 107.17 | AE1-143 | BG_P7_GRCTN_RAPHEL_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 105.55 | 110.01 | AE1-143 | PN_P1-2_PN-500-010T_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 104.22 | 108.27 | AE1-143 | PJM_500_BG_P4_5_CNSTN_L_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 103.32 | 104.29 | AE1-143 | BG_P7_NEAST_RPHLRD_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 101.26 | 102.23 | AE1-143 | AP_P2-3_PE-500-015_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 116.71 | AE1-153 | PJM_500_BG_P1_5013_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 116.71 | AE1-153 | PJM_500_BG_P4_5_CNSTN_M_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.19 | 116.84 | AE1-153 | Base Case | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 106.71 | 108.1 | AE1-153 | BG_P7_CNSTN_NWEST2_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 106.17 | 107.2 | AE1-153 | BG_P7_GRCTN_RAPHEL_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 105.55 | 110.08 | AE1-153 | PN_P1-2_PN-500-010T_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 104.22 | 108.34 | AE1-153 | PJM_500_BG_P4_5_CNSTN_L_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 103.32 | 104.33 | AE1-153 | BG_P7_NEAST_RPHLRD_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 101.26 | 102.23 | AE1-153 | AP_P2-3_PE-500-015_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 100.32 | 102.18 | AE1-153 | PJM_500_BG_P4_5_CNSTN_13_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 116.77 | AE1-155 | PJM_500_BG_P1_5013_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 116.77 | AE1-155 | PJM_500_BG_P4_5_CNSTN_M_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.19 | 116.9 | AE1-155 | Base Case | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 106.71 | 108.16 | AE1-155 | BG_P7_CNSTN_NWEST2_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 106.17 | 107.27 | AE1-155 | BG_P7_GRCTN_RAPHEL_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 105.55 | 110.13 | AE1-155 | PN_P1-2_PN-500-010T_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 104.22 | 108.4 | AE1-155 | PJM_500_BG_P4_5_CNSTN_L_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 103.32 | 104.4 | AE1-155 | BG_P7_NEAST_RPHLRD_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 101.26 | 102.3 | AE1-155 | AP_P2-3_PE-500-015_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 100.32 | 102.24 | AE1-155 | PJM_500_BG_P4_5_CNSTN_13_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 116.8 | AE1-157 | PJM_500_BG_P1_5013_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 116.8 | AE1-157 | PJM_500_BG_P4_5_CNSTN_M_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.19 | 116.93 | AE1-157 | Base Case | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 106.71 | 108.19 | AE1-157 | BG_P7_CNSTN_NWEST2_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 106.17 | 107.3 | AE1-157 | BG_P7_GRCTN_RAPHEL_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 105.55 | 110.16 | AE1-157 | PN_P1-2_PN-500-010T_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 104.22 | 108.42 | AE1-157 | PJM_500_BG_P4_5_CNSTN_L_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 103.32 | 104.43 | AE1-157 | BG_P7_NEAST_RPHLRD_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 101.26 | 102.33 | AE1-157 | AP_P2-3_PE-500-015_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 100.32 | 102.27 | AE1-157 | PJM_500_BG_P4_5_CNSTN_13_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 228.49 | 239.39 | AE1-226 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 224.05 | 234.58 | AE1-226 | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 224.05 | 234.58 | AE1-226 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 224.03 | 234.55 | AE1-226 | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 209.21 | 217.89 | AE1-226 | PECO_P4_PEACH245_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 202.97 | 212.46 | AE1-226 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 198.66 | 207.75 | AE1-226 | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 198.66 | 207.75 | AE1-226 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 198.64 | 207.72 | AE1-226 | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 183.92 | 191.28 | AE1-226 | PECO_P4_PEACH245_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 166.62 | 169.99 | AE1-226 | Base Case | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 130.65 | 132.26 | AE1-226 | Base Case | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 208070 | SAHA12TP | 1 | 230 | 229 | 513 | 628 | 116.86 | 116.55 | AE1-226 | BG_P7_GRCTN_CNSTN_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208393 | FARO DC TIE | 208395 | FARO FF | 1 | 115/69 | 229 | 77 | 114 | 100.26 | 106.34 | AE1-226 | PL_05_P71_000906_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208395 | FARO FF | 208396 | FARO | 1 | 69 | 229 | 194 | 240 | 98.42 | 101.03 | AE1-226 | PL_05_P71_000906_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 228.49 | 239.47 | AE1-229 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 224.05 | 234.67 | AE1-229 | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 224.05 | 234.66 | AE1-229 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 224.03 | 234.64 | AE1-229 | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 209.21 | 217.98 | AE1-229 | PECO_P4_PEACH245_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 202.97 | 212.54 | AE1-229 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 198.66 | 207.84 | AE1-229 | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 198.66 | 207.84 | AE1-229 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 198.64 | 207.81 | AE1-229 | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 183.92 | 191.38 | AE1-229 | PECO_P4_PEACH245_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 463 | 563 | 115.98 | 118.16 | AE1-229 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 463 | 563 | 115.98 | 118.51 | AE1-229 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 463 | 563 | 113.42 | 115.92 | AE1-229 | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 463 | 563 | 113.42 | 116.27 | AE1-229 | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 463 | 563 | 113.37 | 115.86 | AE1-229 | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 463 | 563 | 113.37 | 116.21 | AE1-229 | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 463 | 563 | 113.37 | 115.86 | AE1-229 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 463 | 563 | 113.37 | 116.21 | AE1-229 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 117.5 | AE1-229 | PJM_500_BG_P1_5013_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 117.5 | AE1-229 | PJM_500_BG_P4_5_CNSTN_M_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.19 | 117.87 | AE1-229 | Base Case | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 463 | 578 | 110.56 | 112.49 | AE1-229 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 463 | 578 | 108.07 | 110.31 | AE1-229 | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 463 | 578 | 108.02 | 110.25 | AE1-229 | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 463 | 578 | 108.02 | 110.25 | AE1-229 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 106.71 | 108.87 | AE1-229 | BG_P7_CNSTN_NWEST2_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 106.17 | 107.98 | AE1-229 | BG_P7_GRCTN_RAPHEL_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 463 | 578 | 105.24 | 106.47 | AE1-229 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 105.55 | 110.86 | AE1-229 | PN_P1-2_PN-500-010T_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 104.22 | 109.1 | AE1-229 | PJM_500_BG_P4_5_CNSTN_L_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 103.32 | 105.1 | AE1-229 | BG_P7_NEAST_RPHLRD_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 463 | 578 | 102.74 | 104.28 | AE1-229 | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 463 | 578 | 102.69 | 104.23 | AE1-229 | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 463 | 578 | 102.69 | 104.22 | AE1-229 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 101.26 | 102.94 | AE1-229 | AP_P2-3_PE-500-015_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 100.32 | 102.92 | AE1-229 | PJM_500_BG_P4_5_CNSTN_13_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 117.17 | AE1-240 | PJM_500_BG_P1_5013_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 117.17 | AE1-240 | PJM_500_BG_P4_5_CNSTN_M_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.19 | 117.41 | AE1-240 | Base Case | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 105.55 | 110.54 | AE1-240 | PN_P1-2_PN-500-010T_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 104.22 | 108.79 | AE1-240 | PJM_500_BG_P4_5_CNSTN_L_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 228.49 | 246.25 | AE2-000 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 224.05 | 241.68 | AE2-000 | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 224.05 | 241.68 | AE2-000 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 224.03 | 241.65 | AE2-000 | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 209.21 | 225.05 | AE2-000 | PECO_P4_PEACH245_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 202.97 | 219.23 | AE2-000 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 198.66 | 214.75 | AE2-000 | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 198.66 | 214.75 | AE2-000 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 198.64 | 214.72 | AE2-000 | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 183.92 | 198.35 | AE2-000 | PECO_P4_PEACH245_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 166.62 | 172.71 | AE2-000 | Base Case | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 221089 | WINDYED1 | 221090 | GLENARM2 | 1 | 115 | 232 | 148 | 192 | 141.81 | 143.87 | AE2-000 | BG_P7_GRCTN_RAPHEL_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 221092 | FIVE.FOR | 221096 | ROCKRGE1 | 1 | 115 | 232 | 229 | 256 | 135.39 | 136.39 | AE2-000 | BG_P7_GRCTN_RAPHEL_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 130.65 | 134.84 | AE2-000 | Base Case | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 221089 | WINDYED1 | 221090 | GLENARM2 | 1 | 115 | 232 | 148 | 192 | 131 | 132.34 | AE2-000 | BG_P7_NEAST_RPHLRD_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 2 | 230 | 233 | 559 | 680 | 129.8 | 133.95 | AE2-000 | PEPCO_P1_PP1_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 559 | 680 | 129.8 | 133.95 | AE2-000 | PEPCO_P1_PP2_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 221092 | FIVE.FOR | 221096 | ROCKRGE1 | 1 | 115 | 232 | 229 | 256 | 127.23 | 127.78 | AE2-000 | BG_P7_NEAST_RPHLRD_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 647 | 801 | 122.17 | 126.96 | AE2-000 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 559 | 680 | 122.19 | 124.83 | AE2-000 | DVP_P4-2: 514T595_SRT-SW | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 2 | 230 | 233 | 559 | 680 | 122.19 | 124.83 | AE2-000 | DVP_P4-2: 514T595_SRT-SW | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 463 | 563 | 115.98 | 125.17 | AE2-000 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 463 | 563 | 115.98 | 124.76 | AE2-000 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 647 | 801 | 117.38 | 122.79 | AE2-000 | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 647 | 801 | 117.38 | 122.79 | AE2-000 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 647 | 801 | 117.37 | 122.77 | AE2-000 | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 2 | 230 | 233 | 559 | 680 | 119.41 | 121.93 | AE2-000 | DVP_P4-2: 51482_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 559 | 680 | 119.41 | 121.93 | AE2-000 | DVP_P4-2: 51482_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 463 | 563 | 113.42 | 123.04 | AE2-000 | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 463 | 563 | 113.42 | 122.63 | AE2-000 | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 463 | 563 | 113.37 | 122.98 | AE2-000 | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 463 | 563 | 113.37 | 122.57 | AE2-000 | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 463 | 563 | 113.37 | 122.57 | AE2-000 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 463 | 563 | 113.37 | 122.98 | AE2-000 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 232 | 282 | 116.72 | 121.53 | AE2-000 | PJM_500_BG_P4_5_CNSTN_J_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 232 | 282 | 116.72 | 121.53 | AE2-000 | PJM_500_BG_P1_5011_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 207923 | BRISREAC | 208132 | WHEM TR1 | 1 | 230 | 229 | 493 | 618 | 117.78 | 122.15 | AE2-000 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 207922 | BRIS | 207923 | BRISREAC | RX | 230 | 229 | 506 | 618 | 117.78 | 122.15 | AE2-000 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 2 | 230 | 233 | 559 | 680 | 119.12 | 121.93 | AE2-000 | DVP_P1-2: LN 514_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 2 | 230 | 233 | 559 | 680 | 119.12 | 121.93 | AE2-000 | AP_P1-2_PE-500-407T_SRT-SL | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 559 | 680 | 119.12 | 121.93 | AE2-000 | AP_P1-2_PE-500-407T_SRT-SL | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 559 | 680 | 119.12 | 121.93 | AE2-000 | DVP_P1-2: LN 514_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 232 | 282 | 116.46 | 121.28 | AE2-000 | PEPCO_P4_PP40_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 207922 | BRIS | 207923 | BRISREAC | RX | 230 | 229 | 506 | 618 | 115.13 | 119.9 | AE2-000 | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 207923 | BRISREAC | 208132 | WHEM TR1 | 1 | 230 | 229 | 493 | 618 | 115.13 | 119.9 | AE2-000 | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 207922 | BRIS | 207923 | BRISREAC | RX | 230 | 229 | 506 | 618 | 115.13 | 119.9 | AE2-000 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 207923 | BRISREAC | 208132 | WHEM TR1 | 1 | 230 | 229 | 493 | 618 | 115.13 | 119.9 | AE2-000 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 207922 | BRIS | 207923 | BRISREAC | RX | 230 | 229 | 506 | 618 | 115.12 | 119.89 | AE2-000 | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 207923 | BRISREAC | 208132 | WHEM TR1 | 1 | 230 | 229 | 493 | 618 | 115.12 | 119.89 | AE2-000 | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 463 | 578 | 110.56 | 118.92 | AE2-000 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.19 | 123.2 | AE2-000 | Base Case | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 121.32 | AE2-000 | PJM_500_BG_P1_5013_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 121.31 | AE2-000 | PJM_500_BG_P4_5_CNSTN_M_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 463 | 578 | 108.07 | 116.85 | AE2-000 | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 463 | 578 | 108.02 | 116.79 | AE2-000 | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 463 | 578 | 108.02 | 116.79 | AE2-000 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 235463 | 01TANEY | 1 | 138 | 227/201 | 221 | 268 | 110.75 | 117.41 | AE2-000 | PJM_500_BG_P4_5_CNSTN_J_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 235463 | 01TANEY | 1 | 138 | 227/201 | 221 | 268 | 110.75 | 117.41 | AE2-000 | PJM_500_BG_P1_5011_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 235463 | 01TANEY | 1 | 138 | 227/201 | 221 | 268 | 110.45 | 117.11 | AE2-000 | PEPCO_P4_PP40_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 709 | 869 | 110.18 | 114.51 | AE2-000 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 463 | 578 | 105.24 | 112.89 | AE2-000 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 647 | 801 | 108.33 | 113.85 | AE2-000 | PECO_P4_PEACH245_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 709 | 869 | 108.55 | 113.1 | AE2-000 | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 709 | 869 | 108.55 | 113.1 | AE2-000 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 709 | 869 | 108.54 | 113.09 | AE2-000 | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 207922 | BRIS | 207923 | BRISREAC | RX | 230 | 229 | 506 | 618 | 107.75 | 112.87 | AE2-000 | PECO_P4_PEACH245_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 207923 | BRISREAC | 208132 | WHEM TR1 | 1 | 230 | 229 | 493 | 618 | 107.75 | 112.87 | AE2-000 | PECO_P4_PEACH245_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 106.71 | 112.46 | AE2-000 | BG_P7_CNSTN_NWEST2_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 106.17 | 111.56 | AE2-000 | BG_P7_GRCTN_RAPHEL_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 463 | 578 | 102.74 | 110.82 | AE2-000 | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 463 | 578 | 102.69 | 110.76 | AE2-000 | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 463 | 578 | 102.69 | 110.76 | AE2-000 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 105.55 | 114.72 | AE2-000 | PN_P1-2_PN-500-010T_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 221092 | FIVE.FOR | 221095 | ROCKRGE2 | 1 | 115 | 232 | 245 | 300 | 107.52 | 108.82 | AE2-000 | BG_P7_GRCTN_RAPHEL_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200009 | JUNI | 208004 | JUNI | 2 | 500/230 | 229 | 776 | 1010 | 108.85 | 111.2 | AE2-000 | PL_10_P42_000140_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208131 | WHEM | 208132 | WHEM TR1 | 1 | 230 | 229 | 547 | 618 | 106.32 | 109.16 | AE2-000 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 104.22 | 112.78 | AE2-000 | PJM_500_BG_P4_5_CNSTN_L_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 103.32 | 108.68 | AE2-000 | BG_P7_NEAST_RPHLRD_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204538 | 27STRABAN | 204544 | 27LINCOLN | 1 | 115 | 227 | 257 | 313 | 102.73 | 106.59 | AE2-000 | PJM_500_BG_P4_5_CNSTN_J_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204538 | 27STRABAN | 204544 | 27LINCOLN | 1 | 115 | 227 | 257 | 313 | 102.73 | 106.59 | AE2-000 | PJM_500_BG_P1_5011_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208131 | WHEM | 208132 | WHEM TR1 | 1 | 230 | 229 | 547 | 618 | 103.73 | 106.97 | AE2-000 | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208131 | WHEM | 208132 | WHEM TR1 | 1 | 230 | 229 | 547 | 618 | 103.73 | 106.97 | AE2-000 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208131 | WHEM | 208132 | WHEM TR1 | 1 | 230 | 229 | 547 | 618 | 103.72 | 106.95 | AE2-000 | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204538 | 27STRABAN | 204544 | 27LINCOLN | 1 | 115 | 227 | 257 | 313 | 102.46 | 106.33 | AE2-000 | PEPCO_P4_PP40_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 463 | 563 | 98.5 | 107.55 | AE2-000 | PECO_P4_PEACH245_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 463 | 563 | 98.5 | 107.96 | AE2-000 | PECO_P4_PEACH245_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 221092 | FIVE.FOR | 221094 | GRACE.-1 | 1 | 115 | 232 | 335 | 437 | 103.26 | 104.99 | AE2-000 | BG_P7_GRCTN_RAPHEL_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 204550 | 27ORRTANNA | 1 | 115 | 227 | 133 | 160 | 101.04 | 106.24 | AE2-000 | ME_P1-2_ME-115-068_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 101.26 | 106.1 | AE2-000 | AP_P2-3_PE-500-015_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 709 | 869 | 101.29 | 106.15 | AE2-000 | PECO_P4_PEACH245_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 100.32 | 106.34 | AE2-000 | PJM_500_BG_P4_5_CNSTN_13_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204512 | 27S.RDG | 204693 | 27BOONETOWN | 1 | 230 | 227 | 445 | 531 | 101.56 | 104.25 | AE2-000 | PL_04_P22_102291_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204512 | 27S.RDG | 204693 | 27BOONETOWN | 1 | 230 | 227 | 445 | 531 | 101.56 | 104.25 | AE2-000 | PL_04_P43_102301_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 220964 | GRACETON | 220999 | BAGLEY2 | 13 | 230 | 232 | 1331 | 1594 | 101.97 | 104.87 | AE2-000 | BG_P4_5_GRCTN_3T_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204512 | 27S.RDG | 204693 | 27BOONETOWN | 1 | 230 | 227 | 445 | 531 | 101.52 | 104.25 | AE2-000 | PL_04_P43_102300_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204512 | 27S.RDG | 204693 | 27BOONETOWN | 1 | 230 | 227 | 445 | 531 | 101.52 | 104.25 | AE2-000 | PL_04_P22_102290_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204512 | 27S.RDG | 204693 | 27BOONETOWN | 1 | 230 | 227 | 445 | 531 | 101.52 | 104.25 | AE2-000 | PL_04_P13_101211_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208078 | SAKR | 1 | 230 | 229 | 647 | 801 | 98.95 | 104.29 | AE2-000 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 232 | 282 | 99.33 | 104.72 | AE2-000 | Base Case | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 98.57 | 105.37 | AE2-000 | Base Case | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 97.97 | 106.22 | AE2-000 | AP_P2-3_PE-500-015_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 221092 | FIVE.FOR | 221095 | ROCKRGE2 | 1 | 115 | 232 | 245 | 300 | 100.57 | 101.44 | AE2-000 | BG_P7_NEAST_RPHLRD_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204539 | 27HUNTRSTN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 232 | 282 | 98.13 | 102.99 | AE2-000 | PJM_500_BG_P4_5_CNSTN_J_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204539 | 27HUNTRSTN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 232 | 282 | 98.13 | 102.99 | AE2-000 | PJM_500_BG_P1_5011_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204539 | 27HUNTRSTN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 232 | 282 | 97.87 | 102.74 | AE2-000 | PEPCO_P4_PP40_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 220965 | NEAST339 | 220980 | RAPHAEL | 1 | 230 | 232 | 1098 | 1283 | 99.71 | 102.89 | AE2-000 | BG_P4_5_NEAST_17_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 220965 | NEAST339 | 220980 | RAPHAEL | 1 | 230 | 232 | 1098 | 1283 | 99.71 | 102.96 | AE2-000 | BG_P4_5_NEAST_15_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 204550 | 27ORRTANNA | 1 | 115 | 227 | 133 | 160 | 98.04 | 102.63 | AE2-000 | ME_P2-3_ME-115-035A_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 220965 | NEAST339 | 220980 | RAPHAEL | 1 | 230 | 232 | 1098 | 1283 | 99.42 | 102.73 | AE2-000 | BG_P1_2315_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 204550 | 27ORRTANNA | 1 | 115 | 227 | 133 | 160 | 97.89 | 103.13 | AE2-000 | ME_P2-3_ME-115-013B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 220979 | NEAST317 | 220980 | RAPHAEL | 1 | 230 | 232 | 1098 | 1283 | 99.26 | 102.46 | AE2-000 | BG_P4_5_NEAST_39_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 220979 | NEAST317 | 220980 | RAPHAEL | 1 | 230 | 232 | 1098 | 1283 | 99.26 | 102.46 | AE2-000 | BG_P4_5_NEAST_37_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 220979 | NEAST317 | 220980 | RAPHAEL | 1 | 230 | 232 | 1098 | 1283 | 98.92 | 102.19 | AE2-000 | BG_P1_2337_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 204550 | 27ORRTANNA | 1 | 115 | 227 | 133 | 160 | 97.47 | 102.71 | AE2-000 | ME_P2-3_ME-115-013A_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208078 | SAKR | 1 | 230 | 229 | 647 | 801 | 96.31 | 102.01 | AE2-000 | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208078 | SAKR | 1 | 230 | 229 | 647 | 801 | 96.31 | 102.01 | AE2-000 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208078 | SAKR | 1 | 230 | 229 | 647 | 801 | 96.3 | 102 | AE2-000 | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204529 | 27GERMANTN | 204538 | 27STRABAN | 1 | 115 | 227 | 257 | 313 | 96.79 | 100.2 | AE2-000 | PJM_500_BG_P4_5_CNSTN_J_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204529 | 27GERMANTN | 204538 | 27STRABAN | 1 | 115 | 227 | 257 | 313 | 96.79 | 100.2 | AE2-000 | PJM_500_BG_P1_5011_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 463 | 578 | 93.52 | 102.16 | AE2-000 | PECO_P4_PEACH245_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204529 | 27GERMANTN | 204538 | 27STRABAN | 1 | 115 | 227 | 257 | 313 | 96.52 | 99.94 | AE2-000 | PEPCO_P4_PP40_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208131 | WHEM | 208133 | WHEM TR2 | 1 | 230 | 229 | 547 | 618 | 97.75 | 100.79 | AE2-000 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 232 | 282 | 97.98 | 101.95 | AE2-000 | AP_P2-3_PE-500-015_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208395 | FARO FF | 208396 | FARO | 1 | 69 | 229 | 194 | 240 | 98.42 | 99.94 | AE2-000 | PL_05_P71_000906_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 228.49 | 245.31 | AE2-020 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 224.05 | 240.71 | AE2-020 | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 224.05 | 240.71 | AE2-020 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 224.03 | 240.68 | AE2-020 | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 209.21 | 224.08 | AE2-020 | PECO_P4_PEACH245_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 202.97 | 218.3 | AE2-020 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 198.66 | 213.8 | AE2-020 | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 198.66 | 213.8 | AE2-020 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 198.64 | 213.77 | AE2-020 | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 183.92 | 197.39 | AE2-020 | PECO_P4_PEACH245_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 166.62 | 171.82 | AE2-020 | Base Case | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 221089 | WINDYED1 | 221090 | GLENARM2 | 1 | 115 | 232 | 148 | 192 | 141.81 | 143.57 | AE2-020 | BG_P7_GRCTN_RAPHEL_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 221092 | FIVE.FOR | 221096 | ROCKRGE1 | 1 | 115 | 232 | 229 | 256 | 135.39 | 136.16 | AE2-020 | BG_P7_GRCTN_RAPHEL_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 221089 | WINDYED1 | 221090 | GLENARM2 | 1 | 115 | 232 | 148 | 192 | 131 | 132.05 | AE2-020 | BG_P7_NEAST_RPHLRD_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 130.65 | 134 | AE2-020 | Base Case | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 559 | 680 | 129.8 | 133.8 | AE2-020 | PEPCO_P1_PP2_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 2 | 230 | 233 | 559 | 680 | 129.8 | 133.8 | AE2-020 | PEPCO_P1_PP1_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 221092 | FIVE.FOR | 221096 | ROCKRGE1 | 1 | 115 | 232 | 229 | 256 | 127.23 | 127.55 | AE2-020 | BG_P7_NEAST_RPHLRD_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 647 | 801 | 122.17 | 126.53 | AE2-020 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 559 | 680 | 122.19 | 124.66 | AE2-020 | DVP_P4-2: 514T595_SRT-SW | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 2 | 230 | 233 | 559 | 680 | 122.19 | 124.66 | AE2-020 | DVP_P4-2: 514T595_SRT-SW | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 463 | 563 | 115.98 | 124.95 | AE2-020 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 463 | 563 | 115.98 | 124.54 | AE2-020 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 559 | 680 | 119.41 | 121.77 | AE2-020 | DVP_P4-2: 51482_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 2 | 230 | 233 | 559 | 680 | 119.41 | 121.77 | AE2-020 | DVP_P4-2: 51482_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 463 | 563 | 113.42 | 122.4 | AE2-020 | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 463 | 563 | 113.42 | 122.81 | AE2-020 | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 647 | 801 | 117.38 | 122.34 | AE2-020 | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 647 | 801 | 117.38 | 122.34 | AE2-020 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 647 | 801 | 117.37 | 122.32 | AE2-020 | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 463 | 563 | 113.37 | 122.34 | AE2-020 | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 463 | 563 | 113.37 | 122.75 | AE2-020 | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 463 | 563 | 113.37 | 122.34 | AE2-020 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 463 | 563 | 113.37 | 122.75 | AE2-020 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 2 | 230 | 233 | 559 | 680 | 119.12 | 121.77 | AE2-020 | AP_P1-2_PE-500-407T_SRT-SL | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 2 | 230 | 233 | 559 | 680 | 119.12 | 121.77 | AE2-020 | DVP_P1-2: LN 514_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 559 | 680 | 119.12 | 121.77 | AE2-020 | DVP_P1-2: LN 514_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 559 | 680 | 119.12 | 121.77 | AE2-020 | AP_P1-2_PE-500-407T_SRT-SL | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 207922 | BRIS | 207923 | BRISREAC | RX | 230 | 229 | 506 | 618 | 117.78 | 121.8 | AE2-020 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 207923 | BRISREAC | 208132 | WHEM TR1 | 1 | 230 | 229 | 493 | 618 | 117.78 | 121.8 | AE2-020 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 232 | 282 | 116.72 | 121.11 | AE2-020 | PJM_500_BG_P4_5_CNSTN_J_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 232 | 282 | 116.72 | 121.11 | AE2-020 | PJM_500_BG_P1_5011_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 232 | 282 | 116.46 | 120.86 | AE2-020 | PEPCO_P4_PP40_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 207923 | BRISREAC | 208132 | WHEM TR1 | 1 | 230 | 229 | 493 | 618 | 115.13 | 119.54 | AE2-020 | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 207922 | BRIS | 207923 | BRISREAC | RX | 230 | 229 | 506 | 618 | 115.13 | 119.54 | AE2-020 | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 207922 | BRIS | 207923 | BRISREAC | RX | 230 | 229 | 506 | 618 | 115.13 | 119.54 | AE2-020 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 207923 | BRISREAC | 208132 | WHEM TR1 | 1 | 230 | 229 | 493 | 618 | 115.13 | 119.54 | AE2-020 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 207922 | BRIS | 207923 | BRISREAC | RX | 230 | 229 | 506 | 618 | 115.12 | 119.52 | AE2-020 | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 207923 | BRISREAC | 208132 | WHEM TR1 | 1 | 230 | 229 | 493 | 618 | 115.12 | 119.52 | AE2-020 | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 463 | 578 | 110.56 | 118.71 | AE2-020 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.19 | 122.92 | AE2-020 | Base Case | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 121.1 | AE2-020 | PJM_500_BG_P1_5013_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 121.1 | AE2-020 | PJM_500_BG_P4_5_CNSTN_M_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 463 | 578 | 108.07 | 116.62 | AE2-020 | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 463 | 578 | 108.02 | 116.57 | AE2-020 | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 463 | 578 | 108.02 | 116.56 | AE2-020 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 235463 | 01TANEY | 1 | 138 | 227/201 | 221 | 268 | 110.75 | 116.92 | AE2-020 | PJM_500_BG_P4_5_CNSTN_J_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 235463 | 01TANEY | 1 | 138 | 227/201 | 221 | 268 | 110.75 | 116.92 | AE2-020 | PJM_500_BG_P1_5011_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 235463 | 01TANEY | 1 | 138 | 227/201 | 221 | 268 | 110.45 | 116.61 | AE2-020 | PEPCO_P4_PP40_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 709 | 869 | 110.18 | 114.15 | AE2-020 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 463 | 578 | 105.24 | 112.68 | AE2-020 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 647 | 801 | 108.33 | 113.4 | AE2-020 | PECO_P4_PEACH245_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 709 | 869 | 108.55 | 112.74 | AE2-020 | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 709 | 869 | 108.55 | 112.74 | AE2-020 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 709 | 869 | 108.54 | 112.73 | AE2-020 | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 207923 | BRISREAC | 208132 | WHEM TR1 | 1 | 230 | 229 | 493 | 618 | 107.75 | 112.5 | AE2-020 | PECO_P4_PEACH245_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 207922 | BRIS | 207923 | BRISREAC | RX | 230 | 229 | 506 | 618 | 107.75 | 112.5 | AE2-020 | PECO_P4_PEACH245_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 106.71 | 112.17 | AE2-020 | BG_P7_CNSTN_NWEST2_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 463 | 578 | 102.74 | 110.59 | AE2-020 | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 106.17 | 111.26 | AE2-020 | BG_P7_GRCTN_RAPHEL_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 463 | 578 | 102.69 | 110.53 | AE2-020 | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 463 | 578 | 102.69 | 110.53 | AE2-020 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 105.55 | 114.51 | AE2-020 | PN_P1-2_PN-500-010T_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 221092 | FIVE.FOR | 221095 | ROCKRGE2 | 1 | 115 | 232 | 245 | 300 | 107.52 | 108.62 | AE2-020 | BG_P7_GRCTN_RAPHEL_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208131 | WHEM | 208132 | WHEM TR1 | 1 | 230 | 229 | 547 | 618 | 106.32 | 108.82 | AE2-020 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 104.22 | 112.56 | AE2-020 | PJM_500_BG_P4_5_CNSTN_L_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 103.32 | 108.38 | AE2-020 | BG_P7_NEAST_RPHLRD_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204538 | 27STRABAN | 204544 | 27LINCOLN | 1 | 115 | 227 | 257 | 313 | 102.73 | 106.16 | AE2-020 | PJM_500_BG_P4_5_CNSTN_J_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204538 | 27STRABAN | 204544 | 27LINCOLN | 1 | 115 | 227 | 257 | 313 | 102.73 | 106.16 | AE2-020 | PJM_500_BG_P1_5011_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208131 | WHEM | 208132 | WHEM TR1 | 1 | 230 | 229 | 547 | 618 | 103.73 | 106.62 | AE2-020 | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208131 | WHEM | 208132 | WHEM TR1 | 1 | 230 | 229 | 547 | 618 | 103.73 | 106.62 | AE2-020 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208131 | WHEM | 208132 | WHEM TR1 | 1 | 230 | 229 | 547 | 618 | 103.72 | 106.61 | AE2-020 | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204538 | 27STRABAN | 204544 | 27LINCOLN | 1 | 115 | 227 | 257 | 313 | 102.46 | 105.9 | AE2-020 | PEPCO_P4_PP40_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 463 | 563 | 98.5 | 107.31 | AE2-020 | PECO_P4_PEACH245_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 463 | 563 | 98.5 | 107.72 | AE2-020 | PECO_P4_PEACH245_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 221092 | FIVE.FOR | 221094 | GRACE.-1 | 1 | 115 | 232 | 335 | 437 | 103.26 | 104.81 | AE2-020 | BG_P7_GRCTN_RAPHEL_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 101.26 | 105.84 | AE2-020 | AP_P2-3_PE-500-015_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 204550 | 27ORRTANNA | 1 | 115 | 227 | 133 | 160 | 101.04 | 105.8 | AE2-020 | ME_P1-2_ME-115-068_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 709 | 869 | 101.29 | 105.78 | AE2-020 | PECO_P4_PEACH245_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 100.32 | 106.07 | AE2-020 | PJM_500_BG_P4_5_CNSTN_13_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 220964 | GRACETON | 220999 | BAGLEY2 | 13 | 230 | 232 | 1331 | 1594 | 101.97 | 104.66 | AE2-020 | BG_P4_5_GRCTN_3T_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204512 | 27S.RDG | 204693 | 27BOONETOWN | 1 | 230 | 227 | 445 | 531 | 101.56 | 103.7 | AE2-020 | PL_04_P22_102291_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204512 | 27S.RDG | 204693 | 27BOONETOWN | 1 | 230 | 227 | 445 | 531 | 101.56 | 103.7 | AE2-020 | PL_04_P43_102301_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204512 | 27S.RDG | 204693 | 27BOONETOWN | 1 | 230 | 227 | 445 | 531 | 101.52 | 103.7 | AE2-020 | PL_04_P13_101211_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204512 | 27S.RDG | 204693 | 27BOONETOWN | 1 | 230 | 227 | 445 | 531 | 101.52 | 103.7 | AE2-020 | PL_04_P43_102300_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204512 | 27S.RDG | 204693 | 27BOONETOWN | 1 | 230 | 227 | 445 | 531 | 101.52 | 103.7 | AE2-020 | PL_04_P22_102290_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208078 | SAKR | 1 | 230 | 229 | 647 | 801 | 98.95 | 103.69 | AE2-020 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 98.57 | 105.07 | AE2-020 | Base Case | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 232 | 282 | 99.33 | 104.32 | AE2-020 | Base Case | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 221092 | FIVE.FOR | 221095 | ROCKRGE2 | 1 | 115 | 232 | 245 | 300 | 100.57 | 101.24 | AE2-020 | BG_P7_NEAST_RPHLRD_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 97.97 | 106 | AE2-020 | AP_P2-3_PE-500-015_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204539 | 27HUNTRSTN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 232 | 282 | 98.13 | 102.56 | AE2-020 | PJM_500_BG_P4_5_CNSTN_J_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204539 | 27HUNTRSTN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 232 | 282 | 98.13 | 102.56 | AE2-020 | PJM_500_BG_P1_5011_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 220965 | NEAST339 | 220980 | RAPHAEL | 1 | 230 | 232 | 1098 | 1283 | 99.71 | 102.65 | AE2-020 | BG_P4_5_NEAST_17_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 220965 | NEAST339 | 220980 | RAPHAEL | 1 | 230 | 232 | 1098 | 1283 | 99.71 | 102.72 | AE2-020 | BG_P4_5_NEAST_15_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204539 | 27HUNTRSTN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 232 | 282 | 97.87 | 102.3 | AE2-020 | PEPCO_P4_PP40_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 220965 | NEAST339 | 220980 | RAPHAEL | 1 | 230 | 232 | 1098 | 1283 | 99.42 | 102.48 | AE2-020 | BG_P1_2315_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 204550 | 27ORRTANNA | 1 | 115 | 227 | 133 | 160 | 98.04 | 102.2 | AE2-020 | ME_P2-3_ME-115-035A_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 220979 | NEAST317 | 220980 | RAPHAEL | 1 | 230 | 232 | 1098 | 1283 | 99.26 | 102.22 | AE2-020 | BG_P4_5_NEAST_39_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 220979 | NEAST317 | 220980 | RAPHAEL | 1 | 230 | 232 | 1098 | 1283 | 99.26 | 102.22 | AE2-020 | BG_P4_5_NEAST_37_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 204550 | 27ORRTANNA | 1 | 115 | 227 | 133 | 160 | 97.89 | 102.69 | AE2-020 | ME_P2-3_ME-115-013B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 220979 | NEAST317 | 220980 | RAPHAEL | 1 | 230 | 232 | 1098 | 1283 | 98.92 | 101.95 | AE2-020 | BG_P1_2337_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 204550 | 27ORRTANNA | 1 | 115 | 227 | 133 | 160 | 97.47 | 102.27 | AE2-020 | ME_P2-3_ME-115-013A_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 463 | 578 | 93.52 | 101.93 | AE2-020 | PECO_P4_PEACH245_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204529 | 27GERMANTN | 204538 | 27STRABAN | 1 | 115 | 227 | 257 | 313 | 96.79 | 99.78 | AE2-020 | PJM_500_BG_P4_5_CNSTN_J_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204529 | 27GERMANTN | 204538 | 27STRABAN | 1 | 115 | 227 | 257 | 313 | 96.79 | 99.78 | AE2-020 | PJM_500_BG_P1_5011_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208078 | SAKR | 1 | 230 | 229 | 647 | 801 | 96.31 | 101.4 | AE2-020 | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208078 | SAKR | 1 | 230 | 229 | 647 | 801 | 96.31 | 101.4 | AE2-020 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208078 | SAKR | 1 | 230 | 229 | 647 | 801 | 96.3 | 101.4 | AE2-020 | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208131 | WHEM | 208133 | WHEM TR2 | 1 | 230 | 229 | 547 | 618 | 97.75 | 100.45 | AE2-020 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204529 | 27GERMANTN | 204538 | 27STRABAN | 1 | 115 | 227 | 257 | 313 | 96.52 | 99.52 | AE2-020 | PEPCO_P4_PP40_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 232 | 282 | 97.98 | 101.64 | AE2-020 | AP_P2-3_PE-500-015_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 228.49 | 245.31 | AE2-021 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 224.05 | 240.71 | AE2-021 | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 224.05 | 240.71 | AE2-021 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 224.03 | 240.68 | AE2-021 | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 209.21 | 224.08 | AE2-021 | PECO_P4_PEACH245_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 202.97 | 218.3 | AE2-021 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 198.66 | 213.8 | AE2-021 | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 198.66 | 213.8 | AE2-021 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 198.64 | 213.77 | AE2-021 | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 183.92 | 197.39 | AE2-021 | PECO_P4_PEACH245_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 166.62 | 171.82 | AE2-021 | Base Case | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 221089 | WINDYED1 | 221090 | GLENARM2 | 1 | 115 | 232 | 148 | 192 | 141.81 | 143.57 | AE2-021 | BG_P7_GRCTN_RAPHEL_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 221092 | FIVE.FOR | 221096 | ROCKRGE1 | 1 | 115 | 232 | 229 | 256 | 135.39 | 136.16 | AE2-021 | BG_P7_GRCTN_RAPHEL_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 221089 | WINDYED1 | 221090 | GLENARM2 | 1 | 115 | 232 | 148 | 192 | 131 | 132.05 | AE2-021 | BG_P7_NEAST_RPHLRD_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 130.65 | 134 | AE2-021 | Base Case | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 559 | 680 | 129.8 | 133.8 | AE2-021 | PEPCO_P1_PP2_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 2 | 230 | 233 | 559 | 680 | 129.8 | 133.8 | AE2-021 | PEPCO_P1_PP1_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 221092 | FIVE.FOR | 221096 | ROCKRGE1 | 1 | 115 | 232 | 229 | 256 | 127.23 | 127.55 | AE2-021 | BG_P7_NEAST_RPHLRD_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 647 | 801 | 122.17 | 126.53 | AE2-021 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 559 | 680 | 122.19 | 124.66 | AE2-021 | DVP_P4-2: 514T595_SRT-SW | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 2 | 230 | 233 | 559 | 680 | 122.19 | 124.66 | AE2-021 | DVP_P4-2: 514T595_SRT-SW | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 463 | 563 | 115.98 | 124.95 | AE2-021 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 463 | 563 | 115.98 | 124.54 | AE2-021 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 559 | 680 | 119.41 | 121.77 | AE2-021 | DVP_P4-2: 51482_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 2 | 230 | 233 | 559 | 680 | 119.41 | 121.77 | AE2-021 | DVP_P4-2: 51482_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 463 | 563 | 113.42 | 122.4 | AE2-021 | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 463 | 563 | 113.42 | 122.81 | AE2-021 | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 647 | 801 | 117.38 | 122.34 | AE2-021 | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 647 | 801 | 117.38 | 122.34 | AE2-021 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 647 | 801 | 117.37 | 122.32 | AE2-021 | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 463 | 563 | 113.37 | 122.34 | AE2-021 | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 463 | 563 | 113.37 | 122.75 | AE2-021 | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 463 | 563 | 113.37 | 122.34 | AE2-021 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 463 | 563 | 113.37 | 122.75 | AE2-021 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 2 | 230 | 233 | 559 | 680 | 119.12 | 121.77 | AE2-021 | AP_P1-2_PE-500-407T_SRT-SL | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 2 | 230 | 233 | 559 | 680 | 119.12 | 121.77 | AE2-021 | DVP_P1-2: LN 514_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 559 | 680 | 119.12 | 121.77 | AE2-021 | DVP_P1-2: LN 514_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 559 | 680 | 119.12 | 121.77 | AE2-021 | AP_P1-2_PE-500-407T_SRT-SL | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 207922 | BRIS | 207923 | BRISREAC | RX | 230 | 229 | 506 | 618 | 117.78 | 121.8 | AE2-021 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 207923 | BRISREAC | 208132 | WHEM TR1 | 1 | 230 | 229 | 493 | 618 | 117.78 | 121.8 | AE2-021 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 232 | 282 | 116.72 | 121.11 | AE2-021 | PJM_500_BG_P4_5_CNSTN_J_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 232 | 282 | 116.72 | 121.11 | AE2-021 | PJM_500_BG_P1_5011_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 232 | 282 | 116.46 | 120.86 | AE2-021 | PEPCO_P4_PP40_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 207923 | BRISREAC | 208132 | WHEM TR1 | 1 | 230 | 229 | 493 | 618 | 115.13 | 119.54 | AE2-021 | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 207922 | BRIS | 207923 | BRISREAC | RX | 230 | 229 | 506 | 618 | 115.13 | 119.54 | AE2-021 | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 207922 | BRIS | 207923 | BRISREAC | RX | 230 | 229 | 506 | 618 | 115.13 | 119.54 | AE2-021 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 207923 | BRISREAC | 208132 | WHEM TR1 | 1 | 230 | 229 | 493 | 618 | 115.13 | 119.54 | AE2-021 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 207922 | BRIS | 207923 | BRISREAC | RX | 230 | 229 | 506 | 618 | 115.12 | 119.52 | AE2-021 | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 207923 | BRISREAC | 208132 | WHEM TR1 | 1 | 230 | 229 | 493 | 618 | 115.12 | 119.52 | AE2-021 | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 463 | 578 | 110.56 | 118.71 | AE2-021 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.19 | 122.92 | AE2-021 | Base Case | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 121.1 | AE2-021 | PJM_500_BG_P1_5013_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 121.1 | AE2-021 | PJM_500_BG_P4_5_CNSTN_M_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 463 | 578 | 108.07 | 116.62 | AE2-021 | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 463 | 578 | 108.02 | 116.57 | AE2-021 | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 463 | 578 | 108.02 | 116.56 | AE2-021 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 235463 | 01TANEY | 1 | 138 | 227/201 | 221 | 268 | 110.75 | 116.92 | AE2-021 | PJM_500_BG_P4_5_CNSTN_J_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 235463 | 01TANEY | 1 | 138 | 227/201 | 221 | 268 | 110.75 | 116.92 | AE2-021 | PJM_500_BG_P1_5011_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 235463 | 01TANEY | 1 | 138 | 227/201 | 221 | 268 | 110.45 | 116.61 | AE2-021 | PEPCO_P4_PP40_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 709 | 869 | 110.18 | 114.15 | AE2-021 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 463 | 578 | 105.24 | 112.68 | AE2-021 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 647 | 801 | 108.33 | 113.4 | AE2-021 | PECO_P4_PEACH245_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 709 | 869 | 108.55 | 112.74 | AE2-021 | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 709 | 869 | 108.55 | 112.74 | AE2-021 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 709 | 869 | 108.54 | 112.73 | AE2-021 | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 207923 | BRISREAC | 208132 | WHEM TR1 | 1 | 230 | 229 | 493 | 618 | 107.75 | 112.5 | AE2-021 | PECO_P4_PEACH245_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 207922 | BRIS | 207923 | BRISREAC | RX | 230 | 229 | 506 | 618 | 107.75 | 112.5 | AE2-021 | PECO_P4_PEACH245_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 106.71 | 112.17 | AE2-021 | BG_P7_CNSTN_NWEST2_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 463 | 578 | 102.74 | 110.59 | AE2-021 | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 106.17 | 111.26 | AE2-021 | BG_P7_GRCTN_RAPHEL_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 463 | 578 | 102.69 | 110.53 | AE2-021 | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 463 | 578 | 102.69 | 110.53 | AE2-021 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 105.55 | 114.51 | AE2-021 | PN_P1-2_PN-500-010T_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 221092 | FIVE.FOR | 221095 | ROCKRGE2 | 1 | 115 | 232 | 245 | 300 | 107.52 | 108.62 | AE2-021 | BG_P7_GRCTN_RAPHEL_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208131 | WHEM | 208132 | WHEM TR1 | 1 | 230 | 229 | 547 | 618 | 106.32 | 108.82 | AE2-021 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 104.22 | 112.56 | AE2-021 | PJM_500_BG_P4_5_CNSTN_L_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 103.32 | 108.38 | AE2-021 | BG_P7_NEAST_RPHLRD_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204538 | 27STRABAN | 204544 | 27LINCOLN | 1 | 115 | 227 | 257 | 313 | 102.73 | 106.16 | AE2-021 | PJM_500_BG_P4_5_CNSTN_J_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204538 | 27STRABAN | 204544 | 27LINCOLN | 1 | 115 | 227 | 257 | 313 | 102.73 | 106.16 | AE2-021 | PJM_500_BG_P1_5011_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208131 | WHEM | 208132 | WHEM TR1 | 1 | 230 | 229 | 547 | 618 | 103.73 | 106.62 | AE2-021 | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208131 | WHEM | 208132 | WHEM TR1 | 1 | 230 | 229 | 547 | 618 | 103.73 | 106.62 | AE2-021 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208131 | WHEM | 208132 | WHEM TR1 | 1 | 230 | 229 | 547 | 618 | 103.72 | 106.61 | AE2-021 | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204538 | 27STRABAN | 204544 | 27LINCOLN | 1 | 115 | 227 | 257 | 313 | 102.46 | 105.9 | AE2-021 | PEPCO_P4_PP40_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 463 | 563 | 98.5 | 107.31 | AE2-021 | PECO_P4_PEACH245_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 463 | 563 | 98.5 | 107.72 | AE2-021 | PECO_P4_PEACH245_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 221092 | FIVE.FOR | 221094 | GRACE.-1 | 1 | 115 | 232 | 335 | 437 | 103.26 | 104.81 | AE2-021 | BG_P7_GRCTN_RAPHEL_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 101.26 | 105.84 | AE2-021 | AP_P2-3_PE-500-015_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 204550 | 27ORRTANNA | 1 | 115 | 227 | 133 | 160 | 101.04 | 105.8 | AE2-021 | ME_P1-2_ME-115-068_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 709 | 869 | 101.29 | 105.78 | AE2-021 | PECO_P4_PEACH245_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 100.32 | 106.07 | AE2-021 | PJM_500_BG_P4_5_CNSTN_13_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 220964 | GRACETON | 220999 | BAGLEY2 | 13 | 230 | 232 | 1331 | 1594 | 101.97 | 104.66 | AE2-021 | BG_P4_5_GRCTN_3T_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204512 | 27S.RDG | 204693 | 27BOONETOWN | 1 | 230 | 227 | 445 | 531 | 101.56 | 103.7 | AE2-021 | PL_04_P22_102291_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204512 | 27S.RDG | 204693 | 27BOONETOWN | 1 | 230 | 227 | 445 | 531 | 101.56 | 103.7 | AE2-021 | PL_04_P43_102301_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204512 | 27S.RDG | 204693 | 27BOONETOWN | 1 | 230 | 227 | 445 | 531 | 101.52 | 103.7 | AE2-021 | PL_04_P13_101211_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204512 | 27S.RDG | 204693 | 27BOONETOWN | 1 | 230 | 227 | 445 | 531 | 101.52 | 103.7 | AE2-021 | PL_04_P43_102300_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204512 | 27S.RDG | 204693 | 27BOONETOWN | 1 | 230 | 227 | 445 | 531 | 101.52 | 103.7 | AE2-021 | PL_04_P22_102290_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208078 | SAKR | 1 | 230 | 229 | 647 | 801 | 98.95 | 103.69 | AE2-021 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 98.57 | 105.07 | AE2-021 | Base Case | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 232 | 282 | 99.33 | 104.32 | AE2-021 | Base Case | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 221092 | FIVE.FOR | 221095 | ROCKRGE2 | 1 | 115 | 232 | 245 | 300 | 100.57 | 101.24 | AE2-021 | BG_P7_NEAST_RPHLRD_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 97.97 | 106 | AE2-021 | AP_P2-3_PE-500-015_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204539 | 27HUNTRSTN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 232 | 282 | 98.13 | 102.56 | AE2-021 | PJM_500_BG_P4_5_CNSTN_J_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204539 | 27HUNTRSTN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 232 | 282 | 98.13 | 102.56 | AE2-021 | PJM_500_BG_P1_5011_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 220965 | NEAST339 | 220980 | RAPHAEL | 1 | 230 | 232 | 1098 | 1283 | 99.71 | 102.65 | AE2-021 | BG_P4_5_NEAST_17_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 220965 | NEAST339 | 220980 | RAPHAEL | 1 | 230 | 232 | 1098 | 1283 | 99.71 | 102.72 | AE2-021 | BG_P4_5_NEAST_15_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204539 | 27HUNTRSTN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 232 | 282 | 97.87 | 102.3 | AE2-021 | PEPCO_P4_PP40_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 220965 | NEAST339 | 220980 | RAPHAEL | 1 | 230 | 232 | 1098 | 1283 | 99.42 | 102.48 | AE2-021 | BG_P1_2315_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 204550 | 27ORRTANNA | 1 | 115 | 227 | 133 | 160 | 98.04 | 102.2 | AE2-021 | ME_P2-3_ME-115-035A_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 220979 | NEAST317 | 220980 | RAPHAEL | 1 | 230 | 232 | 1098 | 1283 | 99.26 | 102.22 | AE2-021 | BG_P4_5_NEAST_39_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 220979 | NEAST317 | 220980 | RAPHAEL | 1 | 230 | 232 | 1098 | 1283 | 99.26 | 102.22 | AE2-021 | BG_P4_5_NEAST_37_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 204550 | 27ORRTANNA | 1 | 115 | 227 | 133 | 160 | 97.89 | 102.69 | AE2-021 | ME_P2-3_ME-115-013B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 220979 | NEAST317 | 220980 | RAPHAEL | 1 | 230 | 232 | 1098 | 1283 | 98.92 | 101.95 | AE2-021 | BG_P1_2337_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 204550 | 27ORRTANNA | 1 | 115 | 227 | 133 | 160 | 97.47 | 102.27 | AE2-021 | ME_P2-3_ME-115-013A_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 463 | 578 | 93.52 | 101.93 | AE2-021 | PECO_P4_PEACH245_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204529 | 27GERMANTN | 204538 | 27STRABAN | 1 | 115 | 227 | 257 | 313 | 96.79 | 99.78 | AE2-021 | PJM_500_BG_P4_5_CNSTN_J_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204529 | 27GERMANTN | 204538 | 27STRABAN | 1 | 115 | 227 | 257 | 313 | 96.79 | 99.78 | AE2-021 | PJM_500_BG_P1_5011_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208078 | SAKR | 1 | 230 | 229 | 647 | 801 | 96.31 | 101.4 | AE2-021 | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208078 | SAKR | 1 | 230 | 229 | 647 | 801 | 96.31 | 101.4 | AE2-021 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208078 | SAKR | 1 | 230 | 229 | 647 | 801 | 96.3 | 101.4 | AE2-021 | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208131 | WHEM | 208133 | WHEM TR2 | 1 | 230 | 229 | 547 | 618 | 97.75 | 100.45 | AE2-021 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204529 | 27GERMANTN | 204538 | 27STRABAN | 1 | 115 | 227 | 257 | 313 | 96.52 | 99.52 | AE2-021 | PEPCO_P4_PP40_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 232 | 282 | 97.98 | 101.64 | AE2-021 | AP_P2-3_PE-500-015_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 228.49 | 242 | AE2-022 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 224.05 | 237.28 | AE2-022 | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 224.05 | 237.28 | AE2-022 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 224.03 | 237.25 | AE2-022 | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 209.21 | 220.61 | AE2-022 | PECO_P4_PEACH245_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 202.97 | 215.03 | AE2-022 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 198.66 | 210.41 | AE2-022 | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 198.66 | 210.41 | AE2-022 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 198.64 | 210.39 | AE2-022 | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 183.92 | 193.97 | AE2-022 | PECO_P4_PEACH245_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 166.62 | 170.44 | AE2-022 | Base Case | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 130.65 | 132.7 | AE2-022 | Base Case | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 647 | 801 | 122.17 | 124.87 | AE2-022 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 559 | 680 | 122.19 | 123.82 | AE2-022 | DVP_P4-2: 514T595_SRT-SW | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 2 | 230 | 233 | 559 | 680 | 122.19 | 123.82 | AE2-022 | DVP_P4-2: 514T595_SRT-SW | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 559 | 680 | 119.41 | 120.9 | AE2-022 | DVP_P4-2: 51482_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 2 | 230 | 233 | 559 | 680 | 119.41 | 120.9 | AE2-022 | DVP_P4-2: 51482_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 2 | 230 | 233 | 559 | 680 | 119.12 | 120.9 | AE2-022 | DVP_P1-2: LN 514_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 559 | 680 | 119.12 | 120.9 | AE2-022 | AP_P1-2_PE-500-407T_SRT-SL | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 559 | 680 | 119.12 | 120.9 | AE2-022 | DVP_P1-2: LN 514_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 2 | 230 | 233 | 559 | 680 | 119.12 | 120.9 | AE2-022 | AP_P1-2_PE-500-407T_SRT-SL | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 463 | 563 | 115.98 | 121.26 | AE2-022 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 463 | 563 | 115.98 | 120.88 | AE2-022 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 207922 | BRIS | 207923 | BRISREAC | RX | 230 | 229 | 506 | 618 | 117.78 | 120.45 | AE2-022 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 207923 | BRISREAC | 208132 | WHEM TR1 | 1 | 230 | 229 | 493 | 618 | 117.78 | 120.45 | AE2-022 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 647 | 801 | 117.38 | 120.56 | AE2-022 | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 647 | 801 | 117.38 | 120.56 | AE2-022 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 647 | 801 | 117.37 | 120.54 | AE2-022 | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 232 | 282 | 116.72 | 119.18 | AE2-022 | PJM_500_BG_P4_5_CNSTN_J_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 232 | 282 | 116.72 | 119.18 | AE2-022 | PJM_500_BG_P1_5011_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 232 | 282 | 116.46 | 118.92 | AE2-022 | PEPCO_P4_PP40_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 463 | 563 | 113.42 | 119.06 | AE2-022 | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 463 | 563 | 113.42 | 118.69 | AE2-022 | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 463 | 563 | 113.37 | 118.63 | AE2-022 | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 463 | 563 | 113.37 | 119 | AE2-022 | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 463 | 563 | 113.37 | 119 | AE2-022 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 463 | 563 | 113.37 | 118.63 | AE2-022 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 207922 | BRIS | 207923 | BRISREAC | RX | 230 | 229 | 506 | 618 | 115.13 | 118.13 | AE2-022 | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 207923 | BRISREAC | 208132 | WHEM TR1 | 1 | 230 | 229 | 493 | 618 | 115.13 | 118.13 | AE2-022 | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 207922 | BRIS | 207923 | BRISREAC | RX | 230 | 229 | 506 | 618 | 115.13 | 118.12 | AE2-022 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 207923 | BRISREAC | 208132 | WHEM TR1 | 1 | 230 | 229 | 493 | 618 | 115.13 | 118.12 | AE2-022 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 207922 | BRIS | 207923 | BRISREAC | RX | 230 | 229 | 506 | 618 | 115.12 | 118.11 | AE2-022 | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 207923 | BRISREAC | 208132 | WHEM TR1 | 1 | 230 | 229 | 493 | 618 | 115.12 | 118.11 | AE2-022 | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.19 | 120.04 | AE2-022 | Base Case | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 119.05 | AE2-022 | PJM_500_BG_P1_5013_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 119.04 | AE2-022 | PJM_500_BG_P4_5_CNSTN_M_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 463 | 578 | 110.56 | 115.15 | AE2-022 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 235463 | 01TANEY | 1 | 138 | 227/201 | 221 | 268 | 110.75 | 114.67 | AE2-022 | PJM_500_BG_P4_5_CNSTN_J_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 235463 | 01TANEY | 1 | 138 | 227/201 | 221 | 268 | 110.75 | 114.67 | AE2-022 | PJM_500_BG_P1_5011_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 235463 | 01TANEY | 1 | 138 | 227/201 | 221 | 268 | 110.45 | 114.36 | AE2-022 | PEPCO_P4_PP40_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 463 | 578 | 108.07 | 113.01 | AE2-022 | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 463 | 578 | 108.02 | 112.95 | AE2-022 | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 463 | 578 | 108.02 | 112.95 | AE2-022 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 709 | 869 | 110.18 | 112.75 | AE2-022 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 647 | 801 | 108.33 | 111.6 | AE2-022 | PECO_P4_PEACH245_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 709 | 869 | 108.55 | 111.3 | AE2-022 | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 709 | 869 | 108.55 | 111.3 | AE2-022 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 709 | 869 | 108.54 | 111.29 | AE2-022 | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 207923 | BRISREAC | 208132 | WHEM TR1 | 1 | 230 | 229 | 493 | 618 | 107.75 | 111.07 | AE2-022 | PECO_P4_PEACH245_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 207922 | BRIS | 207923 | BRISREAC | RX | 230 | 229 | 506 | 618 | 107.75 | 111.07 | AE2-022 | PECO_P4_PEACH245_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 463 | 578 | 105.24 | 109.12 | AE2-022 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 106.71 | 110.29 | AE2-022 | BG_P7_CNSTN_NWEST2_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 106.17 | 109.39 | AE2-022 | BG_P7_GRCTN_RAPHEL_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208131 | WHEM | 208132 | WHEM TR1 | 1 | 230 | 229 | 547 | 618 | 106.32 | 107.53 | AE2-022 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 105.55 | 112.43 | AE2-022 | PN_P1-2_PN-500-010T_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 559 | 680 | 105.77 | 108.44 | AE2-022 | PEPCO_P4_PP19_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 463 | 578 | 102.74 | 106.98 | AE2-022 | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 463 | 578 | 102.69 | 106.92 | AE2-022 | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 463 | 578 | 102.69 | 106.92 | AE2-022 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 104.22 | 110.59 | AE2-022 | PJM_500_BG_P4_5_CNSTN_L_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 103.32 | 106.51 | AE2-022 | BG_P7_NEAST_RPHLRD_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208131 | WHEM | 208132 | WHEM TR1 | 1 | 230 | 229 | 547 | 618 | 103.73 | 105.26 | AE2-022 | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208131 | WHEM | 208132 | WHEM TR1 | 1 | 230 | 229 | 547 | 618 | 103.73 | 105.26 | AE2-022 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208131 | WHEM | 208132 | WHEM TR1 | 1 | 230 | 229 | 547 | 618 | 103.72 | 105.25 | AE2-022 | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204538 | 27STRABAN | 204544 | 27LINCOLN | 1 | 115 | 227 | 257 | 313 | 102.73 | 104.22 | AE2-022 | PJM_500_BG_P4_5_CNSTN_J_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204538 | 27STRABAN | 204544 | 27LINCOLN | 1 | 115 | 227 | 257 | 313 | 102.73 | 104.22 | AE2-022 | PJM_500_BG_P1_5011_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204538 | 27STRABAN | 204544 | 27LINCOLN | 1 | 115 | 227 | 257 | 313 | 102.46 | 103.96 | AE2-022 | PEPCO_P4_PP40_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 2 | 230 | 233 | 559 | 680 | 102.87 | 104.58 | AE2-022 | AP_P2-3_PE-500-019C_SRT-SL | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 220964 | GRACETON | 220999 | BAGLEY2 | 13 | 230 | 232 | 1331 | 1594 | 101.97 | 103.7 | AE2-022 | BG_P4_5_GRCTN_3T_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 101.26 | 104.19 | AE2-022 | AP_P2-3_PE-500-015_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 709 | 869 | 101.29 | 104.33 | AE2-022 | PECO_P4_PEACH245_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204512 | 27S.RDG | 204693 | 27BOONETOWN | 1 | 230 | 227 | 445 | 531 | 101.56 | 102.68 | AE2-022 | PL_04_P22_102291_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204512 | 27S.RDG | 204693 | 27BOONETOWN | 1 | 230 | 227 | 445 | 531 | 101.56 | 102.68 | AE2-022 | PL_04_P43_102301_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204512 | 27S.RDG | 204693 | 27BOONETOWN | 1 | 230 | 227 | 445 | 531 | 101.52 | 102.68 | AE2-022 | PL_04_P13_101211_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204512 | 27S.RDG | 204693 | 27BOONETOWN | 1 | 230 | 227 | 445 | 531 | 101.52 | 102.68 | AE2-022 | PL_04_P22_102290_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204512 | 27S.RDG | 204693 | 27BOONETOWN | 1 | 230 | 227 | 445 | 531 | 101.52 | 102.68 | AE2-022 | PL_04_P43_102300_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 463 | 563 | 98.5 | 103.95 | AE2-022 | PECO_P4_PEACH245_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 463 | 563 | 98.5 | 103.57 | AE2-022 | PECO_P4_PEACH245_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 100.32 | 104.28 | AE2-022 | PJM_500_BG_P4_5_CNSTN_13_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208078 | SAKR | 1 | 230 | 229 | 647 | 801 | 98.95 | 101.61 | AE2-022 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 220965 | NEAST339 | 220980 | RAPHAEL | 1 | 230 | 232 | 1098 | 1283 | 99.71 | 101.53 | AE2-022 | BG_P4_5_NEAST_17_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 220965 | NEAST339 | 220980 | RAPHAEL | 1 | 230 | 232 | 1098 | 1283 | 99.71 | 101.6 | AE2-022 | BG_P4_5_NEAST_15_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 220965 | NEAST339 | 220980 | RAPHAEL | 1 | 230 | 232 | 1098 | 1283 | 99.42 | 101.35 | AE2-022 | BG_P1_2315_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 98.57 | 103.15 | AE2-022 | Base Case | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 220979 | NEAST317 | 220980 | RAPHAEL | 1 | 230 | 232 | 1098 | 1283 | 99.26 | 101.12 | AE2-022 | BG_P4_5_NEAST_39_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 220979 | NEAST317 | 220980 | RAPHAEL | 1 | 230 | 232 | 1098 | 1283 | 99.26 | 101.12 | AE2-022 | BG_P4_5_NEAST_37_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 97.97 | 103.71 | AE2-022 | AP_P2-3_PE-500-015_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204539 | 27HUNTRSTN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 232 | 282 | 98.13 | 100.58 | AE2-022 | PJM_500_BG_P4_5_CNSTN_J_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204539 | 27HUNTRSTN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 232 | 282 | 98.13 | 100.58 | AE2-022 | PJM_500_BG_P1_5011_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 220979 | NEAST317 | 220980 | RAPHAEL | 1 | 230 | 232 | 1098 | 1283 | 98.92 | 100.83 | AE2-022 | BG_P1_2337_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 116.78 | AE2-027 | PJM_500_BG_P1_5013_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 116.78 | AE2-027 | PJM_500_BG_P4_5_CNSTN_M_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.19 | 116.9 | AE2-027 | Base Case | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 106.71 | 108.17 | AE2-027 | BG_P7_CNSTN_NWEST2_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 106.17 | 107.28 | AE2-027 | BG_P7_GRCTN_RAPHEL_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 105.55 | 110.14 | AE2-027 | PN_P1-2_PN-500-010T_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 104.22 | 108.41 | AE2-027 | PJM_500_BG_P4_5_CNSTN_L_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 103.32 | 104.41 | AE2-027 | BG_P7_NEAST_RPHLRD_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 101.26 | 102.31 | AE2-027 | AP_P2-3_PE-500-015_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 100.32 | 102.25 | AE2-027 | PJM_500_BG_P4_5_CNSTN_13_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 117.28 | AE2-046 | PJM_500_BG_P1_5013_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 117.28 | AE2-046 | PJM_500_BG_P4_5_CNSTN_M_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.19 | 117.54 | AE2-046 | Base Case | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 106.71 | 108.71 | AE2-046 | BG_P7_CNSTN_NWEST2_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 106.17 | 107.82 | AE2-046 | BG_P7_GRCTN_RAPHEL_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 105.55 | 110.64 | AE2-046 | PN_P1-2_PN-500-010T_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 104.22 | 108.89 | AE2-046 | PJM_500_BG_P4_5_CNSTN_L_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 103.32 | 104.94 | AE2-046 | BG_P7_NEAST_RPHLRD_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 101.26 | 102.8 | AE2-046 | AP_P2-3_PE-500-015_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 100.32 | 102.76 | AE2-046 | PJM_500_BG_P4_5_CNSTN_13_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200009 | JUNI | 208004 | JUNI | 2 | 500/230 | 229 | 776 | 1010 | 108.85 | 110.11 | AE2-060 | PL_10_P42_000140_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 117.26 | AE2-093 | PJM_500_BG_P1_5013_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 117.26 | AE2-093 | PJM_500_BG_P4_5_CNSTN_M_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.19 | 117.54 | AE2-093 | Base Case | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 106.71 | 108.65 | AE2-093 | BG_P7_CNSTN_NWEST2_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 106.17 | 107.76 | AE2-093 | BG_P7_GRCTN_RAPHEL_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 105.55 | 110.63 | AE2-093 | PN_P1-2_PN-500-010T_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 104.22 | 108.87 | AE2-093 | PJM_500_BG_P4_5_CNSTN_L_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 103.32 | 104.88 | AE2-093 | BG_P7_NEAST_RPHLRD_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 101.26 | 102.75 | AE2-093 | AP_P2-3_PE-500-015_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 100.32 | 102.71 | AE2-093 | PJM_500_BG_P4_5_CNSTN_13_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 116.74 | AE2-206 | PJM_500_BG_P1_5013_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 116.74 | AE2-206 | PJM_500_BG_P4_5_CNSTN_M_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.19 | 116.8 | AE2-206 | Base Case | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 106.71 | 108.17 | AE2-206 | BG_P7_CNSTN_NWEST2_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 106.17 | 107.27 | AE2-206 | BG_P7_GRCTN_RAPHEL_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 105.55 | 110.11 | AE2-206 | PN_P1-2_PN-500-010T_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 104.22 | 108.37 | AE2-206 | PJM_500_BG_P4_5_CNSTN_L_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 103.32 | 104.4 | AE2-206 | BG_P7_NEAST_RPHLRD_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 101.26 | 102.33 | AE2-206 | AP_P2-3_PE-500-015_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 100.32 | 102.25 | AE2-206 | PJM_500_BG_P4_5_CNSTN_13_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 228.49 | 237.85 | AE2-217 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 224.05 | 232.98 | AE2-217 | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 224.05 | 232.98 | AE2-217 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 224.03 | 232.95 | AE2-217 | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 209.21 | 216.31 | AE2-217 | PECO_P4_PEACH245_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 202.97 | 210.96 | AE2-217 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 198.66 | 206.2 | AE2-217 | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 198.66 | 206.2 | AE2-217 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 198.64 | 206.17 | AE2-217 | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 183.92 | 189.75 | AE2-217 | PECO_P4_PEACH245_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 116.55 | AE2-217 | PJM_500_BG_P1_5013_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 116.54 | AE2-217 | PJM_500_BG_P4_5_CNSTN_M_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.19 | 116.53 | AE2-217 | Base Case | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 106.71 | 107.98 | AE2-217 | BG_P7_CNSTN_NWEST2_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 106.17 | 107.09 | AE2-217 | BG_P7_GRCTN_RAPHEL_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 105.55 | 109.92 | AE2-217 | PN_P1-2_PN-500-010T_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 104.22 | 108.18 | AE2-217 | PJM_500_BG_P4_5_CNSTN_L_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 103.32 | 104.22 | AE2-217 | BG_P7_NEAST_RPHLRD_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 101.26 | 102.18 | AE2-217 | AP_P2-3_PE-500-015_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 228.49 | 237.83 | AE2-218 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 224.05 | 232.97 | AE2-218 | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 224.05 | 232.97 | AE2-218 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 224.03 | 232.94 | AE2-218 | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 209.21 | 216.29 | AE2-218 | PECO_P4_PEACH245_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 202.97 | 210.95 | AE2-218 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 198.66 | 206.18 | AE2-218 | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 198.66 | 206.18 | AE2-218 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 198.64 | 206.16 | AE2-218 | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 183.92 | 189.74 | AE2-218 | PECO_P4_PEACH245_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 116.54 | AE2-218 | PJM_500_BG_P1_5013_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 116.54 | AE2-218 | PJM_500_BG_P4_5_CNSTN_M_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.19 | 116.53 | AE2-218 | Base Case | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 106.71 | 107.97 | AE2-218 | BG_P7_CNSTN_NWEST2_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 106.17 | 107.08 | AE2-218 | BG_P7_GRCTN_RAPHEL_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 105.55 | 109.91 | AE2-218 | PN_P1-2_PN-500-010T_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 104.22 | 108.18 | AE2-218 | PJM_500_BG_P4_5_CNSTN_L_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 103.32 | 104.21 | AE2-218 | BG_P7_NEAST_RPHLRD_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 101.26 | 102.16 | AE2-218 | AP_P2-3_PE-500-015_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 116.69 | AE2-221 | PJM_500_BG_P1_5013_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 116.69 | AE2-221 | PJM_500_BG_P4_5_CNSTN_M_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.19 | 116.74 | AE2-221 | Base Case | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 106.71 | 108.12 | AE2-221 | BG_P7_CNSTN_NWEST2_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 106.17 | 107.22 | AE2-221 | BG_P7_GRCTN_RAPHEL_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 105.55 | 110.06 | AE2-221 | PN_P1-2_PN-500-010T_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 104.22 | 108.32 | AE2-221 | PJM_500_BG_P4_5_CNSTN_L_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 103.32 | 104.35 | AE2-221 | BG_P7_NEAST_RPHLRD_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 101.26 | 102.28 | AE2-221 | AP_P2-3_PE-500-015_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 100.32 | 102.2 | AE2-221 | PJM_500_BG_P4_5_CNSTN_13_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 116.78 | AE2-230 | PJM_500_BG_P1_5013_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 116.78 | AE2-230 | PJM_500_BG_P4_5_CNSTN_M_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.19 | 116.91 | AE2-230 | Base Case | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 106.71 | 108.17 | AE2-230 | BG_P7_CNSTN_NWEST2_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 106.17 | 107.28 | AE2-230 | BG_P7_GRCTN_RAPHEL_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 105.55 | 110.14 | AE2-230 | PN_P1-2_PN-500-010T_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 104.22 | 108.41 | AE2-230 | PJM_500_BG_P4_5_CNSTN_L_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 103.32 | 104.41 | AE2-230 | BG_P7_NEAST_RPHLRD_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 101.26 | 102.31 | AE2-230 | AP_P2-3_PE-500-015_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 100.32 | 102.25 | AE2-230 | PJM_500_BG_P4_5_CNSTN_13_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 116.85 | AE2-253 | PJM_500_BG_P1_5013_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 116.85 | AE2-253 | PJM_500_BG_P4_5_CNSTN_M_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 116.84 | AE2-297 | PJM_500_BG_P1_5013_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 116.84 | AE2-297 | PJM_500_BG_P4_5_CNSTN_M_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.19 | 116.94 | AE2-297 | Base Case | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 105.55 | 110.2 | AE2-297 | PN_P1-2_PN-500-010T_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 104.22 | 108.46 | AE2-297 | PJM_500_BG_P4_5_CNSTN_L_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 116.82 | AE2-333 | PJM_500_BG_P1_5013_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 116.82 | AE2-333 | PJM_500_BG_P4_5_CNSTN_M_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.19 | 116.96 | AE2-333 | Base Case | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 106.71 | 108.22 | AE2-333 | BG_P7_CNSTN_NWEST2_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 106.17 | 107.33 | AE2-333 | BG_P7_GRCTN_RAPHEL_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 105.55 | 110.19 | AE2-333 | PN_P1-2_PN-500-010T_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 104.22 | 108.45 | AE2-333 | PJM_500_BG_P4_5_CNSTN_L_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 103.32 | 104.46 | AE2-333 | BG_P7_NEAST_RPHLRD_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 101.26 | 102.33 | AE2-333 | AP_P2-3_PE-500-015_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 100.32 | 102.3 | AE2-333 | PJM_500_BG_P4_5_CNSTN_13_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.19 | 117.37 | AE2-334 | Base Case | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 116.85 | AF1-038 | PJM_500_BG_P1_5013_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 116.85 | AF1-038 | PJM_500_BG_P4_5_CNSTN_M_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.19 | 116.96 | AF1-038 | Base Case | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 105.55 | 110.21 | AF1-038 | PN_P1-2_PN-500-010T_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 104.22 | 108.47 | AF1-038 | PJM_500_BG_P4_5_CNSTN_L_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 116.85 | AF1-050 | PJM_500_BG_P1_5013_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 116.85 | AF1-050 | PJM_500_BG_P4_5_CNSTN_M_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.19 | 116.96 | AF1-050 | Base Case | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 105.55 | 110.21 | AF1-050 | PN_P1-2_PN-500-010T_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 104.22 | 108.47 | AF1-050 | PJM_500_BG_P4_5_CNSTN_L_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 116.77 | AF1-147 | PJM_500_BG_P1_5013_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 116.76 | AF1-147 | PJM_500_BG_P4_5_CNSTN_M_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.19 | 116.9 | AF1-147 | Base Case | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 106.71 | 108.15 | AF1-147 | BG_P7_CNSTN_NWEST2_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 106.17 | 107.26 | AF1-147 | BG_P7_GRCTN_RAPHEL_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 105.55 | 110.13 | AF1-147 | PN_P1-2_PN-500-010T_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 104.22 | 108.39 | AF1-147 | PJM_500_BG_P4_5_CNSTN_L_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 103.32 | 104.39 | AF1-147 | BG_P7_NEAST_RPHLRD_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 101.26 | 102.28 | AF1-147 | AP_P2-3_PE-500-015_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 100.32 | 102.23 | AF1-147 | PJM_500_BG_P4_5_CNSTN_13_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 116.82 | AF1-173 | PJM_500_BG_P1_5013_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 116.82 | AF1-173 | PJM_500_BG_P4_5_CNSTN_M_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.19 | 116.95 | AF1-173 | Base Case | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 106.71 | 108.23 | AF1-173 | BG_P7_CNSTN_NWEST2_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 106.17 | 107.34 | AF1-173 | BG_P7_GRCTN_RAPHEL_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 105.55 | 110.19 | AF1-173 | PN_P1-2_PN-500-010T_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 104.22 | 108.45 | AF1-173 | PJM_500_BG_P4_5_CNSTN_L_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 103.32 | 104.47 | AF1-173 | BG_P7_NEAST_RPHLRD_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 228.49 | 237.7 | AF1-227 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 224.05 | 232.83 | AF1-227 | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 224.05 | 232.82 | AF1-227 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 224.03 | 232.8 | AF1-227 | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 209.21 | 216.15 | AF1-227 | PECO_P4_PEACH245_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 202.97 | 210.82 | AF1-227 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 198.66 | 206.05 | AF1-227 | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 198.66 | 206.05 | AF1-227 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 198.64 | 206.02 | AF1-227 | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 183.92 | 189.61 | AF1-227 | PECO_P4_PEACH245_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 116.46 | AF1-227 | PJM_500_BG_P1_5013_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 116.46 | AF1-227 | PJM_500_BG_P4_5_CNSTN_M_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.19 | 116.41 | AF1-227 | Base Case | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 106.71 | 107.91 | AF1-227 | BG_P7_CNSTN_NWEST2_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 106.17 | 107.01 | AF1-227 | BG_P7_GRCTN_RAPHEL_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 105.55 | 109.84 | AF1-227 | PN_P1-2_PN-500-010T_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 104.22 | 108.1 | AF1-227 | PJM_500_BG_P4_5_CNSTN_L_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 103.32 | 104.14 | AF1-227 | BG_P7_NEAST_RPHLRD_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 101.26 | 102.11 | AF1-227 | AP_P2-3_PE-500-015_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.19 | 116.97 | AF2-317 | Base Case | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 228.49 | 254.74 | AG2-055 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 224.05 | 250.44 | AG2-055 | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 224.05 | 250.44 | AG2-055 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 224.03 | 250.41 | AG2-055 | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 209.21 | 233.88 | AG2-055 | PECO_P4_PEACH245_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 202.97 | 227.59 | AG2-055 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 198.66 | 223.38 | AG2-055 | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 198.66 | 223.38 | AG2-055 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 198.64 | 223.35 | AG2-055 | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 183.92 | 207.04 | AG2-055 | PECO_P4_PEACH245_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 166.62 | 177.51 | AG2-055 | Base Case | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 221089 | WINDYED1 | 221090 | GLENARM2 | 1 | 115 | 232 | 148 | 192 | 141.81 | 147.08 | AG2-055 | BG_P7_GRCTN_RAPHEL_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 221092 | FIVE.FOR | 221096 | ROCKRGE1 | 1 | 115 | 232 | 229 | 256 | 135.39 | 138.81 | AG2-055 | BG_P7_GRCTN_RAPHEL_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 130.65 | 139.32 | AG2-055 | Base Case | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 221089 | WINDYED1 | 221090 | GLENARM2 | 1 | 115 | 232 | 148 | 192 | 131 | 135.5 | AG2-055 | BG_P7_NEAST_RPHLRD_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 559 | 680 | 129.8 | 135.73 | AG2-055 | PEPCO_P1_PP2_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 2 | 230 | 233 | 559 | 680 | 129.8 | 135.73 | AG2-055 | PEPCO_P1_PP1_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 221092 | FIVE.FOR | 221096 | ROCKRGE1 | 1 | 115 | 232 | 229 | 256 | 127.23 | 130.16 | AG2-055 | BG_P7_NEAST_RPHLRD_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 463 | 563 | 115.98 | 131.77 | AG2-055 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 463 | 563 | 115.98 | 132.24 | AG2-055 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 647 | 801 | 122.17 | 131.13 | AG2-055 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 463 | 563 | 113.42 | 129.77 | AG2-055 | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 463 | 563 | 113.42 | 130.24 | AG2-055 | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 463 | 563 | 113.37 | 130.18 | AG2-055 | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 463 | 563 | 113.37 | 129.71 | AG2-055 | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 463 | 563 | 113.37 | 129.71 | AG2-055 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 463 | 563 | 113.37 | 130.18 | AG2-055 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 2 | 230 | 233 | 559 | 680 | 122.19 | 126.82 | AG2-055 | DVP_P4-2: 514T595_SRT-SW | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 559 | 680 | 122.19 | 126.82 | AG2-055 | DVP_P4-2: 514T595_SRT-SW | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 647 | 801 | 117.38 | 127.2 | AG2-055 | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 647 | 801 | 117.38 | 127.2 | AG2-055 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 647 | 801 | 117.37 | 127.19 | AG2-055 | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 232 | 282 | 116.72 | 126.15 | AG2-055 | PJM_500_BG_P4_5_CNSTN_J_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 232 | 282 | 116.72 | 126.15 | AG2-055 | PJM_500_BG_P1_5011_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 232 | 282 | 116.46 | 125.9 | AG2-055 | PEPCO_P4_PP40_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 463 | 578 | 110.56 | 125.75 | AG2-055 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 207923 | BRISREAC | 208132 | WHEM TR1 | 1 | 230 | 229 | 493 | 618 | 117.78 | 125.55 | AG2-055 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 207922 | BRIS | 207923 | BRISREAC | RX | 230 | 229 | 506 | 618 | 117.78 | 125.55 | AG2-055 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.19 | 129.21 | AG2-055 | Base Case | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 2 | 230 | 233 | 559 | 680 | 119.41 | 123.98 | AG2-055 | DVP_P4-2: 51482_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 559 | 680 | 119.41 | 123.98 | AG2-055 | DVP_P4-2: 51482_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 2 | 230 | 233 | 559 | 680 | 119.12 | 123.98 | AG2-055 | DVP_P1-2: LN 514_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 2 | 230 | 233 | 559 | 680 | 119.12 | 123.98 | AG2-055 | AP_P1-2_PE-500-407T_SRT-SL | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 559 | 680 | 119.12 | 123.98 | AG2-055 | DVP_P1-2: LN 514_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 559 | 680 | 119.12 | 123.98 | AG2-055 | AP_P1-2_PE-500-407T_SRT-SL | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 463 | 578 | 108.07 | 123.8 | AG2-055 | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 463 | 578 | 108.02 | 123.74 | AG2-055 | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 463 | 578 | 108.02 | 123.74 | AG2-055 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 207923 | BRISREAC | 208132 | WHEM TR1 | 1 | 230 | 229 | 493 | 618 | 115.13 | 123.44 | AG2-055 | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 207922 | BRIS | 207923 | BRISREAC | RX | 230 | 229 | 506 | 618 | 115.13 | 123.44 | AG2-055 | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 207923 | BRISREAC | 208132 | WHEM TR1 | 1 | 230 | 229 | 493 | 618 | 115.13 | 123.43 | AG2-055 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 207922 | BRIS | 207923 | BRISREAC | RX | 230 | 229 | 506 | 618 | 115.13 | 123.43 | AG2-055 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 207922 | BRIS | 207923 | BRISREAC | RX | 230 | 229 | 506 | 618 | 115.12 | 123.42 | AG2-055 | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 207923 | BRISREAC | 208132 | WHEM TR1 | 1 | 230 | 229 | 493 | 618 | 115.12 | 123.42 | AG2-055 | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 221049 | FRED.RD8 | 221051 | CHESTN8A | 1 | 115 | 232 | 149 | 189 | 118.93 | 119.11 | AG2-055 | BG_P7_GRCTN_RAPHEL_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 125.65 | AG2-055 | PJM_500_BG_P1_5013_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 125.65 | AG2-055 | PJM_500_BG_P4_5_CNSTN_M_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 235463 | 01TANEY | 1 | 138 | 227/201 | 221 | 268 | 110.75 | 122.78 | AG2-055 | PJM_500_BG_P4_5_CNSTN_J_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 235463 | 01TANEY | 1 | 138 | 227/201 | 221 | 268 | 110.75 | 122.78 | AG2-055 | PJM_500_BG_P1_5011_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 235463 | 01TANEY | 1 | 138 | 227/201 | 221 | 268 | 110.45 | 122.48 | AG2-055 | PEPCO_P4_PP40_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 463 | 578 | 105.24 | 119.71 | AG2-055 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 208070 | SAHA12TP | 1 | 230 | 229 | 513 | 628 | 116.86 | 118.35 | AG2-055 | BG_P7_GRCTN_CNSTN_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 463 | 578 | 102.74 | 117.76 | AG2-055 | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 463 | 578 | 102.69 | 117.71 | AG2-055 | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 463 | 578 | 102.69 | 117.7 | AG2-055 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 709 | 869 | 110.18 | 117.97 | AG2-055 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 647 | 801 | 108.33 | 118.3 | AG2-055 | PECO_P4_PEACH245_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 221050 | FRED.RD7 | 221054 | CHESTN7A | 1 | 115 | 232 | 149 | 189 | 113.03 | 113.27 | AG2-055 | BG_P7_GRCTN_RAPHEL_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 709 | 869 | 108.55 | 116.65 | AG2-055 | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 709 | 869 | 108.55 | 116.65 | AG2-055 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 709 | 869 | 108.54 | 116.64 | AG2-055 | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 106.71 | 116.65 | AG2-055 | BG_P7_CNSTN_NWEST2_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 106.17 | 115.75 | AG2-055 | BG_P7_GRCTN_RAPHEL_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 221092 | FIVE.FOR | 221096 | ROCKRGE1 | 1 | 115 | 232 | 229 | 256 | 111.54 | 112.09 | AG2-055 | BG_P1_110512_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 207922 | BRIS | 207923 | BRISREAC | RX | 230 | 229 | 506 | 618 | 107.75 | 116.43 | AG2-055 | PECO_P4_PEACH245_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 207923 | BRISREAC | 208132 | WHEM TR1 | 1 | 230 | 229 | 493 | 618 | 107.75 | 116.43 | AG2-055 | PECO_P4_PEACH245_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 105.55 | 119.09 | AG2-055 | PN_P1-2_PN-500-010T_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 221049 | FRED.RD8 | 221051 | CHESTN8A | 1 | 115 | 232 | 149 | 189 | 111.45 | 111.64 | AG2-055 | BG_P7_NEAST_RPHLRD_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 463 | 563 | 98.5 | 115.22 | AG2-055 | PECO_P4_PEACH245_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 463 | 563 | 98.5 | 114.75 | AG2-055 | PECO_P4_PEACH245_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208131 | WHEM | 208132 | WHEM TR1 | 1 | 230 | 229 | 547 | 618 | 106.32 | 112.41 | AG2-055 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 221092 | FIVE.FOR | 221096 | ROCKRGE1 | 1 | 115 | 232 | 229 | 256 | 109.48 | 109.94 | AG2-055 | BG_P4_5_WE512_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 104.22 | 116.97 | AG2-055 | PJM_500_BG_P4_5_CNSTN_L_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 103.32 | 112.85 | AG2-055 | BG_P7_NEAST_RPHLRD_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204538 | 27STRABAN | 204544 | 27LINCOLN | 1 | 115 | 227 | 257 | 313 | 102.73 | 111.23 | AG2-055 | PJM_500_BG_P4_5_CNSTN_J_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204538 | 27STRABAN | 204544 | 27LINCOLN | 1 | 115 | 227 | 257 | 313 | 102.73 | 111.23 | AG2-055 | PJM_500_BG_P1_5011_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 221092 | FIVE.FOR | 221095 | ROCKRGE2 | 1 | 115 | 232 | 245 | 300 | 107.52 | 110.9 | AG2-055 | BG_P7_GRCTN_RAPHEL_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204538 | 27STRABAN | 204544 | 27LINCOLN | 1 | 115 | 227 | 257 | 313 | 102.46 | 110.98 | AG2-055 | PEPCO_P4_PP40_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200009 | JUNI | 208004 | JUNI | 2 | 500/230 | 229 | 776 | 1010 | 108.85 | 112.22 | AG2-055 | PL_10_P42_000140_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208131 | WHEM | 208132 | WHEM TR1 | 1 | 230 | 229 | 547 | 618 | 103.73 | 110.35 | AG2-055 | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208131 | WHEM | 208132 | WHEM TR1 | 1 | 230 | 229 | 547 | 618 | 103.73 | 110.34 | AG2-055 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208131 | WHEM | 208132 | WHEM TR1 | 1 | 230 | 229 | 547 | 618 | 103.72 | 110.33 | AG2-055 | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 204550 | 27ORRTANNA | 1 | 115 | 227 | 133 | 160 | 101.04 | 110.57 | AG2-055 | ME_P1-2_ME-115-068_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208078 | SAKR | 1 | 230 | 229 | 647 | 801 | 98.95 | 109.58 | AG2-055 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 101.26 | 109.77 | AG2-055 | AP_P2-3_PE-500-015_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 100.32 | 110.32 | AG2-055 | PJM_500_BG_P4_5_CNSTN_13_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 709 | 869 | 101.29 | 109.72 | AG2-055 | PECO_P4_PEACH245_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 463 | 578 | 93.52 | 109.17 | AG2-055 | PECO_P4_PEACH245_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 221050 | FRED.RD7 | 221054 | CHESTN7A | 1 | 115 | 232 | 149 | 189 | 105.57 | 105.8 | AG2-055 | BG_P7_NEAST_RPHLRD_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 97.68 | 111.75 | AG2-055 | PL_05_P71_000906_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 221092 | FIVE.FOR | 221094 | GRACE.-1 | 1 | 115 | 232 | 335 | 437 | 103.26 | 107 | AG2-055 | BG_P7_GRCTN_RAPHEL_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204539 | 27HUNTRSTN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 232 | 282 | 98.13 | 107.71 | AG2-055 | PJM_500_BG_P4_5_CNSTN_J_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204539 | 27HUNTRSTN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 232 | 282 | 98.13 | 107.71 | AG2-055 | PJM_500_BG_P1_5011_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204512 | 27S.RDG | 204693 | 27BOONETOWN | 1 | 230 | 227 | 445 | 531 | 101.56 | 107.28 | AG2-055 | PL_04_P22_102291_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204512 | 27S.RDG | 204693 | 27BOONETOWN | 1 | 230 | 227 | 445 | 531 | 101.56 | 107.28 | AG2-055 | PL_04_P43_102301_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 98.57 | 109.63 | AG2-055 | Base Case | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204512 | 27S.RDG | 204693 | 27BOONETOWN | 1 | 230 | 227 | 445 | 531 | 101.52 | 107.28 | AG2-055 | PL_04_P43_102300_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204512 | 27S.RDG | 204693 | 27BOONETOWN | 1 | 230 | 227 | 445 | 531 | 101.52 | 107.28 | AG2-055 | PL_04_P13_101211_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204512 | 27S.RDG | 204693 | 27BOONETOWN | 1 | 230 | 227 | 445 | 531 | 101.52 | 107.28 | AG2-055 | PL_04_P22_102290_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204539 | 27HUNTRSTN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 232 | 282 | 97.87 | 107.46 | AG2-055 | PEPCO_P4_PP40_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208078 | SAKR | 1 | 230 | 229 | 647 | 801 | 96.31 | 107.43 | AG2-055 | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208078 | SAKR | 1 | 230 | 229 | 647 | 801 | 96.31 | 107.43 | AG2-055 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 232 | 282 | 99.33 | 108.59 | AG2-055 | Base Case | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208078 | SAKR | 1 | 230 | 229 | 647 | 801 | 96.3 | 107.43 | AG2-055 | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 220964 | GRACETON | 220999 | BAGLEY2 | 13 | 230 | 232 | 1331 | 1594 | 101.97 | 107.13 | AG2-055 | BG_P4_5_GRCTN_3T_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 204550 | 27ORRTANNA | 1 | 115 | 227 | 133 | 160 | 98.04 | 106.93 | AG2-055 | ME_P2-3_ME-115-035A_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 204550 | 27ORRTANNA | 1 | 115 | 227 | 133 | 160 | 97.89 | 107.46 | AG2-055 | ME_P2-3_ME-115-013B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204529 | 27GERMANTN | 204538 | 27STRABAN | 1 | 115 | 227 | 257 | 313 | 96.79 | 104.8 | AG2-055 | PJM_500_BG_P4_5_CNSTN_J_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204529 | 27GERMANTN | 204538 | 27STRABAN | 1 | 115 | 227 | 257 | 313 | 96.79 | 104.8 | AG2-055 | PJM_500_BG_P1_5011_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 204550 | 27ORRTANNA | 1 | 115 | 227 | 133 | 160 | 97.47 | 107.05 | AG2-055 | ME_P2-3_ME-115-013A_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204529 | 27GERMANTN | 204538 | 27STRABAN | 1 | 115 | 227 | 257 | 313 | 96.52 | 104.55 | AG2-055 | PEPCO_P4_PP40_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 221092 | FIVE.FOR | 221096 | ROCKRGE1 | 1 | 115 | 232 | 229 | 256 | 102 | 103.47 | AG2-055 | BG_P7_CNSTN_NWEST2_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 220965 | NEAST339 | 220980 | RAPHAEL | 1 | 230 | 232 | 1098 | 1283 | 99.71 | 105.53 | AG2-055 | BG_P4_5_NEAST_17_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 220965 | NEAST339 | 220980 | RAPHAEL | 1 | 230 | 232 | 1098 | 1283 | 99.71 | 105.61 | AG2-055 | BG_P4_5_NEAST_15_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 221092 | FIVE.FOR | 221095 | ROCKRGE2 | 1 | 115 | 232 | 245 | 300 | 100.57 | 103.49 | AG2-055 | BG_P7_NEAST_RPHLRD_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208393 | FARO DC TIE | 208395 | FARO FF | 1 | 115/69 | 229 | 77 | 114 | 100.26 | 107.77 | AG2-055 | PL_05_P71_000906_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 220965 | NEAST339 | 220980 | RAPHAEL | 1 | 230 | 232 | 1098 | 1283 | 99.42 | 105.41 | AG2-055 | BG_P1_2315_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 220979 | NEAST317 | 220980 | RAPHAEL | 1 | 230 | 232 | 1098 | 1283 | 99.26 | 105.07 | AG2-055 | BG_P4_5_NEAST_39_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 220979 | NEAST317 | 220980 | RAPHAEL | 1 | 230 | 232 | 1098 | 1283 | 99.26 | 105.07 | AG2-055 | BG_P4_5_NEAST_37_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208131 | WHEM | 208133 | WHEM TR2 | 1 | 230 | 229 | 547 | 618 | 97.75 | 104.03 | AG2-055 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 220979 | NEAST317 | 220980 | RAPHAEL | 1 | 230 | 232 | 1098 | 1283 | 98.92 | 104.83 | AG2-055 | BG_P1_2337_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 232 | 282 | 97.98 | 105.02 | AG2-055 | AP_P2-3_PE-500-015_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208070 | SAHA12TP | 1 | 230 | 229 | 721 | 814 | 102.85 | 103.53 | AG2-055 | BG_P7_GRCTN_CNSTN_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208131 | WHEM | 208132 | WHEM TR1 | 1 | 230 | 229 | 547 | 618 | 96.56 | 103.57 | AG2-055 | PECO_P4_PEACH245_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 203981 | AD2-062_POI | 235188 | 01GREENE | 1 | 138 | 226/201 | 221 | 268 | 95.88 | 105.14 | AG2-055 | PJM_500_BG_P4_5_CNSTN_J_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 203981 | AD2-062_POI | 235188 | 01GREENE | 1 | 138 | 226/201 | 221 | 268 | 95.88 | 105.14 | AG2-055 | PJM_500_BG_P1_5011_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 204550 | 27ORRTANNA | 1 | 115 | 227 | 133 | 160 | 94.89 | 103.82 | AG2-055 | ME_P2-3_ME-115-035B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 230 | 2477 | 2860 | 91.43 | 108.41 | AG2-055 | PECO_P4_PEACH255_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208395 | FARO FF | 208396 | FARO | 1 | 69 | 229 | 194 | 240 | 98.42 | 102.39 | AG2-055 | PL_05_P71_000906_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 232 | 282 | 96.16 | 103.67 | AG2-055 | BG_P7_GRCTN_RAPHEL_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 203981 | AD2-062_POI | 235188 | 01GREENE | 1 | 138 | 226/201 | 221 | 268 | 95.51 | 104.76 | AG2-055 | PEPCO_P4_PP40_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204502 | 27JACKSON | 204514 | 27TMI | 1 | 230 | 227 | 541 | 659 | 94.41 | 102.69 | AG2-055 | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204502 | 27JACKSON | 204514 | 27TMI | 1 | 230 | 227 | 541 | 659 | 94.41 | 102.69 | AG2-055 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204502 | 27JACKSON | 204514 | 27TMI | 1 | 230 | 227 | 541 | 659 | 94.4 | 102.68 | AG2-055 | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 463 | 578 | 88.15 | 103.13 | AG2-055 | PECO_P4_PEACH245_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204502 | 27JACKSON | 204514 | 27TMI | 1 | 230 | 227 | 541 | 659 | 93.76 | 102.16 | AG2-055 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 220980 | RAPHAEL | 220999 | BAGLEY2 | 13 | 230 | 232 | 1331 | 1594 | 97.72 | 101.94 | AG2-055 | BG_P4_5_GRCTN_3T_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208131 | WHEM | 208133 | WHEM TR2 | 1 | 230 | 229 | 547 | 618 | 95.17 | 101.97 | AG2-055 | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208131 | WHEM | 208133 | WHEM TR2 | 1 | 230 | 229 | 547 | 618 | 95.16 | 101.97 | AG2-055 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208131 | WHEM | 208133 | WHEM TR2 | 1 | 230 | 229 | 547 | 618 | 95.15 | 101.95 | AG2-055 | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 221089 | WINDYED1 | 221090 | GLENARM2 | 1 | 115 | 232 | 148 | 192 | 97.24 | 99.34 | AG2-055 | BG_P7_CNSTN_NWEST2_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 221089 | WINDYED1 | 221090 | GLENARM2 | 1 | 115 | 232 | 148 | 192 | 96.88 | 96.94 | AG2-055 | BG_P4_5_WE_NORTH_TIE_SRT-A/* WINDY EDGE #1(NORTH) BUS BLACK-RED BUS TIE BREAKER 221089 | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208020 | MANO TR3 | 1 | 230 | 229 | 602 | 731 | 90.57 | 99.57 | AG2-055 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 221089 | WINDYED1 | 221090 | GLENARM2 | 1 | 115 | 232 | 148 | 192 | 96.72 | 96.69 | AG2-055 | BG_P4_5_WE504_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 221092 | FIVE.FOR | 221094 | GRACE.-1 | 1 | 115 | 232 | 335 | 437 | 96.18 | 99.33 | AG2-055 | BG_P7_NEAST_RPHLRD_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 117.3 | ALDENE_AB | PJM_500_BG_P1_5013_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 117.3 | ALDENE_AB | PJM_500_BG_P4_5_CNSTN_M_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.19 | 117.58 | ALDENE_AB | Base Case | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 106.71 | 108.71 | ALDENE_AB | BG_P7_CNSTN_NWEST2_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 106.17 | 107.82 | ALDENE_AB | BG_P7_GRCTN_RAPHEL_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 105.55 | 110.66 | ALDENE_AB | PN_P1-2_PN-500-010T_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 104.22 | 108.91 | ALDENE_AB | PJM_500_BG_P4_5_CNSTN_L_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 103.32 | 104.94 | ALDENE_AB | BG_P7_NEAST_RPHLRD_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 101.26 | 102.8 | ALDENE_AB | AP_P2-3_PE-500-015_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 100.32 | 102.76 | ALDENE_AB | PJM_500_BG_P4_5_CNSTN_13_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 228.49 | 237.64 | BIGSKY | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 224.05 | 232.77 | BIGSKY | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 224.05 | 232.77 | BIGSKY | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 224.03 | 232.74 | BIGSKY | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 209.21 | 216.1 | BIGSKY | PECO_P4_PEACH245_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 202.97 | 210.76 | BIGSKY | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 198.66 | 205.99 | BIGSKY | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 198.66 | 205.99 | BIGSKY | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 198.64 | 205.97 | BIGSKY | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 183.92 | 189.55 | BIGSKY | PECO_P4_PEACH245_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 116.44 | BIGSKY | PJM_500_BG_P1_5013_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 116.44 | BIGSKY | PJM_500_BG_P4_5_CNSTN_M_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.19 | 116.4 | BIGSKY | Base Case | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 463 | 578 | 108.07 | 108.54 | BIGSKY | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 463 | 578 | 108.02 | 108.49 | BIGSKY | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 463 | 578 | 108.02 | 108.49 | BIGSKY | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 106.71 | 107.87 | BIGSKY | BG_P7_CNSTN_NWEST2_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 106.17 | 106.98 | BIGSKY | BG_P7_GRCTN_RAPHEL_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 105.55 | 109.82 | BIGSKY | PN_P1-2_PN-500-010T_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 104.22 | 108.08 | BIGSKY | PJM_500_BG_P4_5_CNSTN_L_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 103.32 | 104.11 | BIGSKY | BG_P7_NEAST_RPHLRD_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 463 | 578 | 102.74 | 102.52 | BIGSKY | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 463 | 578 | 102.69 | 102.46 | BIGSKY | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 463 | 578 | 102.69 | 102.46 | BIGSKY | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 101.26 | 102.07 | BIGSKY | AP_P2-3_PE-500-015_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 228.49 | 237.88 | BISHOP | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 224.05 | 233.02 | BISHOP | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 224.05 | 233.01 | BISHOP | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 224.03 | 232.99 | BISHOP | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 209.21 | 216.34 | BISHOP | PECO_P4_PEACH245_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 202.97 | 210.99 | BISHOP | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 198.66 | 206.23 | BISHOP | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 198.66 | 206.23 | BISHOP | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 198.64 | 206.2 | BISHOP | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 183.92 | 189.78 | BISHOP | PECO_P4_PEACH245_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 116.57 | BISHOP | PJM_500_BG_P1_5013_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 116.57 | BISHOP | PJM_500_BG_P4_5_CNSTN_M_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.19 | 116.57 | BISHOP | Base Case | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 106.71 | 107.99 | BISHOP | BG_P7_CNSTN_NWEST2_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 106.17 | 107.1 | BISHOP | BG_P7_GRCTN_RAPHEL_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 105.55 | 109.94 | BISHOP | PN_P1-2_PN-500-010T_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 104.22 | 108.2 | BISHOP | PJM_500_BG_P4_5_CNSTN_L_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 103.32 | 104.23 | BISHOP | BG_P7_NEAST_RPHLRD_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 101.26 | 102.18 | BISHOP | AP_P2-3_PE-500-015_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 117.18 | BRUNSWCK_AB | PJM_500_BG_P1_5013_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 117.18 | BRUNSWCK_AB | PJM_500_BG_P4_5_CNSTN_M_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.19 | 117.42 | BRUNSWCK_AB | Base Case | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 105.55 | 110.54 | BRUNSWCK_AB | PN_P1-2_PN-500-010T_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 104.22 | 108.79 | BRUNSWCK_AB | PJM_500_BG_P4_5_CNSTN_L_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 209.21 | 216.47 | CAMPGROVE;RU | PECO_P4_PEACH245_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 183.92 | 189.9 | CAMPGROVE;RU | PECO_P4_PEACH245_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 116.63 | CAMPGROVE;RU | PJM_500_BG_P1_5013_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 116.63 | CAMPGROVE;RU | PJM_500_BG_P4_5_CNSTN_M_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.19 | 116.67 | CAMPGROVE;RU | Base Case | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 106.71 | 108.06 | CAMPGROVE;RU | BG_P7_CNSTN_NWEST2_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 106.17 | 107.17 | CAMPGROVE;RU | BG_P7_GRCTN_RAPHEL_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 105.55 | 110.01 | CAMPGROVE;RU | PN_P1-2_PN-500-010T_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 104.22 | 108.27 | CAMPGROVE;RU | PJM_500_BG_P4_5_CNSTN_L_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 103.32 | 104.3 | CAMPGROVE;RU | BG_P7_NEAST_RPHLRD_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 101.26 | 102.24 | CAMPGROVE;RU | AP_P2-3_PE-500-015_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 228.49 | 237.43 | CAYUGA | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 224.05 | 232.55 | CAYUGA | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 224.05 | 232.55 | CAYUGA | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 224.03 | 232.52 | CAYUGA | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 209.21 | 215.89 | CAYUGA | PECO_P4_PEACH245_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 202.97 | 210.56 | CAYUGA | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 198.66 | 205.78 | CAYUGA | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 198.66 | 205.78 | CAYUGA | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 198.64 | 205.76 | CAYUGA | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 183.92 | 189.35 | CAYUGA | PECO_P4_PEACH245_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 647 | 801 | 117.38 | 118.13 | CAYUGA | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 647 | 801 | 117.38 | 118.12 | CAYUGA | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 647 | 801 | 117.37 | 118.11 | CAYUGA | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 463 | 563 | 115.98 | 116.54 | CAYUGA | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 463 | 563 | 115.98 | 116.2 | CAYUGA | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 463 | 563 | 113.42 | 113.92 | CAYUGA | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 463 | 563 | 113.42 | 114.26 | CAYUGA | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 463 | 563 | 113.37 | 113.86 | CAYUGA | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 463 | 563 | 113.37 | 114.2 | CAYUGA | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 463 | 563 | 113.37 | 113.86 | CAYUGA | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 463 | 563 | 113.37 | 114.2 | CAYUGA | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 116.33 | CAYUGA | PJM_500_BG_P1_5013_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 116.33 | CAYUGA | PJM_500_BG_P4_5_CNSTN_M_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.19 | 116.24 | CAYUGA | Base Case | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 463 | 578 | 110.56 | 110.58 | CAYUGA | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 647 | 801 | 108.33 | 109.17 | CAYUGA | PECO_P4_PEACH245_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 463 | 578 | 108.07 | 108.36 | CAYUGA | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 463 | 578 | 108.02 | 108.31 | CAYUGA | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 463 | 578 | 108.02 | 108.31 | CAYUGA | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 106.71 | 107.76 | CAYUGA | BG_P7_CNSTN_NWEST2_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 106.17 | 106.87 | CAYUGA | BG_P7_GRCTN_RAPHEL_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 105.55 | 109.71 | CAYUGA | PN_P1-2_PN-500-010T_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 463 | 578 | 105.24 | 104.56 | CAYUGA | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 104.22 | 107.97 | CAYUGA | PJM_500_BG_P4_5_CNSTN_L_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 103.32 | 104 | CAYUGA | BG_P7_NEAST_RPHLRD_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 463 | 578 | 102.74 | 102.34 | CAYUGA | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 220964 | GRACETON | 220999 | BAGLEY2 | 13 | 230 | 232 | 1331 | 1594 | 101.97 | 102.43 | CAYUGA | BG_P4_5_GRCTN_3T_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 463 | 578 | 102.69 | 102.29 | CAYUGA | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 463 | 578 | 102.69 | 102.28 | CAYUGA | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 101.26 | 101.98 | CAYUGA | AP_P2-3_PE-500-015_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.19 | 117.35 | CHERRYDALE C | Base Case | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 228.49 | 239.44 | D05 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 224.05 | 234.62 | D05 | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 224.05 | 234.62 | D05 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 224.03 | 234.59 | D05 | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 209.21 | 217.93 | D05 | PECO_P4_PEACH245_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 202.97 | 212.51 | D05 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 198.66 | 207.79 | D05 | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 198.66 | 207.79 | D05 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 198.64 | 207.77 | D05 | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 183.92 | 191.33 | D05 | PECO_P4_PEACH245_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 117.33 | D05 | PJM_500_BG_P1_5013_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 117.33 | D05 | PJM_500_BG_P4_5_CNSTN_M_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.19 | 117.61 | D05 | Base Case | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 106.71 | 108.76 | D05 | BG_P7_CNSTN_NWEST2_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 106.17 | 107.87 | D05 | BG_P7_GRCTN_RAPHEL_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 105.55 | 110.69 | D05 | PN_P1-2_PN-500-010T_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 104.22 | 108.94 | D05 | PJM_500_BG_P4_5_CNSTN_L_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 103.32 | 105 | D05 | BG_P7_NEAST_RPHLRD_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 101.26 | 102.85 | D05 | AP_P2-3_PE-500-015_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 100.32 | 102.81 | D05 | PJM_500_BG_P4_5_CNSTN_13_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 117.25 | DC1 NUG | PJM_500_BG_P1_5013_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 117.25 | DC1 NUG | PJM_500_BG_P4_5_CNSTN_M_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.19 | 117.52 | DC1 NUG | Base Case | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 106.71 | 108.64 | DC1 NUG | BG_P7_CNSTN_NWEST2_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 106.17 | 107.74 | DC1 NUG | BG_P7_GRCTN_RAPHEL_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 105.55 | 110.61 | DC1 NUG | PN_P1-2_PN-500-010T_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 104.22 | 108.86 | DC1 NUG | PJM_500_BG_P4_5_CNSTN_L_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 103.32 | 104.87 | DC1 NUG | BG_P7_NEAST_RPHLRD_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 101.26 | 102.74 | DC1 NUG | AP_P2-3_PE-500-015_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 100.32 | 102.7 | DC1 NUG | PJM_500_BG_P4_5_CNSTN_13_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 117.25 | DC2 NUG | PJM_500_BG_P1_5013_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 117.25 | DC2 NUG | PJM_500_BG_P4_5_CNSTN_M_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.19 | 117.52 | DC2 NUG | Base Case | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 106.71 | 108.64 | DC2 NUG | BG_P7_CNSTN_NWEST2_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 106.17 | 107.74 | DC2 NUG | BG_P7_GRCTN_RAPHEL_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 105.55 | 110.61 | DC2 NUG | PN_P1-2_PN-500-010T_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 104.22 | 108.86 | DC2 NUG | PJM_500_BG_P4_5_CNSTN_L_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 103.32 | 104.87 | DC2 NUG | BG_P7_NEAST_RPHLRD_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 101.26 | 102.74 | DC2 NUG | AP_P2-3_PE-500-015_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 100.32 | 102.7 | DC2 NUG | PJM_500_BG_P4_5_CNSTN_13_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 116.78 | ECOGROVE ;U1 | PJM_500_BG_P1_5013_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 116.78 | ECOGROVE ;U1 | PJM_500_BG_P4_5_CNSTN_M_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.19 | 116.87 | ECOGROVE ;U1 | Base Case | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 106.71 | 108.21 | ECOGROVE ;U1 | BG_P7_CNSTN_NWEST2_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 106.17 | 107.31 | ECOGROVE ;U1 | BG_P7_GRCTN_RAPHEL_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 105.55 | 110.15 | ECOGROVE ;U1 | PN_P1-2_PN-500-010T_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 104.22 | 108.41 | ECOGROVE ;U1 | PJM_500_BG_P4_5_CNSTN_L_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 103.32 | 104.44 | ECOGROVE ;U1 | BG_P7_NEAST_RPHLRD_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 101.26 | 102.36 | ECOGROVE ;U1 | AP_P2-3_PE-500-015_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 100.32 | 102.29 | ECOGROVE ;U1 | PJM_500_BG_P4_5_CNSTN_13_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 228.49 | 239.81 | FAIRLAWN_AB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 224.05 | 235.01 | FAIRLAWN_AB | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 224.05 | 235.01 | FAIRLAWN_AB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 224.03 | 234.98 | FAIRLAWN_AB | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 209.21 | 218.33 | FAIRLAWN_AB | PECO_P4_PEACH245_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 202.97 | 212.88 | FAIRLAWN_AB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 198.66 | 208.18 | FAIRLAWN_AB | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 198.66 | 208.18 | FAIRLAWN_AB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 198.64 | 208.15 | FAIRLAWN_AB | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 183.92 | 191.72 | FAIRLAWN_AB | PECO_P4_PEACH245_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 463 | 563 | 115.98 | 118.53 | FAIRLAWN_AB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 463 | 563 | 115.98 | 118.18 | FAIRLAWN_AB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 463 | 563 | 113.42 | 116.29 | FAIRLAWN_AB | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 463 | 563 | 113.42 | 115.94 | FAIRLAWN_AB | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 463 | 563 | 113.37 | 116.23 | FAIRLAWN_AB | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 463 | 563 | 113.37 | 115.88 | FAIRLAWN_AB | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 463 | 563 | 113.37 | 116.23 | FAIRLAWN_AB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 463 | 563 | 113.37 | 115.88 | FAIRLAWN_AB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 117.57 | FAIRLAWN_AB | PJM_500_BG_P1_5013_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 117.57 | FAIRLAWN_AB | PJM_500_BG_P4_5_CNSTN_M_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.19 | 117.96 | FAIRLAWN_AB | Base Case | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 463 | 578 | 110.56 | 112.51 | FAIRLAWN_AB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 463 | 578 | 108.07 | 110.33 | FAIRLAWN_AB | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 463 | 578 | 108.02 | 110.27 | FAIRLAWN_AB | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 463 | 578 | 108.02 | 110.27 | FAIRLAWN_AB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 106.71 | 108.97 | FAIRLAWN_AB | BG_P7_CNSTN_NWEST2_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 106.17 | 108.08 | FAIRLAWN_AB | BG_P7_GRCTN_RAPHEL_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 463 | 578 | 105.24 | 106.49 | FAIRLAWN_AB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 105.55 | 110.93 | FAIRLAWN_AB | PN_P1-2_PN-500-010T_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 104.22 | 109.17 | FAIRLAWN_AB | PJM_500_BG_P4_5_CNSTN_L_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 103.32 | 105.21 | FAIRLAWN_AB | BG_P7_NEAST_RPHLRD_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 463 | 578 | 102.74 | 104.3 | FAIRLAWN_AB | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 463 | 578 | 102.69 | 104.25 | FAIRLAWN_AB | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 463 | 578 | 102.69 | 104.25 | FAIRLAWN_AB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 101.26 | 103.03 | FAIRLAWN_AB | AP_P2-3_PE-500-015_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 100.32 | 103.01 | FAIRLAWN_AB | PJM_500_BG_P4_5_CNSTN_13_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 228.49 | 237.18 | G07 NFTWR | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 224.05 | 232.29 | G07 NFTWR | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 224.05 | 232.29 | G07 NFTWR | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 224.03 | 232.27 | G07 NFTWR | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 209.21 | 215.59 | G07 NFTWR | PECO_P4_PEACH245_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 202.97 | 210.28 | G07 NFTWR | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 198.66 | 205.5 | G07 NFTWR | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 198.66 | 205.5 | G07 NFTWR | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 198.64 | 205.47 | G07 NFTWR | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 183.92 | 189.02 | G07 NFTWR | PECO_P4_PEACH245_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 166.62 | 168.22 | G07 NFTWR | Base Case | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 130.65 | 130.62 | G07 NFTWR | Base Case | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 647 | 801 | 122.17 | 122.46 | G07 NFTWR | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 647 | 801 | 117.38 | 118 | G07 NFTWR | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 647 | 801 | 117.38 | 118 | G07 NFTWR | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 647 | 801 | 117.37 | 117.98 | G07 NFTWR | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 463 | 563 | 115.98 | 115.91 | G07 NFTWR | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 463 | 563 | 115.98 | 116.24 | G07 NFTWR | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 463 | 563 | 113.42 | 113.63 | G07 NFTWR | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 463 | 563 | 113.42 | 113.96 | G07 NFTWR | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 463 | 563 | 113.37 | 113.57 | G07 NFTWR | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 463 | 563 | 113.37 | 113.9 | G07 NFTWR | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 463 | 563 | 113.37 | 113.9 | G07 NFTWR | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 463 | 563 | 113.37 | 113.57 | G07 NFTWR | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 116.21 | G07 NFTWR | PJM_500_BG_P1_5013_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 116.2 | G07 NFTWR | PJM_500_BG_P4_5_CNSTN_M_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.19 | 116.07 | G07 NFTWR | Base Case | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 709 | 869 | 110.18 | 110.74 | G07 NFTWR | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 463 | 578 | 110.56 | 110.3 | G07 NFTWR | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 709 | 869 | 108.55 | 109.23 | G07 NFTWR | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 709 | 869 | 108.55 | 109.23 | G07 NFTWR | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 709 | 869 | 108.54 | 109.22 | G07 NFTWR | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 647 | 801 | 108.33 | 109.02 | G07 NFTWR | PECO_P4_PEACH245_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 463 | 578 | 108.07 | 108.08 | G07 NFTWR | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 463 | 578 | 108.02 | 108.02 | G07 NFTWR | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 463 | 578 | 108.02 | 108.02 | G07 NFTWR | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 106.71 | 107.65 | G07 NFTWR | BG_P7_CNSTN_NWEST2_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 106.17 | 106.76 | G07 NFTWR | BG_P7_GRCTN_RAPHEL_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 105.55 | 109.56 | G07 NFTWR | PN_P1-2_PN-500-010T_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 463 | 578 | 105.24 | 104.28 | G07 NFTWR | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 104.22 | 107.85 | G07 NFTWR | PJM_500_BG_P4_5_CNSTN_L_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 103.32 | 103.89 | G07 NFTWR | BG_P7_NEAST_RPHLRD_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 220964 | GRACETON | 220999 | BAGLEY2 | 13 | 230 | 232 | 1331 | 1594 | 101.97 | 102.34 | G07 NFTWR | BG_P4_5_GRCTN_3T_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 463 | 578 | 102.74 | 102.06 | G07 NFTWR | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 463 | 578 | 102.69 | 102 | G07 NFTWR | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 463 | 578 | 102.69 | 102 | G07 NFTWR | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 709 | 869 | 101.29 | 102.25 | G07 NFTWR | PECO_P4_PEACH245_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 101.26 | 101.87 | G07 NFTWR | AP_P2-3_PE-500-015_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 117.22 | GLOUCSTR_26 | PJM_500_BG_P1_5013_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 117.22 | GLOUCSTR_26 | PJM_500_BG_P4_5_CNSTN_M_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.19 | 117.48 | GLOUCSTR_26 | Base Case | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 106.71 | 108.62 | GLOUCSTR_26 | BG_P7_CNSTN_NWEST2_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 106.17 | 107.73 | GLOUCSTR_26 | BG_P7_GRCTN_RAPHEL_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 105.55 | 110.58 | GLOUCSTR_26 | PN_P1-2_PN-500-010T_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 104.22 | 108.83 | GLOUCSTR_26 | PJM_500_BG_P4_5_CNSTN_L_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 103.32 | 104.86 | GLOUCSTR_26 | BG_P7_NEAST_RPHLRD_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 101.26 | 102.72 | GLOUCSTR_26 | AP_P2-3_PE-500-015_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 100.32 | 102.68 | GLOUCSTR_26 | PJM_500_BG_P4_5_CNSTN_13_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 228.49 | 237.33 | GR RIDGE | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 224.05 | 232.45 | GR RIDGE | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 224.05 | 232.45 | GR RIDGE | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 224.03 | 232.42 | GR RIDGE | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 209.21 | 215.79 | GR RIDGE | PECO_P4_PEACH245_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 202.97 | 210.47 | GR RIDGE | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 198.66 | 205.69 | GR RIDGE | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 198.66 | 205.69 | GR RIDGE | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 198.64 | 205.66 | GR RIDGE | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 183.92 | 189.25 | GR RIDGE | PECO_P4_PEACH245_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 647 | 801 | 122.17 | 122.53 | GR RIDGE | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 647 | 801 | 117.38 | 118.08 | GR RIDGE | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 647 | 801 | 117.38 | 118.07 | GR RIDGE | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 647 | 801 | 117.37 | 118.06 | GR RIDGE | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 463 | 563 | 115.98 | 116.12 | GR RIDGE | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 463 | 563 | 115.98 | 116.45 | GR RIDGE | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 463 | 563 | 113.42 | 113.84 | GR RIDGE | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 463 | 563 | 113.42 | 114.17 | GR RIDGE | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 463 | 563 | 113.37 | 113.78 | GR RIDGE | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 463 | 563 | 113.37 | 114.12 | GR RIDGE | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 463 | 563 | 113.37 | 113.78 | GR RIDGE | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 463 | 563 | 113.37 | 114.11 | GR RIDGE | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 116.28 | GR RIDGE | PJM_500_BG_P1_5013_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 116.27 | GR RIDGE | PJM_500_BG_P4_5_CNSTN_M_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.19 | 116.17 | GR RIDGE | Base Case | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 709 | 869 | 110.18 | 110.78 | GR RIDGE | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 463 | 578 | 110.56 | 110.5 | GR RIDGE | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 709 | 869 | 108.55 | 109.28 | GR RIDGE | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 709 | 869 | 108.55 | 109.27 | GR RIDGE | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 709 | 869 | 108.54 | 109.27 | GR RIDGE | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 647 | 801 | 108.33 | 109.12 | GR RIDGE | PECO_P4_PEACH245_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 463 | 578 | 108.07 | 108.28 | GR RIDGE | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 463 | 578 | 108.02 | 108.23 | GR RIDGE | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 463 | 578 | 108.02 | 108.23 | GR RIDGE | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 106.71 | 107.71 | GR RIDGE | BG_P7_CNSTN_NWEST2_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 106.17 | 106.82 | GR RIDGE | BG_P7_GRCTN_RAPHEL_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 105.55 | 109.66 | GR RIDGE | PN_P1-2_PN-500-010T_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 463 | 578 | 105.24 | 104.48 | GR RIDGE | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 104.22 | 107.92 | GR RIDGE | PJM_500_BG_P4_5_CNSTN_L_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 103.32 | 103.95 | GR RIDGE | BG_P7_NEAST_RPHLRD_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 220964 | GRACETON | 220999 | BAGLEY2 | 13 | 230 | 232 | 1331 | 1594 | 101.97 | 102.41 | GR RIDGE | BG_P4_5_GRCTN_3T_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 463 | 578 | 102.74 | 102.26 | GR RIDGE | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 463 | 578 | 102.69 | 102.2 | GR RIDGE | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 463 | 578 | 102.69 | 102.2 | GR RIDGE | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 709 | 869 | 101.29 | 102.31 | GR RIDGE | PECO_P4_PEACH245_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 101.26 | 101.94 | GR RIDGE | AP_P2-3_PE-500-015_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 116.83 | GSG-6 ;RU | PJM_500_BG_P1_5013_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 116.83 | GSG-6 ;RU | PJM_500_BG_P4_5_CNSTN_M_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.19 | 116.93 | GSG-6 ;RU | Base Case | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 105.55 | 110.19 | GSG-6 ;RU | PN_P1-2_PN-500-010T_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 104.22 | 108.46 | GSG-6 ;RU | PJM_500_BG_P4_5_CNSTN_L_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 116.77 | K28 | PJM_500_BG_P1_5013_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 116.77 | K28 | PJM_500_BG_P4_5_CNSTN_M_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.19 | 116.85 | K28 | Base Case | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 106.71 | 108.18 | K28 | BG_P7_CNSTN_NWEST2_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 106.17 | 107.29 | K28 | BG_P7_GRCTN_RAPHEL_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 105.55 | 110.13 | K28 | PN_P1-2_PN-500-010T_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 104.22 | 108.39 | K28 | PJM_500_BG_P4_5_CNSTN_L_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 103.32 | 104.42 | K28 | BG_P7_NEAST_RPHLRD_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 101.26 | 102.35 | K28 | AP_P2-3_PE-500-015_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 100.32 | 102.26 | K28 | PJM_500_BG_P4_5_CNSTN_13_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 224.05 | 233.14 | KELLY CRK;1U | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 224.05 | 233.13 | KELLY CRK;1U | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 224.03 | 233.11 | KELLY CRK;1U | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 209.21 | 216.46 | KELLY CRK;1U | PECO_P4_PEACH245_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 183.92 | 189.89 | KELLY CRK;1U | PECO_P4_PEACH245_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 116.63 | KELLY CRK;1U | PJM_500_BG_P1_5013_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 116.63 | KELLY CRK;1U | PJM_500_BG_P4_5_CNSTN_M_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.19 | 116.66 | KELLY CRK;1U | Base Case | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 106.71 | 108.06 | KELLY CRK;1U | BG_P7_CNSTN_NWEST2_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 106.17 | 107.16 | KELLY CRK;1U | BG_P7_GRCTN_RAPHEL_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 105.55 | 110 | KELLY CRK;1U | PN_P1-2_PN-500-010T_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 104.22 | 108.26 | KELLY CRK;1U | PJM_500_BG_P4_5_CNSTN_L_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 103.32 | 104.29 | KELLY CRK;1U | BG_P7_NEAST_RPHLRD_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 101.26 | 102.23 | KELLY CRK;1U | AP_P2-3_PE-500-015_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 117.16 | LINDEN_26 | PJM_500_BG_P1_5013_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 117.15 | LINDEN_26 | PJM_500_BG_P4_5_CNSTN_M_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.19 | 117.39 | LINDEN_26 | Base Case | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 105.55 | 110.52 | LINDEN_26 | PN_P1-2_PN-500-010T_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 104.22 | 108.77 | LINDEN_26 | PJM_500_BG_P4_5_CNSTN_L_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 228.49 | 237.8 | M24 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 224.05 | 232.93 | M24 | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 224.05 | 232.93 | M24 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 224.03 | 232.9 | M24 | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 209.21 | 216.26 | M24 | PECO_P4_PEACH245_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 202.97 | 210.91 | M24 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 198.66 | 206.15 | M24 | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 198.66 | 206.15 | M24 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 198.64 | 206.12 | M24 | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 183.92 | 189.7 | M24 | PECO_P4_PEACH245_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 116.52 | M24 | PJM_500_BG_P1_5013_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 116.52 | M24 | PJM_500_BG_P4_5_CNSTN_M_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.19 | 116.52 | M24 | Base Case | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 106.71 | 107.95 | M24 | BG_P7_CNSTN_NWEST2_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 106.17 | 107.05 | M24 | BG_P7_GRCTN_RAPHEL_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 105.55 | 109.9 | M24 | PN_P1-2_PN-500-010T_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 104.22 | 108.16 | M24 | PJM_500_BG_P4_5_CNSTN_L_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 103.32 | 104.18 | M24 | BG_P7_NEAST_RPHLRD_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 101.26 | 102.14 | M24 | AP_P2-3_PE-500-015_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.19 | 117.36 | MARINGEN | Base Case | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 116.84 | MENDOTA H;RU | PJM_500_BG_P1_5013_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 116.84 | MENDOTA H;RU | PJM_500_BG_P4_5_CNSTN_M_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.19 | 116.94 | MENDOTA H;RU | Base Case | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 105.55 | 110.2 | MENDOTA H;RU | PN_P1-2_PN-500-010T_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 104.22 | 108.46 | MENDOTA H;RU | PJM_500_BG_P4_5_CNSTN_L_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 228.49 | 237.89 | MINONK ;1U | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 224.05 | 233.03 | MINONK ;1U | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 224.05 | 233.03 | MINONK ;1U | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 224.03 | 233 | MINONK ;1U | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 209.21 | 216.35 | MINONK ;1U | PECO_P4_PEACH245_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 202.97 | 211 | MINONK ;1U | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 198.66 | 206.24 | MINONK ;1U | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 198.66 | 206.24 | MINONK ;1U | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 198.64 | 206.21 | MINONK ;1U | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 183.92 | 189.79 | MINONK ;1U | PECO_P4_PEACH245_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 116.57 | MINONK ;1U | PJM_500_BG_P1_5013_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 116.57 | MINONK ;1U | PJM_500_BG_P4_5_CNSTN_M_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.19 | 116.58 | MINONK ;1U | Base Case | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 106.71 | 108 | MINONK ;1U | BG_P7_CNSTN_NWEST2_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 106.17 | 107.11 | MINONK ;1U | BG_P7_GRCTN_RAPHEL_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 105.55 | 109.95 | MINONK ;1U | PN_P1-2_PN-500-010T_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 104.22 | 108.21 | MINONK ;1U | PJM_500_BG_P4_5_CNSTN_L_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 103.32 | 104.24 | MINONK ;1U | BG_P7_NEAST_RPHLRD_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 101.26 | 102.19 | MINONK ;1U | AP_P2-3_PE-500-015_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.19 | 117.36 | MINUEST_L1 | Base Case | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.19 | 117.36 | MINUEST_L2 | Base Case | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200009 | JUNI | 208004 | JUNI | 2 | 500/230 | 229 | 776 | 1010 | 108.85 | 110.12 | N39 | PL_10_P42_000140_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 228.49 | 237.84 | O09 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 224.05 | 232.97 | O09 | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 224.05 | 232.97 | O09 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 224.03 | 232.95 | O09 | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 209.21 | 216.3 | O09 | PECO_P4_PEACH245_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 202.97 | 210.95 | O09 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 198.66 | 206.19 | O09 | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 198.66 | 206.19 | O09 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 198.64 | 206.16 | O09 | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 183.92 | 189.74 | O09 | PECO_P4_PEACH245_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 116.55 | O09 | PJM_500_BG_P1_5013_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 116.54 | O09 | PJM_500_BG_P4_5_CNSTN_M_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.19 | 116.55 | O09 | Base Case | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 106.71 | 107.97 | O09 | BG_P7_CNSTN_NWEST2_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 106.17 | 107.08 | O09 | BG_P7_GRCTN_RAPHEL_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 105.55 | 109.92 | O09 | PN_P1-2_PN-500-010T_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 104.22 | 108.18 | O09 | PJM_500_BG_P4_5_CNSTN_L_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 103.32 | 104.21 | O09 | BG_P7_NEAST_RPHLRD_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 101.26 | 102.16 | O09 | AP_P2-3_PE-500-015_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 228.49 | 237.76 | O29 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 224.05 | 232.89 | O29 | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 224.05 | 232.89 | O29 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 224.03 | 232.87 | O29 | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 209.21 | 216.22 | O29 | PECO_P4_PEACH245_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 202.97 | 210.88 | O29 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 198.66 | 206.11 | O29 | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 198.66 | 206.11 | O29 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 198.64 | 206.09 | O29 | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 183.92 | 189.67 | O29 | PECO_P4_PEACH245_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 116.5 | O29 | PJM_500_BG_P1_5013_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 116.5 | O29 | PJM_500_BG_P4_5_CNSTN_M_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.19 | 116.49 | O29 | Base Case | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 106.71 | 107.93 | O29 | BG_P7_CNSTN_NWEST2_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 106.17 | 107.04 | O29 | BG_P7_GRCTN_RAPHEL_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 105.55 | 109.88 | O29 | PN_P1-2_PN-500-010T_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 104.22 | 108.14 | O29 | PJM_500_BG_P4_5_CNSTN_L_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 103.32 | 104.17 | O29 | BG_P7_NEAST_RPHLRD_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 101.26 | 102.12 | O29 | AP_P2-3_PE-500-015_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 228.49 | 228.76 | O66 NFTWR | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 224.05 | 223.6 | O66 NFTWR | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 224.05 | 223.6 | O66 NFTWR | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 224.03 | 223.58 | O66 NFTWR | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 209.21 | 206.83 | O66 NFTWR | PECO_P4_PEACH245_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 202.97 | 201.99 | O66 NFTWR | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 198.66 | 196.94 | O66 NFTWR | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 198.66 | 196.94 | O66 NFTWR | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 198.64 | 196.91 | O66 NFTWR | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 183.92 | 180.4 | O66 NFTWR | PECO_P4_PEACH245_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 166.62 | 163.34 | O66 NFTWR | Base Case | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 221089 | WINDYED1 | 221090 | GLENARM2 | 1 | 115 | 232 | 148 | 192 | 141.81 | 137.13 | O66 NFTWR | BG_P7_GRCTN_RAPHEL_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 221092 | FIVE.FOR | 221096 | ROCKRGE1 | 1 | 115 | 232 | 229 | 256 | 135.39 | 131.3 | O66 NFTWR | BG_P7_GRCTN_RAPHEL_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 559 | 680 | 129.8 | 130.21 | O66 NFTWR | PEPCO_P1_PP2_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 2 | 230 | 233 | 559 | 680 | 129.8 | 130.21 | O66 NFTWR | PEPCO_P1_PP1_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 221089 | WINDYED1 | 221090 | GLENARM2 | 1 | 115 | 232 | 148 | 192 | 131 | 125.69 | O66 NFTWR | BG_P7_NEAST_RPHLRD_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 130.65 | 126.05 | O66 NFTWR | Base Case | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 221092 | FIVE.FOR | 221096 | ROCKRGE1 | 1 | 115 | 232 | 229 | 256 | 127.23 | 122.76 | O66 NFTWR | BG_P7_NEAST_RPHLRD_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 2 | 230 | 233 | 559 | 680 | 122.19 | 120.66 | O66 NFTWR | DVP_P4-2: 514T595_SRT-SW | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 559 | 680 | 122.19 | 120.66 | O66 NFTWR | DVP_P4-2: 514T595_SRT-SW | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 647 | 801 | 122.17 | 118.33 | O66 NFTWR | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 2 | 230 | 233 | 559 | 680 | 119.41 | 117.64 | O66 NFTWR | DVP_P4-2: 51482_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 559 | 680 | 119.41 | 117.64 | O66 NFTWR | DVP_P4-2: 51482_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 2 | 230 | 233 | 559 | 680 | 119.12 | 117.64 | O66 NFTWR | DVP_P1-2: LN 514_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 559 | 680 | 119.12 | 117.64 | O66 NFTWR | DVP_P1-2: LN 514_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 559 | 680 | 119.12 | 117.64 | O66 NFTWR | AP_P1-2_PE-500-407T_SRT-SL | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 2 | 230 | 233 | 559 | 680 | 119.12 | 117.64 | O66 NFTWR | AP_P1-2_PE-500-407T_SRT-SL | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 207923 | BRISREAC | 208132 | WHEM TR1 | 1 | 230 | 229 | 493 | 618 | 117.78 | 115.13 | O66 NFTWR | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 207922 | BRIS | 207923 | BRISREAC | RX | 230 | 229 | 506 | 618 | 117.78 | 115.13 | O66 NFTWR | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 647 | 801 | 117.38 | 113.62 | O66 NFTWR | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 647 | 801 | 117.38 | 113.62 | O66 NFTWR | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 647 | 801 | 117.37 | 113.61 | O66 NFTWR | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 232 | 282 | 116.72 | 111.85 | O66 NFTWR | PJM_500_BG_P4_5_CNSTN_J_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 232 | 282 | 116.72 | 111.85 | O66 NFTWR | PJM_500_BG_P1_5011_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 232 | 282 | 116.46 | 111.58 | O66 NFTWR | PEPCO_P4_PP40_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 207922 | BRIS | 207923 | BRISREAC | RX | 230 | 229 | 506 | 618 | 115.13 | 112.59 | O66 NFTWR | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 207923 | BRISREAC | 208132 | WHEM TR1 | 1 | 230 | 229 | 493 | 618 | 115.13 | 112.59 | O66 NFTWR | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 207923 | BRISREAC | 208132 | WHEM TR1 | 1 | 230 | 229 | 493 | 618 | 115.13 | 112.59 | O66 NFTWR | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 207922 | BRIS | 207923 | BRISREAC | RX | 230 | 229 | 506 | 618 | 115.13 | 112.59 | O66 NFTWR | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 207922 | BRIS | 207923 | BRISREAC | RX | 230 | 229 | 506 | 618 | 115.12 | 112.58 | O66 NFTWR | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 207923 | BRISREAC | 208132 | WHEM TR1 | 1 | 230 | 229 | 493 | 618 | 115.12 | 112.58 | O66 NFTWR | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 111.99 | O66 NFTWR | PJM_500_BG_P1_5013_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 111.99 | O66 NFTWR | PJM_500_BG_P4_5_CNSTN_M_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 463 | 563 | 115.98 | 109.3 | O66 NFTWR | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 463 | 563 | 115.98 | 109.02 | O66 NFTWR | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200009 | JUNI | 208004 | JUNI | 2 | 500/230 | 229 | 776 | 1010 | 108.85 | 109.36 | O66 NFTWR | PL_10_P42_000140_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 709 | 869 | 110.18 | 107.3 | O66 NFTWR | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.19 | 110.23 | O66 NFTWR | Base Case | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 221092 | FIVE.FOR | 221095 | ROCKRGE2 | 1 | 115 | 232 | 245 | 300 | 107.52 | 104.43 | O66 NFTWR | BG_P7_GRCTN_RAPHEL_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 463 | 563 | 113.42 | 106.61 | O66 NFTWR | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 463 | 563 | 113.42 | 106.89 | O66 NFTWR | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 463 | 563 | 113.37 | 106.55 | O66 NFTWR | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 463 | 563 | 113.37 | 106.84 | O66 NFTWR | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 463 | 563 | 113.37 | 106.55 | O66 NFTWR | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 463 | 563 | 113.37 | 106.83 | O66 NFTWR | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 235463 | 01TANEY | 1 | 138 | 227/201 | 221 | 268 | 110.75 | 106.12 | O66 NFTWR | PJM_500_BG_P4_5_CNSTN_J_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 235463 | 01TANEY | 1 | 138 | 227/201 | 221 | 268 | 110.75 | 106.12 | O66 NFTWR | PJM_500_BG_P1_5011_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 235463 | 01TANEY | 1 | 138 | 227/201 | 221 | 268 | 110.45 | 105.81 | O66 NFTWR | PEPCO_P4_PP40_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 709 | 869 | 108.55 | 105.71 | O66 NFTWR | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 709 | 869 | 108.55 | 105.71 | O66 NFTWR | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 709 | 869 | 108.54 | 105.71 | O66 NFTWR | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 207923 | BRISREAC | 208132 | WHEM TR1 | 1 | 230 | 229 | 493 | 618 | 107.75 | 105.49 | O66 NFTWR | PECO_P4_PEACH245_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 207922 | BRIS | 207923 | BRISREAC | RX | 230 | 229 | 506 | 618 | 107.75 | 105.49 | O66 NFTWR | PECO_P4_PEACH245_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 647 | 801 | 108.33 | 104.61 | O66 NFTWR | PECO_P4_PEACH245_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 463 | 578 | 110.56 | 103.59 | O66 NFTWR | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208131 | WHEM | 208132 | WHEM TR1 | 1 | 230 | 229 | 547 | 618 | 106.32 | 102.44 | O66 NFTWR | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 106.71 | 103.52 | O66 NFTWR | BG_P7_CNSTN_NWEST2_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 106.17 | 102.62 | O66 NFTWR | BG_P7_GRCTN_RAPHEL_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 221092 | FIVE.FOR | 221094 | GRACE.-1 | 1 | 115 | 232 | 335 | 437 | 103.26 | 100.74 | O66 NFTWR | BG_P7_GRCTN_RAPHEL_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213775 | MACDADE | 213925 | RIDLEY | 1 | 230 | 230 | 927 | 927 | 99.07 | 102.29 | O66 NFTWR | PECO_P1-2_220-23_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 105.55 | 105.33 | O66 NFTWR | PN_P1-2_PN-500-010T_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 221092 | FIVE.FOR | 221096 | ROCKRGE1 | 1 | 115 | 232 | 229 | 256 | 102 | 98.47 | O66 NFTWR | BG_P7_CNSTN_NWEST2_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 228.49 | 239.51 | P28 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 224.05 | 234.69 | P28 | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 224.05 | 234.69 | P28 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 224.03 | 234.66 | P28 | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 209.21 | 218.01 | P28 | PECO_P4_PEACH245_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 202.97 | 212.58 | P28 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 198.66 | 207.87 | P28 | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 198.66 | 207.86 | P28 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 198.64 | 207.84 | P28 | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 183.92 | 191.41 | P28 | PECO_P4_PEACH245_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 117.32 | P28 | PJM_500_BG_P1_5013_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 117.32 | P28 | PJM_500_BG_P4_5_CNSTN_M_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.19 | 117.55 | P28 | Base Case | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 106.71 | 108.81 | P28 | BG_P7_CNSTN_NWEST2_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 106.17 | 107.91 | P28 | BG_P7_GRCTN_RAPHEL_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 105.55 | 110.69 | P28 | PN_P1-2_PN-500-010T_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 104.22 | 108.94 | P28 | PJM_500_BG_P4_5_CNSTN_L_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 103.32 | 105.04 | P28 | BG_P7_NEAST_RPHLRD_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 101.26 | 102.89 | P28 | AP_P2-3_PE-500-015_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 100.32 | 102.86 | P28 | PJM_500_BG_P4_5_CNSTN_13_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 116.77 | P59 | PJM_500_BG_P1_5013_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 116.77 | P59 | PJM_500_BG_P4_5_CNSTN_M_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.19 | 116.85 | P59 | Base Case | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 106.71 | 108.19 | P59 | BG_P7_CNSTN_NWEST2_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 106.17 | 107.3 | P59 | BG_P7_GRCTN_RAPHEL_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 105.55 | 110.14 | P59 | PN_P1-2_PN-500-010T_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 104.22 | 108.4 | P59 | PJM_500_BG_P4_5_CNSTN_L_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 103.32 | 104.42 | P59 | BG_P7_NEAST_RPHLRD_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 101.26 | 102.36 | P59 | AP_P2-3_PE-500-015_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 100.32 | 102.27 | P59 | PJM_500_BG_P4_5_CNSTN_13_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 116.83 | PROVIDENC;RU | PJM_500_BG_P1_5013_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 116.83 | PROVIDENC;RU | PJM_500_BG_P4_5_CNSTN_M_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.19 | 116.94 | PROVIDENC;RU | Base Case | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 105.55 | 110.2 | PROVIDENC;RU | PN_P1-2_PN-500-010T_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 104.22 | 108.46 | PROVIDENC;RU | PJM_500_BG_P4_5_CNSTN_L_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 228.49 | 235.45 | Q01/Q03 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 224.05 | 230.51 | Q01/Q03 | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 224.05 | 230.5 | Q01/Q03 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 224.03 | 230.48 | Q01/Q03 | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 209.21 | 213.89 | Q01/Q03 | PECO_P4_PEACH245_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 202.97 | 208.66 | Q01/Q03 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 198.66 | 203.82 | Q01/Q03 | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 198.66 | 203.82 | Q01/Q03 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 198.64 | 203.79 | Q01/Q03 | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 183.92 | 187.43 | Q01/Q03 | PECO_P4_PEACH245_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 166.62 | 167.31 | Q01/Q03 | Base Case | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 130.65 | 129.85 | Q01/Q03 | Base Case | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 647 | 801 | 122.17 | 121.6 | Q01/Q03 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 207923 | BRISREAC | 208132 | WHEM TR1 | 1 | 230 | 229 | 493 | 618 | 117.78 | 117.77 | Q01/Q03 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 207922 | BRIS | 207923 | BRISREAC | RX | 230 | 229 | 506 | 618 | 117.78 | 117.77 | Q01/Q03 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 647 | 801 | 117.38 | 117.08 | Q01/Q03 | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 647 | 801 | 117.38 | 117.08 | Q01/Q03 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 647 | 801 | 117.37 | 117.07 | Q01/Q03 | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 232 | 282 | 116.72 | 115.32 | Q01/Q03 | PJM_500_BG_P4_5_CNSTN_J_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 232 | 282 | 116.72 | 115.32 | Q01/Q03 | PJM_500_BG_P1_5011_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 232 | 282 | 116.46 | 115.05 | Q01/Q03 | PEPCO_P4_PP40_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 207922 | BRIS | 207923 | BRISREAC | RX | 230 | 229 | 506 | 618 | 115.13 | 115.34 | Q01/Q03 | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 207923 | BRISREAC | 208132 | WHEM TR1 | 1 | 230 | 229 | 493 | 618 | 115.13 | 115.34 | Q01/Q03 | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 207922 | BRIS | 207923 | BRISREAC | RX | 230 | 229 | 506 | 618 | 115.13 | 115.34 | Q01/Q03 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 207923 | BRISREAC | 208132 | WHEM TR1 | 1 | 230 | 229 | 493 | 618 | 115.13 | 115.34 | Q01/Q03 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 207922 | BRIS | 207923 | BRISREAC | RX | 230 | 229 | 506 | 618 | 115.12 | 115.32 | Q01/Q03 | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 207923 | BRISREAC | 208132 | WHEM TR1 | 1 | 230 | 229 | 493 | 618 | 115.12 | 115.32 | Q01/Q03 | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 463 | 563 | 115.98 | 114.55 | Q01/Q03 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 463 | 563 | 115.98 | 114.87 | Q01/Q03 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 115.27 | Q01/Q03 | PJM_500_BG_P1_5013_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 115.27 | Q01/Q03 | PJM_500_BG_P4_5_CNSTN_M_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 463 | 563 | 113.42 | 112.24 | Q01/Q03 | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 463 | 563 | 113.42 | 112.56 | Q01/Q03 | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 463 | 563 | 113.37 | 112.18 | Q01/Q03 | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 463 | 563 | 113.37 | 112.51 | Q01/Q03 | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 463 | 563 | 113.37 | 112.18 | Q01/Q03 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 463 | 563 | 113.37 | 112.5 | Q01/Q03 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.19 | 114.77 | Q01/Q03 | Base Case | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 709 | 869 | 110.18 | 109.97 | Q01/Q03 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 235463 | 01TANEY | 1 | 138 | 227/201 | 221 | 268 | 110.75 | 110.17 | Q01/Q03 | PJM_500_BG_P4_5_CNSTN_J_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 235463 | 01TANEY | 1 | 138 | 227/201 | 221 | 268 | 110.75 | 110.17 | Q01/Q03 | PJM_500_BG_P1_5011_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 235463 | 01TANEY | 1 | 138 | 227/201 | 221 | 268 | 110.45 | 109.86 | Q01/Q03 | PEPCO_P4_PP40_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 463 | 578 | 110.56 | 108.98 | Q01/Q03 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 709 | 869 | 108.55 | 108.45 | Q01/Q03 | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 709 | 869 | 108.55 | 108.45 | Q01/Q03 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 709 | 869 | 108.54 | 108.44 | Q01/Q03 | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 647 | 801 | 108.33 | 108.15 | Q01/Q03 | PECO_P4_PEACH245_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 207923 | BRISREAC | 208132 | WHEM TR1 | 1 | 230 | 229 | 493 | 618 | 107.75 | 108.3 | Q01/Q03 | PECO_P4_PEACH245_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 207922 | BRIS | 207923 | BRISREAC | RX | 230 | 229 | 506 | 618 | 107.75 | 108.3 | Q01/Q03 | PECO_P4_PEACH245_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 463 | 578 | 108.07 | 106.73 | Q01/Q03 | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 463 | 578 | 108.02 | 106.67 | Q01/Q03 | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 463 | 578 | 108.02 | 106.67 | Q01/Q03 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208131 | WHEM | 208132 | WHEM TR1 | 1 | 230 | 229 | 547 | 618 | 106.32 | 104.96 | Q01/Q03 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 106.71 | 106.72 | Q01/Q03 | BG_P7_CNSTN_NWEST2_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 559 | 680 | 105.77 | 106.32 | Q01/Q03 | PEPCO_P4_PP19_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 106.17 | 105.84 | Q01/Q03 | BG_P7_GRCTN_RAPHEL_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 105.55 | 108.67 | Q01/Q03 | PN_P1-2_PN-500-010T_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 104.22 | 106.94 | Q01/Q03 | PJM_500_BG_P4_5_CNSTN_L_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 463 | 578 | 105.24 | 102.95 | Q01/Q03 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208131 | WHEM | 208132 | WHEM TR1 | 1 | 230 | 229 | 547 | 618 | 103.73 | 102.59 | Q01/Q03 | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208131 | WHEM | 208132 | WHEM TR1 | 1 | 230 | 229 | 547 | 618 | 103.73 | 102.59 | Q01/Q03 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208131 | WHEM | 208132 | WHEM TR1 | 1 | 230 | 229 | 547 | 618 | 103.72 | 102.58 | Q01/Q03 | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 103.32 | 102.96 | Q01/Q03 | BG_P7_NEAST_RPHLRD_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 220964 | GRACETON | 220999 | BAGLEY2 | 13 | 230 | 232 | 1331 | 1594 | 101.97 | 101.93 | Q01/Q03 | BG_P4_5_GRCTN_3T_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204538 | 27STRABAN | 204544 | 27LINCOLN | 1 | 115 | 227 | 257 | 313 | 102.73 | 100.34 | Q01/Q03 | PJM_500_BG_P4_5_CNSTN_J_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204538 | 27STRABAN | 204544 | 27LINCOLN | 1 | 115 | 227 | 257 | 313 | 102.73 | 100.34 | Q01/Q03 | PJM_500_BG_P1_5011_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204512 | 27S.RDG | 204693 | 27BOONETOWN | 1 | 230 | 227 | 445 | 531 | 101.56 | 100.66 | Q01/Q03 | PL_04_P43_102301_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204512 | 27S.RDG | 204693 | 27BOONETOWN | 1 | 230 | 227 | 445 | 531 | 101.56 | 100.66 | Q01/Q03 | PL_04_P22_102291_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204512 | 27S.RDG | 204693 | 27BOONETOWN | 1 | 230 | 227 | 445 | 531 | 101.52 | 100.66 | Q01/Q03 | PL_04_P43_102300_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204512 | 27S.RDG | 204693 | 27BOONETOWN | 1 | 230 | 227 | 445 | 531 | 101.52 | 100.66 | Q01/Q03 | PL_04_P22_102290_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204512 | 27S.RDG | 204693 | 27BOONETOWN | 1 | 230 | 227 | 445 | 531 | 101.52 | 100.66 | Q01/Q03 | PL_04_P13_101211_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204538 | 27STRABAN | 204544 | 27LINCOLN | 1 | 115 | 227 | 257 | 313 | 102.46 | 100.07 | Q01/Q03 | PEPCO_P4_PP40_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 463 | 578 | 102.74 | 100.7 | Q01/Q03 | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 228.49 | 239.78 | Q27 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 224.05 | 234.97 | Q27 | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 224.05 | 234.97 | Q27 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 224.03 | 234.94 | Q27 | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 209.21 | 218.29 | Q27 | PECO_P4_PEACH245_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 202.97 | 212.84 | Q27 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 198.66 | 208.14 | Q27 | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 198.66 | 208.14 | Q27 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 198.64 | 208.11 | Q27 | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 183.92 | 191.68 | Q27 | PECO_P4_PEACH245_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 166.62 | 169.8 | Q27 | Base Case | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 130.65 | 132.1 | Q27 | Base Case | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 117.46 | Q27 | PJM_500_BG_P1_5013_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 117.46 | Q27 | PJM_500_BG_P4_5_CNSTN_M_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.19 | 117.78 | Q27 | Base Case | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200009 | JUNI | 208004 | JUNI | 2 | 500/230 | 229 | 776 | 1010 | 108.85 | 111.25 | Q27 | PL_10_P42_000140_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 106.71 | 108.91 | Q27 | BG_P7_CNSTN_NWEST2_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 106.17 | 108.01 | Q27 | BG_P7_GRCTN_RAPHEL_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 105.55 | 110.82 | Q27 | PN_P1-2_PN-500-010T_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 104.22 | 109.07 | Q27 | PJM_500_BG_P4_5_CNSTN_L_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 103.32 | 105.14 | Q27 | BG_P7_NEAST_RPHLRD_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 101.26 | 102.97 | Q27 | AP_P2-3_PE-500-015_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 100.32 | 102.95 | Q27 | PJM_500_BG_P4_5_CNSTN_13_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 228.49 | 237.71 | Q57 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 224.05 | 232.84 | Q57 | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 224.05 | 232.84 | Q57 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 224.03 | 232.82 | Q57 | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 209.21 | 216.17 | Q57 | PECO_P4_PEACH245_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 202.97 | 210.83 | Q57 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 198.66 | 206.07 | Q57 | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 198.66 | 206.06 | Q57 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 198.64 | 206.04 | Q57 | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 183.92 | 189.62 | Q57 | PECO_P4_PEACH245_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 116.48 | Q57 | PJM_500_BG_P1_5013_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 116.48 | Q57 | PJM_500_BG_P4_5_CNSTN_M_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.19 | 116.45 | Q57 | Base Case | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 106.71 | 107.91 | Q57 | BG_P7_CNSTN_NWEST2_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 106.17 | 107.02 | Q57 | BG_P7_GRCTN_RAPHEL_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 105.55 | 109.85 | Q57 | PN_P1-2_PN-500-010T_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 104.22 | 108.12 | Q57 | PJM_500_BG_P4_5_CNSTN_L_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 103.32 | 104.14 | Q57 | BG_P7_NEAST_RPHLRD_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 101.26 | 102.11 | Q57 | AP_P2-3_PE-500-015_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 116.68 | R49 | PJM_500_BG_P1_5013_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 116.68 | R49 | PJM_500_BG_P4_5_CNSTN_M_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.19 | 116.72 | R49 | Base Case | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 106.71 | 108.11 | R49 | BG_P7_CNSTN_NWEST2_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 106.17 | 107.22 | R49 | BG_P7_GRCTN_RAPHEL_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 105.55 | 110.05 | R49 | PN_P1-2_PN-500-010T_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 104.22 | 108.31 | R49 | PJM_500_BG_P4_5_CNSTN_L_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 103.32 | 104.35 | R49 | BG_P7_NEAST_RPHLRD_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 101.26 | 102.29 | R49 | AP_P2-3_PE-500-015_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 100.32 | 102.2 | R49 | PJM_500_BG_P4_5_CNSTN_13_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 228.49 | 237.3 | R60 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 224.05 | 232.42 | R60 | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 224.05 | 232.42 | R60 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 224.03 | 232.39 | R60 | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 209.21 | 215.76 | R60 | PECO_P4_PEACH245_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 202.97 | 210.44 | R60 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 198.66 | 205.66 | R60 | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 198.66 | 205.66 | R60 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 198.64 | 205.63 | R60 | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 183.92 | 189.22 | R60 | PECO_P4_PEACH245_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 647 | 801 | 122.17 | 122.52 | R60 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 647 | 801 | 117.38 | 118.06 | R60 | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 647 | 801 | 117.38 | 118.06 | R60 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 647 | 801 | 117.37 | 118.05 | R60 | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 463 | 563 | 115.98 | 116.4 | R60 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 463 | 563 | 115.98 | 116.06 | R60 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 463 | 563 | 113.42 | 114.11 | R60 | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 463 | 563 | 113.42 | 113.78 | R60 | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 463 | 563 | 113.37 | 114.06 | R60 | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 463 | 563 | 113.37 | 113.72 | R60 | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 463 | 563 | 113.37 | 113.72 | R60 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 463 | 563 | 113.37 | 114.06 | R60 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 116.25 | R60 | PJM_500_BG_P1_5013_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 116.25 | R60 | PJM_500_BG_P4_5_CNSTN_M_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.19 | 116.12 | R60 | Base Case | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 709 | 869 | 110.18 | 110.76 | R60 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 463 | 578 | 110.56 | 110.45 | R60 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 709 | 869 | 108.55 | 109.26 | R60 | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 709 | 869 | 108.55 | 109.26 | R60 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 709 | 869 | 108.54 | 109.25 | R60 | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 647 | 801 | 108.33 | 109.11 | R60 | PECO_P4_PEACH245_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 463 | 578 | 108.07 | 108.23 | R60 | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 463 | 578 | 108.02 | 108.17 | R60 | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 463 | 578 | 108.02 | 108.17 | R60 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 106.71 | 107.7 | R60 | BG_P7_CNSTN_NWEST2_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 106.17 | 106.81 | R60 | BG_P7_GRCTN_RAPHEL_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 105.55 | 109.63 | R60 | PN_P1-2_PN-500-010T_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 463 | 578 | 105.24 | 104.42 | R60 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 104.22 | 107.9 | R60 | PJM_500_BG_P4_5_CNSTN_L_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 103.32 | 103.94 | R60 | BG_P7_NEAST_RPHLRD_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 220964 | GRACETON | 220999 | BAGLEY2 | 13 | 230 | 232 | 1331 | 1594 | 101.97 | 102.4 | R60 | BG_P4_5_GRCTN_3T_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 463 | 578 | 102.74 | 102.2 | R60 | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 463 | 578 | 102.69 | 102.15 | R60 | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 463 | 578 | 102.69 | 102.15 | R60 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 709 | 869 | 101.29 | 102.29 | R60 | PECO_P4_PEACH245_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 101.26 | 101.94 | R60 | AP_P2-3_PE-500-015_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 117.2 | RUTGERS | PJM_500_BG_P1_5013_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 117.19 | RUTGERS | PJM_500_BG_P4_5_CNSTN_M_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.19 | 117.44 | RUTGERS | Base Case | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 106.71 | 108.61 | RUTGERS | BG_P7_CNSTN_NWEST2_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 106.17 | 107.71 | RUTGERS | BG_P7_GRCTN_RAPHEL_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 105.55 | 110.56 | RUTGERS | PN_P1-2_PN-500-010T_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 104.22 | 108.81 | RUTGERS | PJM_500_BG_P4_5_CNSTN_L_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 103.32 | 104.84 | RUTGERS | BG_P7_NEAST_RPHLRD_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 100.32 | 102.67 | RUTGERS | PJM_500_BG_P4_5_CNSTN_13_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 100.27 | 102.61 | RUTGERS | PJM_500_BG_P4_5_CNSTN_6_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 228.49 | 237.83 | S06 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 224.05 | 232.96 | S06 | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 224.05 | 232.96 | S06 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 224.03 | 232.94 | S06 | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 209.21 | 216.29 | S06 | PECO_P4_PEACH245_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 202.97 | 210.94 | S06 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 198.66 | 206.18 | S06 | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 198.66 | 206.18 | S06 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 198.64 | 206.15 | S06 | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 183.92 | 189.73 | S06 | PECO_P4_PEACH245_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 116.54 | S06 | PJM_500_BG_P1_5013_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 116.54 | S06 | PJM_500_BG_P4_5_CNSTN_M_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.19 | 116.53 | S06 | Base Case | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 106.71 | 107.97 | S06 | BG_P7_CNSTN_NWEST2_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 106.17 | 107.08 | S06 | BG_P7_GRCTN_RAPHEL_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 105.55 | 109.91 | S06 | PN_P1-2_PN-500-010T_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 104.22 | 108.18 | S06 | PJM_500_BG_P4_5_CNSTN_L_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 103.32 | 104.21 | S06 | BG_P7_NEAST_RPHLRD_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 101.26 | 102.16 | S06 | AP_P2-3_PE-500-015_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 116.83 | S14 | PJM_500_BG_P1_5013_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 116.82 | S14 | PJM_500_BG_P4_5_CNSTN_M_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.19 | 116.94 | S14 | Base Case | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 106.71 | 108.24 | S14 | BG_P7_CNSTN_NWEST2_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 106.17 | 107.35 | S14 | BG_P7_GRCTN_RAPHEL_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 105.55 | 110.19 | S14 | PN_P1-2_PN-500-010T_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 104.22 | 108.45 | S14 | PJM_500_BG_P4_5_CNSTN_L_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 103.32 | 104.47 | S14 | BG_P7_NEAST_RPHLRD_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 228.49 | 237.93 | S36 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 224.05 | 233.07 | S36 | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 224.05 | 233.07 | S36 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 224.03 | 233.04 | S36 | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 209.21 | 216.39 | S36 | PECO_P4_PEACH245_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 202.97 | 211.04 | S36 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 198.66 | 206.28 | S36 | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 198.66 | 206.28 | S36 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 198.64 | 206.25 | S36 | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 183.92 | 189.83 | S36 | PECO_P4_PEACH245_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 116.59 | S36 | PJM_500_BG_P1_5013_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 116.59 | S36 | PJM_500_BG_P4_5_CNSTN_M_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.19 | 116.61 | S36 | Base Case | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 106.71 | 108.02 | S36 | BG_P7_CNSTN_NWEST2_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 106.17 | 107.13 | S36 | BG_P7_GRCTN_RAPHEL_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 105.55 | 109.97 | S36 | PN_P1-2_PN-500-010T_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 104.22 | 108.23 | S36 | PJM_500_BG_P4_5_CNSTN_L_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 103.32 | 104.26 | S36 | BG_P7_NEAST_RPHLRD_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 101.26 | 102.2 | S36 | AP_P2-3_PE-500-015_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 116.75 | S71 | PJM_500_BG_P1_5013_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 116.75 | S71 | PJM_500_BG_P4_5_CNSTN_M_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.19 | 116.82 | S71 | Base Case | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 106.71 | 108.18 | S71 | BG_P7_CNSTN_NWEST2_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 106.17 | 107.28 | S71 | BG_P7_GRCTN_RAPHEL_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 105.55 | 110.12 | S71 | PN_P1-2_PN-500-010T_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 104.22 | 108.38 | S71 | PJM_500_BG_P4_5_CNSTN_L_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 103.32 | 104.41 | S71 | BG_P7_NEAST_RPHLRD_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 101.26 | 102.34 | S71 | AP_P2-3_PE-500-015_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 100.32 | 102.26 | S71 | PJM_500_BG_P4_5_CNSTN_13_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 117.34 | SALEM G3 | PJM_500_BG_P1_5013_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 117.34 | SALEM G3 | PJM_500_BG_P4_5_CNSTN_M_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.19 | 117.65 | SALEM G3 | Base Case | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 106.71 | 108.72 | SALEM G3 | BG_P7_CNSTN_NWEST2_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 106.17 | 107.82 | SALEM G3 | BG_P7_GRCTN_RAPHEL_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 105.55 | 110.71 | SALEM G3 | PN_P1-2_PN-500-010T_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 104.22 | 108.95 | SALEM G3 | PJM_500_BG_P4_5_CNSTN_L_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 103.32 | 104.95 | SALEM G3 | BG_P7_NEAST_RPHLRD_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 101.26 | 102.81 | SALEM G3 | AP_P2-3_PE-500-015_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 100.32 | 102.77 | SALEM G3 | PJM_500_BG_P4_5_CNSTN_13_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 117.27 | SEWAREN_IM | PJM_500_BG_P1_5013_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 117.27 | SEWAREN_IM | PJM_500_BG_P4_5_CNSTN_M_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.19 | 117.54 | SEWAREN_IM | Base Case | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 106.71 | 108.68 | SEWAREN_IM | BG_P7_CNSTN_NWEST2_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 106.17 | 107.79 | SEWAREN_IM | BG_P7_GRCTN_RAPHEL_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 105.55 | 110.63 | SEWAREN_IM | PN_P1-2_PN-500-010T_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 104.22 | 108.88 | SEWAREN_IM | PJM_500_BG_P4_5_CNSTN_L_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 103.32 | 104.91 | SEWAREN_IM | BG_P7_NEAST_RPHLRD_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 101.26 | 102.77 | SEWAREN_IM | AP_P2-3_PE-500-015_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 100.32 | 102.74 | SEWAREN_IM | PJM_500_BG_P4_5_CNSTN_13_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 228.49 | 237.85 | T126 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 224.05 | 232.99 | T126 | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 224.05 | 232.99 | T126 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 224.03 | 232.96 | T126 | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 209.21 | 216.31 | T126 | PECO_P4_PEACH245_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 202.97 | 210.97 | T126 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 198.66 | 206.2 | T126 | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 198.66 | 206.2 | T126 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 198.64 | 206.18 | T126 | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 183.92 | 189.76 | T126 | PECO_P4_PEACH245_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 116.55 | T126 | PJM_500_BG_P1_5013_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 116.55 | T126 | PJM_500_BG_P4_5_CNSTN_M_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.19 | 116.55 | T126 | Base Case | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 106.71 | 107.98 | T126 | BG_P7_CNSTN_NWEST2_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 106.17 | 107.09 | T126 | BG_P7_GRCTN_RAPHEL_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 105.55 | 109.92 | T126 | PN_P1-2_PN-500-010T_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 104.22 | 108.19 | T126 | PJM_500_BG_P4_5_CNSTN_L_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 103.32 | 104.22 | T126 | BG_P7_NEAST_RPHLRD_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 101.26 | 102.17 | T126 | AP_P2-3_PE-500-015_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 228.49 | 237.86 | T127 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 224.05 | 233 | T127 | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 224.05 | 233 | T127 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 224.03 | 232.97 | T127 | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 209.21 | 216.32 | T127 | PECO_P4_PEACH245_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 202.97 | 210.98 | T127 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 198.66 | 206.21 | T127 | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 198.66 | 206.21 | T127 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 198.64 | 206.19 | T127 | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 183.92 | 189.77 | T127 | PECO_P4_PEACH245_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 116.56 | T127 | PJM_500_BG_P1_5013_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 116.56 | T127 | PJM_500_BG_P4_5_CNSTN_M_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.19 | 116.56 | T127 | Base Case | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 106.71 | 107.99 | T127 | BG_P7_CNSTN_NWEST2_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 106.17 | 107.09 | T127 | BG_P7_GRCTN_RAPHEL_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 105.55 | 109.93 | T127 | PN_P1-2_PN-500-010T_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 104.22 | 108.19 | T127 | PJM_500_BG_P4_5_CNSTN_L_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 103.32 | 104.22 | T127 | BG_P7_NEAST_RPHLRD_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 101.26 | 102.17 | T127 | AP_P2-3_PE-500-015_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 116.7 | T157 | PJM_500_BG_P1_5013_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 116.7 | T157 | PJM_500_BG_P4_5_CNSTN_M_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.19 | 116.8 | T157 | Base Case | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 106.71 | 108.09 | T157 | BG_P7_CNSTN_NWEST2_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 106.17 | 107.19 | T157 | BG_P7_GRCTN_RAPHEL_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 105.55 | 110.06 | T157 | PN_P1-2_PN-500-010T_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 104.22 | 108.33 | T157 | PJM_500_BG_P4_5_CNSTN_L_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 103.32 | 104.32 | T157 | BG_P7_NEAST_RPHLRD_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 101.26 | 102.23 | T157 | AP_P2-3_PE-500-015_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 100.32 | 102.17 | T157 | PJM_500_BG_P4_5_CNSTN_13_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 228.49 | 237.45 | TOP CROP | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 224.05 | 232.57 | TOP CROP | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 224.05 | 232.57 | TOP CROP | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 224.03 | 232.54 | TOP CROP | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 209.21 | 215.9 | TOP CROP | PECO_P4_PEACH245_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 202.97 | 210.58 | TOP CROP | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 198.66 | 205.8 | TOP CROP | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 198.66 | 205.8 | TOP CROP | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 198.64 | 205.77 | TOP CROP | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 183.92 | 189.36 | TOP CROP | PECO_P4_PEACH245_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 647 | 801 | 117.38 | 118.13 | TOP CROP | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 647 | 801 | 117.38 | 118.13 | TOP CROP | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 647 | 801 | 117.37 | 118.12 | TOP CROP | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 463 | 563 | 115.98 | 116.55 | TOP CROP | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 463 | 563 | 115.98 | 116.21 | TOP CROP | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 463 | 563 | 113.42 | 113.93 | TOP CROP | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 463 | 563 | 113.42 | 114.27 | TOP CROP | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 463 | 563 | 113.37 | 114.21 | TOP CROP | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 463 | 563 | 113.37 | 113.88 | TOP CROP | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 463 | 563 | 113.37 | 114.21 | TOP CROP | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 463 | 563 | 113.37 | 113.87 | TOP CROP | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 116.33 | TOP CROP | PJM_500_BG_P1_5013_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 116.33 | TOP CROP | PJM_500_BG_P4_5_CNSTN_M_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.19 | 116.25 | TOP CROP | Base Case | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 463 | 578 | 110.56 | 110.59 | TOP CROP | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 647 | 801 | 108.33 | 109.18 | TOP CROP | PECO_P4_PEACH245_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 463 | 578 | 108.07 | 108.38 | TOP CROP | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 463 | 578 | 108.02 | 108.32 | TOP CROP | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 463 | 578 | 108.02 | 108.32 | TOP CROP | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 106.71 | 107.77 | TOP CROP | BG_P7_CNSTN_NWEST2_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 106.17 | 106.88 | TOP CROP | BG_P7_GRCTN_RAPHEL_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 105.55 | 109.71 | TOP CROP | PN_P1-2_PN-500-010T_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 463 | 578 | 105.24 | 104.57 | TOP CROP | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 104.22 | 107.98 | TOP CROP | PJM_500_BG_P4_5_CNSTN_L_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 103.32 | 104 | TOP CROP | BG_P7_NEAST_RPHLRD_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 463 | 578 | 102.74 | 102.35 | TOP CROP | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 463 | 578 | 102.69 | 102.3 | TOP CROP | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 463 | 578 | 102.69 | 102.3 | TOP CROP | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 220964 | GRACETON | 220999 | BAGLEY2 | 13 | 230 | 232 | 1331 | 1594 | 101.97 | 102.43 | TOP CROP | BG_P4_5_GRCTN_3T_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 101.26 | 101.99 | TOP CROP | AP_P2-3_PE-500-015_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 116.8 | TR3_G114 | PJM_500_BG_P1_5013_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 116.79 | TR3_G114 | PJM_500_BG_P4_5_CNSTN_M_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.19 | 116.88 | TR3_G114 | Base Case | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 106.71 | 108.22 | TR3_G114 | BG_P7_CNSTN_NWEST2_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 106.17 | 107.33 | TR3_G114 | BG_P7_GRCTN_RAPHEL_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 105.55 | 110.16 | TR3_G114 | PN_P1-2_PN-500-010T_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 104.22 | 108.42 | TR3_G114 | PJM_500_BG_P4_5_CNSTN_L_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 103.32 | 104.46 | TR3_G114 | BG_P7_NEAST_RPHLRD_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 100.32 | 102.3 | TR3_G114 | PJM_500_BG_P4_5_CNSTN_13_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 100.27 | 102.24 | TR3_G114 | PJM_500_BG_P4_5_CNSTN_6_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 228.49 | 237.04 | TWINGROVE | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 224.05 | 232.14 | TWINGROVE | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 224.05 | 232.14 | TWINGROVE | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 224.03 | 232.12 | TWINGROVE | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 209.21 | 215.49 | TWINGROVE | PECO_P4_PEACH245_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 202.97 | 210.18 | TWINGROVE | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 198.66 | 205.39 | TWINGROVE | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 198.66 | 205.39 | TWINGROVE | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 198.64 | 205.36 | TWINGROVE | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 183.92 | 188.96 | TWINGROVE | PECO_P4_PEACH245_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 166.62 | 168.15 | TWINGROVE | Base Case | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 130.65 | 130.6 | TWINGROVE | Base Case | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 647 | 801 | 122.17 | 122.38 | TWINGROVE | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 647 | 801 | 117.38 | 117.92 | TWINGROVE | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 647 | 801 | 117.38 | 117.92 | TWINGROVE | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 647 | 801 | 117.37 | 117.9 | TWINGROVE | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 463 | 563 | 115.98 | 116.21 | TWINGROVE | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 463 | 563 | 115.98 | 115.88 | TWINGROVE | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 463 | 563 | 113.42 | 113.93 | TWINGROVE | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 463 | 563 | 113.42 | 113.59 | TWINGROVE | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 463 | 563 | 113.37 | 113.87 | TWINGROVE | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 463 | 563 | 113.37 | 113.53 | TWINGROVE | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 463 | 563 | 113.37 | 113.87 | TWINGROVE | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 463 | 563 | 113.37 | 113.53 | TWINGROVE | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 116.12 | TWINGROVE | PJM_500_BG_P1_5013_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 116.12 | TWINGROVE | PJM_500_BG_P4_5_CNSTN_M_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.19 | 115.95 | TWINGROVE | Base Case | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 709 | 869 | 110.18 | 110.65 | TWINGROVE | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 463 | 578 | 110.56 | 110.27 | TWINGROVE | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 709 | 869 | 108.55 | 109.15 | TWINGROVE | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 709 | 869 | 108.55 | 109.14 | TWINGROVE | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 709 | 869 | 108.54 | 109.14 | TWINGROVE | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 647 | 801 | 108.33 | 108.96 | TWINGROVE | PECO_P4_PEACH245_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 463 | 578 | 108.07 | 108.04 | TWINGROVE | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 463 | 578 | 108.02 | 107.99 | TWINGROVE | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 463 | 578 | 108.02 | 107.99 | TWINGROVE | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 106.71 | 107.55 | TWINGROVE | BG_P7_CNSTN_NWEST2_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 106.17 | 106.66 | TWINGROVE | BG_P7_GRCTN_RAPHEL_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 105.55 | 109.5 | TWINGROVE | PN_P1-2_PN-500-010T_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 463 | 578 | 105.24 | 104.24 | TWINGROVE | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 104.22 | 107.77 | TWINGROVE | PJM_500_BG_P4_5_CNSTN_L_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 103.32 | 103.79 | TWINGROVE | BG_P7_NEAST_RPHLRD_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 220964 | GRACETON | 220999 | BAGLEY2 | 13 | 230 | 232 | 1331 | 1594 | 101.97 | 102.33 | TWINGROVE | BG_P4_5_GRCTN_3T_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 463 | 578 | 102.74 | 102.02 | TWINGROVE | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 463 | 578 | 102.69 | 101.96 | TWINGROVE | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 463 | 578 | 102.69 | 101.96 | TWINGROVE | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 709 | 869 | 101.29 | 102.18 | TWINGROVE | PECO_P4_PEACH245_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 101.26 | 101.8 | TWINGROVE | AP_P2-3_PE-500-015_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 116.84 | U2-030 | PJM_500_BG_P1_5013_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 116.84 | U2-030 | PJM_500_BG_P4_5_CNSTN_M_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.19 | 116.96 | U2-030 | Base Case | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 105.55 | 110.21 | U2-030 | PN_P1-2_PN-500-010T_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 104.22 | 108.47 | U2-030 | PJM_500_BG_P4_5_CNSTN_L_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 228.49 | 237.75 | U2-072 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 224.05 | 232.88 | U2-072 | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 224.05 | 232.88 | U2-072 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 224.03 | 232.85 | U2-072 | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 209.21 | 216.21 | U2-072 | PECO_P4_PEACH245_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 202.97 | 210.87 | U2-072 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 198.66 | 206.1 | U2-072 | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 198.66 | 206.1 | U2-072 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 198.64 | 206.07 | U2-072 | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 183.92 | 189.66 | U2-072 | PECO_P4_PEACH245_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 116.49 | U2-072 | PJM_500_BG_P1_5013_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 116.49 | U2-072 | PJM_500_BG_P4_5_CNSTN_M_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.19 | 116.45 | U2-072 | Base Case | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 106.71 | 107.93 | U2-072 | BG_P7_CNSTN_NWEST2_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 106.17 | 107.04 | U2-072 | BG_P7_GRCTN_RAPHEL_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 105.55 | 109.87 | U2-072 | PN_P1-2_PN-500-010T_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 104.22 | 108.13 | U2-072 | PJM_500_BG_P4_5_CNSTN_L_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 103.32 | 104.17 | U2-072 | BG_P7_NEAST_RPHLRD_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 101.26 | 102.13 | U2-072 | AP_P2-3_PE-500-015_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 116.64 | U2-073 | PJM_500_BG_P1_5013_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 116.64 | U2-073 | PJM_500_BG_P4_5_CNSTN_M_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.19 | 116.7 | U2-073 | Base Case | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 106.71 | 108.05 | U2-073 | BG_P7_CNSTN_NWEST2_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 106.17 | 107.16 | U2-073 | BG_P7_GRCTN_RAPHEL_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 105.55 | 110.01 | U2-073 | PN_P1-2_PN-500-010T_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 104.22 | 108.28 | U2-073 | PJM_500_BG_P4_5_CNSTN_L_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 103.32 | 104.28 | U2-073 | BG_P7_NEAST_RPHLRD_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 101.26 | 102.22 | U2-073 | AP_P2-3_PE-500-015_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 100.59 | 101.43 | U2-073 | AP_P2-3_PE-500-018D_SRT-SL | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 228.49 | 237.84 | U2-090 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 224.05 | 232.98 | U2-090 | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 224.05 | 232.98 | U2-090 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 224.03 | 232.95 | U2-090 | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 209.21 | 216.3 | U2-090 | PECO_P4_PEACH245_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 202.97 | 210.96 | U2-090 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 198.66 | 206.2 | U2-090 | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 198.66 | 206.2 | U2-090 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 198.64 | 206.17 | U2-090 | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 183.92 | 189.75 | U2-090 | PECO_P4_PEACH245_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 116.55 | U2-090 | PJM_500_BG_P1_5013_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 116.55 | U2-090 | PJM_500_BG_P4_5_CNSTN_M_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.19 | 116.54 | U2-090 | Base Case | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 106.71 | 107.98 | U2-090 | BG_P7_CNSTN_NWEST2_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 106.17 | 107.09 | U2-090 | BG_P7_GRCTN_RAPHEL_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 105.55 | 109.92 | U2-090 | PN_P1-2_PN-500-010T_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 104.22 | 108.18 | U2-090 | PJM_500_BG_P4_5_CNSTN_L_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 103.32 | 104.21 | U2-090 | BG_P7_NEAST_RPHLRD_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 101.26 | 102.17 | U2-090 | AP_P2-3_PE-500-015_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 228.49 | 237.37 | U3-002 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 224.05 | 232.49 | U3-002 | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 224.05 | 232.48 | U3-002 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 224.03 | 232.46 | U3-002 | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 209.21 | 215.82 | U3-002 | PECO_P4_PEACH245_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 202.97 | 210.5 | U3-002 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 198.66 | 205.72 | U3-002 | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 198.66 | 205.72 | U3-002 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 198.64 | 205.69 | U3-002 | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 183.92 | 189.29 | U3-002 | PECO_P4_PEACH245_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 647 | 801 | 122.17 | 122.55 | U3-002 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 647 | 801 | 117.38 | 118.09 | U3-002 | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 647 | 801 | 117.38 | 118.09 | U3-002 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 647 | 801 | 117.37 | 118.08 | U3-002 | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 463 | 563 | 115.98 | 116.48 | U3-002 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 463 | 563 | 115.98 | 116.14 | U3-002 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 463 | 563 | 113.42 | 113.86 | U3-002 | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 463 | 563 | 113.42 | 114.2 | U3-002 | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 463 | 563 | 113.37 | 113.8 | U3-002 | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 463 | 563 | 113.37 | 114.14 | U3-002 | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 463 | 563 | 113.37 | 114.14 | U3-002 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 463 | 563 | 113.37 | 113.8 | U3-002 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 116.29 | U3-002 | PJM_500_BG_P1_5013_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 116.29 | U3-002 | PJM_500_BG_P4_5_CNSTN_M_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.19 | 116.19 | U3-002 | Base Case | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 463 | 578 | 110.56 | 110.53 | U3-002 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 709 | 869 | 108.55 | 109.29 | U3-002 | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 709 | 869 | 108.55 | 109.29 | U3-002 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 709 | 869 | 108.54 | 109.28 | U3-002 | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 647 | 801 | 108.33 | 109.14 | U3-002 | PECO_P4_PEACH245_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 463 | 578 | 108.07 | 108.31 | U3-002 | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 463 | 578 | 108.02 | 108.25 | U3-002 | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 463 | 578 | 108.02 | 108.25 | U3-002 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 106.71 | 107.73 | U3-002 | BG_P7_CNSTN_NWEST2_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 106.17 | 106.84 | U3-002 | BG_P7_GRCTN_RAPHEL_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 105.55 | 109.67 | U3-002 | PN_P1-2_PN-500-010T_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 463 | 578 | 105.24 | 104.5 | U3-002 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 104.22 | 107.94 | U3-002 | PJM_500_BG_P4_5_CNSTN_L_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 103.32 | 103.96 | U3-002 | BG_P7_NEAST_RPHLRD_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 463 | 578 | 102.74 | 102.28 | U3-002 | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 220964 | GRACETON | 220999 | BAGLEY2 | 13 | 230 | 232 | 1331 | 1594 | 101.97 | 102.41 | U3-002 | BG_P4_5_GRCTN_3T_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 463 | 578 | 102.69 | 102.23 | U3-002 | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 463 | 578 | 102.69 | 102.23 | U3-002 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 101.26 | 101.95 | U3-002 | AP_P2-3_PE-500-015_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 116.78 | V1-011 | PJM_500_BG_P1_5013_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 116.78 | V1-011 | PJM_500_BG_P4_5_CNSTN_M_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.19 | 116.86 | V1-011 | Base Case | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 106.71 | 108.21 | V1-011 | BG_P7_CNSTN_NWEST2_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 106.17 | 107.32 | V1-011 | BG_P7_GRCTN_RAPHEL_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 105.55 | 110.15 | V1-011 | PN_P1-2_PN-500-010T_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 104.22 | 108.41 | V1-011 | PJM_500_BG_P4_5_CNSTN_L_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 103.32 | 104.44 | V1-011 | BG_P7_NEAST_RPHLRD_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 100.32 | 102.29 | V1-011 | PJM_500_BG_P4_5_CNSTN_13_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 100.27 | 102.23 | V1-011 | PJM_500_BG_P4_5_CNSTN_6_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 228.49 | 237.8 | V3-007 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 224.05 | 232.94 | V3-007 | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 224.05 | 232.93 | V3-007 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 224.03 | 232.91 | V3-007 | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 209.21 | 216.26 | V3-007 | PECO_P4_PEACH245_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 202.97 | 210.92 | V3-007 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 198.66 | 206.15 | V3-007 | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 198.66 | 206.15 | V3-007 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 198.64 | 206.13 | V3-007 | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 183.92 | 189.71 | V3-007 | PECO_P4_PEACH245_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 116.52 | V3-007 | PJM_500_BG_P1_5013_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 116.52 | V3-007 | PJM_500_BG_P4_5_CNSTN_M_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.19 | 116.51 | V3-007 | Base Case | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 106.71 | 107.96 | V3-007 | BG_P7_CNSTN_NWEST2_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 106.17 | 107.06 | V3-007 | BG_P7_GRCTN_RAPHEL_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 105.55 | 109.9 | V3-007 | PN_P1-2_PN-500-010T_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 104.22 | 108.16 | V3-007 | PJM_500_BG_P4_5_CNSTN_L_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 103.32 | 104.19 | V3-007 | BG_P7_NEAST_RPHLRD_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 101.26 | 102.15 | V3-007 | AP_P2-3_PE-500-015_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 209.21 | 216.46 | V3-028 | PECO_P4_PEACH245_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 183.92 | 189.9 | V3-028 | PECO_P4_PEACH245_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 116.62 | V3-028 | PJM_500_BG_P1_5013_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 116.62 | V3-028 | PJM_500_BG_P4_5_CNSTN_M_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.19 | 116.64 | V3-028 | Base Case | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 106.71 | 108.06 | V3-028 | BG_P7_CNSTN_NWEST2_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 106.17 | 107.17 | V3-028 | BG_P7_GRCTN_RAPHEL_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 105.55 | 110 | V3-028 | PN_P1-2_PN-500-010T_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 104.22 | 108.26 | V3-028 | PJM_500_BG_P4_5_CNSTN_L_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 103.32 | 104.3 | V3-028 | BG_P7_NEAST_RPHLRD_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 101.26 | 102.24 | V3-028 | AP_P2-3_PE-500-015_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.19 | 117.36 | W1-003 | Base Case | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.19 | 117.36 | W1-004 | Base Case | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.19 | 117.36 | W1-005 | Base Case | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.19 | 117.36 | W1-006 | Base Case | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 228.49 | 237.29 | W1-029 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 224.05 | 232.43 | W1-029 | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 224.05 | 232.43 | W1-029 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 224.03 | 232.4 | W1-029 | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 209.21 | 215.75 | W1-029 | PECO_P4_PEACH245_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 202.97 | 210.42 | W1-029 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 198.66 | 205.65 | W1-029 | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 198.66 | 205.65 | W1-029 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 198.64 | 205.63 | W1-029 | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 183.92 | 189.21 | W1-029 | PECO_P4_PEACH245_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 166.62 | 168.14 | W1-029 | Base Case | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 130.65 | 130.56 | W1-029 | Base Case | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 559 | 680 | 129.8 | 131.44 | W1-029 | PEPCO_P1_PP2_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 2 | 230 | 233 | 559 | 680 | 129.8 | 131.44 | W1-029 | PEPCO_P1_PP1_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 647 | 801 | 122.17 | 122.47 | W1-029 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 559 | 680 | 122.19 | 121.98 | W1-029 | DVP_P4-2: 514T595_SRT-SW | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 2 | 230 | 233 | 559 | 680 | 122.19 | 121.98 | W1-029 | DVP_P4-2: 514T595_SRT-SW | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 559 | 680 | 119.41 | 119.01 | W1-029 | DVP_P4-2: 51482_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 2 | 230 | 233 | 559 | 680 | 119.41 | 119.01 | W1-029 | DVP_P4-2: 51482_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 2 | 230 | 233 | 559 | 680 | 119.12 | 119.01 | W1-029 | DVP_P1-2: LN 514_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 2 | 230 | 233 | 559 | 680 | 119.12 | 119.01 | W1-029 | AP_P1-2_PE-500-407T_SRT-SL | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 559 | 680 | 119.12 | 119.01 | W1-029 | AP_P1-2_PE-500-407T_SRT-SL | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 559 | 680 | 119.12 | 119.01 | W1-029 | DVP_P1-2: LN 514_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 647 | 801 | 117.38 | 118.03 | W1-029 | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 647 | 801 | 117.38 | 118.03 | W1-029 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 647 | 801 | 117.37 | 118.02 | W1-029 | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 463 | 563 | 115.98 | 116.29 | W1-029 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 463 | 563 | 115.98 | 116.62 | W1-029 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 463 | 563 | 113.42 | 114.35 | W1-029 | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 463 | 563 | 113.42 | 114.02 | W1-029 | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 463 | 563 | 113.37 | 113.96 | W1-029 | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 463 | 563 | 113.37 | 114.3 | W1-029 | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 463 | 563 | 113.37 | 113.96 | W1-029 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 463 | 563 | 113.37 | 114.29 | W1-029 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 116.3 | W1-029 | PJM_500_BG_P1_5013_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 116.3 | W1-029 | PJM_500_BG_P4_5_CNSTN_M_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.19 | 116.33 | W1-029 | Base Case | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 709 | 869 | 110.18 | 110.8 | W1-029 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 463 | 578 | 110.56 | 110.67 | W1-029 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 709 | 869 | 108.55 | 109.3 | W1-029 | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 709 | 869 | 108.55 | 109.3 | W1-029 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 709 | 869 | 108.54 | 109.29 | W1-029 | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 647 | 801 | 108.33 | 109.07 | W1-029 | PECO_P4_PEACH245_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 463 | 578 | 108.07 | 108.46 | W1-029 | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 463 | 578 | 108.02 | 108.4 | W1-029 | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 463 | 578 | 108.02 | 108.4 | W1-029 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 106.71 | 107.64 | W1-029 | BG_P7_CNSTN_NWEST2_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 106.17 | 106.75 | W1-029 | BG_P7_GRCTN_RAPHEL_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 105.55 | 109.67 | W1-029 | PN_P1-2_PN-500-010T_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 463 | 578 | 105.24 | 104.65 | W1-029 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 104.22 | 107.94 | W1-029 | PJM_500_BG_P4_5_CNSTN_L_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 103.32 | 103.88 | W1-029 | BG_P7_NEAST_RPHLRD_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 463 | 578 | 102.74 | 102.43 | W1-029 | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 463 | 578 | 102.69 | 102.38 | W1-029 | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 463 | 578 | 102.69 | 102.38 | W1-029 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 220964 | GRACETON | 220999 | BAGLEY2 | 13 | 230 | 232 | 1331 | 1594 | 101.97 | 102.34 | W1-029 | BG_P4_5_GRCTN_3T_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 709 | 869 | 101.29 | 102.32 | W1-029 | PECO_P4_PEACH245_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 101.26 | 101.8 | W1-029 | AP_P2-3_PE-500-015_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 116.85 | W1-056 | PJM_500_BG_P1_5013_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 116.85 | W1-056 | PJM_500_BG_P4_5_CNSTN_M_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.19 | 116.95 | W1-056 | Base Case | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 105.55 | 110.21 | W1-056 | PN_P1-2_PN-500-010T_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 228.49 | 237.31 | W4-005 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 224.05 | 232.42 | W4-005 | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 224.05 | 232.42 | W4-005 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 224.03 | 232.4 | W4-005 | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 209.21 | 215.76 | W4-005 | PECO_P4_PEACH245_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 202.97 | 210.44 | W4-005 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 198.66 | 205.66 | W4-005 | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 198.66 | 205.66 | W4-005 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 198.64 | 205.63 | W4-005 | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 183.92 | 189.23 | W4-005 | PECO_P4_PEACH245_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 647 | 801 | 122.17 | 122.52 | W4-005 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 647 | 801 | 117.38 | 118.06 | W4-005 | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 647 | 801 | 117.38 | 118.06 | W4-005 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 647 | 801 | 117.37 | 118.04 | W4-005 | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 463 | 563 | 115.98 | 116.44 | W4-005 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 463 | 563 | 115.98 | 116.1 | W4-005 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 463 | 563 | 113.42 | 114.16 | W4-005 | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 463 | 563 | 113.42 | 113.82 | W4-005 | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 463 | 563 | 113.37 | 114.1 | W4-005 | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 463 | 563 | 113.37 | 113.77 | W4-005 | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 463 | 563 | 113.37 | 113.77 | W4-005 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 463 | 563 | 113.37 | 114.1 | W4-005 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 116.26 | W4-005 | PJM_500_BG_P1_5013_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 116.26 | W4-005 | PJM_500_BG_P4_5_CNSTN_M_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.19 | 116.16 | W4-005 | Base Case | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 709 | 869 | 110.18 | 110.77 | W4-005 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 463 | 578 | 110.56 | 110.49 | W4-005 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 709 | 869 | 108.55 | 109.26 | W4-005 | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 709 | 869 | 108.55 | 109.26 | W4-005 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 709 | 869 | 108.54 | 109.26 | W4-005 | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 647 | 801 | 108.33 | 109.1 | W4-005 | PECO_P4_PEACH245_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 463 | 578 | 108.07 | 108.27 | W4-005 | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 463 | 578 | 108.02 | 108.21 | W4-005 | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 463 | 578 | 108.02 | 108.21 | W4-005 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 106.71 | 107.69 | W4-005 | BG_P7_CNSTN_NWEST2_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 106.17 | 106.8 | W4-005 | BG_P7_GRCTN_RAPHEL_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 105.55 | 109.64 | W4-005 | PN_P1-2_PN-500-010T_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 463 | 578 | 105.24 | 104.47 | W4-005 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 104.22 | 107.91 | W4-005 | PJM_500_BG_P4_5_CNSTN_L_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 103.32 | 103.93 | W4-005 | BG_P7_NEAST_RPHLRD_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 220964 | GRACETON | 220999 | BAGLEY2 | 13 | 230 | 232 | 1331 | 1594 | 101.97 | 102.4 | W4-005 | BG_P4_5_GRCTN_3T_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 463 | 578 | 102.74 | 102.25 | W4-005 | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 463 | 578 | 102.69 | 102.19 | W4-005 | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 463 | 578 | 102.69 | 102.19 | W4-005 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 709 | 869 | 101.29 | 102.3 | W4-005 | PECO_P4_PEACH245_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 101.26 | 101.92 | W4-005 | AP_P2-3_PE-500-015_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 228.49 | 237.93 | X2-022 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 224.05 | 233.07 | X2-022 | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 224.05 | 233.06 | X2-022 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 224.03 | 233.04 | X2-022 | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 209.21 | 216.39 | X2-022 | PECO_P4_PEACH245_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 202.97 | 211.04 | X2-022 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 198.66 | 206.28 | X2-022 | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 198.66 | 206.28 | X2-022 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 198.64 | 206.25 | X2-022 | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 183.92 | 189.83 | X2-022 | PECO_P4_PEACH245_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 116.59 | X2-022 | PJM_500_BG_P1_5013_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 116.59 | X2-022 | PJM_500_BG_P4_5_CNSTN_M_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.19 | 116.61 | X2-022 | Base Case | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 106.71 | 108.02 | X2-022 | BG_P7_CNSTN_NWEST2_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 106.17 | 107.13 | X2-022 | BG_P7_GRCTN_RAPHEL_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 105.55 | 109.97 | X2-022 | PN_P1-2_PN-500-010T_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 104.22 | 108.23 | X2-022 | PJM_500_BG_P4_5_CNSTN_L_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 103.32 | 104.25 | X2-022 | BG_P7_NEAST_RPHLRD_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 101.26 | 102.2 | X2-022 | AP_P2-3_PE-500-015_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 116.73 | X2-060 | PJM_500_BG_P1_5013_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 116.73 | X2-060 | PJM_500_BG_P4_5_CNSTN_M_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.19 | 116.84 | X2-060 | Base Case | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 106.71 | 108.13 | X2-060 | BG_P7_CNSTN_NWEST2_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 106.17 | 107.23 | X2-060 | BG_P7_GRCTN_RAPHEL_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 105.55 | 110.1 | X2-060 | PN_P1-2_PN-500-010T_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 104.22 | 108.36 | X2-060 | PJM_500_BG_P4_5_CNSTN_L_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 103.32 | 104.36 | X2-060 | BG_P7_NEAST_RPHLRD_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 101.26 | 102.27 | X2-060 | AP_P2-3_PE-500-015_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 100.32 | 102.21 | X2-060 | PJM_500_BG_P4_5_CNSTN_13_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 228.49 | 236.34 | Z1-036 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 224.05 | 231.46 | Z1-036 | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 224.05 | 231.45 | Z1-036 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 224.03 | 231.43 | Z1-036 | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 209.21 | 214.79 | Z1-036 | PECO_P4_PEACH245_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 202.97 | 209.49 | Z1-036 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 198.66 | 204.71 | Z1-036 | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 198.66 | 204.71 | Z1-036 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 198.64 | 204.69 | Z1-036 | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 183.92 | 188.28 | Z1-036 | PECO_P4_PEACH245_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 166.62 | 167.52 | Z1-036 | Base Case | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 130.65 | 130 | Z1-036 | Base Case | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 559 | 680 | 129.8 | 130.85 | Z1-036 | PEPCO_P1_PP2_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 2 | 230 | 233 | 559 | 680 | 129.8 | 130.85 | Z1-036 | PEPCO_P1_PP1_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 647 | 801 | 122.17 | 121.98 | Z1-036 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 559 | 680 | 122.19 | 121.31 | Z1-036 | DVP_P4-2: 514T595_SRT-SW | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 2 | 230 | 233 | 559 | 680 | 122.19 | 121.31 | Z1-036 | DVP_P4-2: 514T595_SRT-SW | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 2 | 230 | 233 | 559 | 680 | 119.41 | 118.32 | Z1-036 | DVP_P4-2: 51482_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 559 | 680 | 119.41 | 118.32 | Z1-036 | DVP_P4-2: 51482_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 2 | 230 | 233 | 559 | 680 | 119.12 | 118.32 | Z1-036 | DVP_P1-2: LN 514_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 2 | 230 | 233 | 559 | 680 | 119.12 | 118.32 | Z1-036 | AP_P1-2_PE-500-407T_SRT-SL | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 559 | 680 | 119.12 | 118.32 | Z1-036 | AP_P1-2_PE-500-407T_SRT-SL | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 559 | 680 | 119.12 | 118.32 | Z1-036 | DVP_P1-2: LN 514_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 207923 | BRISREAC | 208132 | WHEM TR1 | 1 | 230 | 229 | 493 | 618 | 117.78 | 118.11 | Z1-036 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 207922 | BRIS | 207923 | BRISREAC | RX | 230 | 229 | 506 | 618 | 117.78 | 118.11 | Z1-036 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 647 | 801 | 117.38 | 117.52 | Z1-036 | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 647 | 801 | 117.38 | 117.52 | Z1-036 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 647 | 801 | 117.37 | 117.5 | Z1-036 | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 463 | 563 | 115.98 | 115.63 | Z1-036 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 463 | 563 | 115.98 | 115.96 | Z1-036 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 207923 | BRISREAC | 208132 | WHEM TR1 | 1 | 230 | 229 | 493 | 618 | 115.13 | 115.71 | Z1-036 | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 207922 | BRIS | 207923 | BRISREAC | RX | 230 | 229 | 506 | 618 | 115.13 | 115.71 | Z1-036 | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 207923 | BRISREAC | 208132 | WHEM TR1 | 1 | 230 | 229 | 493 | 618 | 115.13 | 115.71 | Z1-036 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 207922 | BRIS | 207923 | BRISREAC | RX | 230 | 229 | 506 | 618 | 115.13 | 115.71 | Z1-036 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 207922 | BRIS | 207923 | BRISREAC | RX | 230 | 229 | 506 | 618 | 115.12 | 115.7 | Z1-036 | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 207923 | BRISREAC | 208132 | WHEM TR1 | 1 | 230 | 229 | 493 | 618 | 115.12 | 115.7 | Z1-036 | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 463 | 563 | 113.42 | 113.35 | Z1-036 | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 463 | 563 | 113.42 | 113.68 | Z1-036 | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 463 | 563 | 113.37 | 113.29 | Z1-036 | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 463 | 563 | 113.37 | 113.63 | Z1-036 | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 463 | 563 | 113.37 | 113.29 | Z1-036 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 463 | 563 | 113.37 | 113.63 | Z1-036 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 115.82 | Z1-036 | PJM_500_BG_P1_5013_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 115.82 | Z1-036 | PJM_500_BG_P4_5_CNSTN_M_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.19 | 115.76 | Z1-036 | Base Case | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 709 | 869 | 110.18 | 110.41 | Z1-036 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 463 | 578 | 110.56 | 110.03 | Z1-036 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 709 | 869 | 108.55 | 108.91 | Z1-036 | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 709 | 869 | 108.55 | 108.91 | Z1-036 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 709 | 869 | 108.54 | 108.9 | Z1-036 | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 647 | 801 | 108.33 | 108.56 | Z1-036 | PECO_P4_PEACH245_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 207922 | BRIS | 207923 | BRISREAC | RX | 230 | 229 | 506 | 618 | 107.75 | 108.66 | Z1-036 | PECO_P4_PEACH245_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 207923 | BRISREAC | 208132 | WHEM TR1 | 1 | 230 | 229 | 493 | 618 | 107.75 | 108.66 | Z1-036 | PECO_P4_PEACH245_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 463 | 578 | 108.07 | 107.81 | Z1-036 | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 463 | 578 | 108.02 | 107.75 | Z1-036 | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 463 | 578 | 108.02 | 107.75 | Z1-036 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 106.71 | 107.11 | Z1-036 | BG_P7_CNSTN_NWEST2_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208131 | WHEM | 208132 | WHEM TR1 | 1 | 230 | 229 | 547 | 618 | 106.32 | 105.29 | Z1-036 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 106.17 | 106.22 | Z1-036 | BG_P7_GRCTN_RAPHEL_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 105.55 | 109.2 | Z1-036 | PN_P1-2_PN-500-010T_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 463 | 578 | 105.24 | 104.01 | Z1-036 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 104.22 | 107.47 | Z1-036 | PJM_500_BG_P4_5_CNSTN_L_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208131 | WHEM | 208132 | WHEM TR1 | 1 | 230 | 229 | 547 | 618 | 103.73 | 102.95 | Z1-036 | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208131 | WHEM | 208132 | WHEM TR1 | 1 | 230 | 229 | 547 | 618 | 103.73 | 102.95 | Z1-036 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208131 | WHEM | 208132 | WHEM TR1 | 1 | 230 | 229 | 547 | 618 | 103.72 | 102.94 | Z1-036 | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 103.32 | 103.35 | Z1-036 | BG_P7_NEAST_RPHLRD_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 220964 | GRACETON | 220999 | BAGLEY2 | 13 | 230 | 232 | 1331 | 1594 | 101.97 | 102.07 | Z1-036 | BG_P4_5_GRCTN_3T_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 463 | 578 | 102.74 | 101.79 | Z1-036 | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 463 | 578 | 102.69 | 101.73 | Z1-036 | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 463 | 578 | 102.69 | 101.73 | Z1-036 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 709 | 869 | 101.29 | 101.94 | Z1-036 | PECO_P4_PEACH245_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 228.49 | 237.8 | Z2-087 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 224.05 | 232.93 | Z2-087 | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 224.05 | 232.93 | Z2-087 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 224.03 | 232.9 | Z2-087 | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 666 | 797 | 209.21 | 216.26 | Z2-087 | PECO_P4_PEACH245_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 202.97 | 210.91 | Z2-087 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 198.66 | 206.15 | Z2-087 | PECO_P1-2_5012_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 198.66 | 206.15 | Z2-087 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 198.64 | 206.12 | Z2-087 | PECO_P4_PEACH235_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 721 | 814 | 183.92 | 189.7 | Z2-087 | PECO_P4_PEACH245_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 116.52 | Z2-087 | PJM_500_BG_P1_5013_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 116.52 | Z2-087 | PJM_500_BG_P4_5_CNSTN_M_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.19 | 116.51 | Z2-087 | Base Case | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 106.71 | 107.95 | Z2-087 | BG_P7_CNSTN_NWEST2_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 106.17 | 107.06 | Z2-087 | BG_P7_GRCTN_RAPHEL_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 105.55 | 109.9 | Z2-087 | PN_P1-2_PN-500-010T_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 104.22 | 108.16 | Z2-087 | PJM_500_BG_P4_5_CNSTN_L_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 103.32 | 104.19 | Z2-087 | BG_P7_NEAST_RPHLRD_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 101.26 | 102.14 | Z2-087 | AP_P2-3_PE-500-015_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 116.8 | Z2-088 | PJM_500_BG_P1_5013_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.54 | 116.8 | Z2-088 | PJM_500_BG_P4_5_CNSTN_M_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 112.19 | 116.92 | Z2-088 | Base Case | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 106.71 | 108.2 | Z2-088 | BG_P7_CNSTN_NWEST2_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 106.17 | 107.31 | Z2-088 | BG_P7_GRCTN_RAPHEL_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 105.55 | 110.16 | Z2-088 | PN_P1-2_PN-500-010T_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 232/230 | 2828 | 3526 | 104.22 | 108.43 | Z2-088 | PJM_500_BG_P4_5_CNSTN_L_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 103.32 | 104.43 | Z2-088 | BG_P7_NEAST_RPHLRD_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 101.26 | 102.34 | Z2-088 | AP_P2-3_PE-500-015_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 233/232 | 2490 | 2815 | 100.32 | 102.28 | Z2-088 | PJM_500_BG_P4_5_CNSTN_13_SRT-A | N/A | No | Related to 2022 Window 3, pending window outcome