## N-1 Thermal
Note | APS and Dominion zones as a whole are quarantined pending Window 3 outcome and are not included in above results
Related to 2022 Window 3, pending window outcome
PJM N-1 Thermal Result (Summer 2028 Case)
FG # | Fr Bus | Fr Name | To Bus | To Name | CKT | KVs | Areas | Rating | DC Ld(%) | AC Ld(%) | Cont Type | Contingency | Conductor/Transformer Rating (MVA) | PJM Accepting Proposals | Reasons for Exclusions | Comments
2023W1-N1-ST1 | 232013 | SILVER RUN | 232002 | CEDAR CK | 1 | 230/230 | 231/235 | 805 | 101.9255 | 104.58 | Line_FB | 'DPL_P4-2_DP6_SRT-A' | 653/808 (SN/SE) | Yes
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230/230 | 229/232 | 797 | 238.6951 | 228.49 | Line_FB | 'PJM_500_BG_P4_5_CNSTN_B_SRT-A' | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230/230 | 229/232 | 797 | 233.8519 | 224.06 | Single | 'PECO_P1-2_5012_SRT-A' | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230/230 | 229/232 | 797 | 233.8519 | 224.06 | Line_FB | 'PJM_500_BG_P4_5_CNSTN_C_SRT-A' | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230/230 | 229/232 | 797 | 233.8269 | 224.04 | Line_FB | 'PECO_P4_PEACH235_SRT-A' | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230/230 | 229/232 | 797 | 217.1644 | 209.22 | Line_FB | 'PECO_P4_PEACH245_SRT-A' | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230/230 | 229/229 | 814 | 211.769 | 202.98 | Line_FB | 'PJM_500_BG_P4_5_CNSTN_B_SRT-A' | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230/230 | 229/229 | 814 | 207.0393 | 198.67 | Single | 'PECO_P1-2_5012_SRT-A' | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230/230 | 229/229 | 814 | 207.0393 | 198.67 | Line_FB | 'PJM_500_BG_P4_5_CNSTN_C_SRT-A' | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230/230 | 229/229 | 814 | 207.0147 | 198.65 | Line_FB | 'PECO_P4_PEACH235_SRT-A' | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230/230 | 229/232 | 797 | 200.3764 | 196.54 | Tower | 'BG_P7_GRCTN_CNSTN_SRT-A' | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230/230 | 229/229 | 814 | 190.5651 | 183.93 | Line_FB | 'PECO_P4_PEACH245_SRT-A' | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230/230 | 229/232 | 797 | 179.6863 | 176.57 | Line_FB | 'PJM_500_BG_P4_5_CNSTN_15_SRT-A' | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230/230 | 229/229 | 814 | 174.2629 | 171.57 | Tower | 'BG_P7_GRCTN_CNSTN_SRT-A' | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230/230 | 229/232 | 666 | 169.0541 | 166.62 | Single | 'BASE CASE' | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230/230 | 229/232 | 797 | 160.1882 | 162.69 | Single | 'PJM_500_BG_P1_5011_SRT-A' | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230/230 | 229/232 | 797 | 161.995 | 159.09 | Bus | 'PJM_500_BG_P2_CNSTN_230-S_SRT-A' | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230/230 | 229/232 | 797 | 161.995 | 159.09 | Single | 'BG_P1_CNSTN_500-4_SRT-A' | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230/230 | 229/232 | 797 | 161.9322 | 159.03 | Bus | 'PJM_500_BG_P2_CNSTN_230-N_SRT-A' | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230/230 | 229/232 | 797 | 161.9322 | 159.03 | Single | 'BG_P1_CNSTN_500-2_SRT-A' | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230/230 | 229/229 | 814 | 154.0049 | 151.92 | Line_FB | 'PJM_500_BG_P4_5_CNSTN_15_SRT-A' | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230/230 | 229/232 | 797 | 152.9987 | 150.24 | Bus | 'PECO_P2-2_NOTT230B_SRT-A' | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230/230 | 229/232 | 797 | 147.4028 | 145.37 | Tower | 'PL_04_P71_100954_SRT-A' | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230/230 | 229/232 | 797 | 146.4492 | 144.64 | Tower | 'BG_P7_WCHPL_BRNDN_SRT-A' | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230/230 | 229/232 | 797 | 145.7967 | 143.94 | Tower | 'DVP_P7-1: LN 2114-535_SRT-SW' | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230/230 | 229/232 | 797 | 146.0477 | 143.83 | Bus | 'ME_P2-2_ME-115-003_SRT-A' | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230/230 | 229/232 | 797 | 145.9473 | 143.74 | Bus | 'AP_P2-2_PE-138-073_SRT-A' | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230/230 | 229/232 | 797 | 145.9473 | 143.74 | Tower | 'AP_P7-1_PE-138-022T_SRT-A' | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 221090 | GLENARM2 | 221089 | WINDYED1 | 1 | 115/115 | 232/232 | 192 | 140.8854 | 141.81 | Tower | 'BG_P7_GRCTN_RAPHEL_SRT-A' | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230/230 | 229/229 | 814 | 134.9017 | 139.45 | Single | 'PJM_500_BG_P1_5011_SRT-A' | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 221092 | FIVE.FOR | 221096 | ROCKRGE1 | 1 | 115/115 | 232/232 | 256 | 134.1406 | 135.39 | Tower | 'BG_P7_GRCTN_RAPHEL_SRT-A' | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230/230 | 229/229 | 814 | 136.6708 | 134.9 | Bus | 'PJM_500_BG_P2_CNSTN_230-S_SRT-A' | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230/230 | 229/229 | 814 | 136.6708 | 134.9 | Single | 'BG_P1_CNSTN_500-4_SRT-A' | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230/230 | 229/229 | 814 | 136.6093 | 134.84 | Bus | 'PJM_500_BG_P2_CNSTN_230-N_SRT-A' | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230/230 | 229/229 | 814 | 136.6093 | 134.84 | Single | 'BG_P1_CNSTN_500-2_SRT-A' | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230/230 | 229/229 | 814 | 139.2506 | 134.67 | Single | 'PJM_500_BG_P1_5013_SRT-A' | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 221090 | GLENARM2 | 221089 | WINDYED1 | 1 | 115/115 | 232/232 | 192 | 129.375 | 131 | Tower | 'BG_P7_NEAST_RPHLRD_SRT-A' | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 223938 | DICKH230 | 223937 | DICK 230 | 2 | 230/230 | 233/233 | 680 | 132.2794 | 129.82 | Single | 'PEPCO_P1_PP1_SRT-A' | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 223938 | DICKH230 | 223937 | DICK 230 | 1 | 230/230 | 233/233 | 680 | 132.2794 | 129.82 | Single | 'PEPCO_P1_PP2_SRT-A' | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 221092 | FIVE.FOR | 221096 | ROCKRGE1 | 1 | 115/115 | 232/232 | 256 | 125.5469 | 127.24 | Tower | 'BG_P7_NEAST_RPHLRD_SRT-A' | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230/230 | 229/229 | 814 | 127.8747 | 126.33 | Bus | 'PECO_P2-2_NOTT230B_SRT-A' | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 223938 | DICKH230 | 223937 | DICK 230 | 2 | 230/230 | 233/233 | 680 | 122.9706 | 122.19 | Line_FB | 'DVP_P4-2: 514T595_SRT-SW' | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 223938 | DICKH230 | 223937 | DICK 230 | 1 | 230/230 | 233/233 | 680 | 122.9706 | 122.19 | Line_FB | 'DVP_P4-2: 514T595_SRT-SW' | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230/230 | 227/229 | 801 | 123.2085 | 122.16 | Line_FB | 'PJM_500_BG_P4_5_CNSTN_B_SRT-A' | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230/230 | 229/229 | 814 | 122.3956 | 121.69 | Tower | 'PL_04_P71_100954_SRT-A' | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230/230 | 229/229 | 814 | 121.4619 | 121.12 | Tower | 'BG_P7_WCHPL_BRNDN_SRT-A' | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230/230 | 229/229 | 814 | 120.8108 | 120.35 | Tower | 'DVP_P7-1: LN 2114-535_SRT-SW' | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230/230 | 229/229 | 814 | 121.0565 | 120.21 | Bus | 'ME_P2-2_ME-115-003_SRT-A' | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230/230 | 229/229 | 814 | 120.9705 | 120.12 | Bus | 'AP_P2-2_PE-138-073_SRT-A' | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230/230 | 229/229 | 814 | 120.9705 | 120.12 | Tower | 'AP_P7-1_PE-138-022T_SRT-A' | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 223938 | DICKH230 | 223937 | DICK 230 | 2 | 230/230 | 233/233 | 680 | 120.0294 | 119.41 | Line_FB | 'DVP_P4-2: 51482_SRT-A' | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 223938 | DICKH230 | 223937 | DICK 230 | 1 | 230/230 | 233/233 | 680 | 120.0294 | 119.41 | Line_FB | 'DVP_P4-2: 51482_SRT-A' | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 223938 | DICKH230 | 223937 | DICK 230 | 2 | 230/230 | 233/233 | 680 | 120.0294 | 119.11 | Single | 'DVP_P1-2: LN 514_SRT-A' | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 223938 | DICKH230 | 223937 | DICK 230 | 2 | 230/230 | 233/233 | 680 | 120.0294 | 119.11 | Single | 'AP_P1-2_PE-500-407T_SRT-SL' | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 223938 | DICKH230 | 223937 | DICK 230 | 1 | 230/230 | 233/233 | 680 | 120.0294 | 119.11 | Single | 'DVP_P1-2: LN 514_SRT-A' | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 223938 | DICKH230 | 223937 | DICK 230 | 1 | 230/230 | 233/233 | 680 | 120.0294 | 119.11 | Single | 'AP_P1-2_PE-500-407T_SRT-SL' | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 221051 | CHESTN8A | 221049 | FRED.RD8 | 1 | 115/115 | 232/232 | 189 | 116.6667 | 118.93 | Tower | 'BG_P7_GRCTN_RAPHEL_SRT-A' | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 207923 | BRISREAC | 208132 | WHEM TR1 | 1 | 230/230 | 229/229 | 618 | 119.0939 | 117.78 | Line_FB | 'PJM_500_BG_P4_5_CNSTN_B_SRT-A' | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 207922 | BRIS | 207923 | BRISREAC | RX | 230/230 | 229/229 | 618 | 119.0939 | 117.78 | Line_FB | 'PJM_500_BG_P4_5_CNSTN_B_SRT-A' | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230/230 | 227/229 | 801 | 118.789 | 117.39 | Single | 'PECO_P1-2_5012_SRT-A' | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230/230 | 227/229 | 801 | 118.789 | 117.38 | Line_FB | 'PJM_500_BG_P4_5_CNSTN_C_SRT-A' | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230/230 | 227/229 | 801 | 118.7765 | 117.37 | Line_FB | 'PECO_P4_PEACH235_SRT-A' | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 208070 | SAHA12TP | 1 | 230/230 | 229/229 | 628 | 117.3726 | 116.85 | Tower | 'BG_P7_GRCTN_CNSTN_SRT-A' | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 205912 | AD1-020 TAP | 204544 | 27LINCOLN | 1 | 115/115 | 227/227 | 282 | 117.234 | 116.73 | Single | 'PJM_500_BG_P1_5011_SRT-A' | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 205912 | AD1-020 TAP | 204544 | 27LINCOLN | 1 | 115/115 | 227/227 | 282 | 117.234 | 116.72 | Line_FB | 'PJM_500_BG_P4_5_CNSTN_J_SRT-A' | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 205912 | AD1-020 TAP | 204544 | 27LINCOLN | 1 | 115/115 | 227/227 | 282 | 116.9858 | 116.46 | Line_FB | 'PEPCO_P4_PP40_SRT-A' | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230/230 | 230/230 | 563 | 117.2647 | 115.99 | Line_FB | 'PJM_500_BG_P4_5_CNSTN_B_SRT-A' | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230/230 | 230/230 | 563 | 117.6199 | 115.99 | Line_FB | 'PJM_500_BG_P4_5_CNSTN_B_SRT-A' | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 207923 | BRISREAC | 208132 | WHEM TR1 | 1 | 230/230 | 229/229 | 618 | 116.7152 | 115.14 | Single | 'PECO_P1-2_5012_SRT-A' | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 207922 | BRIS | 207923 | BRISREAC | RX | 230/230 | 229/229 | 618 | 116.7152 | 115.14 | Single | 'PECO_P1-2_5012_SRT-A' | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 207923 | BRISREAC | 208132 | WHEM TR1 | 1 | 230/230 | 229/229 | 618 | 116.7152 | 115.13 | Line_FB | 'PJM_500_BG_P4_5_CNSTN_C_SRT-A' | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 207922 | BRIS | 207923 | BRISREAC | RX | 230/230 | 229/229 | 618 | 116.7152 | 115.13 | Line_FB | 'PJM_500_BG_P4_5_CNSTN_C_SRT-A' | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 207923 | BRISREAC | 208132 | WHEM TR1 | 1 | 230/230 | 229/229 | 618 | 116.699 | 115.12 | Line_FB | 'PECO_P4_PEACH235_SRT-A' | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 207922 | BRIS | 207923 | BRISREAC | RX | 230/230 | 229/229 | 618 | 116.699 | 115.12 | Line_FB | 'PECO_P4_PEACH235_SRT-A' | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230/230 | 230/230 | 563 | 115.0089 | 113.44 | Line_FB | 'PECO_P4_PEACH235_SRT-A' | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230/230 | 230/230 | 563 | 115.3641 | 113.44 | Line_FB | 'PECO_P4_PEACH235_SRT-A' | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230/230 | 230/230 | 563 | 114.9556 | 113.39 | Single | 'PECO_P1-2_5012_SRT-A' | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230/230 | 230/230 | 563 | 114.9556 | 113.39 | Line_FB | 'PJM_500_BG_P4_5_CNSTN_C_SRT-A' | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230/230 | 230/230 | 563 | 115.2931 | 113.39 | Single | 'PECO_P1-2_5012_SRT-A' | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230/230 | 230/230 | 563 | 115.2931 | 113.39 | Line_FB | 'PJM_500_BG_P4_5_CNSTN_C_SRT-A' | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 221054 | CHESTN7A | 221050 | FRED.RD7 | 1 | 115/115 | 232/232 | 189 | 110.8466 | 113.03 | Tower | 'BG_P7_GRCTN_RAPHEL_SRT-A' | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200004 | CNASTONE | 1 | 500/500 | 230/232 | 3526 | 116.9994 | 112.54 | Single | 'PJM_500_BG_P1_5013_SRT-A' | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200004 | CNASTONE | 1 | 500/500 | 230/232 | 3526 | 116.9966 | 112.54 | Line_FB | 'PJM_500_BG_P4_5_CNSTN_M_SRT-A' | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500/500 | 232/230 | 2828 | 117.1676 | 112.18 | Single | 'BASE CASE' | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 221092 | FIVE.FOR | 221096 | ROCKRGE1 | 1 | 115/115 | 232/232 | 256 | 109.1406 | 111.54 | Single | 'BG_P1_110512_SRT-A' | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 221051 | CHESTN8A | 221049 | FRED.RD8 | 1 | 115/115 | 232/232 | 189 | 109.2593 | 111.45 | Tower | 'BG_P7_NEAST_RPHLRD_SRT-A' | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 235463 | 01TANEY | 1 | 138/138 | 227/201 | 268 | 112.3881 | 110.76 | Single | 'PJM_500_BG_P1_5011_SRT-A' | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 235463 | 01TANEY | 1 | 138/138 | 227/201 | 268 | 112.4254 | 110.75 | Line_FB | 'PJM_500_BG_P4_5_CNSTN_J_SRT-A' | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230/230 | 230/230 | 578 | 111.6263 | 110.58 | Line_FB | 'PJM_500_BG_P4_5_CNSTN_B_SRT-A' | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 235463 | 01TANEY | 1 | 138/138 | 227/201 | 268 | 112.0896 | 110.46 | Line_FB | 'PEPCO_P4_PP40_SRT-A' | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 207922 | BRIS | 204515 | 27YORKANA | 1 | 230/230 | 229/227 | 869 | 111.3579 | 110.18 | Line_FB | 'PJM_500_BG_P4_5_CNSTN_B_SRT-A' | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 221092 | FIVE.FOR | 221096 | ROCKRGE1 | 1 | 115/115 | 232/232 | 256 | 106.9922 | 109.48 | Line_FB | 'BG_P4_5_WE512_SRT-A' | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 207922 | BRIS | 204515 | 27YORKANA | 1 | 230/230 | 229/227 | 869 | 109.8734 | 108.55 | Single | 'PECO_P1-2_5012_SRT-A' | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 207922 | BRIS | 204515 | 27YORKANA | 1 | 230/230 | 229/227 | 869 | 109.8734 | 108.55 | Line_FB | 'PJM_500_BG_P4_5_CNSTN_C_SRT-A' | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 207922 | BRIS | 204515 | 27YORKANA | 1 | 230/230 | 229/227 | 869 | 109.8619 | 108.54 | Line_FB | 'PECO_P4_PEACH235_SRT-A' | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230/230 | 227/229 | 801 | 109.8127 | 108.33 | Line_FB | 'PECO_P4_PEACH245_SRT-A' | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230/230 | 230/230 | 578 | 109.4291 | 108.09 | Line_FB | 'PECO_P4_PEACH235_SRT-A' | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230/230 | 230/230 | 578 | 109.3772 | 108.04 | Single | 'PECO_P1-2_5012_SRT-A' | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230/230 | 230/230 | 578 | 109.3772 | 108.04 | Line_FB | 'PJM_500_BG_P4_5_CNSTN_C_SRT-A' | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 207923 | BRISREAC | 208132 | WHEM TR1 | 1 | 230/230 | 229/229 | 618 | 109.6602 | 107.75 | Line_FB | 'PECO_P4_PEACH245_SRT-A' | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 207922 | BRIS | 207923 | BRISREAC | RX | 230/230 | 229/229 | 618 | 109.6602 | 107.75 | Line_FB | 'PECO_P4_PEACH245_SRT-A' | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 221092 | FIVE.FOR | 221095 | ROCKRGE2 | 1 | 115/115 | 232/232 | 300 | 106.8667 | 107.53 | Tower | 'BG_P7_GRCTN_RAPHEL_SRT-A' | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200003 | BRIGHTON | 1 | 500/500 | 232/233 | 2815 | 108.4227 | 106.71 | Tower | 'BG_P7_CNSTN_NWEST2_SRT-A' | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208132 | WHEM TR1 | 208131 | WHEM | 1 | 230/230 | 229/229 | 618 | 106.2298 | 106.32 | Line_FB | 'PJM_500_BG_P4_5_CNSTN_B_SRT-A' | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200003 | BRIGHTON | 1 | 500/500 | 232/233 | 2815 | 107.5275 | 106.17 | Tower | 'BG_P7_GRCTN_RAPHEL_SRT-A' | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 223938 | DICKH230 | 223937 | DICK 230 | 1 | 230/230 | 233/233 | 680 | 107.3088 | 105.77 | Line_FB | 'PEPCO_P4_PP19_SRT-A' | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 221054 | CHESTN7A | 221050 | FRED.RD7 | 1 | 115/115 | 232/232 | 189 | 103.4392 | 105.57 | Tower | 'BG_P7_NEAST_RPHLRD_SRT-A' | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200004 | CNASTONE | 1 | 500/500 | 230/232 | 3526 | 110.3602 | 105.55 | Single | 'PN_P1-2_PN-500-010T_SRT-A' | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230/230 | 230/232 | 578 | 105.6055 | 105.26 | Line_FB | 'PJM_500_BG_P4_5_CNSTN_B_SRT-A' | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200004 | CNASTONE | 1 | 500/500 | 230/232 | 3526 | 108.6188 | 104.22 | Line_FB | 'PJM_500_BG_P4_5_CNSTN_L_SRT-A' | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208132 | WHEM TR1 | 208131 | WHEM | 1 | 230/230 | 229/229 | 618 | 103.9159 | 103.74 | Single | 'PECO_P1-2_5012_SRT-A' | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208132 | WHEM TR1 | 208131 | WHEM | 1 | 230/230 | 229/229 | 618 | 103.9159 | 103.73 | Line_FB | 'PJM_500_BG_P4_5_CNSTN_C_SRT-A' | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208132 | WHEM TR1 | 208131 | WHEM | 1 | 230/230 | 229/229 | 618 | 103.8997 | 103.72 | Line_FB | 'PECO_P4_PEACH235_SRT-A' | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200003 | BRIGHTON | 1 | 500/500 | 232/233 | 2815 | 104.6536 | 103.32 | Tower | 'BG_P7_NEAST_RPHLRD_SRT-A' | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 221094 | GRACE.-1 | 221092 | FIVE.FOR | 1 | 115/115 | 232/232 | 437 | 103.0892 | 103.26 | Tower | 'BG_P7_GRCTN_RAPHEL_SRT-A' | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 223938 | DICKH230 | 223937 | DICK 230 | 2 | 230/230 | 233/233 | 680 | 103.7206 | 102.87 | Line_FB | 'AP_P2-3_PE-500-019C_SRT-SL' | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 223938 | DICKH230 | 223937 | DICK 230 | 1 | 230/230 | 233/233 | 680 | 103.7206 | 102.87 | Line_FB | 'AP_P2-3_PE-500-019C_SRT-SL' | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208070 | SAHA12TP | 208019 | MANO | 1 | 230/230 | 229/229 | 814 | 102.7764 | 102.84 | Tower | 'BG_P7_GRCTN_CNSTN_SRT-A' | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230/230 | 230/232 | 578 | 103.4083 | 102.76 | Line_FB | 'PECO_P4_PEACH235_SRT-A' | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 204538 | 27STRABAN | 1 | 115/115 | 227/227 | 313 | 102.2684 | 102.74 | Single | 'PJM_500_BG_P1_5011_SRT-A' | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 204538 | 27STRABAN | 1 | 115/115 | 227/227 | 313 | 102.2684 | 102.73 | Line_FB | 'PJM_500_BG_P4_5_CNSTN_J_SRT-A' | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230/230 | 230/232 | 578 | 103.3391 | 102.71 | Single | 'PECO_P1-2_5012_SRT-A' | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230/230 | 230/232 | 578 | 103.3391 | 102.71 | Line_FB | 'PJM_500_BG_P4_5_CNSTN_C_SRT-A' | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 204538 | 27STRABAN | 1 | 115/115 | 227/227 | 313 | 102.0128 | 102.47 | Line_FB | 'PEPCO_P4_PP40_SRT-A' | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 221092 | FIVE.FOR | 221096 | ROCKRGE1 | 1 | 115/115 | 232/232 | 256 | 100.3516 | 102 | Tower | 'BG_P7_CNSTN_NWEST2_SRT-A' | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 220964 | GRACETON | 220999 | BAGLEY2 | 13 | 230/230 | 232/232 | 1594 | 102.7541 | 101.97 | Line_FB | 'BG_P4_5_GRCTN_3T_SRT-A' | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204693 | 27BOONETOWN | 204512 | 27S.RDG | 1 | 230/230 | 227/227 | 531 | 101.6761 | 101.57 | Bus | 'PL_04_P22_102291_SRT-A' | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204693 | 27BOONETOWN | 204512 | 27S.RDG | 1 | 230/230 | 227/227 | 531 | 101.6761 | 101.57 | Line_FB | 'PL_04_P43_102301_SRT-A' | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204693 | 27BOONETOWN | 204512 | 27S.RDG | 1 | 230/230 | 227/227 | 531 | 101.6761 | 101.53 | Bus | 'PL_04_P22_102290_SRT-A' | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204693 | 27BOONETOWN | 204512 | 27S.RDG | 1 | 230/230 | 227/227 | 531 | 101.6761 | 101.53 | Single | 'PL_04_P13_101211_SRT-A' | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204693 | 27BOONETOWN | 204512 | 27S.RDG | 1 | 230/230 | 227/227 | 531 | 101.6761 | 101.53 | Line_FB | 'PL_04_P43_102300_SRT-A' | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 207922 | BRIS | 204515 | 27YORKANA | 1 | 230/230 | 229/227 | 869 | 102.8884 | 101.29 | Line_FB | 'PECO_P4_PEACH245_SRT-A' | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200003 | BRIGHTON | 1 | 500/500 | 232/233 | 2815 | 102.5471 | 101.27 | Line_FB | 'AP_P2-3_PE-500-015_SRT-A' | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204693 | 27BOONETOWN | 204512 | 27S.RDG | 1 | 230/230 | 227/227 | 531 | 101.2429 | 101.18 | Line_FB | 'PL_04_P42_101309_SRT-A' | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 204550 | 27ORRTANNA | 204544 | 27LINCOLN | 1 | 115/115 | 227/227 | 160 | 102.25 | 101.05 | Single | 'ME_P1-2_ME-115-068_SRT-A' | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200003 | BRIGHTON | 1 | 500/500 | 232/233 | 2815 | 101.7123 | 100.59 | Line_FB | 'AP_P2-3_PE-500-018C_SRT-SL' | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200003 | BRIGHTON | 1 | 500/500 | 232/233 | 2815 | 101.7123 | 100.59 | Line_FB | 'AP_P2-3_PE-500-018D_SRT-SL' | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 221092 | FIVE.FOR | 221095 | ROCKRGE2 | 1 | 115/115 | 232/232 | 300 | 99.5333 | 100.58 | Tower | 'BG_P7_NEAST_RPHLRD_SRT-A' | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200003 | BRIGHTON | 1 | 500/500 | 232/233 | 2815 | 101.6661 | 100.57 | Single | 'AP_P1-2_PE-500-001_SRT-SL' | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200003 | BRIGHTON | 1 | 500/500 | 232/233 | 2815 | 101.6661 | 100.57 | Single | 'AP_P1-2_WP-500-DRT17_SRT-SL' | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200003 | BRIGHTON | 1 | 500/500 | 232/233 | 2815 | 101.6661 | 100.57 | Line_FB | 'AP_P2-3_PE-500-016_SRT-SL' | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 221092 | FIVE.FOR | 221096 | ROCKRGE1 | 1 | 115/115 | 232/232 | 256 | 97.6172 | 100.38 | Line_FB | 'BG_P4_5_WE_EAST_TIE_SRT-A' | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200003 | BRIGHTON | 1 | 500/500 | 232/233 | 2815 | 102.4902 | 100.33 | Line_FB | 'PJM_500_BG_P4_5_CNSTN_13_SRT-A' | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208395 | FARO FF | 208393 | FARO DC TIE | 1 | 69/115 | 229/229 | 114 | 103.0702 | 100.26 | Tower | 'PL_05_P71_000906_SRT-A' | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 223938 | DICKH230 | 223937 | DICK 230 | 2 | 230/230 | 233/233 | 680 | 102.0735 | 100.2 | Tower | 'PEPCO_P7_2PEPCO_SRT-A' | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 223938 | DICKH230 | 223937 | DICK 230 | 1 | 230/230 | 233/233 | 680 | 102.0735 | 100.2 | Tower | 'PEPCO_P7_2PEPCO_SRT-A' | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230/230 | 229/232 | 797 | 155.3701 | 153.08 | Single | 'BG_P21:TO:220963 CONASTON 230 220964 GRACETON 230 23_SRT-A' | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230/230 | 229/232 | 797 | 155.3701 | 153.08 | Single | 'BG_P21:TO:220963 CONASTON 230 220964 GRACETON 230 24_SRT-A' | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230/230 | 229/232 | 797 | 155.3701 | 153.06 | Single | 'BG_P21:FROM:220963 CONASTON 230 220964 GRACETON 230 23_SRT-A' | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230/230 | 229/232 | 797 | 155.3701 | 153.06 | Single | 'BG_P21:FROM:220963 CONASTON 230 220964 GRACETON 230 24_SRT-A' | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230/230 | 229/232 | 797 | 155.0565 | 152.9 | Single | 'BG_P21:FROM:208394 PPL-BGE TIE 115 221092 FIVE.FOR 115 1 _SRT-A' | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230/230 | 229/229 | 814 | 130.1843 | 129.31 | Single | 'BG_P21:TO:220963 CONASTON 230 220964 GRACETON 230 24_SRT-A' | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230/230 | 229/229 | 814 | 130.1843 | 129.31 | Single | 'BG_P21:TO:220963 CONASTON 230 220964 GRACETON 230 23_SRT-A' | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230/230 | 229/229 | 814 | 130.1843 | 129.28 | Single | 'BG_P21:FROM:220963 CONASTON 230 220964 GRACETON 230 23_SRT-A' | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230/230 | 229/229 | 814 | 130.1843 | 129.28 | Single | 'BG_P21:FROM:220963 CONASTON 230 220964 GRACETON 230 24_SRT-A' | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230/230 | 229/229 | 814 | 129.8894 | 129.08 | Single | 'BG_P21:TO:208394 PPL-BGE TIE 115 221092 FIVE.FOR 115 1 _SRT-A' | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 221090 | GLENARM2 | 221089 | WINDYED1 | 1 | 115/115 | 232/232 | 192 | 102.9688 | 106.67 | Single | 'BG_P21:FROM:221092 FIVE.FOR 115 221096 ROCKRGE1 115 1 _SRT-A' | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 221090 | GLENARM2 | 221089 | WINDYED1 | 1 | 115/115 | 232/232 | 192 | 102.9688 | 106.66 | Single | 'BG_P21:TO:221092 FIVE.FOR 115 221096 ROCKRGE1 115 1 _SRT-A' | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 221092 | FIVE.FOR | 221096 | ROCKRGE1 | 1 | 115/115 | 232/232 | 256 | 102.5391 | 105.16 | Single | 'BG_P21:FROM:221092 FIVE.FOR 115 221095 ROCKRGE2 115 1 _SRT-A' | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 221092 | FIVE.FOR | 221096 | ROCKRGE1 | 1 | 115/115 | 232/232 | 256 | 102.5391 | 105.15 | Single | 'BG_P21:TO:221092 FIVE.FOR 115 221095 ROCKRGE2 115 1 _SRT-A' | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230/230 | 229/232 | 666 | 169.0541 | 166.62 | Basecase | 'BASE CASE' | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230/230 | 229/229 | 721 | 131.387 | 130.65 | Basecase | 'BASE CASE' | N/A | No | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500/500 | 232/230 | 2828 | 117.1676 | 112.18 | Basecase | 'BASE CASE' | N/A | No | Related to 2022 Window 3, pending window outcome

## N-1 Volt Mag
Note | APS and Dominion zones as a whole are quarantined pending Window 3 outcome and are not included in above results
Related to 2022 Window 3, pending window outcome
PJM N-1 Voltage Magnitude Result (Summer 2028 Case)
FG# | Bus # | Name | KV | Area | ContVolt | BaseVolt | Upper/Lower Limit | Cont Type | Contingency | PJM Accepting Proposals | Reasons for Exclusions | Comments
N/A | 204713 | 27JOHNSCTRL | 115 | 227 | 0.9171 | 0.9949 | 0.92 | Line_FB | ME_P2-3_ME-115-032AT_SRT-A | No | Related to 2022 Window 3, pending window outcome
N/A | 204565 | 27WINDSOR | 115 | 227 | 0.9004 | 1.0096 | 0.92 | Line_FB | ME_P2-3_ME-115-032AT_SRT-A | No | Related to 2022 Window 3, pending window outcome
N/A | 204565 | 27WINDSOR | 115 | 227 | 0.909 | 1.0096 | 0.92 | Line_FB | ME_P2-3_ME-115-032B_SRT-A | No | Related to 2022 Window 3, pending window outcome
N/A | 204565 | 27WINDSOR | 115 | 227 | 0.909 | 1.0096 | 0.92 | Bus | ME_P2-2_ME-115-030_SRT-A | No | Related to 2022 Window 3, pending window outcome
N/A | 204565 | 27WINDSOR | 115 | 227 | 0.912 | 1.0096 | 0.92 | Line_FB | ME_P2-3_ME-115-032E_SRT-A | No | Related to 2022 Window 3, pending window outcome
N/A | 204565 | 27WINDSOR | 115 | 227 | 0.916 | 1.0096 | 0.92 | Tower | ME_P7-1_ME-115-017T_SRT-A | No | Related to 2022 Window 3, pending window outcome
N/A | 204565 | 27WINDSOR | 115 | 227 | 0.9165 | 1.0096 | 0.92 | Single | ME_P1-2_ME-115-057_SRT-A | No | Related to 2022 Window 3, pending window outcome
N/A | 204560 | 27TOLNA | 115 | 227 | 0.9141 | 0.995 | 0.92 | Line_FB | ME_P2-3_ME-115-032AT_SRT-A | No | Related to 2022 Window 3, pending window outcome
N/A | 204525 | 27XROADS | 115 | 227 | 0.9076 | 0.9984 | 0.92 | Line_FB | ME_P2-3_ME-115-032AT_SRT-A | No | Related to 2022 Window 3, pending window outcome
N/A | 204525 | 27XROADS | 115 | 227 | 0.9161 | 0.9984 | 0.92 | Line_FB | ME_P2-3_ME-115-032B_SRT-A | No | Related to 2022 Window 3, pending window outcome
N/A | 204525 | 27XROADS | 115 | 227 | 0.9161 | 0.9984 | 0.92 | Bus | ME_P2-2_ME-115-030_SRT-A | No | Related to 2022 Window 3, pending window outcome
N/A | 204525 | 27XROADS | 115 | 227 | 0.9191 | 0.9984 | 0.92 | Line_FB | ME_P2-3_ME-115-032E_SRT-A | No | Related to 2022 Window 3, pending window outcome
N/A | 204789 | 27BELLEVANS | 69 | 227 | 0.9055 | 0.9787 | 0.92 | Single | ME_P1-2_MEL-69-018_SRT-A | No | Related to 2022 Window 3, pending window outcome
N/A | 204772 | 27LICKDALE | 69 | 227 | 0.9197 | 0.983 | 0.92 | Single | ME_P1-2_MEL-69-018_SRT-A | No | Related to 2022 Window 3, pending window outcome
N/A | 204712 | 27FREDRCKS | 69 | 227 | 0.9086 | 0.9816 | 0.92 | Single | ME_P1-2_MEL-69-018_SRT-A | No | Related to 2022 Window 3, pending window outcome
N/A | 223958 | NORBK010 | 230 | 233 | 1.0607 | 1.0243 | 1.05 | Single | P21:TO:FROM:223954 MZION024 230 223958 NORBK010 230 1 _SRT-A | No | Related to 2022 Window 3, pending window outcome
N/A | 223958 | NORBK010 | 230 | 233 | 1.0621 | 1.0243 | 1.05 | Single | P21:FROM:223954 MZION024 230 223958 NORBK010 230 1 _SRT-A | No | Related to 2022 Window 3, pending window outcome
N/A | 223954 | MZION024 | 230 | 233 | 1.0622 | 1.0229 | 1.05 | Single | P21:FROM:223954 MZION024 230 223958 NORBK010 230 1 _SRT-A | No | Related to 2022 Window 3, pending window outcome
N/A | 220985 | PERRY361 | 230 | 232 | 1.0627 | 1.0322 | 1.05 | Single | BG_P21:TO:220980 RAPHAEL 230 220981 OTTR PT1 230 1 _SRT-A | No | Related to 2022 Window 3, pending window outcome
N/A | 220985 | PERRY361 | 230 | 232 | 1.0633 | 1.0322 | 1.05 | Single | BG_P21:TO:220981 OTTR PT1 230 220985 PERRY361 230 1 _SRT-A | No | Related to 2022 Window 3, pending window outcome
N/A | 220985 | PERRY361 | 230 | 232 | 1.0637 | 1.0322 | 1.05 | Single | BG_P21:FROM:220980 RAPHAEL 230 220981 OTTR PT1 230 1 _SRT-A | No | Related to 2022 Window 3, pending window outcome
N/A | 220985 | PERRY361 | 230 | 232 | 1.0639 | 1.0322 | 1.05 | Single | BG_P21:FROM:220981 OTTR PT1 230 220985 PERRY361 230 1 _SRT-A | No | Related to 2022 Window 3, pending window outcome
N/A | 220981 | OTTR PT1 | 230 | 232 | 1.0625 | 1.0274 | 1.05 | Single | BG_P21:TO:220980 RAPHAEL 230 220981 OTTR PT1 230 1 _SRT-A | No | Related to 2022 Window 3, pending window outcome
N/A | 220981 | OTTR PT1 | 230 | 232 | 1.0637 | 1.0274 | 1.05 | Single | BG_P21:FROM:220980 RAPHAEL 230 220981 OTTR PT1 230 1 _SRT-A | No | Related to 2022 Window 3, pending window outcome

## N-1 Volt Drop
Note | APS and Dominion zones as a whole are quarantined pending Window 3 outcome and are not included in above results
Related to 2022 Window 3, pending window outcome
PJM N-1 Voltage Drop Result (Summer 2028)
FG# | Bus # | Name | KV | Area | ContVolt | BaseVolt | Vdrop(%) | Cont Type | Contingency | PJM Accepting Proposals | Reasons for Exclusions | Comment
N/A | 204565 | 27WINDSOR | 115 | 227 | 0.8965 | 1.0096 | 11.31 | Line_FB | ME_P2-3_ME-115-032AT_SRT-A | No | Related to 2022 Window 3, pending window outcome
N/A | 204565 | 27WINDSOR | 115 | 227 | 0.9077 | 1.0096 | 10.19 | Line_FB | ME_P2-3_ME-115-032B_SRT-A | No
N/A | 204565 | 27WINDSOR | 115 | 227 | 0.9077 | 1.0096 | 10.19 | Bus | ME_P2-2_ME-115-030_SRT-A | No
N/A | 220978 | SNOW.R18 | 230 | 232 | 0.4107 | 1.02 | 60.93 | Single | BG_P21:TO:220941 H.RDGE16 230 220943 SNOW18TP 230 1 _SRT-A | No
N/A | 220978 | SNOW.R18 | 230 | 232 | 0.4189 | 1.02 | 60.11 | Single | BG_P21:FROM:220941 H.RDGE16 230 220943 SNOW18TP 230 1 _SRT-A | No
N/A | 220952 | W.LAKE8A | 230 | 232 | 0.4092 | 1.0194 | 61.02 | Single | BG_P21:TO:220941 H.RDGE16 230 220943 SNOW18TP 230 1 _SRT-A | No
N/A | 220952 | W.LAKE8A | 230 | 232 | 0.4175 | 1.0194 | 60.19 | Single | BG_P21:FROM:220941 H.RDGE16 230 220943 SNOW18TP 230 1 _SRT-A | No
N/A | 220948 | COLUMB18 | 230 | 232 | 0.41 | 1.0199 | 60.99 | Single | BG_P21:TO:220941 H.RDGE16 230 220943 SNOW18TP 230 1 _SRT-A | No
N/A | 220948 | COLUMB18 | 230 | 232 | 0.4183 | 1.0199 | 60.16 | Single | BG_P21:FROM:220941 H.RDGE16 230 220943 SNOW18TP 230 1 _SRT-A | No
N/A | 220943 | SNOW18TP | 230 | 232 | 0.4102 | 1.02 | 60.98 | Single | BG_P21:TO:220941 H.RDGE16 230 220943 SNOW18TP 230 1 _SRT-A | No
N/A | 220943 | SNOW18TP | 230 | 232 | 0.4185 | 1.02 | 60.15 | Single | BG_P21:FROM:220941 H.RDGE16 230 220943 SNOW18TP 230 1 _SRT-A | No