## N-1 Thermal
Note | APS and Dominion zones as a whole are quarantined pending Window 3 outcome and are not included in above results
Related to 2022 Window 3, pending window outcome
PJM N-1 Thermal Result (Winter 2028 Case)
FG # | Fr Bus | Fr Name | To Bus | To Name | CKT | KVs | Areas | Rating | DC Ld(%) | AC Ld(%) | Cont Type | Contingency | Conductor/Transformer Rating (MVA) | PJM Accepting Proposals | Reasons for Exclusions | Comments
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230/230 | 230/230 | 617 | 225.1864 | 239.26 | Line_FB | 'PJM_500_BG_P4_5_CNSTN_B_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230/230 | 230/230 | 617 | 224.2464 | 238.13 | Line_FB | 'PECO_P4_PEACH235_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230/230 | 230/230 | 617 | 224.1815 | 238.07 | Line_FB | 'PJM_500_BG_P4_5_CNSTN_C_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230/230 | 230/230 | 617 | 224.1815 | 238.07 | Single | 'PECO_P1-2_5012_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230/230 | 230/230 | 617 | 209.3355 | 218.77 | Line_FB | 'PECO_P4_PEACH245_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230/230 | 230/230 | 617 | 125.5267 | 127.85 | Tower | 'BG_P7_GRCTN_CNSTN_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230/230 | 230/230 | 617 | 118.363 | 123.21 | Line_FB | 'PEPCO_P4_PP40_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230/230 | 230/230 | 617 | 118.1848 | 122.98 | Single | 'PJM_500_BG_P1_5011_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230/230 | 230/230 | 521 | 115.7582 | 117.89 | Single | 'BASE CASE' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230/230 | 230/230 | 617 | 115.1053 | 115.55 | Single | 'PECO_P1-2_5014_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230/230 | 230/230 | 617 | 113.0146 | 115.36 | Single | 'BG_P1_CNSTN_500-4_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230/230 | 230/230 | 617 | 113.0146 | 115.36 | Bus | 'PJM_500_BG_P2_CNSTN_230-S_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230/230 | 230/230 | 617 | 112.966 | 115.31 | Bus | 'PJM_500_BG_P2_CNSTN_230-N_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230/230 | 230/230 | 617 | 111.3938 | 113.26 | Tower | 'PL_05_P71_000906_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230/230 | 230/230 | 617 | 109.8055 | 111.49 | Bus | 'PL_05_P22_000674_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230/230 | 230/230 | 617 | 104.6515 | 106.18 | Tower | 'PL_04_P71_001014_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230/230 | 230/230 | 617 | 102.7391 | 104.39 | Bus | 'PL_04_P22_102817_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230/230 | 230/230 | 617 | 102.6094 | 104.26 | Tower | 'PL_04_P71_000904_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230/230 | 230/230 | 617 | 102.5446 | 104.22 | Tower | 'PL_04_P71_001822_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230/230 | 230/230 | 617 | 100.8266 | 102.77 | Bus | 'AP_P2-2_WP-500-DRT16_SRT-W' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230/230 | 230/230 | 617 | 227.2123 | 239.26 | Line_FB | 'PJM_500_BG_P4_5_CNSTN_B_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230/230 | 230/230 | 617 | 226.2723 | 238.13 | Line_FB | 'PECO_P4_PEACH235_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230/230 | 230/230 | 617 | 226.2075 | 238.07 | Line_FB | 'PJM_500_BG_P4_5_CNSTN_C_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230/230 | 230/230 | 617 | 226.2075 | 238.07 | Single | 'PECO_P1-2_5012_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230/230 | 230/230 | 617 | 211.3614 | 218.77 | Line_FB | 'PECO_P4_PEACH245_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230/230 | 230/230 | 617 | 127.5365 | 127.85 | Tower | 'BG_P7_GRCTN_CNSTN_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230/230 | 230/230 | 617 | 120.389 | 123.21 | Line_FB | 'PEPCO_P4_PP40_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230/230 | 230/230 | 617 | 120.2107 | 122.98 | Single | 'PJM_500_BG_P1_5011_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230/230 | 230/230 | 521 | 118.1382 | 117.89 | Single | 'BASE CASE' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230/230 | 230/230 | 617 | 117.1151 | 115.55 | Single | 'PECO_P1-2_5014_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230/230 | 230/230 | 617 | 115.0405 | 115.36 | Single | 'BG_P1_CNSTN_500-4_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230/230 | 230/230 | 617 | 115.0405 | 115.36 | Bus | 'PJM_500_BG_P2_CNSTN_230-S_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230/230 | 230/230 | 617 | 114.9919 | 115.31 | Bus | 'PJM_500_BG_P2_CNSTN_230-N_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230/230 | 230/230 | 617 | 113.4036 | 113.26 | Tower | 'PL_05_P71_000906_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230/230 | 230/230 | 617 | 111.8152 | 111.49 | Bus | 'PL_05_P22_000674_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230/230 | 230/230 | 617 | 106.6613 | 106.18 | Tower | 'PL_04_P71_001014_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230/230 | 230/230 | 617 | 104.7488 | 104.39 | Bus | 'PL_04_P22_102817_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230/230 | 230/230 | 617 | 104.6191 | 104.26 | Tower | 'PL_04_P71_000904_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230/230 | 230/230 | 617 | 104.5705 | 104.22 | Tower | 'PL_04_P71_001822_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230/230 | 230/230 | 617 | 102.8363 | 102.77 | Bus | 'AP_P2-2_WP-500-DRT16_SRT-W' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230/230 | 230/230 | 639 | 215.0861 | 229.03 | Line_FB | 'PJM_500_BG_P4_5_CNSTN_B_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230/230 | 230/230 | 639 | 214.1784 | 227.94 | Line_FB | 'PECO_P4_PEACH235_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230/230 | 230/230 | 639 | 214.1158 | 227.88 | Line_FB | 'PJM_500_BG_P4_5_CNSTN_C_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230/230 | 230/230 | 639 | 214.1158 | 227.88 | Single | 'PECO_P1-2_5012_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230/230 | 230/230 | 639 | 199.7809 | 209.17 | Line_FB | 'PECO_P4_PEACH245_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230/230 | 230/230 | 639 | 118.8576 | 121.17 | Tower | 'BG_P7_GRCTN_CNSTN_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230/230 | 230/230 | 639 | 111.9405 | 116.7 | Line_FB | 'PEPCO_P4_PP40_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230/230 | 230/230 | 639 | 111.7684 | 116.48 | Single | 'PJM_500_BG_P1_5011_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230/230 | 230/230 | 521 | 112.8599 | 115.15 | Single | 'BASE CASE' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230/230 | 230/230 | 639 | 108.7793 | 109.35 | Single | 'PECO_P1-2_5014_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230/230 | 230/230 | 639 | 106.7762 | 109.18 | Single | 'BG_P1_CNSTN_500-4_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230/230 | 230/230 | 639 | 106.7762 | 109.18 | Bus | 'PJM_500_BG_P2_CNSTN_230-S_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230/230 | 230/230 | 639 | 106.7293 | 109.13 | Bus | 'PJM_500_BG_P2_CNSTN_230-N_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230/230 | 230/230 | 639 | 105.2113 | 107.15 | Tower | 'PL_05_P71_000906_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230/230 | 230/230 | 639 | 103.6776 | 105.43 | Bus | 'PL_05_P22_000674_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230/230 | 230/230 | 639 | 98.7011 | 100.31 | Tower | 'PL_04_P71_001014_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230/230 | 230/232 | 639 | 210.8294 | 225.83 | Line_FB | 'PJM_500_BG_P4_5_CNSTN_B_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230/230 | 230/232 | 639 | 209.9218 | 224.73 | Line_FB | 'PECO_P4_PEACH235_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230/230 | 230/232 | 639 | 209.8592 | 224.68 | Single | 'PECO_P1-2_5012_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230/230 | 230/232 | 639 | 209.8592 | 224.67 | Line_FB | 'PJM_500_BG_P4_5_CNSTN_C_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230/230 | 230/232 | 639 | 195.5243 | 205.83 | Line_FB | 'PECO_P4_PEACH245_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230/230 | 230/232 | 639 | 114.5853 | 117.33 | Tower | 'BG_P7_GRCTN_CNSTN_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230/230 | 230/232 | 639 | 107.6839 | 112.88 | Line_FB | 'PEPCO_P4_PP40_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230/230 | 230/232 | 639 | 107.4961 | 112.66 | Single | 'PJM_500_BG_P1_5011_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230/230 | 230/232 | 521 | 107.6392 | 110.55 | Single | 'BASE CASE' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230/230 | 230/232 | 639 | 104.5227 | 105.65 | Single | 'PECO_P1-2_5014_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230/230 | 230/232 | 639 | 102.5196 | 105.48 | Single | 'BG_P1_CNSTN_500-4_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230/230 | 230/232 | 639 | 102.5196 | 105.48 | Bus | 'PJM_500_BG_P2_CNSTN_230-S_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230/230 | 230/232 | 639 | 102.4726 | 105.43 | Bus | 'PJM_500_BG_P2_CNSTN_230-N_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230/230 | 230/232 | 639 | 100.939 | 103.43 | Tower | 'PL_05_P71_000906_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230/230 | 230/232 | 639 | 99.4053 | 101.71 | Bus | 'PL_05_P22_000674_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 205912 | AD1-020 TAP | 204544 | 27LINCOLN | 1 | 115/115 | 227/227 | 334 | 174.491 | 177.28 | Line_FB | 'PJM_500_BG_P4_5_CNSTN_J_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 205912 | AD1-020 TAP | 204544 | 27LINCOLN | 1 | 115/115 | 227/227 | 334 | 174.491 | 177.28 | Single | 'PJM_500_BG_P1_5011_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 205912 | AD1-020 TAP | 204544 | 27LINCOLN | 1 | 115/115 | 227/227 | 334 | 174.3713 | 177.16 | Line_FB | 'PEPCO_P4_PP40_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 205912 | AD1-020 TAP | 204544 | 27LINCOLN | 1 | 115/115 | 227/227 | 334 | 151.4371 | 150.15 | Line_FB | 'PJM_500_BG_P4_5_CNSTN_C_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 205912 | AD1-020 TAP | 204544 | 27LINCOLN | 1 | 115/115 | 227/227 | 334 | 151.4371 | 150.15 | Single | 'PECO_P1-2_5012_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 205912 | AD1-020 TAP | 204544 | 27LINCOLN | 1 | 115/115 | 227/227 | 334 | 151.4371 | 150.14 | Line_FB | 'PECO_P4_PEACH235_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 205912 | AD1-020 TAP | 204544 | 27LINCOLN | 1 | 115/115 | 227/227 | 334 | 151.2575 | 149.8 | Line_FB | 'PJM_500_BG_P4_5_CNSTN_B_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 205912 | AD1-020 TAP | 204544 | 27LINCOLN | 1 | 115/115 | 227/227 | 334 | 144.5509 | 143.61 | Single | 'ME_P1-2_ME-115-061_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 205912 | AD1-020 TAP | 204544 | 27LINCOLN | 1 | 115/115 | 227/227 | 334 | 138.8922 | 139.98 | Tower | 'BG_P7_GRCTN_RAPHEL_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 205912 | AD1-020 TAP | 204544 | 27LINCOLN | 1 | 115/115 | 227/227 | 334 | 138.982 | 139.62 | Single | 'AP_P1-2_PE-500-001_SRT-W' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 205912 | AD1-020 TAP | 204544 | 27LINCOLN | 1 | 115/115 | 227/227 | 334 | 138.5329 | 139.4 | Tower | 'BG_P7_CNSTN_NWEST2_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 205912 | AD1-020 TAP | 204544 | 27LINCOLN | 1 | 115/115 | 227/227 | 334 | 139.8204 | 138.59 | Bus | 'ME_P2-2_ME-115-0102A-8_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 205912 | AD1-020 TAP | 204544 | 27LINCOLN | 1 | 115/115 | 227/227 | 334 | 136.6467 | 137.37 | Tower | 'BG_P7_NEAST_RPHLRD_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 205912 | AD1-020 TAP | 204544 | 27LINCOLN | 1 | 115/115 | 227/227 | 334 | 132.8144 | 131.49 | Bus | 'AP_P2-2_WP-500-DRT16_SRT-W' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 205912 | AD1-020 TAP | 204544 | 27LINCOLN | 1 | 115/115 | 227/227 | 334 | 131.5269 | 130.78 | Tower | 'BG_P7_GRNITE_HIRDG_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 205912 | AD1-020 TAP | 204544 | 27LINCOLN | 1 | 115/115 | 227/227 | 334 | 130.9281 | 130.59 | Bus | 'AP_P2-2_WP-138-074_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 205912 | AD1-020 TAP | 204544 | 27LINCOLN | 1 | 115/115 | 227/227 | 334 | 130.988 | 130.19 | Tower | 'BG_P7_NWEST_GRNITE_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 205912 | AD1-020 TAP | 204544 | 27LINCOLN | 1 | 115/115 | 227/227 | 334 | 129.491 | 128.16 | Bus | 'ME_P2-2_ME-115-002T_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 205912 | AD1-020 TAP | 204544 | 27LINCOLN | 1 | 115/115 | 227/227 | 334 | 129.012 | 127.75 | Bus | 'PL_05_P22_000674_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204539 | 27HUNTRSTN | 205912 | AD1-020 TAP | 1 | 115/115 | 227/227 | 334 | 174.0719 | 175.59 | Line_FB | 'PJM_500_BG_P4_5_CNSTN_J_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204539 | 27HUNTRSTN | 205912 | AD1-020 TAP | 1 | 115/115 | 227/227 | 334 | 174.0719 | 175.59 | Single | 'PJM_500_BG_P1_5011_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204539 | 27HUNTRSTN | 205912 | AD1-020 TAP | 1 | 115/115 | 227/227 | 334 | 173.9521 | 175.47 | Line_FB | 'PEPCO_P4_PP40_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204539 | 27HUNTRSTN | 205912 | AD1-020 TAP | 1 | 115/115 | 227/227 | 263 | 159.2395 | 156.09 | Single | 'BASE CASE' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204539 | 27HUNTRSTN | 205912 | AD1-020 TAP | 1 | 115/115 | 227/227 | 334 | 151.018 | 150.32 | Line_FB | 'PJM_500_BG_P4_5_CNSTN_C_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204539 | 27HUNTRSTN | 205912 | AD1-020 TAP | 1 | 115/115 | 227/227 | 334 | 151.018 | 150.32 | Single | 'PECO_P1-2_5012_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204539 | 27HUNTRSTN | 205912 | AD1-020 TAP | 1 | 115/115 | 227/227 | 334 | 151.018 | 150.31 | Line_FB | 'PECO_P4_PEACH235_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204539 | 27HUNTRSTN | 205912 | AD1-020 TAP | 1 | 115/115 | 227/227 | 334 | 150.8383 | 149.92 | Line_FB | 'PJM_500_BG_P4_5_CNSTN_B_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204539 | 27HUNTRSTN | 205912 | AD1-020 TAP | 1 | 115/115 | 227/227 | 334 | 144.1317 | 142.13 | Single | 'ME_P1-2_ME-115-061_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204539 | 27HUNTRSTN | 205912 | AD1-020 TAP | 1 | 115/115 | 227/227 | 334 | 138.4731 | 138.48 | Tower | 'BG_P7_GRCTN_RAPHEL_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204539 | 27HUNTRSTN | 205912 | AD1-020 TAP | 1 | 115/115 | 227/227 | 334 | 138.5629 | 138.1 | Single | 'AP_P1-2_WP-500-DRT17_SRT-W' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204539 | 27HUNTRSTN | 205912 | AD1-020 TAP | 1 | 115/115 | 227/227 | 334 | 138.1437 | 137.89 | Tower | 'BG_P7_CNSTN_NWEST2_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204539 | 27HUNTRSTN | 205912 | AD1-020 TAP | 1 | 115/115 | 227/227 | 334 | 139.4012 | 137.1 | Bus | 'ME_P2-2_ME-115-0102A-8_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204539 | 27HUNTRSTN | 205912 | AD1-020 TAP | 1 | 115/115 | 227/227 | 334 | 136.2275 | 135.87 | Tower | 'BG_P7_NEAST_RPHLRD_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204539 | 27HUNTRSTN | 205912 | AD1-020 TAP | 1 | 115/115 | 227/227 | 334 | 132.3952 | 130.01 | Bus | 'AP_P2-2_WP-500-DRT16_SRT-W' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204539 | 27HUNTRSTN | 205912 | AD1-020 TAP | 1 | 115/115 | 227/227 | 334 | 131.1078 | 129.31 | Tower | 'BG_P7_GRNITE_HIRDG_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204539 | 27HUNTRSTN | 205912 | AD1-020 TAP | 1 | 115/115 | 227/227 | 334 | 130.509 | 129.12 | Bus | 'AP_P2-2_WP-138-074_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204539 | 27HUNTRSTN | 205912 | AD1-020 TAP | 1 | 115/115 | 227/227 | 334 | 130.5689 | 128.72 | Tower | 'BG_P7_NWEST_GRNITE_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204539 | 27HUNTRSTN | 205912 | AD1-020 TAP | 1 | 115/115 | 227/227 | 334 | 129.0719 | 126.71 | Bus | 'ME_P2-2_ME-115-002T_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204539 | 27HUNTRSTN | 205912 | AD1-020 TAP | 1 | 115/115 | 227/227 | 334 | 128.5928 | 126.29 | Bus | 'PL_05_P22_000674_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 235463 | 01TANEY | 1 | 138/138 | 227/201 | 317 | 178.4543 | 172.53 | Line_FB | 'PJM_500_BG_P4_5_CNSTN_J_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 235463 | 01TANEY | 1 | 138/138 | 227/201 | 317 | 178.4543 | 172.53 | Single | 'PJM_500_BG_P1_5011_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 235463 | 01TANEY | 1 | 138/138 | 227/201 | 317 | 178.2965 | 172.42 | Line_FB | 'PEPCO_P4_PP40_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 235463 | 01TANEY | 1 | 138/138 | 227/201 | 250 | 153 | 151.61 | Single | 'BASE CASE' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 235463 | 01TANEY | 1 | 138/138 | 227/201 | 317 | 137.7603 | 136.24 | Line_FB | 'AP_P2-3_PE-500-016_SRT-W' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 235463 | 01TANEY | 1 | 138/138 | 227/201 | 317 | 137.8549 | 136.18 | Line_FB | 'AP_P2-3_PE-500-015_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 235463 | 01TANEY | 1 | 138/138 | 227/201 | 317 | 136.183 | 135.81 | Tower | 'BG_P7_GRCTN_RAPHEL_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 235463 | 01TANEY | 1 | 138/138 | 227/201 | 317 | 136.4353 | 135.35 | Line_FB | 'AP_P2-3_PE-500-018D_SRT-W' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 235463 | 01TANEY | 1 | 138/138 | 227/201 | 317 | 135.7729 | 135.2 | Tower | 'BG_P7_CNSTN_NWEST2_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 235463 | 01TANEY | 1 | 138/138 | 227/201 | 317 | 136.2776 | 135.07 | Single | 'AP_P1-2_WP-500-DRT17_SRT-W' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 235463 | 01TANEY | 1 | 138/138 | 227/201 | 317 | 136.2776 | 135.07 | Single | 'AP_P1-2_PE-500-001_SRT-W' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 235463 | 01TANEY | 1 | 138/138 | 227/201 | 317 | 136.1199 | 134.7 | Single | 'AP_P1-2_PE-500-004_SRT-W' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 235463 | 01TANEY | 1 | 138/138 | 227/201 | 317 | 133.5016 | 133.11 | Tower | 'BG_P7_NEAST_RPHLRD_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 235463 | 01TANEY | 1 | 138/138 | 227/201 | 317 | 128.959 | 126.88 | Bus | 'AP_P2-2_WP-500-DRT16_SRT-W' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 235463 | 01TANEY | 1 | 138/138 | 227/201 | 317 | 127.4132 | 126.3 | Tower | 'BG_P7_GRNITE_HIRDG_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 235463 | 01TANEY | 1 | 138/138 | 227/201 | 317 | 126.7508 | 126.13 | Bus | 'AP_P2-2_WP-138-074_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 235463 | 01TANEY | 1 | 138/138 | 227/201 | 317 | 126.8139 | 125.67 | Tower | 'BG_P7_NWEST_GRNITE_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 235463 | 01TANEY | 1 | 138/138 | 227/201 | 317 | 125.0158 | 123.64 | Bus | 'ME_P2-2_ME-115-002T_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 235463 | 01TANEY | 1 | 138/138 | 227/201 | 317 | 124.4479 | 123.14 | Bus | 'PL_05_P22_000674_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 235463 | 01TANEY | 1 | 138/138 | 227/201 | 317 | 124.5741 | 122.89 | Bus | 'AP_P2-2_WP-500-DRT17_SRT-W' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 204538 | 27STRABAN | 1 | 115/115 | 227/227 | 371 | 163.7736 | 168.7 | Line_FB | 'PJM_500_BG_P4_5_CNSTN_J_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 204538 | 27STRABAN | 1 | 115/115 | 227/227 | 371 | 163.7736 | 168.7 | Single | 'PJM_500_BG_P1_5011_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 204538 | 27STRABAN | 1 | 115/115 | 227/227 | 371 | 163.6388 | 168.58 | Line_FB | 'PEPCO_P4_PP40_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 204538 | 27STRABAN | 1 | 115/115 | 227/227 | 371 | 140.4043 | 140.96 | Line_FB | 'PJM_500_BG_P4_5_CNSTN_C_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 204538 | 27STRABAN | 1 | 115/115 | 227/227 | 371 | 140.3774 | 140.96 | Line_FB | 'PECO_P4_PEACH235_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 204538 | 27STRABAN | 1 | 115/115 | 227/227 | 371 | 140.4043 | 140.96 | Single | 'PECO_P1-2_5012_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 204538 | 27STRABAN | 1 | 115/115 | 227/227 | 371 | 140.2156 | 140.61 | Line_FB | 'PJM_500_BG_P4_5_CNSTN_B_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 204538 | 27STRABAN | 1 | 115/115 | 227/227 | 371 | 127.655 | 131 | Tower | 'BG_P7_GRCTN_RAPHEL_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 204538 | 27STRABAN | 1 | 115/115 | 227/227 | 371 | 127.7628 | 130.62 | Single | 'AP_P1-2_PE-500-001_SRT-W' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 204538 | 27STRABAN | 1 | 115/115 | 227/227 | 371 | 127.7628 | 130.62 | Single | 'AP_P1-2_WP-500-DRT17_SRT-W' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 204538 | 27STRABAN | 1 | 115/115 | 227/227 | 371 | 127.3046 | 130.41 | Tower | 'BG_P7_CNSTN_NWEST2_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 204538 | 27STRABAN | 1 | 115/115 | 227/227 | 371 | 125.3639 | 128.36 | Tower | 'BG_P7_NEAST_RPHLRD_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 204538 | 27STRABAN | 1 | 115/115 | 227/227 | 371 | 121.5094 | 122.4 | Bus | 'AP_P2-2_WP-500-DRT16_SRT-W' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 204538 | 27STRABAN | 1 | 115/115 | 227/227 | 371 | 120.1887 | 121.69 | Tower | 'BG_P7_GRNITE_HIRDG_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 204538 | 27STRABAN | 1 | 115/115 | 227/227 | 371 | 119.5957 | 121.49 | Bus | 'AP_P2-2_WP-138-074_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 204538 | 27STRABAN | 1 | 115/115 | 227/227 | 371 | 119.6496 | 121.09 | Tower | 'BG_P7_NWEST_GRNITE_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 204538 | 27STRABAN | 1 | 115/115 | 227/227 | 371 | 118.1132 | 119.04 | Bus | 'ME_P2-2_ME-115-002T_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 204538 | 27STRABAN | 1 | 115/115 | 227/227 | 371 | 117.655 | 118.62 | Bus | 'PL_05_P22_000674_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 204538 | 27STRABAN | 1 | 115/115 | 227/227 | 371 | 117.7628 | 118.45 | Bus | 'AP_P2-2_WP-500-DRT17_SRT-W' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230/230 | 229/232 | 889 | 173.2396 | 168.49 | Line_FB | 'PJM_500_BG_P4_5_CNSTN_B_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230/230 | 229/232 | 889 | 172.2835 | 166.84 | Line_FB | 'PJM_500_BG_P4_5_CNSTN_C_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230/230 | 229/232 | 889 | 172.2835 | 166.84 | Single | 'PECO_P1-2_5012_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230/230 | 229/232 | 889 | 172.261 | 166.83 | Line_FB | 'PECO_P4_PEACH235_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230/230 | 229/232 | 889 | 164.3195 | 159.37 | Line_FB | 'PECO_P4_PEACH245_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230/230 | 229/232 | 889 | 146.5129 | 146.99 | Tower | 'BG_P7_GRCTN_CNSTN_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230/230 | 229/232 | 889 | 141.4848 | 141.11 | Line_FB | 'PJM_500_BG_P4_5_CNSTN_15_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230/230 | 229/232 | 889 | 118.4927 | 117.2 | Single | 'PL_04_P12_000260_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230/230 | 229/232 | 889 | 108.3352 | 110.94 | Single | 'PJM_500_BG_P1_5011_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230/230 | 229/232 | 746 | 111.2601 | 109.7 | Single | 'BASE CASE' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230/230 | 229/232 | 889 | 107.4466 | 105.46 | Bus | 'PECO_P2-2_NOTT230B_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230/230 | 229/232 | 889 | 106.5354 | 104.88 | Single | 'PECO_P1-2_220-08_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230/230 | 229/232 | 889 | 105.3768 | 104.17 | Bus | 'PJM_500_BG_P2_CNSTN_230-S_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230/230 | 229/232 | 889 | 105.3318 | 104.13 | Bus | 'PJM_500_BG_P2_CNSTN_230-N_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230/230 | 229/232 | 897 | 164.1249 | 165.59 | Line_FB | 'PJM_500_BG_P4_5_CNSTN_B_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230/230 | 229/232 | 897 | 162.2631 | 162.56 | Line_FB | 'PECO_P4_PEACH235_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230/230 | 229/232 | 897 | 162.2742 | 162.56 | Line_FB | 'PJM_500_BG_P4_5_CNSTN_C_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230/230 | 229/232 | 897 | 162.2742 | 162.56 | Single | 'PECO_P1-2_5012_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230/230 | 229/232 | 897 | 153.3222 | 151.83 | Line_FB | 'PECO_P4_PEACH245_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204538 | 27STRABAN | 204529 | 27GERMANTN | 1 | 115/115 | 227/227 | 371 | 157.9784 | 164.16 | Line_FB | 'PJM_500_BG_P4_5_CNSTN_J_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204538 | 27STRABAN | 204529 | 27GERMANTN | 1 | 115/115 | 227/227 | 371 | 157.9784 | 164.16 | Single | 'PJM_500_BG_P1_5011_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204538 | 27STRABAN | 204529 | 27GERMANTN | 1 | 115/115 | 227/227 | 371 | 157.8437 | 164.03 | Line_FB | 'PEPCO_P4_PP40_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204538 | 27STRABAN | 204529 | 27GERMANTN | 1 | 115/115 | 227/227 | 371 | 134.6092 | 136.67 | Line_FB | 'PJM_500_BG_P4_5_CNSTN_C_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204538 | 27STRABAN | 204529 | 27GERMANTN | 1 | 115/115 | 227/227 | 371 | 134.6092 | 136.67 | Single | 'PECO_P1-2_5012_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204538 | 27STRABAN | 204529 | 27GERMANTN | 1 | 115/115 | 227/227 | 371 | 134.6092 | 136.66 | Line_FB | 'PECO_P4_PEACH235_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204538 | 27STRABAN | 204529 | 27GERMANTN | 1 | 115/115 | 227/227 | 371 | 134.4205 | 136.31 | Line_FB | 'PJM_500_BG_P4_5_CNSTN_B_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204538 | 27STRABAN | 204529 | 27GERMANTN | 1 | 115/115 | 227/227 | 371 | 121.8598 | 126.55 | Tower | 'BG_P7_GRCTN_RAPHEL_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204538 | 27STRABAN | 204529 | 27GERMANTN | 1 | 115/115 | 227/227 | 371 | 121.9677 | 126.16 | Single | 'AP_P1-2_PE-500-001_SRT-W' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204538 | 27STRABAN | 204529 | 27GERMANTN | 1 | 115/115 | 227/227 | 371 | 121.9677 | 126.16 | Single | 'AP_P1-2_WP-500-DRT17_SRT-W' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204538 | 27STRABAN | 204529 | 27GERMANTN | 1 | 115/115 | 227/227 | 371 | 121.5364 | 125.96 | Tower | 'BG_P7_CNSTN_NWEST2_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204538 | 27STRABAN | 204529 | 27GERMANTN | 1 | 115/115 | 227/227 | 371 | 119.5957 | 123.9 | Tower | 'BG_P7_NEAST_RPHLRD_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204538 | 27STRABAN | 204529 | 27GERMANTN | 1 | 115/115 | 227/227 | 371 | 115.7143 | 117.96 | Bus | 'AP_P2-2_WP-500-DRT16_SRT-W' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204538 | 27STRABAN | 204529 | 27GERMANTN | 1 | 115/115 | 227/227 | 371 | 114.3935 | 117.25 | Tower | 'BG_P7_GRNITE_HIRDG_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204538 | 27STRABAN | 204529 | 27GERMANTN | 1 | 115/115 | 227/227 | 371 | 113.8005 | 117.05 | Bus | 'AP_P2-2_WP-138-074_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204538 | 27STRABAN | 204529 | 27GERMANTN | 1 | 115/115 | 227/227 | 371 | 113.8814 | 116.65 | Tower | 'BG_P7_NWEST_GRNITE_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204538 | 27STRABAN | 204529 | 27GERMANTN | 1 | 115/115 | 227/227 | 371 | 112.345 | 114.6 | Bus | 'ME_P2-2_ME-115-002T_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204538 | 27STRABAN | 204529 | 27GERMANTN | 1 | 115/115 | 227/227 | 371 | 111.8598 | 114.19 | Bus | 'PL_05_P22_000674_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204538 | 27STRABAN | 204529 | 27GERMANTN | 1 | 115/115 | 227/227 | 371 | 111.9677 | 114.01 | Bus | 'AP_P2-2_WP-500-DRT17_SRT-W' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204550 | 27ORRTANNA | 204544 | 27LINCOLN | 1 | 115/115 | 227/227 | 189 | 164.3386 | 164 | Single | 'ME_P1-2_ME-115-068_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204550 | 27ORRTANNA | 204544 | 27LINCOLN | 1 | 115/115 | 227/227 | 189 | 162.5397 | 163.92 | Line_FB | 'ME_P2-3_ME-115-035A_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204550 | 27ORRTANNA | 204544 | 27LINCOLN | 1 | 115/115 | 227/227 | 189 | 163.8624 | 162.41 | Single | 'ME_P1-2_ME-115-067_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204550 | 27ORRTANNA | 204544 | 27LINCOLN | 1 | 115/115 | 227/227 | 189 | 162.0106 | 161.56 | Line_FB | 'ME_P2-3_ME-115-013B_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204550 | 27ORRTANNA | 204544 | 27LINCOLN | 1 | 115/115 | 227/227 | 189 | 160.2646 | 161.44 | Line_FB | 'ME_P2-3_ME-115-035B_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204550 | 27ORRTANNA | 204544 | 27LINCOLN | 1 | 115/115 | 227/227 | 189 | 161.6931 | 161.24 | Line_FB | 'ME_P2-3_ME-115-013A_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204550 | 27ORRTANNA | 204544 | 27LINCOLN | 1 | 115/115 | 227/227 | 189 | 157.1958 | 155.26 | Line_FB | 'ME_P2-3_ME-115-0102-A_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204550 | 27ORRTANNA | 204544 | 27LINCOLN | 1 | 115/115 | 227/227 | 189 | 157.1958 | 155.26 | Bus | 'ME_P2-2_ME-115-0102-4_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500/500 | 225/225 | 3464 | 168.4555 | 162.44 | Single | 'BASE CASE' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 221090 | GLENARM2 | 221089 | WINDYED1 | 1 | 115/115 | 232/232 | 222 | 157.7928 | 161.86 | Tower | 'BG_P7_GRCTN_RAPHEL_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 221090 | GLENARM2 | 221089 | WINDYED1 | 1 | 115/115 | 232/232 | 222 | 144.3243 | 149.4 | Tower | 'BG_P7_NEAST_RPHLRD_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 221090 | GLENARM2 | 221089 | WINDYED1 | 1 | 115/115 | 232/232 | 222 | 108.2883 | 113.94 | Tower | 'BG_P7_CNSTN_NWEST2_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 221090 | GLENARM2 | 221089 | WINDYED1 | 1 | 115/115 | 232/232 | 222 | 107.3423 | 113.39 | Line_FB | 'PEPCO_P4_PP40_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 221090 | GLENARM2 | 221089 | WINDYED1 | 1 | 115/115 | 232/232 | 222 | 107.2072 | 113.2 | Line_FB | 'PJM_500_BG_P4_5_CNSTN_J_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 221090 | GLENARM2 | 221089 | WINDYED1 | 1 | 115/115 | 232/232 | 222 | 107.2072 | 113.2 | Single | 'PJM_500_BG_P1_5011_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 221090 | GLENARM2 | 221089 | WINDYED1 | 1 | 115/115 | 232/232 | 222 | 105.0901 | 112.56 | Line_FB | 'BG_P4_5_WE_NORTH_TIE_SRT-A/* WINDY EDGE #1(NORTH) BUS BLACK-RED BUS TIE BREAKER 221089' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 221090 | GLENARM2 | 221089 | WINDYED1 | 1 | 115/115 | 232/232 | 222 | 104.955 | 112.35 | Line_FB | 'BG_P4_5_WE504_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 221090 | GLENARM2 | 221089 | WINDYED1 | 1 | 115/115 | 232/232 | 222 | 104.7297 | 112.16 | Bus | 'BG_P2_WE_115-N-RED_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 221090 | GLENARM2 | 221089 | WINDYED1 | 1 | 115/115 | 232/232 | 222 | 100.8559 | 108.64 | Line_FB | 'BG_P4_5_WE506_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 221090 | GLENARM2 | 221089 | WINDYED1 | 1 | 115/115 | 232/232 | 222 | 97.9279 | 106.02 | Single | 'BG_P1_110511_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200003 | BRIGHTON | 1 | 500/500 | 225/225 | 3183 | 153.9774 | 158.52 | Tower | 'BG_P7_CNSTN_NWEST2_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200003 | BRIGHTON | 1 | 500/500 | 225/225 | 3183 | 152.2872 | 157.19 | Tower | 'BG_P7_GRCTN_RAPHEL_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200003 | BRIGHTON | 1 | 500/500 | 225/225 | 3183 | 148.9255 | 153.54 | Tower | 'BG_P7_NEAST_RPHLRD_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200003 | BRIGHTON | 1 | 500/500 | 225/225 | 3183 | 146.7515 | 149.91 | Line_FB | 'PJM_500_BG_P4_5_CNSTN_13_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200003 | BRIGHTON | 1 | 500/500 | 225/225 | 3183 | 146.6824 | 149.83 | Line_FB | 'PJM_500_BG_P4_5_CNSTN_6_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200003 | BRIGHTON | 1 | 500/500 | 225/225 | 3183 | 144.3701 | 148.67 | Line_FB | 'AP_P2-3_PE-500-016_SRT-W' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200003 | BRIGHTON | 1 | 500/500 | 225/225 | 3183 | 144.4329 | 148.65 | Line_FB | 'AP_P2-3_PE-500-015_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200003 | BRIGHTON | 1 | 500/500 | 225/225 | 3183 | 143.547 | 147.78 | Single | 'AP_P1-2_PE-500-001_SRT-W' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200003 | BRIGHTON | 1 | 500/500 | 225/225 | 3183 | 143.547 | 147.78 | Single | 'AP_P1-2_WP-500-DRT17_SRT-W' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200003 | BRIGHTON | 1 | 500/500 | 225/225 | 3183 | 143.4967 | 147.72 | Line_FB | 'AP_P2-3_PE-500-018C_SRT-W' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200003 | BRIGHTON | 1 | 500/500 | 225/225 | 3183 | 143.0129 | 147.15 | Single | 'AP_P1-2_PE-500-004_SRT-W' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200003 | BRIGHTON | 1 | 500/500 | 225/225 | 3183 | 143.0129 | 147.15 | Single | 'AP_P1-2_WP-500-006_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200003 | BRIGHTON | 1 | 500/500 | 225/225 | 3183 | 141.3604 | 144.14 | Tower | 'BG_P7_GRNITE_HIRDG_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200003 | BRIGHTON | 1 | 500/500 | 225/225 | 3183 | 140.776 | 143.48 | Tower | 'BG_P7_NWEST_GRNITE_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200003 | BRIGHTON | 1 | 500/500 | 225/225 | 3183 | 140.9237 | 143.46 | Bus | 'PJM_500_BG_P2_CNSTN_230-S_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200003 | BRIGHTON | 1 | 500/500 | 225/225 | 3183 | 140.8985 | 143.43 | Bus | 'PJM_500_BG_P2_CNSTN_230-N_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200003 | BRIGHTON | 1 | 500/500 | 225/225 | 3183 | 139.1266 | 141.45 | Bus | 'AP_P2-2_WP-500-DRT16_SRT-W' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200003 | BRIGHTON | 1 | 500/500 | 225/225 | 3183 | 135.9598 | 138.28 | Bus | 'ME_P2-2_ME-115-003_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200003 | BRIGHTON | 1 | 500/500 | 225/225 | 3183 | 135.6739 | 138.04 | Bus | 'AP_P2-2_PE-138-073_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 205912 | AD1-020 TAP | 1 | 115/115 | 227/227 | 263 | 159.7719 | 157.92 | Single | 'BASE CASE' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200004 | CNASTONE | 1 | 500/500 | 225/225 | 4030 | 162.4615 | 157.59 | Line_FB | 'PJM_500_BG_P4_5_CNSTN_M_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200004 | CNASTONE | 1 | 500/500 | 225/225 | 4030 | 162.4615 | 157.59 | Single | 'PJM_500_BG_P1_5013_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200004 | CNASTONE | 1 | 500/500 | 225/225 | 4030 | 156.0298 | 150.88 | Single | 'PN_P1-2_PN-500-010T_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200004 | CNASTONE | 1 | 500/500 | 225/225 | 4030 | 153.3375 | 148.21 | Line_FB | 'PJM_500_BG_P4_5_CNSTN_L_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200004 | CNASTONE | 1 | 500/500 | 225/225 | 4030 | 153.6427 | 148.2 | Line_FB | 'PECO_P4_NOTTI55_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200004 | CNASTONE | 1 | 500/500 | 225/225 | 4030 | 153.4417 | 148.02 | Bus | 'PECO_P2-2_NOTT230B_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200004 | CNASTONE | 1 | 500/500 | 225/225 | 4030 | 153.469 | 148 | Line_FB | 'PECO_P4_NOTTI785_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200004 | CNASTONE | 1 | 500/500 | 225/225 | 4030 | 153.196 | 147.81 | Line_FB | 'PECO_P4_NOTTI85_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200004 | CNASTONE | 1 | 500/500 | 225/225 | 4030 | 153.1365 | 147.79 | Single | 'PECO_P1-2_220-08_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200004 | CNASTONE | 1 | 500/500 | 225/225 | 4030 | 152.7295 | 147.54 | Single | 'PECO_P1-2_220-93_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200004 | CNASTONE | 1 | 500/500 | 225/225 | 4030 | 150.9529 | 145.99 | Tower | 'PL_05_P71_000906_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200004 | CNASTONE | 1 | 500/500 | 225/225 | 4030 | 149.8958 | 144.5 | Tower | 'PL_04_P71_001014_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200004 | CNASTONE | 1 | 500/500 | 225/225 | 4030 | 149.2407 | 144.12 | Bus | 'PL_05_P22_000674_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200004 | CNASTONE | 1 | 500/500 | 225/225 | 4030 | 148.603 | 143.38 | Bus | 'AP_P2-2_WP-500-DRT16_SRT-W' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200004 | CNASTONE | 1 | 500/500 | 225/225 | 4030 | 148.2705 | 143.01 | Bus | 'PL_04_P22_102817_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200004 | CNASTONE | 1 | 500/500 | 225/225 | 4030 | 148.2208 | 142.97 | Tower | 'PL_04_P71_000904_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200004 | CNASTONE | 1 | 500/500 | 225/225 | 4030 | 148.2035 | 142.95 | Tower | 'PL_04_P71_001822_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200004 | CNASTONE | 1 | 500/500 | 225/225 | 4030 | 147.7717 | 142.42 | Bus | 'AEP_P2-2_#6188_05HANG R 765_1_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200004 | CNASTONE | 1 | 500/500 | 225/225 | 4030 | 146.9007 | 141.73 | Tower | 'DVP_P7-1: LN 2106-2111_SRT-SW' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200065 | PCHBTM2S | 200064 | PCHBTM1S | Z1 | 500/500 | 225/225 | 3277 | 162.0049 | 154.77 | Line_FB | 'PECO_P4_PEACH255_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200065 | PCHBTM2S | 200064 | PCHBTM1S | Z1 | 500/500 | 225/225 | 3277 | 139.3409 | 133.17 | Single | 'PECO_P1-2_PBTIE2_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200065 | PCHBTM2S | 200064 | PCHBTM1S | Z1 | 500/500 | 225/225 | 3277 | 138.3796 | 132.28 | Line_FB | 'PECO_P4_PEACH055_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200065 | PCHBTM2S | 200064 | PCHBTM1S | Z1 | 500/500 | 225/225 | 3277 | 132.3833 | 126.55 | Line_FB | 'PECO_P4_PEACH045_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200065 | PCHBTM2S | 200064 | PCHBTM1S | Z1 | 500/500 | 225/225 | 3277 | 123.2835 | 117.9 | Line_FB | 'PECO_P4_PEACH225_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230/230 | 227/229 | 903 | 144.6622 | 152.66 | Line_FB | 'PJM_500_BG_P4_5_CNSTN_B_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230/230 | 227/229 | 903 | 143.1561 | 150.2 | Line_FB | 'PJM_500_BG_P4_5_CNSTN_C_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230/230 | 227/229 | 903 | 143.1561 | 150.2 | Single | 'PECO_P1-2_5012_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230/230 | 227/229 | 903 | 143.134 | 150.19 | Line_FB | 'PECO_P4_PEACH235_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230/230 | 227/229 | 903 | 136.0687 | 140.23 | Line_FB | 'PECO_P4_PEACH245_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500/500 | 225/225 | 2901 | 145.0845 | 147.26 | Single | 'BASE CASE' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204538 | 27STRABAN | 204544 | 27LINCOLN | 1 | 115/115 | 227/227 | 291 | 145.8419 | 146.84 | Single | 'BASE CASE' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 221092 | FIVE.FOR | 221096 | ROCKRGE1 | 1 | 115/115 | 232/232 | 293 | 142.0478 | 145.53 | Tower | 'BG_P7_GRCTN_RAPHEL_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 221092 | FIVE.FOR | 221096 | ROCKRGE1 | 1 | 115/115 | 232/232 | 293 | 131.8771 | 136.02 | Tower | 'BG_P7_NEAST_RPHLRD_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 221092 | FIVE.FOR | 221096 | ROCKRGE1 | 1 | 115/115 | 232/232 | 293 | 111.1604 | 116.17 | Single | 'BG_P1_110512_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 221092 | FIVE.FOR | 221096 | ROCKRGE1 | 1 | 115/115 | 232/232 | 293 | 109.3515 | 114.41 | Line_FB | 'BG_P4_5_WE512_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 221092 | FIVE.FOR | 221096 | ROCKRGE1 | 1 | 115/115 | 232/232 | 293 | 105.0512 | 109.29 | Tower | 'BG_P7_CNSTN_NWEST2_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 221092 | FIVE.FOR | 221096 | ROCKRGE1 | 1 | 115/115 | 232/232 | 293 | 103.7201 | 108.25 | Line_FB | 'PEPCO_P4_PP40_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 221092 | FIVE.FOR | 221096 | ROCKRGE1 | 1 | 115/115 | 232/232 | 293 | 103.5836 | 108.1 | Line_FB | 'PJM_500_BG_P4_5_CNSTN_J_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 221092 | FIVE.FOR | 221096 | ROCKRGE1 | 1 | 115/115 | 232/232 | 293 | 103.5836 | 108.1 | Single | 'PJM_500_BG_P1_5011_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 221092 | FIVE.FOR | 221096 | ROCKRGE1 | 1 | 115/115 | 232/232 | 293 | 101.57 | 106.9 | Line_FB | 'BG_P4_5_WE_EAST_TIE_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 221092 | FIVE.FOR | 221096 | ROCKRGE1 | 1 | 115/115 | 232/232 | 293 | 101.1263 | 106.54 | Line_FB | 'BG_P4_5_WE518_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 221092 | FIVE.FOR | 221096 | ROCKRGE1 | 1 | 115/115 | 232/232 | 293 | 101.1263 | 106.54 | Bus | 'BG_P2_WE_115-E-BLK_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200065 | PCHBTM2S | 200064 | PCHBTM1S | Z2 | 500/500 | 225/225 | 3022 | 151.2244 | 144.5 | Line_FB | 'PECO_P4_PEACH025_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200065 | PCHBTM2S | 200064 | PCHBTM1S | Z2 | 500/500 | 225/225 | 3022 | 151.0986 | 144.41 | Single | 'PECO_P1-2_PBTIE1_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200065 | PCHBTM2S | 200064 | PCHBTM1S | Z2 | 500/500 | 225/225 | 3022 | 139.4408 | 133.49 | Line_FB | 'PECO_P4_PEACH205_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200065 | PCHBTM2S | 200064 | PCHBTM1S | Z2 | 500/500 | 225/225 | 3022 | 133.7293 | 127.9 | Line_FB | 'PECO_P4_PEACH015_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230/230 | 229/229 | 911 | 149.4621 | 143.82 | Line_FB | 'PJM_500_BG_P4_5_CNSTN_B_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230/230 | 229/229 | 911 | 148.5181 | 142.23 | Line_FB | 'PJM_500_BG_P4_5_CNSTN_C_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230/230 | 229/229 | 911 | 148.5181 | 142.23 | Single | 'PECO_P1-2_5012_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230/230 | 229/229 | 911 | 148.5071 | 142.22 | Line_FB | 'PECO_P4_PEACH235_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230/230 | 229/229 | 911 | 140.6476 | 135.51 | Line_FB | 'PECO_P4_PEACH245_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230/230 | 229/229 | 911 | 123.3809 | 125.86 | Tower | 'BG_P7_GRCTN_CNSTN_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230/230 | 229/229 | 911 | 118.4632 | 119.49 | Line_FB | 'PJM_500_BG_P4_5_CNSTN_15_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204514 | 27TMI | 204502 | 27JACKSON | 1 | 230/230 | 227/227 | 781 | 133.4059 | 142.26 | Line_FB | 'PJM_500_BG_P4_5_CNSTN_C_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204514 | 27TMI | 204502 | 27JACKSON | 1 | 230/230 | 227/227 | 781 | 133.4059 | 142.26 | Single | 'PECO_P1-2_5012_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204514 | 27TMI | 204502 | 27JACKSON | 1 | 230/230 | 227/227 | 781 | 133.3931 | 142.25 | Line_FB | 'PECO_P4_PEACH235_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204514 | 27TMI | 204502 | 27JACKSON | 1 | 230/230 | 227/227 | 781 | 133.2138 | 141.95 | Line_FB | 'PJM_500_BG_P4_5_CNSTN_B_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204514 | 27TMI | 204502 | 27JACKSON | 1 | 230/230 | 227/227 | 781 | 125.749 | 131.57 | Line_FB | 'PECO_P4_PEACH245_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204529 | 27GERMANTN | 204538 | 27STRABAN | 1 | 115/115 | 227/227 | 291 | 138.488 | 141.19 | Single | 'BASE CASE' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 221058 | DOLFD T1 | 221055 | HARRIS1A | 1 | 115/115 | 232/232 | 201 | 140.796 | 140.95 | Tower | 'BG_P7_NWEST_GRNITE_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 207922 | BRIS | 204515 | 27YORKANA | 1 | 230/230 | 229/227 | 1031 | 131.1542 | 139.51 | Line_FB | 'PJM_500_BG_P4_5_CNSTN_B_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 207922 | BRIS | 204515 | 27YORKANA | 1 | 230/230 | 229/227 | 1031 | 130.6693 | 138.72 | Line_FB | 'PJM_500_BG_P4_5_CNSTN_C_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 207922 | BRIS | 204515 | 27YORKANA | 1 | 230/230 | 229/227 | 1031 | 130.6693 | 138.72 | Single | 'PECO_P1-2_5012_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 207922 | BRIS | 204515 | 27YORKANA | 1 | 230/230 | 229/227 | 1031 | 130.6596 | 138.71 | Line_FB | 'PECO_P4_PEACH235_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 207922 | BRIS | 204515 | 27YORKANA | 1 | 230/230 | 229/227 | 1031 | 125.063 | 129.8 | Line_FB | 'PECO_P4_PEACH245_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204528 | 27GARDNERS | 200504 | 26CARLISLE | 1 | 115/115 | 227/226 | 190 | 130 | 138.88 | Line_FB | 'PN_P2-3_PN-115-0331-B_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204528 | 27GARDNERS | 200504 | 26CARLISLE | 1 | 115/115 | 227/226 | 190 | 128.4211 | 137.12 | Single | 'PN_P1-2_PN-115-094_A_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204528 | 27GARDNERS | 200504 | 26CARLISLE | 1 | 115/115 | 227/226 | 190 | 128.2632 | 136.2 | Line_FB | 'PN_P2-3_PN-115-58B_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204528 | 27GARDNERS | 200504 | 26CARLISLE | 1 | 115/115 | 227/226 | 190 | 128.9474 | 136.15 | Single | 'PN_P1-3_PN-115-040_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204528 | 27GARDNERS | 200504 | 26CARLISLE | 1 | 115/115 | 227/226 | 190 | 128.9474 | 136.15 | Bus | 'PN_P2-2_PN-115-030_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204528 | 27GARDNERS | 200504 | 26CARLISLE | 1 | 115/115 | 227/226 | 190 | 128.1053 | 136.13 | Single | 'PN_P1-2_PN-115-094_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204528 | 27GARDNERS | 200504 | 26CARLISLE | 1 | 115/115 | 227/226 | 190 | 125.7368 | 131.59 | Line_FB | 'PN_P2-3_PN-230-0014-12_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204528 | 27GARDNERS | 200504 | 26CARLISLE | 1 | 115/115 | 227/226 | 190 | 125.7368 | 131.17 | Line_FB | 'PN_P2-3_PN-230-0014-11_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204528 | 27GARDNERS | 200504 | 26CARLISLE | 1 | 115/115 | 227/226 | 190 | 125.7368 | 131.17 | Single | 'PN_P1-3_PN-230-020A_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204528 | 27GARDNERS | 200504 | 26CARLISLE | 1 | 115/115 | 227/226 | 190 | 125.6316 | 131.15 | Bus | 'PN_P2-2_PN-115-031_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204528 | 27GARDNERS | 200504 | 26CARLISLE | 1 | 115/115 | 227/226 | 190 | 121.8947 | 128.48 | Single | 'PN_P1-2_PN-115-097_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204528 | 27GARDNERS | 200504 | 26CARLISLE | 1 | 115/115 | 227/226 | 190 | 121.8947 | 128.47 | Line_FB | 'PN_P2-3_PN-115-40A_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204528 | 27GARDNERS | 200504 | 26CARLISLE | 1 | 115/115 | 227/226 | 190 | 94.4211 | 100.82 | Bus | 'ME_P2-2_ME-115-003_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200512 | 26LEWISTWN | 200519 | 26REED TAP | 1 | 115/115 | 226/226 | 271 | 128.4502 | 137.77 | Line_FB | 'PJM_500_BG_P4_5_CNSTN_C_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200512 | 26LEWISTWN | 200519 | 26REED TAP | 1 | 115/115 | 226/226 | 271 | 128.4502 | 137.77 | Line_FB | 'PECO_P4_PEACH235_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200512 | 26LEWISTWN | 200519 | 26REED TAP | 1 | 115/115 | 226/226 | 271 | 128.4502 | 137.77 | Single | 'PECO_P1-2_5012_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200512 | 26LEWISTWN | 200519 | 26REED TAP | 1 | 115/115 | 226/226 | 271 | 128.3764 | 137.54 | Line_FB | 'PJM_500_BG_P4_5_CNSTN_B_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200512 | 26LEWISTWN | 200519 | 26REED TAP | 1 | 115/115 | 226/226 | 271 | 125.6089 | 131.29 | Line_FB | 'PECO_P4_PEACH245_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200512 | 26LEWISTWN | 200519 | 26REED TAP | 1 | 115/115 | 226/226 | 271 | 121.9926 | 125.29 | Line_FB | 'PJM_500_BG_P4_5_CNSTN_J_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200512 | 26LEWISTWN | 200519 | 26REED TAP | 1 | 115/115 | 226/226 | 271 | 121.9926 | 125.29 | Single | 'PJM_500_BG_P1_5011_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200512 | 26LEWISTWN | 200519 | 26REED TAP | 1 | 115/115 | 226/226 | 271 | 121.9188 | 120.85 | Bus | 'ME_P2-2_ME-115-002T_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200512 | 26LEWISTWN | 200519 | 26REED TAP | 1 | 115/115 | 226/226 | 271 | 121.6605 | 120.62 | Single | 'ME_P1-2_ME-115-058T_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200512 | 26LEWISTWN | 200519 | 26REED TAP | 1 | 115/115 | 226/226 | 228 | 122.5439 | 119.24 | Single | 'BASE CASE' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200512 | 26LEWISTWN | 200519 | 26REED TAP | 1 | 115/115 | 226/226 | 271 | 118.8192 | 117.97 | Single | 'PN_P1-2_PN-115-095_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200512 | 26LEWISTWN | 200519 | 26REED TAP | 1 | 115/115 | 226/226 | 271 | 109.2251 | 106.77 | Bus | 'AP_P2-2_WP-500-DRT16_SRT-W' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200512 | 26LEWISTWN | 200519 | 26REED TAP | 1 | 115/115 | 226/226 | 271 | 107.0849 | 106 | Tower | 'BG_P7_CNSTN_NWEST2_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200512 | 26LEWISTWN | 200519 | 26REED TAP | 1 | 115/115 | 226/226 | 271 | 106.9004 | 105.98 | Tower | 'BG_P7_GRCTN_RAPHEL_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200512 | 26LEWISTWN | 200519 | 26REED TAP | 1 | 115/115 | 226/226 | 271 | 108.524 | 105.27 | Bus | 'ME_P2-2_ME-115-018_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200512 | 26LEWISTWN | 200519 | 26REED TAP | 1 | 115/115 | 226/226 | 271 | 106.3838 | 105.08 | Tower | 'BG_P7_NEAST_RPHLRD_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200512 | 26LEWISTWN | 200519 | 26REED TAP | 1 | 115/115 | 226/226 | 271 | 106.7897 | 104.35 | Tower | 'AP_P7-1_PE-138-003_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200512 | 26LEWISTWN | 200519 | 26REED TAP | 1 | 115/115 | 226/226 | 271 | 106.0517 | 103.61 | Tower | 'AP_P7-1_PE-138-017_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200512 | 26LEWISTWN | 200519 | 26REED TAP | 1 | 115/115 | 226/226 | 271 | 106.0886 | 103.53 | Bus | 'AP_P2-2_PE-138-021B_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200512 | 26LEWISTWN | 200519 | 26REED TAP | 1 | 115/115 | 226/226 | 271 | 105.8672 | 103.17 | Bus | 'AP_P2-2_WP-500-DRT15_SRT-W' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 203981 | AD2-062_POI | 235188 | 01GREENE | 1 | 138/138 | 226/201 | 317 | 145.5205 | 136.59 | Line_FB | 'PJM_500_BG_P4_5_CNSTN_J_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 203981 | AD2-062_POI | 235188 | 01GREENE | 1 | 138/138 | 226/201 | 317 | 145.5205 | 136.59 | Single | 'PJM_500_BG_P1_5011_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 203981 | AD2-062_POI | 235188 | 01GREENE | 1 | 138/138 | 226/201 | 317 | 145.3312 | 136.47 | Line_FB | 'PEPCO_P4_PP40_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 203981 | AD2-062_POI | 235188 | 01GREENE | 1 | 138/138 | 226/201 | 250 | 130.6 | 130.02 | Single | 'BASE CASE' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 203981 | AD2-062_POI | 235188 | 01GREENE | 1 | 138/138 | 226/201 | 317 | 139.653 | 121.71 | Line_FB | 'PJM_500_BG_P4_5_CNSTN_B_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 203981 | AD2-062_POI | 235188 | 01GREENE | 1 | 138/138 | 226/201 | 317 | 139.9054 | 121.3 | Line_FB | 'PJM_500_BG_P4_5_CNSTN_C_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 203981 | AD2-062_POI | 235188 | 01GREENE | 1 | 138/138 | 226/201 | 317 | 139.8738 | 121.3 | Line_FB | 'PECO_P4_PEACH235_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 203981 | AD2-062_POI | 235188 | 01GREENE | 1 | 138/138 | 226/201 | 317 | 139.9054 | 121.3 | Single | 'PECO_P1-2_5012_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 203981 | AD2-062_POI | 235188 | 01GREENE | 1 | 138/138 | 226/201 | 317 | 123.6909 | 119.77 | Single | 'AP_P1-2_PE-500-004_SRT-W' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 203981 | AD2-062_POI | 235188 | 01GREENE | 1 | 138/138 | 226/201 | 317 | 123.6909 | 119.77 | Single | 'AP_P1-2_WP-500-006_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 203981 | AD2-062_POI | 235188 | 01GREENE | 1 | 138/138 | 226/201 | 317 | 113.817 | 112.89 | Tower | 'BG_P7_GRCTN_RAPHEL_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 203981 | AD2-062_POI | 235188 | 01GREENE | 1 | 138/138 | 226/201 | 317 | 114.7634 | 112.68 | Bus | 'ME_P2-2_ME-115-003_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 203981 | AD2-062_POI | 235188 | 01GREENE | 1 | 138/138 | 226/201 | 317 | 113.5016 | 112.46 | Tower | 'BG_P7_CNSTN_NWEST2_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 203981 | AD2-062_POI | 235188 | 01GREENE | 1 | 138/138 | 226/201 | 317 | 113.9117 | 112.18 | Tower | 'AP_P7-1_PE-138-022T_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 203981 | AD2-062_POI | 235188 | 01GREENE | 1 | 138/138 | 226/201 | 317 | 113.9117 | 112.18 | Bus | 'AP_P2-2_PE-138-073_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 203981 | AD2-062_POI | 235188 | 01GREENE | 1 | 138/138 | 226/201 | 317 | 113.3438 | 111.96 | Bus | 'AP_P2-2_PE-138-003_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 203981 | AD2-062_POI | 235188 | 01GREENE | 1 | 138/138 | 226/201 | 317 | 112.0189 | 111.21 | Tower | 'BG_P7_NEAST_RPHLRD_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 203981 | AD2-062_POI | 235188 | 01GREENE | 1 | 138/138 | 226/201 | 317 | 111.9243 | 109.41 | Bus | 'AP_P2-2_WP-500-DRT16_SRT-W' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 203981 | AD2-062_POI | 235188 | 01GREENE | 1 | 138/138 | 226/201 | 317 | 109.7792 | 108.09 | Tower | 'AP_P7-1_PE-138-003_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 203981 | AD2-062_POI | 235188 | 01GREENE | 1 | 138/138 | 226/201 | 317 | 107.918 | 106.49 | Bus | 'AP_P2-2_PE-138-021B_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200532 | 26ROXBURY | 203981 | AD2-062_POI | 1 | 138/138 | 226/226 | 317 | 144.795 | 135.28 | Line_FB | 'PJM_500_BG_P4_5_CNSTN_J_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200532 | 26ROXBURY | 203981 | AD2-062_POI | 1 | 138/138 | 226/226 | 317 | 144.795 | 135.28 | Single | 'PJM_500_BG_P1_5011_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200532 | 26ROXBURY | 203981 | AD2-062_POI | 1 | 138/138 | 226/226 | 317 | 144.6057 | 135.15 | Line_FB | 'PEPCO_P4_PP40_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200532 | 26ROXBURY | 203981 | AD2-062_POI | 1 | 138/138 | 226/226 | 250 | 129.68 | 128.41 | Single | 'BASE CASE' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200532 | 26ROXBURY | 203981 | AD2-062_POI | 1 | 138/138 | 226/226 | 317 | 138.9274 | 120.42 | Line_FB | 'PJM_500_BG_P4_5_CNSTN_B_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200532 | 26ROXBURY | 203981 | AD2-062_POI | 1 | 138/138 | 226/226 | 317 | 139.1798 | 120.01 | Line_FB | 'PECO_P4_PEACH235_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200532 | 26ROXBURY | 203981 | AD2-062_POI | 1 | 138/138 | 226/226 | 317 | 139.1798 | 120.01 | Line_FB | 'PJM_500_BG_P4_5_CNSTN_C_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200532 | 26ROXBURY | 203981 | AD2-062_POI | 1 | 138/138 | 226/226 | 317 | 139.1798 | 120.01 | Single | 'PECO_P1-2_5012_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200532 | 26ROXBURY | 203981 | AD2-062_POI | 1 | 138/138 | 226/226 | 317 | 122.9653 | 118.49 | Single | 'AP_P1-2_WP-500-006_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200532 | 26ROXBURY | 203981 | AD2-062_POI | 1 | 138/138 | 226/226 | 317 | 122.9653 | 118.49 | Single | 'AP_P1-2_PE-500-004_SRT-W' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200532 | 26ROXBURY | 203981 | AD2-062_POI | 1 | 138/138 | 226/226 | 317 | 113.0915 | 111.61 | Tower | 'BG_P7_GRCTN_RAPHEL_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200532 | 26ROXBURY | 203981 | AD2-062_POI | 1 | 138/138 | 226/226 | 317 | 114.0379 | 111.41 | Bus | 'ME_P2-2_ME-115-003_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200532 | 26ROXBURY | 203981 | AD2-062_POI | 1 | 138/138 | 226/226 | 317 | 112.776 | 111.18 | Tower | 'BG_P7_CNSTN_NWEST2_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200532 | 26ROXBURY | 203981 | AD2-062_POI | 1 | 138/138 | 226/226 | 317 | 113.1861 | 110.88 | Tower | 'AP_P7-1_PE-138-022T_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200532 | 26ROXBURY | 203981 | AD2-062_POI | 1 | 138/138 | 226/226 | 317 | 113.1861 | 110.88 | Bus | 'AP_P2-2_PE-138-073_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200532 | 26ROXBURY | 203981 | AD2-062_POI | 1 | 138/138 | 226/226 | 317 | 112.6183 | 110.66 | Bus | 'AP_P2-2_PE-138-003_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200532 | 26ROXBURY | 203981 | AD2-062_POI | 1 | 138/138 | 226/226 | 317 | 111.2934 | 109.93 | Tower | 'BG_P7_NEAST_RPHLRD_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200532 | 26ROXBURY | 203981 | AD2-062_POI | 1 | 138/138 | 226/226 | 317 | 111.1987 | 108.14 | Bus | 'AP_P2-2_WP-500-DRT16_SRT-W' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200532 | 26ROXBURY | 203981 | AD2-062_POI | 1 | 138/138 | 226/226 | 317 | 109.0536 | 106.81 | Tower | 'AP_P7-1_PE-138-003_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200532 | 26ROXBURY | 203981 | AD2-062_POI | 1 | 138/138 | 226/226 | 317 | 107.1924 | 105.22 | Bus | 'AP_P2-2_PE-138-021B_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 207922 | BRIS | 207923 | BRISREAC | RX | 230/230 | 229/229 | 676 | 125.3698 | 134.76 | Line_FB | 'PJM_500_BG_P4_5_CNSTN_B_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 207922 | BRIS | 207923 | BRISREAC | RX | 230/230 | 229/229 | 676 | 124.6302 | 133.5 | Line_FB | 'PJM_500_BG_P4_5_CNSTN_C_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 207922 | BRIS | 207923 | BRISREAC | RX | 230/230 | 229/229 | 676 | 124.6302 | 133.5 | Single | 'PECO_P1-2_5012_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 207922 | BRIS | 207923 | BRISREAC | RX | 230/230 | 229/229 | 676 | 124.6154 | 133.49 | Line_FB | 'PECO_P4_PEACH235_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 207922 | BRIS | 207923 | BRISREAC | RX | 230/230 | 229/229 | 676 | 119.5118 | 125.24 | Line_FB | 'PECO_P4_PEACH245_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 207923 | BRISREAC | 208132 | WHEM TR1 | 1 | 230/230 | 229/229 | 676 | 125.3698 | 134.75 | Line_FB | 'PJM_500_BG_P4_5_CNSTN_B_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 207923 | BRISREAC | 208132 | WHEM TR1 | 1 | 230/230 | 229/229 | 676 | 124.6302 | 133.5 | Line_FB | 'PJM_500_BG_P4_5_CNSTN_C_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 207923 | BRISREAC | 208132 | WHEM TR1 | 1 | 230/230 | 229/229 | 676 | 124.6302 | 133.5 | Single | 'PECO_P1-2_5012_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 207923 | BRISREAC | 208132 | WHEM TR1 | 1 | 230/230 | 229/229 | 676 | 124.6154 | 133.49 | Line_FB | 'PECO_P4_PEACH235_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 207923 | BRISREAC | 208132 | WHEM TR1 | 1 | 230/230 | 229/229 | 676 | 119.5118 | 125.24 | Line_FB | 'PECO_P4_PEACH245_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208078 | SAKR | 208030 | MLWD TR1 | 1 | 230/230 | 229/229 | 903 | 125.6478 | 134.22 | Line_FB | 'PJM_500_BG_P4_5_CNSTN_B_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208078 | SAKR | 208030 | MLWD TR1 | 1 | 230/230 | 229/229 | 903 | 124.9169 | 133.21 | Line_FB | 'PJM_500_BG_P4_5_CNSTN_C_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208078 | SAKR | 208030 | MLWD TR1 | 1 | 230/230 | 229/229 | 903 | 124.9169 | 133.21 | Line_FB | 'PECO_P4_PEACH235_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208078 | SAKR | 208030 | MLWD TR1 | 1 | 230/230 | 229/229 | 903 | 124.9169 | 133.21 | Single | 'PECO_P1-2_5012_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208078 | SAKR | 208030 | MLWD TR1 | 1 | 230/230 | 229/229 | 903 | 117.6412 | 123.11 | Line_FB | 'PECO_P4_PEACH245_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 221057 | DOLFD T0 | 221056 | HARRIS0A | 1 | 115/115 | 232/232 | 201 | 133.8308 | 133.85 | Tower | 'BG_P7_NWEST_GRNITE_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200519 | 26REED TAP | 200522 | 26SHADE GP | 1 | 115/115 | 226/226 | 271 | 120.7011 | 132.61 | Line_FB | 'PJM_500_BG_P4_5_CNSTN_C_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200519 | 26REED TAP | 200522 | 26SHADE GP | 1 | 115/115 | 226/226 | 271 | 120.7011 | 132.61 | Line_FB | 'PECO_P4_PEACH235_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200519 | 26REED TAP | 200522 | 26SHADE GP | 1 | 115/115 | 226/226 | 271 | 120.7011 | 132.61 | Single | 'PECO_P1-2_5012_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200519 | 26REED TAP | 200522 | 26SHADE GP | 1 | 115/115 | 226/226 | 271 | 120.6273 | 132.4 | Line_FB | 'PJM_500_BG_P4_5_CNSTN_B_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200519 | 26REED TAP | 200522 | 26SHADE GP | 1 | 115/115 | 226/226 | 271 | 117.8967 | 126.24 | Line_FB | 'PECO_P4_PEACH245_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200519 | 26REED TAP | 200522 | 26SHADE GP | 1 | 115/115 | 226/226 | 271 | 114.2435 | 120.34 | Line_FB | 'PJM_500_BG_P4_5_CNSTN_J_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200519 | 26REED TAP | 200522 | 26SHADE GP | 1 | 115/115 | 226/226 | 271 | 114.2435 | 120.34 | Single | 'PJM_500_BG_P1_5011_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200519 | 26REED TAP | 200522 | 26SHADE GP | 1 | 115/115 | 226/226 | 271 | 114.2066 | 115.98 | Bus | 'ME_P2-2_ME-115-002T_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200519 | 26REED TAP | 200522 | 26SHADE GP | 1 | 115/115 | 226/226 | 271 | 113.9483 | 115.76 | Single | 'ME_P1-2_ME-115-058T_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200519 | 26REED TAP | 200522 | 26SHADE GP | 1 | 115/115 | 226/226 | 224 | 115.3571 | 115.59 | Single | 'BASE CASE' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200519 | 26REED TAP | 200522 | 26SHADE GP | 1 | 115/115 | 226/226 | 271 | 111.0701 | 113.12 | Single | 'PN_P1-2_PN-115-095_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200519 | 26REED TAP | 200522 | 26SHADE GP | 1 | 115/115 | 226/226 | 271 | 101.5129 | 101.95 | Bus | 'AP_P2-2_WP-500-DRT16_SRT-W' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200519 | 26REED TAP | 200522 | 26SHADE GP | 1 | 115/115 | 226/226 | 271 | 99.3358 | 101.19 | Tower | 'BG_P7_CNSTN_NWEST2_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200519 | 26REED TAP | 200522 | 26SHADE GP | 1 | 115/115 | 226/226 | 271 | 99.1513 | 101.17 | Tower | 'BG_P7_GRCTN_RAPHEL_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200519 | 26REED TAP | 200522 | 26SHADE GP | 1 | 115/115 | 226/226 | 271 | 100.8118 | 100.48 | Bus | 'ME_P2-2_ME-115-018_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200519 | 26REED TAP | 200522 | 26SHADE GP | 1 | 115/115 | 226/226 | 271 | 98.6347 | 100.28 | Tower | 'BG_P7_NEAST_RPHLRD_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220972 | GRANITE1 | 1 | 230/230 | 232/232 | 829 | 135.3559 | 131.4 | Line_FB | 'PEPCO_P4_PP40_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220972 | GRANITE1 | 1 | 230/230 | 232/232 | 829 | 134.7286 | 130.73 | Line_FB | 'PJM_500_BG_P4_5_CNSTN_J_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220972 | GRANITE1 | 1 | 230/230 | 232/232 | 829 | 134.7286 | 130.73 | Single | 'PJM_500_BG_P1_5011_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220972 | GRANITE1 | 1 | 230/230 | 232/232 | 829 | 108.3595 | 106.87 | Tower | 'BG_P7_GRCTN_RAPHEL_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220972 | GRANITE1 | 1 | 230/230 | 232/232 | 829 | 106.2847 | 104.95 | Line_FB | 'BG_P4_5_NW230-4_2326_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220972 | GRANITE1 | 1 | 230/230 | 232/232 | 829 | 103.3172 | 102.09 | Tower | 'BG_P7_NEAST_RPHLRD_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204529 | 27GERMANTN | 204530 | 27GERMANTN | 1 | 115/138 | 227/227 | 453 | 124.8786 | 130.88 | Line_FB | 'PJM_500_BG_P4_5_CNSTN_J_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204529 | 27GERMANTN | 204530 | 27GERMANTN | 1 | 115/138 | 227/227 | 453 | 124.8786 | 130.88 | Single | 'PJM_500_BG_P1_5011_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204529 | 27GERMANTN | 204530 | 27GERMANTN | 1 | 115/138 | 227/227 | 453 | 124.7682 | 130.79 | Line_FB | 'PEPCO_P4_PP40_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204529 | 27GERMANTN | 204530 | 27GERMANTN | 1 | 115/138 | 227/227 | 453 | 105.7174 | 108.04 | Line_FB | 'PJM_500_BG_P4_5_CNSTN_C_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204529 | 27GERMANTN | 204530 | 27GERMANTN | 1 | 115/138 | 227/227 | 453 | 105.7174 | 108.04 | Line_FB | 'PECO_P4_PEACH235_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204529 | 27GERMANTN | 204530 | 27GERMANTN | 1 | 115/138 | 227/227 | 453 | 105.7174 | 108.04 | Single | 'PECO_P1-2_5012_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204529 | 27GERMANTN | 204530 | 27GERMANTN | 1 | 115/138 | 227/227 | 453 | 105.585 | 107.74 | Line_FB | 'PJM_500_BG_P4_5_CNSTN_B_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204529 | 27GERMANTN | 204530 | 27GERMANTN | 1 | 115/138 | 227/227 | 453 | 95.298 | 100.11 | Tower | 'BG_P7_GRCTN_RAPHEL_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220973 | GRANITE6 | 1 | 230/230 | 232/232 | 829 | 133.269 | 129.5 | Line_FB | 'PEPCO_P4_PP40_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220973 | GRANITE6 | 1 | 230/230 | 232/232 | 829 | 132.6779 | 128.87 | Line_FB | 'PJM_500_BG_P4_5_CNSTN_J_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220973 | GRANITE6 | 1 | 230/230 | 232/232 | 829 | 132.6779 | 128.87 | Single | 'PJM_500_BG_P1_5011_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220973 | GRANITE6 | 1 | 230/230 | 232/232 | 829 | 109.2159 | 107.95 | Tower | 'BG_P7_GRCTN_RAPHEL_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220973 | GRANITE6 | 1 | 230/230 | 232/232 | 829 | 105.959 | 104.42 | Line_FB | 'BG_P4_5_NW230-5_2311_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220973 | GRANITE6 | 1 | 230/230 | 232/232 | 829 | 103.9083 | 102.86 | Tower | 'BG_P7_NEAST_RPHLRD_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230/230 | 233/345 | 1508 | 129.3037 | 127.58 | Line_FB | 'DVP_P4-2: 514T595_SRT-SW' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230/230 | 233/345 | 1508 | 127.5663 | 125.88 | Line_FB | 'DVP_P4-2: 51482_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230/230 | 233/345 | 1508 | 127.5663 | 125.78 | Single | 'AP_P1-2_PE-500-407T_SRT-W' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230/230 | 233/345 | 1508 | 127.5663 | 125.78 | Single | 'DVP_P1-2: LN 514_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230/230 | 233/345 | 1508 | 117.752 | 115.86 | Line_FB | 'AP_P2-3_PE-500-019C_SRT-W' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204539 | 27HUNTRSTN | 204550 | 27ORRTANNA | 1 | 115/115 | 227/227 | 264 | 127.3485 | 127.12 | Single | 'ME_P1-2_ME-115-068_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204539 | 27HUNTRSTN | 204550 | 27ORRTANNA | 1 | 115/115 | 227/227 | 264 | 126.0606 | 127.08 | Line_FB | 'ME_P2-3_ME-115-035A_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204539 | 27HUNTRSTN | 204550 | 27ORRTANNA | 1 | 115/115 | 227/227 | 264 | 127.0076 | 125.9 | Single | 'ME_P1-2_ME-115-067_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204539 | 27HUNTRSTN | 204550 | 27ORRTANNA | 1 | 115/115 | 227/227 | 264 | 125.7197 | 125.36 | Line_FB | 'ME_P2-3_ME-115-013B_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204539 | 27HUNTRSTN | 204550 | 27ORRTANNA | 1 | 115/115 | 227/227 | 264 | 124.4318 | 125.28 | Line_FB | 'ME_P2-3_ME-115-035B_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204539 | 27HUNTRSTN | 204550 | 27ORRTANNA | 1 | 115/115 | 227/227 | 264 | 125.4924 | 125.12 | Line_FB | 'ME_P2-3_ME-115-013A_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204539 | 27HUNTRSTN | 204550 | 27ORRTANNA | 1 | 115/115 | 227/227 | 264 | 122.2348 | 120.75 | Line_FB | 'ME_P2-3_ME-115-0102-A_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204539 | 27HUNTRSTN | 204550 | 27ORRTANNA | 1 | 115/115 | 227/227 | 264 | 122.2348 | 120.75 | Bus | 'ME_P2-2_ME-115-0102-4_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208020 | MANO TR3 | 208019 | MANO | 1 | 230/230 | 229/229 | 793 | 112.7238 | 126.62 | Line_FB | 'PJM_500_BG_P4_5_CNSTN_B_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208020 | MANO TR3 | 208019 | MANO | 1 | 230/230 | 229/229 | 793 | 111.9042 | 125.42 | Line_FB | 'PJM_500_BG_P4_5_CNSTN_C_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208020 | MANO TR3 | 208019 | MANO | 1 | 230/230 | 229/229 | 793 | 111.9042 | 125.42 | Line_FB | 'PECO_P4_PEACH235_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208020 | MANO TR3 | 208019 | MANO | 1 | 230/230 | 229/229 | 793 | 111.9042 | 125.42 | Single | 'PECO_P1-2_5012_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208020 | MANO TR3 | 208019 | MANO | 1 | 230/230 | 229/229 | 793 | 104.7163 | 114.69 | Line_FB | 'PECO_P4_PEACH245_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220972 | GRANITE1 | 220953 | HOWARD12 | 1 | 230/230 | 232/232 | 772 | 130.1943 | 126.24 | Line_FB | 'PEPCO_P4_PP40_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220972 | GRANITE1 | 220953 | HOWARD12 | 1 | 230/230 | 232/232 | 772 | 129.2876 | 125.25 | Line_FB | 'PJM_500_BG_P4_5_CNSTN_J_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220972 | GRANITE1 | 220953 | HOWARD12 | 1 | 230/230 | 232/232 | 772 | 129.2876 | 125.25 | Single | 'PJM_500_BG_P1_5011_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220973 | GRANITE6 | 220954 | HOWARD32 | 1 | 230/230 | 232/232 | 772 | 129.0155 | 125.51 | Line_FB | 'PEPCO_P4_PP40_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220973 | GRANITE6 | 220954 | HOWARD32 | 1 | 230/230 | 232/232 | 772 | 128.2254 | 124.65 | Line_FB | 'PJM_500_BG_P4_5_CNSTN_J_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220973 | GRANITE6 | 220954 | HOWARD32 | 1 | 230/230 | 232/232 | 772 | 128.2254 | 124.65 | Single | 'PJM_500_BG_P1_5011_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223938 | DICKH230 | 223937 | DICK 230 | 2 | 230/230 | 233/233 | 793 | 127.2509 | 125.5 | Line_FB | 'DVP_P4-2: 514T595_SRT-SW' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223938 | DICKH230 | 223937 | DICK 230 | 2 | 230/230 | 233/233 | 793 | 126.0025 | 124.31 | Line_FB | 'DVP_P4-2: 51482_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223938 | DICKH230 | 223937 | DICK 230 | 2 | 230/230 | 233/233 | 793 | 126.0025 | 124.23 | Single | 'DVP_P1-2: LN 514_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223938 | DICKH230 | 223937 | DICK 230 | 2 | 230/230 | 233/233 | 793 | 126.0025 | 124.23 | Single | 'AP_P1-2_PE-500-407T_SRT-W' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223938 | DICKH230 | 223937 | DICK 230 | 2 | 230/230 | 233/233 | 793 | 119.2182 | 116.48 | Single | 'PEPCO_P1_PP1_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223938 | DICKH230 | 223937 | DICK 230 | 2 | 230/230 | 233/233 | 793 | 110.1892 | 108.32 | Line_FB | 'AP_P2-3_PE-500-019C_SRT-W' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223938 | DICKH230 | 223937 | DICK 230 | 1 | 230/230 | 233/233 | 793 | 127.2509 | 125.5 | Line_FB | 'DVP_P4-2: 514T595_SRT-SW' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223938 | DICKH230 | 223937 | DICK 230 | 1 | 230/230 | 233/233 | 793 | 126.0025 | 124.31 | Line_FB | 'DVP_P4-2: 51482_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223938 | DICKH230 | 223937 | DICK 230 | 1 | 230/230 | 233/233 | 793 | 126.0025 | 124.23 | Single | 'DVP_P1-2: LN 514_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223938 | DICKH230 | 223937 | DICK 230 | 1 | 230/230 | 233/233 | 793 | 126.0025 | 124.23 | Single | 'AP_P1-2_PE-500-407T_SRT-W' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223938 | DICKH230 | 223937 | DICK 230 | 1 | 230/230 | 233/233 | 793 | 119.2182 | 116.48 | Single | 'PEPCO_P1_PP2_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223938 | DICKH230 | 223937 | DICK 230 | 1 | 230/230 | 233/233 | 793 | 113.4678 | 110.83 | Line_FB | 'PEPCO_P4_PP19_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223938 | DICKH230 | 223937 | DICK 230 | 1 | 230/230 | 233/233 | 793 | 110.1892 | 108.32 | Line_FB | 'AP_P2-3_PE-500-019C_SRT-W' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208394 | PPL-BGE TIE | 221092 | FIVE.FOR | 1 | 115/115 | 229/232 | 247 | 121.9838 | 124.91 | Tower | 'PL_05_P71_000906_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208394 | PPL-BGE TIE | 221092 | FIVE.FOR | 1 | 115/115 | 229/232 | 247 | 118.8259 | 120.32 | Line_FB | 'PJM_500_BG_P4_5_CNSTN_B_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208394 | PPL-BGE TIE | 221092 | FIVE.FOR | 1 | 115/115 | 229/232 | 247 | 118.7449 | 120.15 | Line_FB | 'PECO_P4_PEACH235_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208394 | PPL-BGE TIE | 221092 | FIVE.FOR | 1 | 115/115 | 229/232 | 247 | 118.7449 | 120.15 | Line_FB | 'PJM_500_BG_P4_5_CNSTN_C_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208394 | PPL-BGE TIE | 221092 | FIVE.FOR | 1 | 115/115 | 229/232 | 247 | 118.7449 | 120.15 | Single | 'PECO_P1-2_5012_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208394 | PPL-BGE TIE | 221092 | FIVE.FOR | 1 | 115/115 | 229/232 | 247 | 112.9555 | 118.79 | Tower | 'BG_P7_GRCTN_RAPHEL_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208394 | PPL-BGE TIE | 221092 | FIVE.FOR | 1 | 115/115 | 229/232 | 247 | 114.332 | 115.92 | Line_FB | 'PECO_P4_PEACH245_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208394 | PPL-BGE TIE | 221092 | FIVE.FOR | 1 | 115/115 | 229/232 | 247 | 108.8259 | 114.09 | Tower | 'BG_P7_NEAST_RPHLRD_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208394 | PPL-BGE TIE | 221092 | FIVE.FOR | 1 | 115/115 | 229/232 | 247 | 109.2713 | 113.07 | Line_FB | 'BG_P4_5_GRCTN_2T_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208394 | PPL-BGE TIE | 221092 | FIVE.FOR | 1 | 115/115 | 229/232 | 247 | 105.8704 | 112.35 | Single | 'PJM_500_BG_P1_5011_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208394 | PPL-BGE TIE | 221092 | FIVE.FOR | 1 | 115/115 | 229/232 | 247 | 105.6275 | 109.19 | Single | 'PL_04_P12_000257_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208394 | PPL-BGE TIE | 221092 | FIVE.FOR | 1 | 115/115 | 229/232 | 247 | 105.6275 | 109.19 | Bus | 'PL_05_P22_000674_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208394 | PPL-BGE TIE | 221092 | FIVE.FOR | 1 | 115/115 | 229/232 | 247 | 100.9312 | 106.83 | Tower | 'BG_P7_CNSTN_NWEST2_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208394 | PPL-BGE TIE | 221092 | FIVE.FOR | 1 | 115/115 | 229/232 | 247 | 96.2348 | 101.18 | Tower | 'PL_04_P71_001819_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208395 | FARO FF | 208393 | FARO DC TIE | 2 | 69/115 | 229/229 | 120 | 128 | 124.23 | Tower | 'PL_05_P71_000906_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208395 | FARO FF | 208393 | FARO DC TIE | 2 | 69/115 | 229/229 | 120 | 124.75 | 119.45 | Line_FB | 'PJM_500_BG_P4_5_CNSTN_B_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208395 | FARO FF | 208393 | FARO DC TIE | 2 | 69/115 | 229/229 | 120 | 124.6667 | 119.13 | Line_FB | 'PJM_500_BG_P4_5_CNSTN_C_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208395 | FARO FF | 208393 | FARO DC TIE | 2 | 69/115 | 229/229 | 120 | 124.6667 | 119.13 | Single | 'PECO_P1-2_5012_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208395 | FARO FF | 208393 | FARO DC TIE | 2 | 69/115 | 229/229 | 120 | 124.6667 | 119.12 | Line_FB | 'PECO_P4_PEACH235_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208395 | FARO FF | 208393 | FARO DC TIE | 2 | 69/115 | 229/229 | 120 | 118.75 | 116.85 | Tower | 'BG_P7_GRCTN_RAPHEL_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208395 | FARO FF | 208393 | FARO DC TIE | 2 | 69/115 | 229/229 | 120 | 120.0833 | 115.32 | Line_FB | 'PECO_P4_PEACH245_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208395 | FARO FF | 208393 | FARO DC TIE | 2 | 69/115 | 229/229 | 120 | 114.9167 | 113.25 | Line_FB | 'BG_P4_5_GRCTN_2T_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208395 | FARO FF | 208393 | FARO DC TIE | 2 | 69/115 | 229/229 | 120 | 114.5 | 112.99 | Tower | 'BG_P7_NEAST_RPHLRD_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208395 | FARO FF | 208393 | FARO DC TIE | 2 | 69/115 | 229/229 | 120 | 111.4167 | 111.92 | Single | 'PJM_500_BG_P1_5011_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208395 | FARO FF | 208393 | FARO DC TIE | 2 | 69/115 | 229/229 | 120 | 111.1667 | 109.94 | Single | 'PL_04_P12_000257_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208395 | FARO FF | 208393 | FARO DC TIE | 2 | 69/115 | 229/229 | 120 | 111.1667 | 109.94 | Bus | 'PL_05_P22_000674_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208395 | FARO FF | 208393 | FARO DC TIE | 2 | 69/115 | 229/229 | 120 | 106.3333 | 106.85 | Tower | 'BG_P7_CNSTN_NWEST2_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208395 | FARO FF | 208393 | FARO DC TIE | 2 | 69/115 | 229/229 | 120 | 101.5 | 102.57 | Tower | 'PL_04_P71_001819_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208395 | FARO FF | 208393 | FARO DC TIE | 1 | 69/115 | 229/229 | 120 | 128 | 124.23 | Tower | 'PL_05_P71_000906_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208395 | FARO FF | 208393 | FARO DC TIE | 1 | 69/115 | 229/229 | 120 | 124.75 | 119.45 | Line_FB | 'PJM_500_BG_P4_5_CNSTN_B_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208395 | FARO FF | 208393 | FARO DC TIE | 1 | 69/115 | 229/229 | 120 | 124.6667 | 119.13 | Line_FB | 'PJM_500_BG_P4_5_CNSTN_C_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208395 | FARO FF | 208393 | FARO DC TIE | 1 | 69/115 | 229/229 | 120 | 124.6667 | 119.13 | Single | 'PECO_P1-2_5012_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208395 | FARO FF | 208393 | FARO DC TIE | 1 | 69/115 | 229/229 | 120 | 124.6667 | 119.12 | Line_FB | 'PECO_P4_PEACH235_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208395 | FARO FF | 208393 | FARO DC TIE | 1 | 69/115 | 229/229 | 120 | 118.75 | 116.85 | Tower | 'BG_P7_GRCTN_RAPHEL_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208395 | FARO FF | 208393 | FARO DC TIE | 1 | 69/115 | 229/229 | 120 | 120.0833 | 115.32 | Line_FB | 'PECO_P4_PEACH245_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208395 | FARO FF | 208393 | FARO DC TIE | 1 | 69/115 | 229/229 | 120 | 114.9167 | 113.25 | Line_FB | 'BG_P4_5_GRCTN_2T_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208395 | FARO FF | 208393 | FARO DC TIE | 1 | 69/115 | 229/229 | 120 | 114.4167 | 112.99 | Tower | 'BG_P7_NEAST_RPHLRD_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208395 | FARO FF | 208393 | FARO DC TIE | 1 | 69/115 | 229/229 | 120 | 111.4167 | 111.92 | Single | 'PJM_500_BG_P1_5011_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208395 | FARO FF | 208393 | FARO DC TIE | 1 | 69/115 | 229/229 | 120 | 111.1667 | 109.94 | Single | 'PL_04_P12_000257_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208395 | FARO FF | 208393 | FARO DC TIE | 1 | 69/115 | 229/229 | 120 | 111.1667 | 109.94 | Bus | 'PL_05_P22_000674_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208395 | FARO FF | 208393 | FARO DC TIE | 1 | 69/115 | 229/229 | 120 | 106.3333 | 106.85 | Tower | 'BG_P7_CNSTN_NWEST2_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208395 | FARO FF | 208393 | FARO DC TIE | 1 | 69/115 | 229/229 | 120 | 101.5 | 102.57 | Tower | 'PL_04_P71_001819_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204693 | 27BOONETOWN | 204512 | 27S.RDG | 1 | 230/230 | 227/227 | 607 | 107.6606 | 122.99 | Line_FB | 'PECO_P4_PEACH235_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204693 | 27BOONETOWN | 204512 | 27S.RDG | 1 | 230/230 | 227/227 | 607 | 107.6442 | 122.96 | Line_FB | 'PJM_500_BG_P4_5_CNSTN_C_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204693 | 27BOONETOWN | 204512 | 27S.RDG | 1 | 230/230 | 227/227 | 607 | 107.6442 | 122.96 | Single | 'PECO_P1-2_5012_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204693 | 27BOONETOWN | 204512 | 27S.RDG | 1 | 230/230 | 227/227 | 607 | 107.8254 | 122.82 | Line_FB | 'PJM_500_BG_P4_5_CNSTN_B_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204693 | 27BOONETOWN | 204512 | 27S.RDG | 1 | 230/230 | 227/227 | 607 | 105.8814 | 115.28 | Line_FB | 'PECO_P4_PEACH245_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204693 | 27BOONETOWN | 204512 | 27S.RDG | 1 | 230/230 | 227/227 | 607 | 110.0329 | 109.36 | Line_FB | 'PL_04_P42_101307_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204693 | 27BOONETOWN | 204512 | 27S.RDG | 1 | 230/230 | 227/227 | 607 | 108.2702 | 107.67 | Bus | 'PL_04_P22_102291_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204693 | 27BOONETOWN | 204512 | 27S.RDG | 1 | 230/230 | 227/227 | 607 | 108.2702 | 107.65 | Single | 'PL_04_P13_101211_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204693 | 27BOONETOWN | 204512 | 27S.RDG | 1 | 230/230 | 227/227 | 607 | 108.2702 | 107.65 | Bus | 'PL_04_P22_102290_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208031 | MLWD TR2 | 1 | 230/230 | 229/229 | 911 | 112.8869 | 122.89 | Line_FB | 'PJM_500_BG_P4_5_CNSTN_B_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208031 | MLWD TR2 | 1 | 230/230 | 229/229 | 911 | 112.1844 | 121.85 | Line_FB | 'PJM_500_BG_P4_5_CNSTN_C_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208031 | MLWD TR2 | 1 | 230/230 | 229/229 | 911 | 112.1734 | 121.85 | Line_FB | 'PECO_P4_PEACH235_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208031 | MLWD TR2 | 1 | 230/230 | 229/229 | 911 | 112.1844 | 121.85 | Single | 'PECO_P1-2_5012_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208031 | MLWD TR2 | 1 | 230/230 | 229/229 | 911 | 105.4116 | 112.3 | Line_FB | 'PECO_P4_PEACH245_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200025 | W CHAPEL | 1 | 500/500 | 225/225 | 1732 | 124.0762 | 122.3 | Line_FB | 'PEPCO_P4_PP41_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200520 | 26ROXBURY | 200532 | 26ROXBURY | 2 | 115/138 | 226/226 | 435 | 105.5172 | 120.28 | Line_FB | 'PJM_500_BG_P4_5_CNSTN_J_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200520 | 26ROXBURY | 200532 | 26ROXBURY | 2 | 115/138 | 226/226 | 435 | 105.5172 | 120.28 | Single | 'PJM_500_BG_P1_5011_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200520 | 26ROXBURY | 200532 | 26ROXBURY | 2 | 115/138 | 226/226 | 435 | 105.3793 | 120.13 | Line_FB | 'PEPCO_P4_PP40_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200520 | 26ROXBURY | 200532 | 26ROXBURY | 2 | 115/138 | 226/226 | 435 | 101.4253 | 116.68 | Line_FB | 'PJM_500_BG_P4_5_CNSTN_C_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200520 | 26ROXBURY | 200532 | 26ROXBURY | 2 | 115/138 | 226/226 | 435 | 101.4253 | 116.68 | Line_FB | 'PECO_P4_PEACH235_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200520 | 26ROXBURY | 200532 | 26ROXBURY | 2 | 115/138 | 226/226 | 435 | 101.4253 | 116.68 | Single | 'PECO_P1-2_5012_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200520 | 26ROXBURY | 200532 | 26ROXBURY | 2 | 115/138 | 226/226 | 435 | 101.2414 | 116.35 | Line_FB | 'PJM_500_BG_P4_5_CNSTN_B_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200520 | 26ROXBURY | 200532 | 26ROXBURY | 2 | 115/138 | 226/226 | 435 | N/A | 101.98 | Single | 'AP_P1-2_PE-500-004_SRT-W' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200520 | 26ROXBURY | 200532 | 26ROXBURY | 2 | 115/138 | 226/226 | 435 | N/A | 101.98 | Single | 'AP_P1-2_WP-500-006_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200520 | 26ROXBURY | 200532 | 26ROXBURY | 2 | 115/138 | 226/226 | 435 | N/A | 101.64 | Single | 'AP_P1-2_PE-500-001_SRT-W' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 221092 | FIVE.FOR | 221095 | ROCKRGE2 | 1 | 115/115 | 232/232 | 340 | 117.1176 | 119.56 | Tower | 'BG_P7_GRCTN_RAPHEL_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 221092 | FIVE.FOR | 221095 | ROCKRGE2 | 1 | 115/115 | 232/232 | 340 | 108.3235 | 111.37 | Tower | 'BG_P7_NEAST_RPHLRD_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220980 | RAPHAEL | 220965 | NEAST339 | 1 | 230/230 | 232/232 | 1340 | 120.1045 | 119.46 | Single | 'BG_P1_2315_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220980 | RAPHAEL | 220965 | NEAST339 | 1 | 230/230 | 232/232 | 1340 | 119.6791 | 119.25 | Line_FB | 'BG_P4_5_NEAST_17_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220980 | RAPHAEL | 220965 | NEAST339 | 1 | 230/230 | 232/232 | 1340 | 119.8358 | 119.25 | Line_FB | 'BG_P4_5_NEAST_15_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220980 | RAPHAEL | 220965 | NEAST339 | 1 | 230/230 | 232/232 | 1340 | 108.6418 | 107.24 | Line_FB | 'PEPCO_P4_PP40_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220980 | RAPHAEL | 220965 | NEAST339 | 1 | 230/230 | 232/232 | 1340 | 108.5448 | 107.11 | Line_FB | 'PJM_500_BG_P4_5_CNSTN_J_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220980 | RAPHAEL | 220965 | NEAST339 | 1 | 230/230 | 232/232 | 1340 | 108.5448 | 107.11 | Single | 'PJM_500_BG_P1_5011_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220980 | RAPHAEL | 220965 | NEAST339 | 1 | 230/230 | 232/232 | 1340 | 103.0224 | 102.37 | Tower | 'BG_P7_CNSTN_NWEST2_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208132 | WHEM TR1 | 208131 | WHEM | 1 | 230/230 | 229/229 | 691 | 109.5948 | 119.43 | Line_FB | 'PJM_500_BG_P4_5_CNSTN_B_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208132 | WHEM TR1 | 208131 | WHEM | 1 | 230/230 | 229/229 | 691 | 108.8857 | 118.28 | Line_FB | 'PJM_500_BG_P4_5_CNSTN_C_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208132 | WHEM TR1 | 208131 | WHEM | 1 | 230/230 | 229/229 | 691 | 108.8857 | 118.28 | Single | 'PECO_P1-2_5012_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208132 | WHEM TR1 | 208131 | WHEM | 1 | 230/230 | 229/229 | 691 | 108.8712 | 118.27 | Line_FB | 'PECO_P4_PEACH235_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208132 | WHEM TR1 | 208131 | WHEM | 1 | 230/230 | 229/229 | 691 | 104.0955 | 110.69 | Line_FB | 'PECO_P4_PEACH245_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220963 | CONASTON | 220962 | NWEST311 | 1 | 230/230 | 232/232 | 1381 | 115.0181 | 118.78 | Line_FB | 'PEPCO_P4_PP40_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220963 | CONASTON | 220962 | NWEST311 | 1 | 230/230 | 232/232 | 1381 | 114.6705 | 118.36 | Line_FB | 'PJM_500_BG_P4_5_CNSTN_J_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220963 | CONASTON | 220962 | NWEST311 | 1 | 230/230 | 232/232 | 1381 | 114.6705 | 118.36 | Single | 'PJM_500_BG_P1_5011_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220963 | CONASTON | 220962 | NWEST311 | 1 | 230/230 | 232/232 | 1381 | 106.6184 | 111.45 | Tower | 'BG_P7_GRCTN_RAPHEL_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220963 | CONASTON | 220962 | NWEST311 | 1 | 230/230 | 232/232 | 1381 | 101.7741 | 105.99 | Tower | 'BG_P7_NEAST_RPHLRD_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220963 | CONASTON | 220962 | NWEST311 | 1 | 230/230 | 232/232 | 1381 | 102.9689 | 105.01 | Single | 'BG_P1_2322_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220963 | CONASTON | 220962 | NWEST311 | 1 | 230/230 | 232/232 | 1381 | 102.9109 | 104.9 | Line_FB | 'BG_P4_5_NW2322_230-4_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220963 | CONASTON | 220962 | NWEST311 | 1 | 230/230 | 232/232 | 1381 | 101.5568 | 103.63 | Line_FB | 'BG_P4_5_NW230-2_2322_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220980 | RAPHAEL | 220979 | NEAST317 | 1 | 230/230 | 232/232 | 1340 | 119.1791 | 118.58 | Single | 'BG_P1_2337_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220980 | RAPHAEL | 220979 | NEAST317 | 1 | 230/230 | 232/232 | 1340 | 118.8433 | 118.31 | Line_FB | 'BG_P4_5_NEAST_39_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220980 | RAPHAEL | 220979 | NEAST317 | 1 | 230/230 | 232/232 | 1340 | 118.8433 | 118.31 | Line_FB | 'BG_P4_5_NEAST_37_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220980 | RAPHAEL | 220979 | NEAST317 | 1 | 230/230 | 232/232 | 1340 | 105.5224 | 104.17 | Line_FB | 'PEPCO_P4_PP40_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220980 | RAPHAEL | 220979 | NEAST317 | 1 | 230/230 | 232/232 | 1340 | 105.4179 | 104.04 | Line_FB | 'PJM_500_BG_P4_5_CNSTN_J_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220980 | RAPHAEL | 220979 | NEAST317 | 1 | 230/230 | 232/232 | 1340 | 105.4179 | 104.04 | Single | 'PJM_500_BG_P1_5011_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220980 | RAPHAEL | 220979 | NEAST317 | 1 | 230/230 | 232/232 | 1340 | 100.903 | 100.26 | Tower | 'BG_P7_CNSTN_NWEST2_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220963 | CONASTON | 220961 | NWEST326 | 1 | 230/230 | 232/232 | 1381 | 114.6778 | 118.44 | Line_FB | 'PEPCO_P4_PP40_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220963 | CONASTON | 220961 | NWEST326 | 1 | 230/230 | 232/232 | 1381 | 114.3374 | 118.03 | Line_FB | 'PJM_500_BG_P4_5_CNSTN_J_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220963 | CONASTON | 220961 | NWEST326 | 1 | 230/230 | 232/232 | 1381 | 114.3374 | 118.03 | Single | 'PJM_500_BG_P1_5011_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220963 | CONASTON | 220961 | NWEST326 | 1 | 230/230 | 232/232 | 1381 | 106.7415 | 111.58 | Tower | 'BG_P7_GRCTN_RAPHEL_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220963 | CONASTON | 220961 | NWEST326 | 1 | 230/230 | 232/232 | 1381 | 101.861 | 106.07 | Tower | 'BG_P7_NEAST_RPHLRD_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220963 | CONASTON | 220961 | NWEST326 | 1 | 230/230 | 232/232 | 1381 | 102.8965 | 104.93 | Single | 'BG_P1_2310_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220963 | CONASTON | 220961 | NWEST326 | 1 | 230/230 | 232/232 | 1381 | 102.8313 | 104.86 | Line_FB | 'BG_P4_5_NW2310_230-5_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220963 | CONASTON | 220961 | NWEST326 | 1 | 230/230 | 232/232 | 1381 | 101.4555 | 103.52 | Line_FB | 'BG_P4_5_NW2371_2310_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220963 | CONASTON | 220961 | NWEST326 | 1 | 230/230 | 232/232 | 1381 | 101.4555 | 103.52 | Line_FB | 'BG_P4_5_NW230-3_2310_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208396 | FARO | 208395 | FARO FF | 1 | 69/69 | 229/229 | 270 | 113.7778 | 116.31 | Tower | 'PL_05_P71_000906_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208396 | FARO | 208395 | FARO FF | 1 | 69/69 | 229/229 | 270 | 110.8889 | 112.01 | Line_FB | 'PJM_500_BG_P4_5_CNSTN_B_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208396 | FARO | 208395 | FARO FF | 1 | 69/69 | 229/229 | 270 | 110.8519 | 111.85 | Line_FB | 'PECO_P4_PEACH235_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208396 | FARO | 208395 | FARO FF | 1 | 69/69 | 229/229 | 270 | 110.8519 | 111.85 | Line_FB | 'PJM_500_BG_P4_5_CNSTN_C_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208396 | FARO | 208395 | FARO FF | 1 | 69/69 | 229/229 | 270 | 110.8519 | 111.85 | Single | 'PECO_P1-2_5012_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208396 | FARO | 208395 | FARO FF | 1 | 69/69 | 229/229 | 270 | 105.5556 | 110.6 | Tower | 'BG_P7_GRCTN_RAPHEL_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208396 | FARO | 208395 | FARO FF | 1 | 69/69 | 229/229 | 270 | 106.7778 | 107.91 | Line_FB | 'PECO_P4_PEACH245_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208396 | FARO | 208395 | FARO FF | 1 | 69/69 | 229/229 | 270 | 101.7778 | 106.21 | Tower | 'BG_P7_NEAST_RPHLRD_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208396 | FARO | 208395 | FARO FF | 1 | 69/69 | 229/229 | 270 | 102.1481 | 105.26 | Line_FB | 'BG_P4_5_GRCTN_2T_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208396 | FARO | 208395 | FARO FF | 1 | 69/69 | 229/229 | 270 | 99.0741 | 104.58 | Single | 'PJM_500_BG_P1_5011_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208396 | FARO | 208395 | FARO FF | 1 | 69/69 | 229/229 | 270 | 98.8148 | 101.66 | Single | 'PL_04_P12_000257_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208396 | FARO | 208395 | FARO FF | 1 | 69/69 | 229/229 | 270 | 98.8148 | 101.66 | Bus | 'PL_05_P22_000674_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 221051 | CHESTN8A | 221049 | FRED.RD8 | 1 | 115/115 | 232/232 | 215 | 112 | 115.94 | Tower | 'BG_P7_GRCTN_RAPHEL_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 221051 | CHESTN8A | 221049 | FRED.RD8 | 1 | 115/115 | 232/232 | 215 | 102.9767 | 106.42 | Tower | 'BG_P7_NEAST_RPHLRD_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 2 | 500/230 | 225/232 | 2168 | 109.917 | 115.28 | Line_FB | 'PEPCO_P4_PP40_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 2 | 500/230 | 225/232 | 2168 | 109.7417 | 115.05 | Line_FB | 'PJM_500_BG_P4_5_CNSTN_J_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 2 | 500/230 | 225/232 | 2168 | 109.7417 | 115.05 | Single | 'PJM_500_BG_P1_5011_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 2 | 500/230 | 225/232 | 2168 | 108.7269 | 112.04 | Line_FB | 'PJM_500_BG_P4_5_CNSTN_15_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 2 | 500/230 | 225/232 | 2168 | 99.1974 | 101.97 | Single | 'BG_P1_CNSTN_500-2_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 2 | 500/230 | 225/232 | 2168 | 99.1974 | 101.97 | Bus | 'PJM_500_BG_P2_CNSTN_230-N_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 1 | 500/230 | 225/232 | 2168 | 109.6817 | 115.04 | Line_FB | 'PEPCO_P4_PP40_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 1 | 500/230 | 225/232 | 2168 | 109.5111 | 114.81 | Line_FB | 'PJM_500_BG_P4_5_CNSTN_J_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 1 | 500/230 | 225/232 | 2168 | 109.5065 | 114.81 | Single | 'PJM_500_BG_P1_5011_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 1 | 500/230 | 225/232 | 2168 | 99.0867 | 101.85 | Single | 'BG_P1_CNSTN_500-4_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 1 | 500/230 | 225/232 | 2168 | 99.0867 | 101.85 | Bus | 'PJM_500_BG_P2_CNSTN_230-S_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220964 | GRACETON | 220999 | BAGLEY2 | 13 | 230/230 | 232/232 | 1795 | 113.6936 | 114.75 | Line_FB | 'BG_P4_5_GRCTN_3T_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220964 | GRACETON | 220999 | BAGLEY2 | 13 | 230/230 | 232/232 | 1795 | 101.7326 | 102.5 | Single | 'BG_P1_2305_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208031 | MLWD TR2 | 208020 | MANO TR3 | 1 | 230/230 | 229/229 | 903 | 102.9679 | 114.21 | Line_FB | 'PJM_500_BG_P4_5_CNSTN_B_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208031 | MLWD TR2 | 208020 | MANO TR3 | 1 | 230/230 | 229/229 | 903 | 102.2702 | 113.1 | Line_FB | 'PJM_500_BG_P4_5_CNSTN_C_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208031 | MLWD TR2 | 208020 | MANO TR3 | 1 | 230/230 | 229/229 | 903 | 102.2702 | 113.1 | Line_FB | 'PECO_P4_PEACH235_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208031 | MLWD TR2 | 208020 | MANO TR3 | 1 | 230/230 | 229/229 | 903 | 102.2702 | 113.1 | Single | 'PECO_P1-2_5012_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208031 | MLWD TR2 | 208020 | MANO TR3 | 1 | 230/230 | 229/229 | 903 | 95.8915 | 103.89 | Line_FB | 'PECO_P4_PEACH245_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 204529 | 27GERMANTN | 1 | 138/115 | 227/227 | 347 | 110.2305 | 113.73 | Single | 'BASE CASE' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208393 | FARO DC TIE | 208395 | FARO FF | 1 | 115/69 | 229/229 | 96.9 | 111.3519 | 112.71 | Single | 'BASE CASE' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200504 | 26CARLISLE | 200520 | 26ROXBURY | 1 | 115/115 | 226/226 | 190 | 102.2105 | 112.68 | Single | 'PN_P1-2_PN-115-094_A_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200504 | 26CARLISLE | 200520 | 26ROXBURY | 1 | 115/115 | 226/226 | 190 | 102.1053 | 111.85 | Line_FB | 'PN_P2-3_PN-115-58B_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200504 | 26CARLISLE | 200520 | 26ROXBURY | 1 | 115/115 | 226/226 | 190 | 102.7368 | 111.81 | Single | 'PN_P1-3_PN-115-040_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200504 | 26CARLISLE | 200520 | 26ROXBURY | 1 | 115/115 | 226/226 | 190 | 102.7368 | 111.81 | Bus | 'PN_P2-2_PN-115-030_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200504 | 26CARLISLE | 200520 | 26ROXBURY | 1 | 115/115 | 226/226 | 190 | 101.8947 | 111.8 | Single | 'PN_P1-2_PN-115-094_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200504 | 26CARLISLE | 200520 | 26ROXBURY | 1 | 115/115 | 226/226 | 190 | 93 | 108.4 | Line_FB | 'PN_P2-3_PN-115-0331-B_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200504 | 26CARLISLE | 200520 | 26ROXBURY | 1 | 115/115 | 226/226 | 190 | 99.5789 | 107.52 | Line_FB | 'PN_P2-3_PN-230-0014-12_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200504 | 26CARLISLE | 200520 | 26ROXBURY | 1 | 115/115 | 226/226 | 190 | 99.5789 | 107.11 | Line_FB | 'PN_P2-3_PN-230-0014-11_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200504 | 26CARLISLE | 200520 | 26ROXBURY | 1 | 115/115 | 226/226 | 190 | 99.5789 | 107.11 | Single | 'PN_P1-3_PN-230-020A_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200504 | 26CARLISLE | 200520 | 26ROXBURY | 1 | 115/115 | 226/226 | 190 | 99.5263 | 107.08 | Bus | 'PN_P2-2_PN-115-031_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200504 | 26CARLISLE | 200520 | 26ROXBURY | 1 | 115/115 | 226/226 | 190 | 95.8947 | 104.46 | Line_FB | 'PN_P2-3_PN-115-40A_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200504 | 26CARLISLE | 200520 | 26ROXBURY | 1 | 115/115 | 226/226 | 190 | 95.8947 | 104.46 | Single | 'PN_P1-2_PN-115-097_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 221054 | CHESTN7A | 221050 | FRED.RD7 | 1 | 115/115 | 232/232 | 215 | 107.7674 | 111.66 | Tower | 'BG_P7_GRCTN_RAPHEL_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 221054 | CHESTN7A | 221050 | FRED.RD7 | 1 | 115/115 | 232/232 | 215 | 98.7907 | 102.12 | Tower | 'BG_P7_NEAST_RPHLRD_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220999 | BAGLEY2 | 220980 | RAPHAEL | 13 | 230/230 | 232/232 | 1795 | 109.2758 | 111.51 | Line_FB | 'BG_P4_5_GRCTN_3T_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208131 | WHEM | 208133 | WHEM TR2 | 1 | 230/230 | 229/229 | 691 | 102.0695 | 110.83 | Line_FB | 'PJM_500_BG_P4_5_CNSTN_B_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208131 | WHEM | 208133 | WHEM TR2 | 1 | 230/230 | 229/229 | 691 | 101.3603 | 109.69 | Line_FB | 'PJM_500_BG_P4_5_CNSTN_C_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208131 | WHEM | 208133 | WHEM TR2 | 1 | 230/230 | 229/229 | 691 | 101.3603 | 109.69 | Line_FB | 'PECO_P4_PEACH235_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208131 | WHEM | 208133 | WHEM TR2 | 1 | 230/230 | 229/229 | 691 | 101.3603 | 109.69 | Single | 'PECO_P1-2_5012_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208131 | WHEM | 208133 | WHEM TR2 | 1 | 230/230 | 229/229 | 691 | 96.5847 | 102.41 | Line_FB | 'PECO_P4_PEACH245_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 221094 | GRACE.-1 | 221092 | FIVE.FOR | 1 | 115/115 | 232/232 | 498 | 107.51 | 108.42 | Tower | 'BG_P7_GRCTN_RAPHEL_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200102 | AA1-076 MAIN | 200101 | VINCO | 1 | 500/500 | 225/225 | 999 | 102.9429 | 108.24 | Line_FB | 'PECO_P4_PEACH245_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200102 | AA1-076 MAIN | 200101 | VINCO | 1 | 500/500 | 225/225 | 999 | N/A | 107.63 | Line_FB | 'PJM_500_BG_P4_5_CNSTN_C_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200102 | AA1-076 MAIN | 200101 | VINCO | 1 | 500/500 | 225/225 | 999 | N/A | 107.63 | Line_FB | 'PECO_P4_PEACH235_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200102 | AA1-076 MAIN | 200101 | VINCO | 1 | 500/500 | 225/225 | 999 | N/A | 107.63 | Single | 'PECO_P1-2_5012_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200102 | AA1-076 MAIN | 200101 | VINCO | 1 | 500/500 | 225/225 | 999 | N/A | 107.56 | Line_FB | 'PJM_500_BG_P4_5_CNSTN_B_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200102 | AA1-076 MAIN | 200101 | VINCO | 1 | 500/500 | 225/225 | 999 | N/A | 101.52 | Single | 'PN_P1-1_DRT-500-006-DRT_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200102 | AA1-076 MAIN | 200101 | VINCO | 1 | 500/500 | 225/225 | 999 | N/A | 101.52 | Single | 'PN_P1-1_PN-500-002_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200102 | AA1-076 MAIN | 200101 | VINCO | 1 | 500/500 | 225/225 | 999 | N/A | 101.41 | Line_FB | 'PN_P2-3_PN-500-001E-DRT_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200102 | AA1-076 MAIN | 200101 | VINCO | 1 | 500/500 | 225/225 | 999 | N/A | 101.41 | Single | 'PN_P1-1_PN-500-001_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200102 | AA1-076 MAIN | 200101 | VINCO | 1 | 500/500 | 225/225 | 999 | N/A | 101.41 | Single | 'PN_P1-1_DRT-500-005-DRT_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200009 | JUNI | 208004 | JUNI | 2 | 500/230 | 225/229 | 1040 | 108.4519 | 107.87 | Line_FB | 'PL_10_P42_000140_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200023 | WESC | 211321 | WESC | 3 | 500/138 | 225/229 | 537 | 102.7188 | 106.46 | Line_FB | 'PL_20_P24_001468_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208393 | FARO DC TIE | 208395 | FARO FF | 2 | 115/69 | 229/229 | 102.9 | 104.8591 | 106.14 | Single | 'BASE CASE' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208133 | WHEM TR2 | 208021 | MANO TR4 | 2 | 230/230 | 229/229 | 593 | 96.6442 | 105.55 | Line_FB | 'PJM_500_BG_P4_5_CNSTN_B_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208133 | WHEM TR2 | 208021 | MANO TR4 | 2 | 230/230 | 229/229 | 593 | 95.8347 | 104.33 | Line_FB | 'PJM_500_BG_P4_5_CNSTN_C_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208133 | WHEM TR2 | 208021 | MANO TR4 | 2 | 230/230 | 229/229 | 593 | 95.8347 | 104.33 | Single | 'PECO_P1-2_5012_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208133 | WHEM TR2 | 208021 | MANO TR4 | 2 | 230/230 | 229/229 | 593 | 95.8347 | 104.32 | Line_FB | 'PECO_P4_PEACH235_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200099 | LAUS | 208045 | LAUS | 3 | 500/230 | 225/229 | 1200 | 103.5167 | 105.29 | Line_FB | 'PJM_500_BG_P4_5_CNSTN_B_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200099 | LAUS | 208045 | LAUS | 3 | 500/230 | 225/229 | 1200 | 103.2083 | 104.82 | Line_FB | 'PJM_500_BG_P4_5_CNSTN_C_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200099 | LAUS | 208045 | LAUS | 3 | 500/230 | 225/229 | 1200 | 103.2083 | 104.82 | Single | 'PECO_P1-2_5012_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200099 | LAUS | 208045 | LAUS | 3 | 500/230 | 225/229 | 1200 | 103.2 | 104.81 | Line_FB | 'PECO_P4_PEACH235_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200026 | HUNTERTN | 200004 | CNASTONE | 1 | 500/500 | 225/225 | 3024 | 99.7321 | 103.82 | Line_FB | 'PECO_P4_PEACH235_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200026 | HUNTERTN | 200004 | CNASTONE | 1 | 500/500 | 225/225 | 3024 | 99.7321 | 103.82 | Line_FB | 'PJM_500_BG_P4_5_CNSTN_C_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200026 | HUNTERTN | 200004 | CNASTONE | 1 | 500/500 | 225/225 | 3024 | 99.7354 | 103.82 | Single | 'PECO_P1-2_5012_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200026 | HUNTERTN | 200004 | CNASTONE | 1 | 500/500 | 225/225 | 3024 | 98.8128 | 102.37 | Line_FB | 'PJM_500_BG_P4_5_CNSTN_B_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200026 | HUNTERTN | 200004 | CNASTONE | 1 | 500/500 | 225/225 | 3024 | 98.9021 | 101.07 | Line_FB | 'PECO_P4_PEACH245_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 221100 | GLENARM1 | 221088 | WINDYED2 | 1 | 115/115 | 232/232 | 353 | 101.3031 | 103.67 | Tower | 'BG_P7_GRCTN_RAPHEL_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208142 | WIGR-115 | 204520 | 27ALLEN | 1 | 115/115 | 229/227 | 351.4 | 95.7598 | 103.54 | Line_FB | 'PJM_500_BG_P4_5_CNSTN_C_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208142 | WIGR-115 | 204520 | 27ALLEN | 1 | 115/115 | 229/227 | 351.4 | 95.7314 | 103.54 | Line_FB | 'PECO_P4_PEACH235_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208142 | WIGR-115 | 204520 | 27ALLEN | 1 | 115/115 | 229/227 | 351.4 | 95.7598 | 103.54 | Single | 'PECO_P1-2_5012_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208142 | WIGR-115 | 204520 | 27ALLEN | 1 | 115/115 | 229/227 | 351.4 | 95.5037 | 103.21 | Line_FB | 'PJM_500_BG_P4_5_CNSTN_B_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220964 | GRACETON | 221000 | BAGLEY | 5 | 230/230 | 232/232 | 1795 | 101.727 | 102.5 | Single | 'BG_P1_2313_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220964 | GRACETON | 221094 | GRACE.-1 | 1 | 230/115 | 232/232 | 510 | 105.1569 | 102.38 | Tower | 'BG_P7_GRCTN_RAPHEL_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220965 | NEAST339 | 220977 | RIV2339 | 1 | 230/230 | 232/232 | 991 | 103.7941 | 102.37 | Line_FB | 'PEPCO_P4_PP40_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220965 | NEAST339 | 220977 | RIV2339 | 1 | 230/230 | 232/232 | 991 | 103.7437 | 102.3 | Line_FB | 'PJM_500_BG_P4_5_CNSTN_J_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220965 | NEAST339 | 220977 | RIV2339 | 1 | 230/230 | 232/232 | 991 | 103.7437 | 102.3 | Single | 'PJM_500_BG_P1_5011_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220979 | NEAST317 | 220966 | RIV2317 | 1 | 230/230 | 232/232 | 940 | 103.3723 | 102.34 | Line_FB | 'PEPCO_P4_PP40_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220979 | NEAST317 | 220966 | RIV2317 | 1 | 230/230 | 232/232 | 940 | 103.3298 | 102.27 | Line_FB | 'PJM_500_BG_P4_5_CNSTN_J_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220979 | NEAST317 | 220966 | RIV2317 | 1 | 230/230 | 232/232 | 940 | 103.3298 | 102.27 | Single | 'PJM_500_BG_P1_5011_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208393 | FARO DC TIE | 208394 | PPL-BGE TIE | 1 | 115/115 | 229/229 | 302 | 101.457 | 102.19 | Tower | 'PL_05_P71_000906_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 221089 | WINDYED1 | 221090 | GLENARM2 | 1 | 115/115 | 232/232 | 176 | 93.9205 | 101.56 | Single | 'BASE CASE' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208395 | FARO FF | 208396 | FARO | 1 | 69/69 | 229/229 | 223 | 96.8161 | 101.1 | Single | 'BASE CASE' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 223960 | BRG 1T 230 | 1 | 500/230 | 225/233 | 1498 | 100.5808 | 100.98 | Line_FB | 'PEPCO_P4_PP41_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204550 | 27ORRTANNA | 204544 | 27LINCOLN | 1 | 115/115 | 227/227 | 189 | 163.8624 | 162.41 | Single | 'ME_P2-1_ME-115-0003_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204539 | 27HUNTRSTN | 205912 | AD1-020 TAP | 1 | 115/115 | 227/227 | 334 | 134.7305 | 133.52 | Single | 'AP_P2-1_WP-138-AD2062-A_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204539 | 27HUNTRSTN | 205912 | AD1-020 TAP | 1 | 115/115 | 227/227 | 334 | 134.6707 | 133.23 | Single | 'PN_P2-1_PN-115-117_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204539 | 27HUNTRSTN | 205912 | AD1-020 TAP | 1 | 115/115 | 227/227 | 334 | 130.8683 | 129.5 | Single | 'AP_P2-1_WP-138-0213-A_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204539 | 27HUNTRSTN | 205912 | AD1-020 TAP | 1 | 115/115 | 227/227 | 334 | 131.2874 | 129.23 | Single | 'PL_05_P21_000395_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 235463 | 01TANEY | 1 | 138/138 | 227/201 | 317 | 131.735 | 130.7 | Single | 'AP_P2-1_WP-138-AD2062-A_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 235463 | 01TANEY | 1 | 138/138 | 227/201 | 317 | 131.6719 | 130.63 | Single | 'PN_P2-1_PN-115-117_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 235463 | 01TANEY | 1 | 138/138 | 227/201 | 317 | 127.1609 | 126.52 | Single | 'AP_P2-1_WP-138-0213-A_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 235463 | 01TANEY | 1 | 138/138 | 227/201 | 317 | 127.6341 | 126.24 | Single | 'PL_05_P21_000395_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200004 | CNASTONE | 1 | 500/500 | 225/225 | 4030 | 153.3921 | 148 | Single | 'PECO_P2-1_NOTT85_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200004 | CNASTONE | 1 | 500/500 | 225/225 | 4030 | 153.0199 | 147.8 | Single | 'PECO_P2-1_COOP220-08_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200004 | CNASTONE | 1 | 500/500 | 225/225 | 4030 | 152.7965 | 147.6 | Single | 'PECO_P2-1_COOP125_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200004 | CNASTONE | 1 | 500/500 | 225/225 | 4030 | 152.6377 | 147.45 | Single | 'BG_P21:TO:214084 COOPER 230 220964 GRACETON 230 1 _SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200003 | BRIGHTON | 1 | 500/500 | 225/225 | 3183 | 139.5256 | 142.27 | Single | 'BG_P21:FROM:220962 NWEST311 230 220963 CONASTON 230 1 _SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200003 | BRIGHTON | 1 | 500/500 | 225/225 | 3183 | 139.5256 | 142.27 | Single | 'BG_P21:TO:220962 NWEST311 230 220963 CONASTON 230 1 _SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200003 | BRIGHTON | 1 | 500/500 | 225/225 | 3183 | 139.4659 | 142.21 | Single | 'BG_P21:TO:220961 NWEST326 230 220963 CONASTON 230 1 _SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200003 | BRIGHTON | 1 | 500/500 | 225/225 | 3183 | 139.4659 | 142.21 | Single | 'BG_P21:FROM:220961 NWEST326 230 220963 CONASTON 230 1 _SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 205912 | AD1-020 TAP | 204544 | 27LINCOLN | 1 | 115/115 | 227/227 | 334 | 135.1497 | 135.01 | Single | 'AP_P2-1_WP-138-AD2062-A_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 205912 | AD1-020 TAP | 204544 | 27LINCOLN | 1 | 115/115 | 227/227 | 334 | 135.0898 | 134.69 | Single | 'PN_P2-1_PN-115-117_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 205912 | AD1-020 TAP | 204544 | 27LINCOLN | 1 | 115/115 | 227/227 | 334 | 131.2874 | 130.97 | Single | 'AP_P2-1_WP-138-0213-A_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 205912 | AD1-020 TAP | 204544 | 27LINCOLN | 1 | 115/115 | 227/227 | 334 | 131.7066 | 130.69 | Single | 'PL_05_P21_000395_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204528 | 27GARDNERS | 200504 | 26CARLISLE | 1 | 115/115 | 227/226 | 190 | 125.6316 | 131.16 | Single | 'PN_P2-1_PN-115-076_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204528 | 27GARDNERS | 200504 | 26CARLISLE | 1 | 115/115 | 227/226 | 190 | 121.8947 | 128.46 | Single | 'PN_P2-1_PN-115-077_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204528 | 27GARDNERS | 200504 | 26CARLISLE | 1 | 115/115 | 227/226 | 190 | 95.6316 | 101.87 | Single | 'ME_P2-1_ME-115-0002_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204528 | 27GARDNERS | 200504 | 26CARLISLE | 1 | 115/115 | 227/226 | 190 | 94.6316 | 101.09 | Single | 'ME_P2-1_ME-115-0001_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 203981 | AD2-062_POI | 235188 | 01GREENE | 1 | 138/138 | 226/201 | 317 | 115.7098 | 113.4 | Single | 'ME_P2-1_ME-115-0002_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 203981 | AD2-062_POI | 235188 | 01GREENE | 1 | 138/138 | 226/201 | 317 | 115.0789 | 112.93 | Single | 'ME_P2-1_ME-115-0001_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 203981 | AD2-062_POI | 235188 | 01GREENE | 1 | 138/138 | 226/201 | 317 | 114.4795 | 112.48 | Single | 'AP_P2-1_PE-138-083_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 203981 | AD2-062_POI | 235188 | 01GREENE | 1 | 138/138 | 226/201 | 317 | 113.3438 | 111.96 | Single | 'AP_P2-1_PE-138-028_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200532 | 26ROXBURY | 203981 | AD2-062_POI | 1 | 138/138 | 226/226 | 317 | 114.9842 | 112.12 | Single | 'ME_P2-1_ME-115-0002_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200532 | 26ROXBURY | 203981 | AD2-062_POI | 1 | 138/138 | 226/226 | 317 | 114.3533 | 111.66 | Single | 'ME_P2-1_ME-115-0001_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200532 | 26ROXBURY | 203981 | AD2-062_POI | 1 | 138/138 | 226/226 | 317 | 113.7539 | 111.2 | Single | 'AP_P2-1_PE-138-083_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200532 | 26ROXBURY | 203981 | AD2-062_POI | 1 | 138/138 | 226/226 | 317 | 112.6183 | 110.66 | Single | 'AP_P2-1_PE-138-028_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 204538 | 27STRABAN | 1 | 115/115 | 227/227 | 371 | 123.8814 | 125.97 | Single | 'AP_P2-1_WP-138-AD2062-A_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 204538 | 27STRABAN | 1 | 115/115 | 227/227 | 371 | 123.8005 | 125.66 | Single | 'PN_P2-1_PN-115-117_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 204538 | 27STRABAN | 1 | 115/115 | 227/227 | 371 | 119.9461 | 121.88 | Single | 'AP_P2-1_WP-138-0213-A_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 204538 | 27STRABAN | 1 | 115/115 | 227/227 | 371 | 120.3504 | 121.61 | Single | 'PL_05_P21_000395_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204539 | 27HUNTRSTN | 204550 | 27ORRTANNA | 1 | 115/115 | 227/227 | 264 | 127.0076 | 125.9 | Single | 'ME_P2-1_ME-115-0003_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204538 | 27STRABAN | 204529 | 27GERMANTN | 1 | 115/115 | 227/227 | 371 | 118.0863 | 121.52 | Single | 'AP_P2-1_WP-138-AD2062-A_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204538 | 27STRABAN | 204529 | 27GERMANTN | 1 | 115/115 | 227/227 | 371 | 118.0323 | 121.21 | Single | 'PN_P2-1_PN-115-117_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204538 | 27STRABAN | 204529 | 27GERMANTN | 1 | 115/115 | 227/227 | 371 | 114.1509 | 117.44 | Single | 'AP_P2-1_WP-138-0213-A_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204538 | 27STRABAN | 204529 | 27GERMANTN | 1 | 115/115 | 227/227 | 371 | 114.5822 | 117.16 | Single | 'PL_05_P21_000395_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200512 | 26LEWISTWN | 200519 | 26REED TAP | 1 | 115/115 | 226/226 | 271 | 121.6605 | 120.62 | Single | 'PN_P2-1_PN-115-079T_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200512 | 26LEWISTWN | 200519 | 26REED TAP | 1 | 115/115 | 226/226 | 271 | 114.2435 | 112.34 | Single | 'PN_P2-1_PN-115-078_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200512 | 26LEWISTWN | 200519 | 26REED TAP | 1 | 115/115 | 226/226 | 271 | 111.2177 | 108.28 | Single | 'PN_P2-1_PN-46-041_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200512 | 26LEWISTWN | 200519 | 26REED TAP | 1 | 115/115 | 226/226 | 271 | 109.4465 | 107.01 | Single | 'PN_P2-1_PN-46-045_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 221090 | GLENARM2 | 221089 | WINDYED1 | 1 | 115/115 | 232/232 | 222 | 112.6577 | 119.96 | Single | 'BG_P21:FROM:221092 FIVE.FOR 115 221096 ROCKRGE1 115 1 _SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 221090 | GLENARM2 | 221089 | WINDYED1 | 1 | 115/115 | 232/232 | 222 | 112.6577 | 119.95 | Single | 'BG_P21:TO:221092 FIVE.FOR 115 221096 ROCKRGE1 115 1 _SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 221090 | GLENARM2 | 221089 | WINDYED1 | 1 | 115/115 | 232/232 | 222 | 102.973 | 110.71 | Single | 'BG_P21:TO:221088 WINDYED2 115 221100 GLENARM1 115 1 _SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 221090 | GLENARM2 | 221089 | WINDYED1 | 1 | 115/115 | 232/232 | 222 | 102.973 | 110.7 | Single | 'BG_P21:FROM:221088 WINDYED2 115 221100 GLENARM1 115 1 _SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220980 | RAPHAEL | 220965 | NEAST339 | 1 | 230/230 | 232/232 | 1340 | 120.1045 | 119.46 | Single | 'BG_P21:FROM:220979 NEAST317 230 220980 RAPHAEL 230 1 _SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220980 | RAPHAEL | 220965 | NEAST339 | 1 | 230/230 | 232/232 | 1340 | 120.1045 | 119.46 | Single | 'BG_P21:TO:220979 NEAST317 230 220980 RAPHAEL 230 1 _SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220980 | RAPHAEL | 220979 | NEAST317 | 1 | 230/230 | 232/232 | 1340 | 119.1791 | 118.58 | Single | 'BG_P21:TO:220965 NEAST339 230 220980 RAPHAEL 230 1 _SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220980 | RAPHAEL | 220979 | NEAST317 | 1 | 230/230 | 232/232 | 1340 | 119.1791 | 118.58 | Single | 'BG_P21:FROM:220965 NEAST339 230 220980 RAPHAEL 230 1 _SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230/230 | 230/230 | 617 | 109.3355 | 111.09 | Single | 'BG_P21:FROM:208071 PPL-BGE TIE 230 220964 GRACETON 230 1 _SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230/230 | 230/230 | 617 | 109.3355 | 111.09 | Single | 'PL_04_P21_000390_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230/230 | 230/230 | 617 | 106.8395 | 108.54 | Single | 'PL_04_P21_000389_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230/230 | 230/230 | 617 | 103.3549 | 105.12 | Single | 'BG_P21:TO:220963 CONASTON 230 220964 GRACETON 230 23_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230/230 | 230/230 | 617 | 111.3452 | 111.09 | Single | 'BG_P21:FROM:208071 PPL-BGE TIE 230 220964 GRACETON 230 1 _SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230/230 | 230/230 | 617 | 111.3452 | 111.09 | Single | 'PL_04_P21_000390_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230/230 | 230/230 | 617 | 108.8493 | 108.54 | Single | 'PL_04_P21_000389_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230/230 | 230/230 | 617 | 105.3647 | 105.13 | Single | 'BG_P21:FROM:220963 CONASTON 230 220964 GRACETON 230 23_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230/230 | 229/232 | 889 | 118.4927 | 117.21 | Single | 'BG_P21:TO:208048 PPL-BGE TIE 230 220963 CONASTON 230 1 _SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230/230 | 229/232 | 889 | 118.4927 | 117.2 | Single | 'BG_P21:FROM:208048 PPL-BGE TIE 230 220963 CONASTON 230 1 _SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230/230 | 229/232 | 889 | 118.4927 | 117.2 | Single | 'PL_05_P21_000394_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230/230 | 229/232 | 889 | 107.4353 | 105.49 | Single | 'PECO_P2-1_NOTT85_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200519 | 26REED TAP | 200522 | 26SHADE GP | 1 | 115/115 | 226/226 | 271 | 113.9483 | 115.76 | Single | 'PN_P2-1_PN-115-079T_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200519 | 26REED TAP | 200522 | 26SHADE GP | 1 | 115/115 | 226/226 | 271 | 106.4945 | 107.53 | Single | 'PN_P2-1_PN-115-078_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200519 | 26REED TAP | 200522 | 26SHADE GP | 1 | 115/115 | 226/226 | 271 | 103.5055 | 103.5 | Single | 'PN_P2-1_PN-46-041_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200519 | 26REED TAP | 200522 | 26SHADE GP | 1 | 115/115 | 226/226 | 271 | 101.6974 | 102.24 | Single | 'PN_P2-1_PN-46-045_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230/230 | 230/230 | 639 | 103.2081 | 105.05 | Single | 'BG_P21:FROM:208071 PPL-BGE TIE 230 220964 GRACETON 230 1 _SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230/230 | 230/230 | 639 | 103.2081 | 105.04 | Single | 'PL_04_P21_000390_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230/230 | 230/230 | 639 | 100.8138 | 102.58 | Single | 'PL_04_P21_000389_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208395 | FARO FF | 208393 | FARO DC TIE | 2 | 69/115 | 229/229 | 120 | 114.0833 | 114.57 | Single | 'BG_P21:TO:221092 FIVE.FOR 115 221094 GRACE.-1 115 1 _SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208395 | FARO FF | 208393 | FARO DC TIE | 2 | 69/115 | 229/229 | 120 | 114.0833 | 114.56 | Single | 'BG_P21:FROM:221092 FIVE.FOR 115 221094 GRACE.-1 115 1 _SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208395 | FARO FF | 208393 | FARO DC TIE | 2 | 69/115 | 229/229 | 120 | 115.0833 | 113.39 | Single | 'PL_04_P21_000390_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208395 | FARO FF | 208393 | FARO DC TIE | 2 | 69/115 | 229/229 | 120 | 115.0833 | 113.39 | Single | 'BG_P21:FROM:208071 PPL-BGE TIE 230 220964 GRACETON 230 1 _SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208395 | FARO FF | 208393 | FARO DC TIE | 2 | 69/115 | 229/229 | 120 | 109.6667 | 108.66 | Single | 'PL_04_P21_000389_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208395 | FARO FF | 208393 | FARO DC TIE | 1 | 69/115 | 229/229 | 120 | 114.0833 | 114.57 | Single | 'BG_P21:TO:221092 FIVE.FOR 115 221094 GRACE.-1 115 1 _SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208395 | FARO FF | 208393 | FARO DC TIE | 1 | 69/115 | 229/229 | 120 | 114.0833 | 114.56 | Single | 'BG_P21:FROM:221092 FIVE.FOR 115 221094 GRACE.-1 115 1 _SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208395 | FARO FF | 208393 | FARO DC TIE | 1 | 69/115 | 229/229 | 120 | 115.0833 | 113.4 | Single | 'PL_04_P21_000390_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208395 | FARO FF | 208393 | FARO DC TIE | 1 | 69/115 | 229/229 | 120 | 115.0833 | 113.39 | Single | 'BG_P21:FROM:208071 PPL-BGE TIE 230 220964 GRACETON 230 1 _SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208394 | PPL-BGE TIE | 221092 | FIVE.FOR | 1 | 115/115 | 229/232 | 247 | 108.4615 | 113.74 | Single | 'BG_P21:TO:221092 FIVE.FOR 115 221094 GRACE.-1 115 1 _SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208394 | PPL-BGE TIE | 221092 | FIVE.FOR | 1 | 115/115 | 229/232 | 247 | 108.4615 | 113.73 | Single | 'BG_P21:FROM:221092 FIVE.FOR 115 221094 GRACE.-1 115 1 _SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208394 | PPL-BGE TIE | 221092 | FIVE.FOR | 1 | 115/115 | 229/232 | 247 | 109.3927 | 112.83 | Single | 'PL_04_P21_000390_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208394 | PPL-BGE TIE | 221092 | FIVE.FOR | 1 | 115/115 | 229/232 | 247 | 109.3927 | 112.82 | Single | 'BG_P21:FROM:208071 PPL-BGE TIE 230 220964 GRACETON 230 1 _SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208394 | PPL-BGE TIE | 221092 | FIVE.FOR | 1 | 115/115 | 229/232 | 247 | 104.17 | 107.86 | Single | 'PL_04_P21_000389_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 221092 | FIVE.FOR | 221096 | ROCKRGE1 | 1 | 115/115 | 232/232 | 293 | 105.6997 | 110.97 | Single | 'BG_P21:FROM:221092 FIVE.FOR 115 221095 ROCKRGE2 115 1 _SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 221092 | FIVE.FOR | 221096 | ROCKRGE1 | 1 | 115/115 | 232/232 | 293 | 105.6997 | 110.97 | Single | 'BG_P21:TO:221092 FIVE.FOR 115 221095 ROCKRGE2 115 1 _SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 221092 | FIVE.FOR | 221096 | ROCKRGE1 | 1 | 115/115 | 232/232 | 293 | 99.727 | 105.22 | Single | 'BG_P21:FROM:221089 WINDYED1 115 221090 GLENARM2 115 1 _SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 221092 | FIVE.FOR | 221096 | ROCKRGE1 | 1 | 115/115 | 232/232 | 293 | 99.727 | 105.22 | Single | 'BG_P21:TO:221089 WINDYED1 115 221090 GLENARM2 115 1 _SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230/230 | 230/232 | 639 | 98.9515 | 101.33 | Single | 'BG_P21:FROM:208071 PPL-BGE TIE 230 220964 GRACETON 230 1 _SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230/230 | 230/232 | 639 | 98.9515 | 101.32 | Single | 'PL_04_P21_000390_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200504 | 26CARLISLE | 200520 | 26ROXBURY | 1 | 115/115 | 226/226 | 190 | 99.5263 | 107.09 | Single | 'PN_P2-1_PN-115-076_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200504 | 26CARLISLE | 200520 | 26ROXBURY | 1 | 115/115 | 226/226 | 190 | 95.8421 | 104.45 | Single | 'PN_P2-1_PN-115-077_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208396 | FARO | 208395 | FARO FF | 1 | 69/69 | 229/229 | 270 | 101.4074 | 105.82 | Single | 'BG_P21:FROM:221092 FIVE.FOR 115 221094 GRACE.-1 115 1 _SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208396 | FARO | 208395 | FARO FF | 1 | 69/69 | 229/229 | 270 | 101.4074 | 105.82 | Single | 'BG_P21:TO:221092 FIVE.FOR 115 221094 GRACE.-1 115 1 _SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208396 | FARO | 208395 | FARO FF | 1 | 69/69 | 229/229 | 270 | 102.2963 | 105.06 | Single | 'PL_04_P21_000390_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208396 | FARO | 208395 | FARO FF | 1 | 69/69 | 229/229 | 270 | 102.2963 | 105.05 | Single | 'BG_P21:FROM:208071 PPL-BGE TIE 230 220964 GRACETON 230 1 _SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220963 | CONASTON | 220962 | NWEST311 | 1 | 230/230 | 232/232 | 1381 | 102.9689 | 105.01 | Single | 'BG_P21:TO:220961 NWEST326 230 220963 CONASTON 230 1 _SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220963 | CONASTON | 220962 | NWEST311 | 1 | 230/230 | 232/232 | 1381 | 102.9689 | 105.01 | Single | 'BG_P21:FROM:220961 NWEST326 230 220963 CONASTON 230 1 _SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220963 | CONASTON | 220961 | NWEST326 | 1 | 230/230 | 232/232 | 1381 | 102.8965 | 104.94 | Single | 'BG_P21:TO:220962 NWEST311 230 220963 CONASTON 230 1 _SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220963 | CONASTON | 220961 | NWEST326 | 1 | 230/230 | 232/232 | 1381 | 102.8965 | 104.93 | Single | 'BG_P21:FROM:220962 NWEST311 230 220963 CONASTON 230 1 _SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200504 | 26CARLISLE | 204528 | 27GARDNERS | 1 | 115/115 | 226/227 | 150 | 96.1333 | 102.99 | Single | 'BASE CASE' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220964 | GRACETON | 221000 | BAGLEY | 5 | 230/230 | 232/232 | 1795 | 101.4652 | 102.32 | Single | 'BG_P21:FROM:220964 GRACETON 230 220999 BAGLEY2 230 13_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220964 | GRACETON | 221000 | BAGLEY | 5 | 230/230 | 232/232 | 1795 | 101.4652 | 102.31 | Single | 'BG_P21:TO:220964 GRACETON 230 220999 BAGLEY2 230 13_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220964 | GRACETON | 221000 | BAGLEY | 5 | 230/230 | 232/232 | 1795 | 100.3343 | 101.5 | Single | 'BG_P21:FROM:220980 RAPHAEL 230 220999 BAGLEY2 230 13_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220964 | GRACETON | 221000 | BAGLEY | 5 | 230/230 | 232/232 | 1795 | 100.3343 | 101.5 | Single | 'BG_P21:TO:220980 RAPHAEL 230 220999 BAGLEY2 230 13_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220964 | GRACETON | 220999 | BAGLEY2 | 13 | 230/230 | 232/232 | 1795 | 101.4206 | 102.28 | Single | 'BG_P21:FROM:220964 GRACETON 230 221000 BAGLEY 230 5 _SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220964 | GRACETON | 220999 | BAGLEY2 | 13 | 230/230 | 232/232 | 1795 | 101.4206 | 102.27 | Single | 'BG_P21:TO:220964 GRACETON 230 221000 BAGLEY 230 5 _SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220964 | GRACETON | 220999 | BAGLEY2 | 13 | 230/230 | 232/232 | 1795 | 100.0836 | 101.24 | Single | 'BG_P21:TO:220980 RAPHAEL 230 221000 BAGLEY 230 5 _SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220964 | GRACETON | 220999 | BAGLEY2 | 13 | 230/230 | 232/232 | 1795 | 100.0836 | 101.24 | Single | 'BG_P21:FROM:220980 RAPHAEL 230 221000 BAGLEY 230 5 _SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220999 | BAGLEY2 | 220980 | RAPHAEL | 13 | 230/230 | 232/232 | 1795 | 99.3928 | 100.83 | Single | 'BG_P21:FROM:220964 GRACETON 230 221000 BAGLEY 230 5 _SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220999 | BAGLEY2 | 220980 | RAPHAEL | 13 | 230/230 | 232/232 | 1795 | 99.3928 | 100.82 | Single | 'BG_P21:TO:220964 GRACETON 230 221000 BAGLEY 230 5 _SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200532 | 26ROXBURY | 200520 | 26ROXBURY | 2 | 138/115 | 226/226 | 364 | N/A | 100.71 | Single | 'BASE CASE' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 221000 | BAGLEY | 220980 | RAPHAEL | 5 | 230/230 | 232/232 | 1795 | 99.0752 | 100.52 | Single | 'BG_P21:FROM:220964 GRACETON 230 220999 BAGLEY2 230 13_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 221000 | BAGLEY | 220980 | RAPHAEL | 5 | 230/230 | 232/232 | 1795 | 99.0752 | 100.51 | Single | 'BG_P21:TO:220964 GRACETON 230 220999 BAGLEY2 230 13_SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220972 | GRANITE1 | 1 | 230/230 | 232/232 | 829 | 101.7491 | 100.34 | Single | 'BG_P21:FROM:220961 NWEST326 230 220973 GRANITE6 230 1 _SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220972 | GRANITE1 | 1 | 230/230 | 232/232 | 829 | 101.7491 | 100.34 | Single | 'BG_P21:TO:220961 NWEST326 230 220973 GRANITE6 230 1 _SRT-A' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 235450 | 01CARROL | 235463 | 01TANEY | 1 | 138/138 | 201/201 | 250 | 137.84 | 144.53 | Single | 'BASE CASE' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 235188 | 01GREENE | 235557 | 01LETTER | 1 | 138/138 | 201/201 | 250 | 115.52 | 117.22 | Single | 'BASE CASE' |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 235187 | 01GRANDP | 235557 | 01LETTER | 1 | 138/138 | 201/201 | 250 | 111.12 | 114.45 | Single | 'BASE CASE' |  | NO | Related to 2022 Window 3, pending window outcome

## N-1 Volt Mag
Note | APS and Dominion zones as a whole are quarantined pending Window 3 outcome and are not included in above results
Related to 2022 Window 3, pending window outcome
PJM N-1 Voltage Magnitude Result (Winter 2028 Case)
FG# | Bus # | Name | KV | Area | ContVolt | BaseVolt | Upper/Lower Limit | Cont Type | Contingency | PJM Accepting Proposals | Reasons for Exclusions | Comments
N/A | 214219 | NOTTNGH3 | 230 | 230 | 0.9412 | 1.0198 | 0.95 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 214219 | NOTTNGH3 | 230 | 230 | 0.9428 | 1.0198 | 0.95 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 214219 | NOTTNGH3 | 230 | 230 | 0.9429 | 1.0198 | 0.95 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 214219 | NOTTNGH3 | 230 | 230 | 0.9429 | 1.0198 | 0.95 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 214218 | NOTTNGH2 | 230 | 230 | 0.9412 | 1.0199 | 0.95 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 214218 | NOTTNGH2 | 230 | 230 | 0.9428 | 1.0199 | 0.95 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 214218 | NOTTNGH2 | 230 | 230 | 0.9429 | 1.0199 | 0.95 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 214218 | NOTTNGH2 | 230 | 230 | 0.9429 | 1.0199 | 0.95 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 214087 | COOPER2 | 230 | 230 | 0.9014 | 0.9944 | 0.95 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 214087 | COOPER2 | 230 | 230 | 0.9025 | 0.9944 | 0.95 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 214087 | COOPER2 | 230 | 230 | 0.9025 | 0.9944 | 0.95 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 214087 | COOPER2 | 230 | 230 | 0.9025 | 0.9944 | 0.95 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 214087 | COOPER2 | 230 | 230 | 0.9264 | 0.9944 | 0.95 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 230 | 230 | 0.9021 | 0.9945 | 0.95 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 230 | 230 | 0.9032 | 0.9945 | 0.95 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 230 | 230 | 0.9032 | 0.9945 | 0.95 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 230 | 230 | 0.9032 | 0.9945 | 0.95 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 230 | 230 | 0.9269 | 0.9945 | 0.95 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 230 | 230 | 0.8904 | 0.9942 | 0.95 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 230 | 230 | 0.8917 | 0.9942 | 0.95 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 230 | 230 | 0.8918 | 0.9942 | 0.95 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 230 | 230 | 0.8918 | 0.9942 | 0.95 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 230 | 230 | 0.9184 | 0.9942 | 0.95 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 230 | 230 | 0.8497 | 1.0026 | 0.95 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 230 | 230 | 0.8521 | 1.0026 | 0.95 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 230 | 230 | 0.8522 | 1.0026 | 0.95 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 230 | 230 | 0.8522 | 1.0026 | 0.95 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 230 | 230 | 0.8946 | 1.0026 | 0.95 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 230 | 230 | 0.9411 | 1.02 | 0.95 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 230 | 230 | 0.9427 | 1.02 | 0.95 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 230 | 230 | 0.9428 | 1.02 | 0.95 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 230 | 230 | 0.9428 | 1.02 | 0.95 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208141 | WIGR | 230 | 229 | 0.9129 | 1.0229 | 0.92 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208141 | WIGR | 230 | 229 | 0.913 | 1.0229 | 0.92 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208141 | WIGR | 230 | 229 | 0.913 | 1.0229 | 0.92 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208141 | WIGR | 230 | 229 | 0.9167 | 1.0229 | 0.92 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208136 | WSHO | 230 | 229 | 0.9125 | 1.0241 | 0.92 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208136 | WSHO | 230 | 229 | 0.9125 | 1.0241 | 0.92 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208136 | WSHO | 230 | 229 | 0.9125 | 1.0241 | 0.92 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208136 | WSHO | 230 | 229 | 0.9159 | 1.0241 | 0.92 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208088 | SMAN TR4 | 230 | 229 | 0.8996 | 1.0196 | 0.92 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208088 | SMAN TR4 | 230 | 229 | 0.8996 | 1.0196 | 0.92 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208088 | SMAN TR4 | 230 | 229 | 0.8996 | 1.0196 | 0.92 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208088 | SMAN TR4 | 230 | 229 | 0.9007 | 1.0196 | 0.92 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208087 | SMAN TR3 | 230 | 229 | 0.8996 | 1.0196 | 0.92 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208087 | SMAN TR3 | 230 | 229 | 0.8996 | 1.0196 | 0.92 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208087 | SMAN TR3 | 230 | 229 | 0.8996 | 1.0196 | 0.92 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208087 | SMAN TR3 | 230 | 229 | 0.9007 | 1.0196 | 0.92 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208083 | SAKRCAPB | 230 | 229 | 0.9014 | 1.0187 | 0.92 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208083 | SAKRCAPB | 230 | 229 | 0.9014 | 1.0187 | 0.92 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208083 | SAKRCAPB | 230 | 229 | 0.9014 | 1.0187 | 0.92 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208083 | SAKRCAPB | 230 | 229 | 0.9018 | 1.0187 | 0.92 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208082 | SAKRCAPA | 230 | 229 | 0.9015 | 1.0188 | 0.92 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208082 | SAKRCAPA | 230 | 229 | 0.9015 | 1.0188 | 0.92 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208082 | SAKRCAPA | 230 | 229 | 0.9015 | 1.0188 | 0.92 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208082 | SAKRCAPA | 230 | 229 | 0.9019 | 1.0188 | 0.92 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208078 | SAKR | 230 | 229 | 0.9014 | 1.0187 | 0.92 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208078 | SAKR | 230 | 229 | 0.9014 | 1.0187 | 0.92 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208078 | SAKR | 230 | 229 | 0.9014 | 1.0187 | 0.92 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208078 | SAKR | 230 | 229 | 0.9018 | 1.0187 | 0.92 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208045 | LAUS | 230 | 229 | 0.9199 | 1.0128 | 0.92 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208045 | LAUS | 230 | 229 | 0.9199 | 1.0128 | 0.92 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208045 | LAUS | 230 | 229 | 0.9199 | 1.0128 | 0.92 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208031 | MLWD TR2 | 230 | 229 | 0.9194 | 1.017 | 0.92 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 230 | 229 | 0.919 | 1.0169 | 0.92 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 207990 | HUMMTPST | 230 | 229 | 0.92 | 1.0253 | 0.92 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 207990 | HUMMTPST | 230 | 229 | 0.92 | 1.0253 | 0.92 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 207990 | HUMMTPST | 230 | 229 | 0.92 | 1.0253 | 0.92 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 207923 | BRISREAC | 230 | 229 | 0.9084 | 1.0292 | 0.92 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 207923 | BRISREAC | 230 | 229 | 0.9084 | 1.0292 | 0.92 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 207923 | BRISREAC | 230 | 229 | 0.9084 | 1.0292 | 0.92 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 207923 | BRISREAC | 230 | 229 | 0.9089 | 1.0292 | 0.92 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 207922 | BRIS | 230 | 229 | 0.9092 | 1.0304 | 0.92 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 207922 | BRIS | 230 | 229 | 0.9092 | 1.0304 | 0.92 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 207922 | BRIS | 230 | 229 | 0.9092 | 1.0304 | 0.92 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 207922 | BRIS | 230 | 229 | 0.9113 | 1.0304 | 0.92 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204709 | 27MIDDJCT8 | 230 | 227 | 0.9126 | 1.0265 | 0.92 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204709 | 27MIDDJCT8 | 230 | 227 | 0.9126 | 1.0265 | 0.92 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204709 | 27MIDDJCT8 | 230 | 227 | 0.9126 | 1.0265 | 0.92 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204709 | 27MIDDJCT8 | 230 | 227 | 0.9154 | 1.0265 | 0.92 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204692 | 27WILLOWDR | 230 | 227 | 0.9168 | 1.0256 | 0.92 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204692 | 27WILLOWDR | 230 | 227 | 0.9168 | 1.0256 | 0.92 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204692 | 27WILLOWDR | 230 | 227 | 0.9168 | 1.0256 | 0.92 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204692 | 27WILLOWDR | 230 | 227 | 0.9197 | 1.0256 | 0.92 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204575 | 27HUNTRST1 | 230 | 227 | 0.89 | 1.0214 | 0.92 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204575 | 27HUNTRST1 | 230 | 227 | 0.89 | 1.0214 | 0.92 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204575 | 27HUNTRST1 | 230 | 227 | 0.89 | 1.0214 | 0.92 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204575 | 27HUNTRST1 | 230 | 227 | 0.893 | 1.0214 | 0.92 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 230 | 227 | 0.879 | 1.0162 | 0.92 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 230 | 227 | 0.879 | 1.0162 | 0.92 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 230 | 227 | 0.879 | 1.0162 | 0.92 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 230 | 227 | 0.8794 | 1.0162 | 0.92 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 230 | 227 | 0.9173 | 1.0162 | 0.92 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204514 | 27TMI | 230 | 227 | 0.9114 | 1.0263 | 0.92 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204514 | 27TMI | 230 | 227 | 0.9114 | 1.0263 | 0.92 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204514 | 27TMI | 230 | 227 | 0.9114 | 1.0263 | 0.92 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204514 | 27TMI | 230 | 227 | 0.9142 | 1.0263 | 0.92 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204504 | 27MIDD JCT | 230 | 227 | 0.9126 | 1.0265 | 0.92 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204504 | 27MIDD JCT | 230 | 227 | 0.9126 | 1.0265 | 0.92 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204504 | 27MIDD JCT | 230 | 227 | 0.9126 | 1.0265 | 0.92 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204504 | 27MIDD JCT | 230 | 227 | 0.9154 | 1.0265 | 0.92 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204502 | 27JACKSON | 230 | 227 | 0.8709 | 1.0136 | 0.92 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204502 | 27JACKSON | 230 | 227 | 0.8709 | 1.0136 | 0.92 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204502 | 27JACKSON | 230 | 227 | 0.8709 | 1.0136 | 0.92 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204502 | 27JACKSON | 230 | 227 | 0.8732 | 1.0136 | 0.92 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204502 | 27JACKSON | 230 | 227 | 0.91 | 1.0136 | 0.92 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 221130 | COL.GAS | 115 | 232 | 0.8997 | 0.971 | 0.92 | Tower | BG_P7_GRCTN_RAPHEL_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 221130 | COL.GAS | 115 | 232 | 0.9152 | 0.971 | 0.92 | Tower | BG_P7_NEAST_RPHLRD_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 221099 | C.PIPE J | 115 | 232 | 0.8997 | 0.971 | 0.92 | Tower | BG_P7_GRCTN_RAPHEL_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 221099 | C.PIPE J | 115 | 232 | 0.9152 | 0.971 | 0.92 | Tower | BG_P7_NEAST_RPHLRD_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 221098 | C.PIPE12 | 115 | 232 | 0.8999 | 0.9712 | 0.92 | Tower | BG_P7_GRCTN_RAPHEL_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 221098 | C.PIPE12 | 115 | 232 | 0.9154 | 0.9712 | 0.92 | Tower | BG_P7_NEAST_RPHLRD_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 221097 | C.PIPE11 | 115 | 232 | 0.9002 | 0.9723 | 0.92 | Tower | BG_P7_GRCTN_RAPHEL_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 221097 | C.PIPE11 | 115 | 232 | 0.916 | 0.9723 | 0.92 | Tower | BG_P7_NEAST_RPHLRD_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 221096 | ROCKRGE1 | 115 | 232 | 0.8856 | 0.9666 | 0.92 | Tower | BG_P7_GRCTN_RAPHEL_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 221096 | ROCKRGE1 | 115 | 232 | 0.9037 | 0.9666 | 0.92 | Tower | BG_P7_NEAST_RPHLRD_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 221095 | ROCKRGE2 | 115 | 232 | 0.8861 | 0.9659 | 0.92 | Tower | BG_P7_GRCTN_RAPHEL_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 221095 | ROCKRGE2 | 115 | 232 | 0.9038 | 0.9659 | 0.92 | Tower | BG_P7_NEAST_RPHLRD_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 221094 | GRACE.-1 | 115 | 232 | 0.8802 | 0.9592 | 0.92 | Tower | BG_P7_GRCTN_RAPHEL_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 221094 | GRACE.-1 | 115 | 232 | 0.8993 | 0.9592 | 0.92 | Tower | BG_P7_NEAST_RPHLRD_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 221092 | FIVE.FOR | 115 | 232 | 0.8764 | 0.9592 | 0.92 | Tower | BG_P7_GRCTN_RAPHEL_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 221092 | FIVE.FOR | 115 | 232 | 0.8956 | 0.9592 | 0.92 | Tower | BG_P7_NEAST_RPHLRD_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208720 | RED FRONT | 115 | 229 | 0.8811 | 1.0206 | 0.92 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208720 | RED FRONT | 115 | 229 | 0.8811 | 1.0206 | 0.92 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208720 | RED FRONT | 115 | 229 | 0.8811 | 1.0206 | 0.92 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208720 | RED FRONT | 115 | 229 | 0.8819 | 1.0206 | 0.92 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208394 | PPL-BGE TIE | 115 | 229 | 0.8782 | 0.9596 | 0.92 | Tower | BG_P7_GRCTN_RAPHEL_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208394 | PPL-BGE TIE | 115 | 229 | 0.897 | 0.9596 | 0.92 | Tower | BG_P7_NEAST_RPHLRD_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208393 | FARO DC TIE | 115 | 229 | 0.905 | 0.9706 | 0.92 | Tower | BG_P7_GRCTN_RAPHEL_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208393 | FARO DC TIE | 115 | 229 | 0.9197 | 0.9706 | 0.92 | Tower | BG_P7_NEAST_RPHLRD_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208142 | WIGR-115 | 115 | 229 | 0.9049 | 1.0224 | 0.92 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208142 | WIGR-115 | 115 | 229 | 0.9049 | 1.0224 | 0.92 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208142 | WIGR-115 | 115 | 229 | 0.9049 | 1.0224 | 0.92 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208142 | WIGR-115 | 115 | 229 | 0.9086 | 1.0224 | 0.92 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 205948 | AE1-129_MAIN | 115 | 227 | 0.8924 | 1.0129 | 0.92 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 205948 | AE1-129_MAIN | 115 | 227 | 0.8924 | 1.0129 | 0.92 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 205948 | AE1-129_MAIN | 115 | 227 | 0.8924 | 1.0129 | 0.92 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 205948 | AE1-129_MAIN | 115 | 227 | 0.8948 | 1.0129 | 0.92 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 205947 | AE1-129_POI | 115 | 227 | 0.8911 | 1.0129 | 0.92 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 205947 | AE1-129_POI | 115 | 227 | 0.8911 | 1.0129 | 0.92 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 205947 | AE1-129_POI | 115 | 227 | 0.8911 | 1.0129 | 0.92 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 205947 | AE1-129_POI | 115 | 227 | 0.8936 | 1.0129 | 0.92 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 205931 | AF2-100 C | 115 | 227 | 0.8739 | 1.0088 | 0.92 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 205931 | AF2-100 C | 115 | 227 | 0.8739 | 1.0088 | 0.92 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 205931 | AF2-100 C | 115 | 227 | 0.8739 | 1.0088 | 0.92 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 205931 | AF2-100 C | 115 | 227 | 0.8762 | 1.0088 | 0.92 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 205931 | AF2-100 C | 115 | 227 | 0.9139 | 1.0088 | 0.92 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 205930 | AF2-099 C | 115 | 227 | 0.8739 | 1.0088 | 0.92 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 205930 | AF2-099 C | 115 | 227 | 0.8739 | 1.0088 | 0.92 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 205930 | AF2-099 C | 115 | 227 | 0.8739 | 1.0088 | 0.92 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 205930 | AF2-099 C | 115 | 227 | 0.8762 | 1.0088 | 0.92 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 205930 | AF2-099 C | 115 | 227 | 0.9139 | 1.0088 | 0.92 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 205922 | AF2-268 E | 115 | 227 | 0.914 | 1.0078 | 0.92 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 205922 | AF2-268 E | 115 | 227 | 0.914 | 1.0078 | 0.92 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 205922 | AF2-268 E | 115 | 227 | 0.914 | 1.0078 | 0.92 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 205922 | AF2-268 E | 115 | 227 | 0.9166 | 1.0078 | 0.92 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 205921 | AF2-151 C | 115 | 227 | 0.8969 | 1.0207 | 0.92 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 205921 | AF2-151 C | 115 | 227 | 0.8969 | 1.0207 | 0.92 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 205921 | AF2-151 C | 115 | 227 | 0.8969 | 1.0207 | 0.92 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 205921 | AF2-151 C | 115 | 227 | 0.9003 | 1.0207 | 0.92 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 205920 | AF2-101 C | 115 | 227 | 0.904 | 1.0246 | 0.92 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 205920 | AF2-101 C | 115 | 227 | 0.904 | 1.0246 | 0.92 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 205920 | AF2-101 C | 115 | 227 | 0.904 | 1.0246 | 0.92 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 205920 | AF2-101 C | 115 | 227 | 0.9076 | 1.0246 | 0.92 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 205913 | AD1-020 MAIN | 115 | 227 | 0.9197 | 1.0131 | 0.92 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 205913 | AD1-020 MAIN | 115 | 227 | 0.9197 | 1.0131 | 0.92 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 205913 | AD1-020 MAIN | 115 | 227 | 0.9197 | 1.0131 | 0.92 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 205912 | AD1-020 TAP | 115 | 227 | 0.9196 | 1.0131 | 0.92 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 205912 | AD1-020 TAP | 115 | 227 | 0.9196 | 1.0131 | 0.92 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 205912 | AD1-020 TAP | 115 | 227 | 0.9196 | 1.0131 | 0.92 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204715 | 27EISENHOWER | 115 | 227 | 0.8681 | 0.9954 | 0.92 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204715 | 27EISENHOWER | 115 | 227 | 0.8681 | 0.9954 | 0.92 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204715 | 27EISENHOWER | 115 | 227 | 0.8681 | 0.9954 | 0.92 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204715 | 27EISENHOWER | 115 | 227 | 0.8708 | 0.9954 | 0.92 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204715 | 27EISENHOWER | 115 | 227 | 0.9068 | 0.9954 | 0.92 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204713 | 27JOHNSCTRL | 115 | 227 | 0.8559 | 0.9966 | 0.92 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204713 | 27JOHNSCTRL | 115 | 227 | 0.8559 | 0.9966 | 0.92 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204713 | 27JOHNSCTRL | 115 | 227 | 0.8559 | 0.9966 | 0.92 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204713 | 27JOHNSCTRL | 115 | 227 | 0.8575 | 0.9966 | 0.92 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204713 | 27JOHNSCTRL | 115 | 227 | 0.8966 | 0.9966 | 0.92 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204701 | 27YORKANAB | 115 | 227 | 0.8815 | 1.0211 | 0.92 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204701 | 27YORKANAB | 115 | 227 | 0.8815 | 1.0211 | 0.92 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204701 | 27YORKANAB | 115 | 227 | 0.8815 | 1.0211 | 0.92 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204701 | 27YORKANAB | 115 | 227 | 0.8823 | 1.0211 | 0.92 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204700 | 27JACKSON6 | 115 | 227 | 0.8778 | 1.0121 | 0.92 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204700 | 27JACKSON6 | 115 | 227 | 0.8779 | 1.0121 | 0.92 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204700 | 27JACKSON6 | 115 | 227 | 0.8779 | 1.0121 | 0.92 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204700 | 27JACKSON6 | 115 | 227 | 0.8802 | 1.0121 | 0.92 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204700 | 27JACKSON6 | 115 | 227 | 0.9171 | 1.0121 | 0.92 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204687 | 27PROSPECT | 115 | 227 | 0.8806 | 1.0203 | 0.92 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204687 | 27PROSPECT | 115 | 227 | 0.8806 | 1.0203 | 0.92 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204687 | 27PROSPECT | 115 | 227 | 0.8806 | 1.0203 | 0.92 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204687 | 27PROSPECT | 115 | 227 | 0.8815 | 1.0203 | 0.92 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204682 | 27ES3 | 115 | 227 | 0.8841 | 1.0123 | 0.92 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204682 | 27ES3 | 115 | 227 | 0.8842 | 1.0123 | 0.92 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204682 | 27ES3 | 115 | 227 | 0.8842 | 1.0123 | 0.92 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204682 | 27ES3 | 115 | 227 | 0.8867 | 1.0123 | 0.92 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204681 | 27REDFRONT+ | 115 | 227 | 0.8811 | 1.0206 | 0.92 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204681 | 27REDFRONT+ | 115 | 227 | 0.8811 | 1.0206 | 0.92 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204681 | 27REDFRONT+ | 115 | 227 | 0.8811 | 1.0206 | 0.92 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204681 | 27REDFRONT+ | 115 | 227 | 0.8819 | 1.0206 | 0.92 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204669 | 27TEX E | 115 | 227 | 0.9111 | 1.0207 | 0.92 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204669 | 27TEX E | 115 | 227 | 0.9111 | 1.0207 | 0.92 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204669 | 27TEX E | 115 | 227 | 0.9111 | 1.0207 | 0.92 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204669 | 27TEX E | 115 | 227 | 0.9141 | 1.0207 | 0.92 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204668 | 27TEX E TP | 115 | 227 | 0.9115 | 1.0211 | 0.92 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204668 | 27TEX E TP | 115 | 227 | 0.9115 | 1.0211 | 0.92 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204668 | 27TEX E TP | 115 | 227 | 0.9116 | 1.0211 | 0.92 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204668 | 27TEX E TP | 115 | 227 | 0.9146 | 1.0211 | 0.92 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204660 | 27YK H STA | 115 | 227 | 0.8967 | 1.0202 | 0.92 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204660 | 27YK H STA | 115 | 227 | 0.8967 | 1.0202 | 0.92 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204660 | 27YK H STA | 115 | 227 | 0.8967 | 1.0202 | 0.92 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204660 | 27YK H STA | 115 | 227 | 0.8994 | 1.0202 | 0.92 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204598 | 27MIDD JCT | 115 | 227 | 0.9024 | 1.0237 | 0.92 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204598 | 27MIDD JCT | 115 | 227 | 0.9024 | 1.0237 | 0.92 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204598 | 27MIDD JCT | 115 | 227 | 0.9024 | 1.0237 | 0.92 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204598 | 27MIDD JCT | 115 | 227 | 0.9051 | 1.0237 | 0.92 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204597 | 27COLLINS | 115 | 227 | 0.8993 | 1.0218 | 0.92 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204597 | 27COLLINS | 115 | 227 | 0.8993 | 1.0218 | 0.92 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204597 | 27COLLINS | 115 | 227 | 0.8993 | 1.0218 | 0.92 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204597 | 27COLLINS | 115 | 227 | 0.9019 | 1.0218 | 0.92 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204596 | 27MJ5 REAC | 115 | 227 | 0.9032 | 1.0234 | 0.92 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204596 | 27MJ5 REAC | 115 | 227 | 0.9032 | 1.0234 | 0.92 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204596 | 27MJ5 REAC | 115 | 227 | 0.9032 | 1.0234 | 0.92 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204596 | 27MJ5 REAC | 115 | 227 | 0.906 | 1.0234 | 0.92 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204595 | 27MJ2 REAC | 115 | 227 | 0.9032 | 1.0234 | 0.92 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204595 | 27MJ2 REAC | 115 | 227 | 0.9032 | 1.0234 | 0.92 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204595 | 27MJ2 REAC | 115 | 227 | 0.9032 | 1.0234 | 0.92 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204595 | 27MJ2 REAC | 115 | 227 | 0.906 | 1.0234 | 0.92 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204573 | 27SPRNGWOD | 115 | 227 | 0.8744 | 1.0131 | 0.92 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204573 | 27SPRNGWOD | 115 | 227 | 0.8744 | 1.0131 | 0.92 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204573 | 27SPRNGWOD | 115 | 227 | 0.8744 | 1.0131 | 0.92 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204573 | 27SPRNGWOD | 115 | 227 | 0.8756 | 1.0131 | 0.92 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204573 | 27SPRNGWOD | 115 | 227 | 0.9151 | 1.0131 | 0.92 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204572 | 27RAINTREE | 115 | 227 | 0.878 | 1.0084 | 0.92 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204572 | 27RAINTREE | 115 | 227 | 0.878 | 1.0084 | 0.92 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204572 | 27RAINTREE | 115 | 227 | 0.878 | 1.0084 | 0.92 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204572 | 27RAINTREE | 115 | 227 | 0.8804 | 1.0084 | 0.92 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204572 | 27RAINTREE | 115 | 227 | 0.9185 | 1.0084 | 0.92 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204571 | 27ZIONS VW | 115 | 227 | 0.8835 | 1.0089 | 0.92 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204571 | 27ZIONS VW | 115 | 227 | 0.8835 | 1.0089 | 0.92 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204571 | 27ZIONS VW | 115 | 227 | 0.8835 | 1.0089 | 0.92 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204571 | 27ZIONS VW | 115 | 227 | 0.8859 | 1.0089 | 0.92 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204570 | 27YORKANA | 115 | 227 | 0.8817 | 1.0214 | 0.92 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204570 | 27YORKANA | 115 | 227 | 0.8817 | 1.0214 | 0.92 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204570 | 27YORKANA | 115 | 227 | 0.8817 | 1.0214 | 0.92 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204570 | 27YORKANA | 115 | 227 | 0.8825 | 1.0214 | 0.92 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204569 | 27YORK INC | 115 | 227 | 0.874 | 1.0103 | 0.92 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204569 | 27YORK INC | 115 | 227 | 0.874 | 1.0103 | 0.92 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204569 | 27YORK INC | 115 | 227 | 0.874 | 1.0103 | 0.92 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204569 | 27YORK INC | 115 | 227 | 0.8758 | 1.0103 | 0.92 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204569 | 27YORK INC | 115 | 227 | 0.9149 | 1.0103 | 0.92 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204568 | 27YOE TAP | 115 | 227 | 0.8743 | 1.0146 | 0.92 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204568 | 27YOE TAP | 115 | 227 | 0.8743 | 1.0146 | 0.92 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204568 | 27YOE TAP | 115 | 227 | 0.8743 | 1.0146 | 0.92 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204568 | 27YOE TAP | 115 | 227 | 0.8752 | 1.0146 | 0.92 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204568 | 27YOE TAP | 115 | 227 | 0.9133 | 1.0146 | 0.92 | Line_FB | ME_P2-3_ME-115-032AT_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204568 | 27YOE TAP | 115 | 227 | 0.9145 | 1.0146 | 0.92 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204567 | 27YOE | 115 | 227 | 0.8762 | 1.0153 | 0.92 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204567 | 27YOE | 115 | 227 | 0.8762 | 1.0153 | 0.92 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204567 | 27YOE | 115 | 227 | 0.8762 | 1.0153 | 0.92 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204567 | 27YOE | 115 | 227 | 0.8773 | 1.0153 | 0.92 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204567 | 27YOE | 115 | 227 | 0.9167 | 1.0153 | 0.92 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204566 | 27YK HAVEN | 115 | 227 | 0.8965 | 1.0201 | 0.92 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204566 | 27YK HAVEN | 115 | 227 | 0.8965 | 1.0201 | 0.92 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204566 | 27YK HAVEN | 115 | 227 | 0.8966 | 1.0201 | 0.92 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204566 | 27YK HAVEN | 115 | 227 | 0.8992 | 1.0201 | 0.92 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204565 | 27WINDSOR | 115 | 227 | 0.8692 | 1.0099 | 0.92 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204565 | 27WINDSOR | 115 | 227 | 0.8692 | 1.0099 | 0.92 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204565 | 27WINDSOR | 115 | 227 | 0.8692 | 1.0099 | 0.92 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204565 | 27WINDSOR | 115 | 227 | 0.8703 | 1.0099 | 0.92 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204565 | 27WINDSOR | 115 | 227 | 0.9096 | 1.0099 | 0.92 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204565 | 27WINDSOR | 115 | 227 | 0.9133 | 1.0099 | 0.92 | Line_FB | ME_P2-3_ME-115-032AT_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204564 | 27WHITEFRD | 115 | 227 | 0.8729 | 1.0116 | 0.92 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204564 | 27WHITEFRD | 115 | 227 | 0.8729 | 1.0116 | 0.92 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204564 | 27WHITEFRD | 115 | 227 | 0.8729 | 1.0116 | 0.92 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204564 | 27WHITEFRD | 115 | 227 | 0.8743 | 1.0116 | 0.92 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204564 | 27WHITEFRD | 115 | 227 | 0.9139 | 1.0116 | 0.92 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204563 | 27WESTGATE | 115 | 227 | 0.8725 | 1.007 | 0.92 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204563 | 27WESTGATE | 115 | 227 | 0.8725 | 1.007 | 0.92 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204563 | 27WESTGATE | 115 | 227 | 0.8725 | 1.007 | 0.92 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204563 | 27WESTGATE | 115 | 227 | 0.8747 | 1.007 | 0.92 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204563 | 27WESTGATE | 115 | 227 | 0.9132 | 1.007 | 0.92 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204562 | 27W.HELLAM | 115 | 227 | 0.8771 | 1.0168 | 0.92 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204562 | 27W.HELLAM | 115 | 227 | 0.8771 | 1.0168 | 0.92 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204562 | 27W.HELLAM | 115 | 227 | 0.8771 | 1.0168 | 0.92 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204562 | 27W.HELLAM | 115 | 227 | 0.8781 | 1.0168 | 0.92 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204562 | 27W.HELLAM | 115 | 227 | 0.9174 | 1.0168 | 0.92 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204561 | 27VIOLET H | 115 | 227 | 0.8736 | 1.0117 | 0.92 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204561 | 27VIOLET H | 115 | 227 | 0.8736 | 1.0117 | 0.92 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204561 | 27VIOLET H | 115 | 227 | 0.8736 | 1.0117 | 0.92 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204561 | 27VIOLET H | 115 | 227 | 0.875 | 1.0117 | 0.92 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204561 | 27VIOLET H | 115 | 227 | 0.9145 | 1.0117 | 0.92 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204560 | 27TOLNA | 115 | 227 | 0.8558 | 0.9967 | 0.92 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204560 | 27TOLNA | 115 | 227 | 0.8558 | 0.9967 | 0.92 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204560 | 27TOLNA | 115 | 227 | 0.8558 | 0.9967 | 0.92 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204560 | 27TOLNA | 115 | 227 | 0.8573 | 0.9967 | 0.92 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204560 | 27TOLNA | 115 | 227 | 0.8965 | 0.9967 | 0.92 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204559 | 27TAXVILLE | 115 | 227 | 0.8739 | 1.0088 | 0.92 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204559 | 27TAXVILLE | 115 | 227 | 0.8739 | 1.0088 | 0.92 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204559 | 27TAXVILLE | 115 | 227 | 0.8739 | 1.0088 | 0.92 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204559 | 27TAXVILLE | 115 | 227 | 0.8762 | 1.0088 | 0.92 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204559 | 27TAXVILLE | 115 | 227 | 0.9139 | 1.0088 | 0.92 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204558 | 27SMITH TP | 115 | 227 | 0.8725 | 1.007 | 0.92 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204558 | 27SMITH TP | 115 | 227 | 0.8725 | 1.007 | 0.92 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204558 | 27SMITH TP | 115 | 227 | 0.8725 | 1.007 | 0.92 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204558 | 27SMITH TP | 115 | 227 | 0.8746 | 1.007 | 0.92 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204558 | 27SMITH TP | 115 | 227 | 0.9132 | 1.007 | 0.92 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204557 | 27SMITH ST | 115 | 227 | 0.8723 | 1.0057 | 0.92 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204557 | 27SMITH ST | 115 | 227 | 0.8723 | 1.0057 | 0.92 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204557 | 27SMITH ST | 115 | 227 | 0.8724 | 1.0057 | 0.92 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204557 | 27SMITH ST | 115 | 227 | 0.8746 | 1.0057 | 0.92 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204557 | 27SMITH ST | 115 | 227 | 0.9132 | 1.0057 | 0.92 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204556 | 27ROUND TP | 115 | 227 | 0.902 | 1.0253 | 0.92 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204556 | 27ROUND TP | 115 | 227 | 0.902 | 1.0253 | 0.92 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204556 | 27ROUND TP | 115 | 227 | 0.902 | 1.0253 | 0.92 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204556 | 27ROUND TP | 115 | 227 | 0.9054 | 1.0253 | 0.92 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204555 | 27QUEEN ST | 115 | 227 | 0.8739 | 1.0124 | 0.92 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204555 | 27QUEEN ST | 115 | 227 | 0.8739 | 1.0124 | 0.92 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204555 | 27QUEEN ST | 115 | 227 | 0.8739 | 1.0124 | 0.92 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204555 | 27QUEEN ST | 115 | 227 | 0.8752 | 1.0124 | 0.92 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204555 | 27QUEEN ST | 115 | 227 | 0.9147 | 1.0124 | 0.92 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204554 | 27PLEASVIL | 115 | 227 | 0.8738 | 1.0121 | 0.92 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204554 | 27PLEASVIL | 115 | 227 | 0.8738 | 1.0121 | 0.92 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204554 | 27PLEASVIL | 115 | 227 | 0.8739 | 1.0121 | 0.92 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204554 | 27PLEASVIL | 115 | 227 | 0.8754 | 1.0121 | 0.92 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204554 | 27PLEASVIL | 115 | 227 | 0.9149 | 1.0121 | 0.92 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204553 | 27PH GLATR | 115 | 227 | 0.8722 | 1.004 | 0.92 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204553 | 27PH GLATR | 115 | 227 | 0.8722 | 1.004 | 0.92 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204553 | 27PH GLATR | 115 | 227 | 0.8722 | 1.004 | 0.92 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204553 | 27PH GLATR | 115 | 227 | 0.8747 | 1.004 | 0.92 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204553 | 27PH GLATR | 115 | 227 | 0.9114 | 1.004 | 0.92 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204552 | 27P.P.G.I. | 115 | 227 | 0.9044 | 1.0266 | 0.92 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204552 | 27P.P.G.I. | 115 | 227 | 0.9044 | 1.0266 | 0.92 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204552 | 27P.P.G.I. | 115 | 227 | 0.9044 | 1.0266 | 0.92 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204552 | 27P.P.G.I. | 115 | 227 | 0.9079 | 1.0266 | 0.92 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204551 | 27OXFORD | 115 | 227 | 0.893 | 1.0073 | 0.92 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204551 | 27OXFORD | 115 | 227 | 0.893 | 1.0073 | 0.92 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204551 | 27OXFORD | 115 | 227 | 0.893 | 1.0073 | 0.92 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204551 | 27OXFORD | 115 | 227 | 0.8957 | 1.0073 | 0.92 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204550 | 27ORRTANNA | 115 | 227 | 0.914 | 1.0078 | 0.92 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204550 | 27ORRTANNA | 115 | 227 | 0.914 | 1.0078 | 0.92 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204550 | 27ORRTANNA | 115 | 227 | 0.914 | 1.0078 | 0.92 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204550 | 27ORRTANNA | 115 | 227 | 0.9166 | 1.0078 | 0.92 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204549 | 27NEWBERRY | 115 | 227 | 0.8971 | 1.0207 | 0.92 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204549 | 27NEWBERRY | 115 | 227 | 0.8971 | 1.0207 | 0.92 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204549 | 27NEWBERRY | 115 | 227 | 0.8971 | 1.0207 | 0.92 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204549 | 27NEWBERRY | 115 | 227 | 0.8999 | 1.0207 | 0.92 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204548 | 27N.HANOVR | 115 | 227 | 0.8692 | 0.996 | 0.92 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204548 | 27N.HANOVR | 115 | 227 | 0.8692 | 0.996 | 0.92 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204548 | 27N.HANOVR | 115 | 227 | 0.8692 | 0.996 | 0.92 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204548 | 27N.HANOVR | 115 | 227 | 0.8719 | 0.996 | 0.92 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204548 | 27N.HANOVR | 115 | 227 | 0.9078 | 0.996 | 0.92 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204547 | 27MT ROSE | 115 | 227 | 0.8734 | 1.0116 | 0.92 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204547 | 27MT ROSE | 115 | 227 | 0.8734 | 1.0116 | 0.92 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204547 | 27MT ROSE | 115 | 227 | 0.8734 | 1.0116 | 0.92 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204547 | 27MT ROSE | 115 | 227 | 0.8748 | 1.0116 | 0.92 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204547 | 27MT ROSE | 115 | 227 | 0.9144 | 1.0116 | 0.92 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204546 | 27MOUNTAIN | 115 | 227 | 0.9051 | 1.0272 | 0.92 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204546 | 27MOUNTAIN | 115 | 227 | 0.9051 | 1.0272 | 0.92 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204546 | 27MOUNTAIN | 115 | 227 | 0.9051 | 1.0272 | 0.92 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204546 | 27MOUNTAIN | 115 | 227 | 0.9086 | 1.0272 | 0.92 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204545 | 27MENGES M | 115 | 227 | 0.8723 | 1.0046 | 0.92 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204545 | 27MENGES M | 115 | 227 | 0.8723 | 1.0046 | 0.92 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204545 | 27MENGES M | 115 | 227 | 0.8723 | 1.0046 | 0.92 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204545 | 27MENGES M | 115 | 227 | 0.8748 | 1.0046 | 0.92 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204545 | 27MENGES M | 115 | 227 | 0.9115 | 1.0046 | 0.92 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 115 | 227 | 0.9104 | 0.9976 | 0.92 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 115 | 227 | 0.9104 | 0.9976 | 0.92 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 115 | 227 | 0.9104 | 0.9976 | 0.92 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 115 | 227 | 0.9127 | 0.9976 | 0.92 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204542 | 27JE BAKER | 115 | 227 | 0.8755 | 1.0102 | 0.92 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204542 | 27JE BAKER | 115 | 227 | 0.8755 | 1.0102 | 0.92 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204542 | 27JE BAKER | 115 | 227 | 0.8755 | 1.0102 | 0.92 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204542 | 27JE BAKER | 115 | 227 | 0.8778 | 1.0102 | 0.92 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204542 | 27JE BAKER | 115 | 227 | 0.9151 | 1.0102 | 0.92 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204541 | 27BAKER TP | 115 | 227 | 0.8758 | 1.0104 | 0.92 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204541 | 27BAKER TP | 115 | 227 | 0.8758 | 1.0104 | 0.92 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204541 | 27BAKER TP | 115 | 227 | 0.8758 | 1.0104 | 0.92 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204541 | 27BAKER TP | 115 | 227 | 0.8782 | 1.0104 | 0.92 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204541 | 27BAKER TP | 115 | 227 | 0.9154 | 1.0104 | 0.92 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204540 | 27JACKSON | 115 | 227 | 0.8776 | 1.012 | 0.92 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204540 | 27JACKSON | 115 | 227 | 0.8776 | 1.012 | 0.92 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204540 | 27JACKSON | 115 | 227 | 0.8776 | 1.012 | 0.92 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204540 | 27JACKSON | 115 | 227 | 0.88 | 1.012 | 0.92 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204540 | 27JACKSON | 115 | 227 | 0.9169 | 1.012 | 0.92 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204538 | 27STRABAN | 115 | 227 | 0.918 | 0.9934 | 0.92 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204538 | 27STRABAN | 115 | 227 | 0.918 | 0.9934 | 0.92 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204538 | 27STRABAN | 115 | 227 | 0.918 | 0.9934 | 0.92 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204538 | 27STRABAN | 115 | 227 | 0.92 | 0.9934 | 0.92 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204537 | 27HILL | 115 | 227 | 0.8568 | 0.9967 | 0.92 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204537 | 27HILL | 115 | 227 | 0.8568 | 0.9967 | 0.92 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204537 | 27HILL | 115 | 227 | 0.8568 | 0.9967 | 0.92 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204537 | 27HILL | 115 | 227 | 0.8586 | 0.9967 | 0.92 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204537 | 27HILL | 115 | 227 | 0.8974 | 0.9967 | 0.92 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204536 | 27HARLEY D | 115 | 227 | 0.8737 | 1.0108 | 0.92 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204536 | 27HARLEY D | 115 | 227 | 0.8737 | 1.0108 | 0.92 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204536 | 27HARLEY D | 115 | 227 | 0.8737 | 1.0108 | 0.92 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204536 | 27HARLEY D | 115 | 227 | 0.8754 | 1.0108 | 0.92 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204536 | 27HARLEY D | 115 | 227 | 0.9146 | 1.0108 | 0.92 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204535 | 27HAMILTON | 115 | 227 | 0.8914 | 1.0134 | 0.92 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204535 | 27HAMILTON | 115 | 227 | 0.8914 | 1.0134 | 0.92 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204535 | 27HAMILTON | 115 | 227 | 0.8914 | 1.0134 | 0.92 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204535 | 27HAMILTON | 115 | 227 | 0.8941 | 1.0134 | 0.92 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204534 | 27GLADES | 115 | 227 | 0.8732 | 1.0125 | 0.92 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204534 | 27GLADES | 115 | 227 | 0.8732 | 1.0125 | 0.92 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204534 | 27GLADES | 115 | 227 | 0.8732 | 1.0125 | 0.92 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204534 | 27GLADES | 115 | 227 | 0.8745 | 1.0125 | 0.92 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204534 | 27GLADES | 115 | 227 | 0.914 | 1.0125 | 0.92 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204532 | 27GITTS RN | 115 | 227 | 0.8674 | 0.9954 | 0.92 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204532 | 27GITTS RN | 115 | 227 | 0.8674 | 0.9954 | 0.92 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204532 | 27GITTS RN | 115 | 227 | 0.8674 | 0.9954 | 0.92 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204532 | 27GITTS RN | 115 | 227 | 0.8701 | 0.9954 | 0.92 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204532 | 27GITTS RN | 115 | 227 | 0.9062 | 0.9954 | 0.92 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204528 | 27GARDNERS | 115 | 227 | 0.9025 | 1.0205 | 0.92 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204528 | 27GARDNERS | 115 | 227 | 0.9025 | 1.0205 | 0.92 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204528 | 27GARDNERS | 115 | 227 | 0.9025 | 1.0205 | 0.92 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204528 | 27GARDNERS | 115 | 227 | 0.9057 | 1.0205 | 0.92 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204527 | 27FAIRVIEW | 115 | 227 | 0.8612 | 0.9901 | 0.92 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204527 | 27FAIRVIEW | 115 | 227 | 0.8612 | 0.9901 | 0.92 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204527 | 27FAIRVIEW | 115 | 227 | 0.8613 | 0.9901 | 0.92 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204527 | 27FAIRVIEW | 115 | 227 | 0.864 | 0.9901 | 0.92 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204527 | 27FAIRVIEW | 115 | 227 | 0.9003 | 0.9901 | 0.92 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204526 | 27DILLSBRG | 115 | 227 | 0.8969 | 1.0207 | 0.92 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204526 | 27DILLSBRG | 115 | 227 | 0.8969 | 1.0207 | 0.92 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204526 | 27DILLSBRG | 115 | 227 | 0.8969 | 1.0207 | 0.92 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204526 | 27DILLSBRG | 115 | 227 | 0.9003 | 1.0207 | 0.92 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204525 | 27XROADS | 115 | 227 | 0.8585 | 0.9997 | 0.92 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204525 | 27XROADS | 115 | 227 | 0.8585 | 0.9997 | 0.92 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204525 | 27XROADS | 115 | 227 | 0.8585 | 0.9997 | 0.92 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204525 | 27XROADS | 115 | 227 | 0.8599 | 0.9997 | 0.92 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204525 | 27XROADS | 115 | 227 | 0.8992 | 0.9997 | 0.92 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204525 | 27XROADS | 115 | 227 | 0.9195 | 0.9997 | 0.92 | Line_FB | ME_P2-3_ME-115-032AT_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204524 | 27CLY 978 | 115 | 227 | 0.8952 | 1.0192 | 0.92 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204524 | 27CLY 978 | 115 | 227 | 0.8952 | 1.0192 | 0.92 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204524 | 27CLY 978 | 115 | 227 | 0.8952 | 1.0192 | 0.92 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204524 | 27CLY 978 | 115 | 227 | 0.8979 | 1.0192 | 0.92 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204523 | 27CLY 975 | 115 | 227 | 0.8952 | 1.0193 | 0.92 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204523 | 27CLY 975 | 115 | 227 | 0.8952 | 1.0193 | 0.92 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204523 | 27CLY 975 | 115 | 227 | 0.8952 | 1.0193 | 0.92 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204523 | 27CLY 975 | 115 | 227 | 0.8979 | 1.0193 | 0.92 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204522 | 27CAT TRAC | 115 | 227 | 0.873 | 1.0117 | 0.92 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204522 | 27CAT TRAC | 115 | 227 | 0.873 | 1.0117 | 0.92 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204522 | 27CAT TRAC | 115 | 227 | 0.873 | 1.0117 | 0.92 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204522 | 27CAT TRAC | 115 | 227 | 0.8745 | 1.0117 | 0.92 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204522 | 27CAT TRAC | 115 | 227 | 0.914 | 1.0117 | 0.92 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204521 | 27BAIR | 115 | 227 | 0.8705 | 1.0066 | 0.92 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204521 | 27BAIR | 115 | 227 | 0.8705 | 1.0066 | 0.92 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204521 | 27BAIR | 115 | 227 | 0.8705 | 1.0066 | 0.92 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204521 | 27BAIR | 115 | 227 | 0.8727 | 1.0066 | 0.92 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204521 | 27BAIR | 115 | 227 | 0.9102 | 1.0066 | 0.92 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204520 | 27ALLEN | 115 | 227 | 0.9039 | 1.0246 | 0.92 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204520 | 27ALLEN | 115 | 227 | 0.9039 | 1.0246 | 0.92 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204520 | 27ALLEN | 115 | 227 | 0.904 | 1.0246 | 0.92 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204520 | 27ALLEN | 115 | 227 | 0.9075 | 1.0246 | 0.92 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 200522 | 26SHADE GP | 115 | 226 | 0.9051 | 0.9937 | 0.92 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 200522 | 26SHADE GP | 115 | 226 | 0.9051 | 0.9937 | 0.92 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 200522 | 26SHADE GP | 115 | 226 | 0.9051 | 0.9937 | 0.92 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 200522 | 26SHADE GP | 115 | 226 | 0.9079 | 0.9937 | 0.92 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 200508 | 26HILL VAL | 115 | 226 | 0.9003 | 0.9927 | 0.92 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 200508 | 26HILL VAL | 115 | 226 | 0.9003 | 0.9927 | 0.92 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 200508 | 26HILL VAL | 115 | 226 | 0.9004 | 0.9927 | 0.92 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 200508 | 26HILL VAL | 115 | 226 | 0.9033 | 0.9927 | 0.92 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 205953 | AE1-196_MAIN | 69 | 227 | 0.8866 | 1.0052 | 0.92 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 205953 | AE1-196_MAIN | 69 | 227 | 0.8867 | 1.0052 | 0.92 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 205953 | AE1-196_MAIN | 69 | 227 | 0.8867 | 1.0052 | 0.92 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 205953 | AE1-196_MAIN | 69 | 227 | 0.8886 | 1.0052 | 0.92 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 205952 | AE1-196_POI | 69 | 227 | 0.8863 | 1.0051 | 0.92 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 205952 | AE1-196_POI | 69 | 227 | 0.8863 | 1.0051 | 0.92 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 205952 | AE1-196_POI | 69 | 227 | 0.8864 | 1.0051 | 0.92 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 205952 | AE1-196_POI | 69 | 227 | 0.8883 | 1.0051 | 0.92 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 205943 | AE1-185 GEN | 69 | 227 | 0.8891 | 1.0098 | 0.92 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 205943 | AE1-185 GEN | 69 | 227 | 0.8891 | 1.0098 | 0.92 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 205943 | AE1-185 GEN | 69 | 227 | 0.8891 | 1.0098 | 0.92 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 205943 | AE1-185 GEN | 69 | 227 | 0.8912 | 1.0098 | 0.92 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 205942 | AE1-185 TAP | 69 | 227 | 0.889 | 1.0096 | 0.92 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 205942 | AE1-185 TAP | 69 | 227 | 0.889 | 1.0096 | 0.92 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 205942 | AE1-185 TAP | 69 | 227 | 0.889 | 1.0096 | 0.92 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 205942 | AE1-185 TAP | 69 | 227 | 0.891 | 1.0096 | 0.92 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 205936 | AD2-116_POI | 69 | 227 | 0.8844 | 1.0037 | 0.92 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 205936 | AD2-116_POI | 69 | 227 | 0.8844 | 1.0037 | 0.92 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 205936 | AD2-116_POI | 69 | 227 | 0.8844 | 1.0037 | 0.92 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 205936 | AD2-116_POI | 69 | 227 | 0.8863 | 1.0037 | 0.92 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 205935 | AD2-116_MAIN | 69 | 227 | 0.8846 | 1.0037 | 0.92 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 205935 | AD2-116_MAIN | 69 | 227 | 0.8846 | 1.0037 | 0.92 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 205935 | AD2-116_MAIN | 69 | 227 | 0.8847 | 1.0037 | 0.92 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 205935 | AD2-116_MAIN | 69 | 227 | 0.8865 | 1.0037 | 0.92 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204789 | 27BELLEVANS | 69 | 227 | 0.9023 | 0.9864 | 0.92 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204789 | 27BELLEVANS | 69 | 227 | 0.9023 | 0.9864 | 0.92 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204789 | 27BELLEVANS | 69 | 227 | 0.9023 | 0.9864 | 0.92 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204789 | 27BELLEVANS | 69 | 227 | 0.905 | 0.9864 | 0.92 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204788 | 27HERSHEYB | 69 | 227 | 0.8998 | 0.9869 | 0.92 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204788 | 27HERSHEYB | 69 | 227 | 0.8998 | 0.9869 | 0.92 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204788 | 27HERSHEYB | 69 | 227 | 0.8998 | 0.9869 | 0.92 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204788 | 27HERSHEYB | 69 | 227 | 0.9024 | 0.9869 | 0.92 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204787 | 27REHRERSBRG | 69 | 227 | 0.889 | 0.9707 | 0.92 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204787 | 27REHRERSBRG | 69 | 227 | 0.889 | 0.9707 | 0.92 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204787 | 27REHRERSBRG | 69 | 227 | 0.889 | 0.9707 | 0.92 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204787 | 27REHRERSBRG | 69 | 227 | 0.8916 | 0.9707 | 0.92 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204786 | 27REHRERBRG+ | 69 | 227 | 0.8936 | 0.9748 | 0.92 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204786 | 27REHRERBRG+ | 69 | 227 | 0.8936 | 0.9748 | 0.92 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204786 | 27REHRERBRG+ | 69 | 227 | 0.8936 | 0.9748 | 0.92 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204786 | 27REHRERBRG+ | 69 | 227 | 0.8961 | 0.9748 | 0.92 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204782 | 27W.LEB | 69 | 227 | 0.9141 | 0.994 | 0.92 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204782 | 27W.LEB | 69 | 227 | 0.9141 | 0.994 | 0.92 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204782 | 27W.LEB | 69 | 227 | 0.9141 | 0.994 | 0.92 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204782 | 27W.LEB | 69 | 227 | 0.9167 | 0.994 | 0.92 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204781 | 27TURFCLUB | 69 | 227 | 0.9196 | 1.0094 | 0.92 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204781 | 27TURFCLUB | 69 | 227 | 0.9196 | 1.0094 | 0.92 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204781 | 27TURFCLUB | 69 | 227 | 0.9196 | 1.0094 | 0.92 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204779 | 27SWAT HIL | 69 | 227 | 0.8974 | 0.9862 | 0.92 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204779 | 27SWAT HIL | 69 | 227 | 0.8974 | 0.9862 | 0.92 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204779 | 27SWAT HIL | 69 | 227 | 0.8974 | 0.9862 | 0.92 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204779 | 27SWAT HIL | 69 | 227 | 0.8998 | 0.9862 | 0.92 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204778 | 27STOUCHBG | 69 | 227 | 0.917 | 0.9967 | 0.92 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204778 | 27STOUCHBG | 69 | 227 | 0.9171 | 0.9967 | 0.92 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204778 | 27STOUCHBG | 69 | 227 | 0.9171 | 0.9967 | 0.92 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204778 | 27STOUCHBG | 69 | 227 | 0.9196 | 0.9967 | 0.92 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204777 | 27OLMSTED | 69 | 227 | 0.9023 | 0.9917 | 0.92 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204777 | 27OLMSTED | 69 | 227 | 0.9023 | 0.9917 | 0.92 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204777 | 27OLMSTED | 69 | 227 | 0.9023 | 0.9917 | 0.92 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204777 | 27OLMSTED | 69 | 227 | 0.9047 | 0.9917 | 0.92 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204776 | 27MYERSTWN | 69 | 227 | 0.9167 | 0.9961 | 0.92 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204776 | 27MYERSTWN | 69 | 227 | 0.9167 | 0.9961 | 0.92 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204776 | 27MYERSTWN | 69 | 227 | 0.9167 | 0.9961 | 0.92 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204776 | 27MYERSTWN | 69 | 227 | 0.9192 | 0.9961 | 0.92 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204775 | 27MILLARDS | 69 | 227 | 0.9005 | 0.9872 | 0.92 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204775 | 27MILLARDS | 69 | 227 | 0.9005 | 0.9872 | 0.92 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204775 | 27MILLARDS | 69 | 227 | 0.9005 | 0.9872 | 0.92 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204775 | 27MILLARDS | 69 | 227 | 0.9031 | 0.9872 | 0.92 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204774 | 27MILL ST | 69 | 227 | 0.9019 | 0.9916 | 0.92 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204774 | 27MILL ST | 69 | 227 | 0.902 | 0.9916 | 0.92 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204774 | 27MILL ST | 69 | 227 | 0.902 | 0.9916 | 0.92 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204774 | 27MILL ST | 69 | 227 | 0.9044 | 0.9916 | 0.92 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204773 | 27MIDDLETN | 69 | 227 | 0.9031 | 0.9926 | 0.92 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204773 | 27MIDDLETN | 69 | 227 | 0.9031 | 0.9926 | 0.92 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204773 | 27MIDDLETN | 69 | 227 | 0.9031 | 0.9926 | 0.92 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204773 | 27MIDDLETN | 69 | 227 | 0.9055 | 0.9926 | 0.92 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204772 | 27LICKDALE | 69 | 227 | 0.9046 | 0.9906 | 0.92 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204772 | 27LICKDALE | 69 | 227 | 0.9046 | 0.9906 | 0.92 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204772 | 27LICKDALE | 69 | 227 | 0.9047 | 0.9906 | 0.92 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204772 | 27LICKDALE | 69 | 227 | 0.9073 | 0.9906 | 0.92 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204769 | 27INDTNGAP | 69 | 227 | 0.9097 | 0.9974 | 0.92 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204769 | 27INDTNGAP | 69 | 227 | 0.9098 | 0.9974 | 0.92 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204769 | 27INDTNGAP | 69 | 227 | 0.9098 | 0.9974 | 0.92 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204769 | 27INDTNGAP | 69 | 227 | 0.9124 | 0.9974 | 0.92 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204768 | 27GRANTVLE | 69 | 227 | 0.9187 | 1.0089 | 0.92 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204768 | 27GRANTVLE | 69 | 227 | 0.9187 | 1.0089 | 0.92 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204768 | 27GRANTVLE | 69 | 227 | 0.9187 | 1.0089 | 0.92 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204766 | 27FRYSTOWN | 69 | 227 | 0.8925 | 0.9739 | 0.92 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204766 | 27FRYSTOWN | 69 | 227 | 0.8925 | 0.9739 | 0.92 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204766 | 27FRYSTOWN | 69 | 227 | 0.8925 | 0.9739 | 0.92 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204766 | 27FRYSTOWN | 69 | 227 | 0.8951 | 0.9739 | 0.92 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204765 | 27CLEONA | 69 | 227 | 0.9169 | 0.9967 | 0.92 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204765 | 27CLEONA | 69 | 227 | 0.9169 | 0.9967 | 0.92 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204765 | 27CLEONA | 69 | 227 | 0.9169 | 0.9967 | 0.92 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204765 | 27CLEONA | 69 | 227 | 0.9195 | 0.9967 | 0.92 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204764 | 27CMPBLTWN | 69 | 227 | 0.8992 | 0.9875 | 0.92 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204764 | 27CMPBLTWN | 69 | 227 | 0.8993 | 0.9875 | 0.92 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204764 | 27CMPBLTWN | 69 | 227 | 0.8993 | 0.9875 | 0.92 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204764 | 27CMPBLTWN | 69 | 227 | 0.9018 | 0.9875 | 0.92 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204763 | 27CAMP TAP | 69 | 227 | 0.9033 | 0.992 | 0.92 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204763 | 27CAMP TAP | 69 | 227 | 0.9034 | 0.992 | 0.92 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204763 | 27CAMP TAP | 69 | 227 | 0.9034 | 0.992 | 0.92 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204763 | 27CAMP TAP | 69 | 227 | 0.9059 | 0.992 | 0.92 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204762 | 27BAYER | 69 | 227 | 0.9175 | 0.9969 | 0.92 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204762 | 27BAYER | 69 | 227 | 0.9176 | 0.9969 | 0.92 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204762 | 27BAYER | 69 | 227 | 0.9176 | 0.9969 | 0.92 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204761 | 27BROAD ST | 69 | 227 | 0.9134 | 0.9933 | 0.92 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204761 | 27BROAD ST | 69 | 227 | 0.9135 | 0.9933 | 0.92 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204761 | 27BROAD ST | 69 | 227 | 0.9135 | 0.9933 | 0.92 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204761 | 27BROAD ST | 69 | 227 | 0.916 | 0.9933 | 0.92 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204760 | 27ANNVILLE | 69 | 227 | 0.9072 | 0.9911 | 0.92 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204760 | 27ANNVILLE | 69 | 227 | 0.9073 | 0.9911 | 0.92 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204760 | 27ANNVILLE | 69 | 227 | 0.9073 | 0.9911 | 0.92 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204760 | 27ANNVILLE | 69 | 227 | 0.9098 | 0.9911 | 0.92 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204759 | 27ALCOA | 69 | 227 | 0.918 | 0.9973 | 0.92 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204759 | 27ALCOA | 69 | 227 | 0.918 | 0.9973 | 0.92 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204759 | 27ALCOA | 69 | 227 | 0.918 | 0.9973 | 0.92 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204758 | 27WOOD ST | 69 | 227 | 0.9028 | 0.9923 | 0.92 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204758 | 27WOOD ST | 69 | 227 | 0.9028 | 0.9923 | 0.92 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204758 | 27WOOD ST | 69 | 227 | 0.9028 | 0.9923 | 0.92 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204758 | 27WOOD ST | 69 | 227 | 0.9052 | 0.9923 | 0.92 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204757 | 27WOODTP86 | 69 | 227 | 0.9029 | 0.9924 | 0.92 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204757 | 27WOODTP86 | 69 | 227 | 0.9029 | 0.9924 | 0.92 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204757 | 27WOODTP86 | 69 | 227 | 0.9029 | 0.9924 | 0.92 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204757 | 27WOODTP86 | 69 | 227 | 0.9053 | 0.9924 | 0.92 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204756 | 27WOODTP72 | 69 | 227 | 0.9029 | 0.9925 | 0.92 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204756 | 27WOODTP72 | 69 | 227 | 0.9029 | 0.9925 | 0.92 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204756 | 27WOODTP72 | 69 | 227 | 0.9029 | 0.9925 | 0.92 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204756 | 27WOODTP72 | 69 | 227 | 0.9053 | 0.9925 | 0.92 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204724 | 27LEHI CEM | 69 | 227 | 0.8843 | 1.0036 | 0.92 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204724 | 27LEHI CEM | 69 | 227 | 0.8843 | 1.0036 | 0.92 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204724 | 27LEHI CEM | 69 | 227 | 0.8843 | 1.0036 | 0.92 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204724 | 27LEHI CEM | 69 | 227 | 0.8862 | 1.0036 | 0.92 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204723 | 27HOKES | 69 | 227 | 0.8846 | 1.0039 | 0.92 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204723 | 27HOKES | 69 | 227 | 0.8846 | 1.0039 | 0.92 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204723 | 27HOKES | 69 | 227 | 0.8846 | 1.0039 | 0.92 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204723 | 27HOKES | 69 | 227 | 0.8865 | 1.0039 | 0.92 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204722 | 27GRANTLEY | 69 | 227 | 0.8753 | 0.998 | 0.92 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204722 | 27GRANTLEY | 69 | 227 | 0.8753 | 0.998 | 0.92 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204722 | 27GRANTLEY | 69 | 227 | 0.8753 | 0.998 | 0.92 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204722 | 27GRANTLEY | 69 | 227 | 0.8771 | 0.998 | 0.92 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204722 | 27GRANTLEY | 69 | 227 | 0.9165 | 0.998 | 0.92 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204721 | 27YORK INT | 69 | 227 | 0.8751 | 0.9978 | 0.92 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204721 | 27YORK INT | 69 | 227 | 0.8751 | 0.9978 | 0.92 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204721 | 27YORK INT | 69 | 227 | 0.8751 | 0.9978 | 0.92 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204721 | 27YORK INT | 69 | 227 | 0.8769 | 0.9978 | 0.92 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204721 | 27YORK INT | 69 | 227 | 0.9163 | 0.9978 | 0.92 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204712 | 27FREDRCKS | 69 | 227 | 0.9051 | 0.9889 | 0.92 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204712 | 27FREDRCKS | 69 | 227 | 0.9051 | 0.9889 | 0.92 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204712 | 27FREDRCKS | 69 | 227 | 0.9051 | 0.9889 | 0.92 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204712 | 27FREDRCKS | 69 | 227 | 0.9077 | 0.9889 | 0.92 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204708 | 27NCORNWAL | 69 | 227 | 0.9146 | 0.9943 | 0.92 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204708 | 27NCORNWAL | 69 | 227 | 0.9146 | 0.9943 | 0.92 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204708 | 27NCORNWAL | 69 | 227 | 0.9146 | 0.9943 | 0.92 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204708 | 27NCORNWAL | 69 | 227 | 0.9171 | 0.9943 | 0.92 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204602 | 27N.HERSHY | 69 | 227 | 0.9187 | 1.0091 | 0.92 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204602 | 27N.HERSHY | 69 | 227 | 0.9188 | 1.0091 | 0.92 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204602 | 27N.HERSHY | 69 | 227 | 0.9188 | 1.0091 | 0.92 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204601 | 27MIDD JCT | 69 | 227 | 0.9007 | 0.9895 | 0.92 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204601 | 27MIDD JCT | 69 | 227 | 0.9007 | 0.9895 | 0.92 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204601 | 27MIDD JCT | 69 | 227 | 0.9007 | 0.9895 | 0.92 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204601 | 27MIDD JCT | 69 | 227 | 0.903 | 0.9895 | 0.92 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204579 | 27VIOLET H | 69 | 227 | 0.8729 | 0.9974 | 0.92 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204579 | 27VIOLET H | 69 | 227 | 0.8729 | 0.9974 | 0.92 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204579 | 27VIOLET H | 69 | 227 | 0.8729 | 0.9974 | 0.92 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204579 | 27VIOLET H | 69 | 227 | 0.8746 | 0.9974 | 0.92 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204579 | 27VIOLET H | 69 | 227 | 0.914 | 0.9974 | 0.92 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204578 | 27SMITH ST | 69 | 227 | 0.8923 | 1.0134 | 0.92 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204578 | 27SMITH ST | 69 | 227 | 0.8923 | 1.0134 | 0.92 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204578 | 27SMITH ST | 69 | 227 | 0.8923 | 1.0134 | 0.92 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204578 | 27SMITH ST | 69 | 227 | 0.8944 | 1.0134 | 0.92 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204577 | 27JACKSON1 | 69 | 227 | 0.8873 | 1.0106 | 0.92 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204577 | 27JACKSON1 | 69 | 227 | 0.8873 | 1.0106 | 0.92 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204577 | 27JACKSON1 | 69 | 227 | 0.8873 | 1.0106 | 0.92 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204577 | 27JACKSON1 | 69 | 227 | 0.8895 | 1.0106 | 0.92 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 220978 | SNOW.R18 | 230 | 232 | 0.4419 | 1.0136 | 0.92 | Single | BG_P21:FROM:220941 H.RDGE16 230 220943 SNOW18TP 230 1 _SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 220978 | SNOW.R18 | 230 | 232 | 0.4481 | 1.0136 | 0.92 | Single | BG_P21:TO:220941 H.RDGE16 230 220943 SNOW18TP 230 1 _SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 220952 | W.LAKE8A | 230 | 232 | 0.4406 | 1.0131 | 0.92 | Single | BG_P21:FROM:220941 H.RDGE16 230 220943 SNOW18TP 230 1 _SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 220952 | W.LAKE8A | 230 | 232 | 0.4468 | 1.0131 | 0.92 | Single | BG_P21:TO:220941 H.RDGE16 230 220943 SNOW18TP 230 1 _SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 220948 | COLUMB18 | 230 | 232 | 0.4413 | 1.0136 | 0.92 | Single | BG_P21:FROM:220941 H.RDGE16 230 220943 SNOW18TP 230 1 _SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 220948 | COLUMB18 | 230 | 232 | 0.4475 | 1.0136 | 0.92 | Single | BG_P21:TO:220941 H.RDGE16 230 220943 SNOW18TP 230 1 _SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 220943 | SNOW18TP | 230 | 232 | 0.4415 | 1.0136 | 0.92 | Single | BG_P21:FROM:220941 H.RDGE16 230 220943 SNOW18TP 230 1 _SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 220943 | SNOW18TP | 230 | 232 | 0.4477 | 1.0136 | 0.92 | Single | BG_P21:TO:220941 H.RDGE16 230 220943 SNOW18TP 230 1 _SRT-A | NO | Related to 2022 Window 3, pending window outcome

## N-1 Volt Drop
Note | APS and Dominion zones as a whole are quarantined pending Window 3 outcome and are not included in above results
Related to 2022 Window 3, pending window outcome
PJM N-1 Voltage Drop Result (Winter 2028)
FG# | Bus # | Name | KV | Area | ContVolt | BaseVolt | Vdrop(%) | Cont Type | Contingency | PJM Accepting Proposals | Reasons for Exclusions | Comment
N/A | 200185 | HUNTECAP | 500 | 225 | 0.9539 | 1.0622 | 10.83 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 200185 | HUNTECAP | 500 | 225 | 0.954 | 1.0622 | 10.82 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 200185 | HUNTECAP | 500 | 225 | 0.954 | 1.0622 | 10.82 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 200185 | HUNTECAP | 500 | 225 | 0.9557 | 1.0622 | 10.65 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 200185 | HUNTECAP | 500 | 225 | 0.9776 | 1.0622 | 8.46 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 200184 | 3MILECAP | 500 | 225 | 0.9422 | 1.0683 | 12.61 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 200184 | 3MILECAP | 500 | 225 | 0.9455 | 1.0683 | 12.28 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 200184 | 3MILECAP | 500 | 225 | 0.9459 | 1.0683 | 12.24 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 200184 | 3MILECAP | 500 | 225 | 0.9459 | 1.0683 | 12.24 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 200184 | 3MILECAP | 500 | 225 | 0.998 | 1.0683 | 7.03 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 200102 | AA1-076 MAIN | 500 | 225 | 0.9964 | 1.0558 | 5.94 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 200102 | AA1-076 MAIN | 500 | 225 | 0.9965 | 1.0558 | 5.93 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 200102 | AA1-076 MAIN | 500 | 225 | 0.9965 | 1.0558 | 5.93 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 200102 | AA1-076 MAIN | 500 | 225 | 0.9967 | 1.0558 | 5.91 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 200101 | VINCO | 500 | 225 | 0.9961 | 1.056 | 5.99 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 200101 | VINCO | 500 | 225 | 0.9962 | 1.056 | 5.98 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 200101 | VINCO | 500 | 225 | 0.9962 | 1.056 | 5.98 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 200101 | VINCO | 500 | 225 | 0.9965 | 1.056 | 5.95 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 200100 | CNASTCAP | 500 | 225 | 0.9911 | 1.0542 | 6.31 | Single | 200004 CNASTONE 500 _SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 200099 | LAUS | 500 | 225 | 0.9539 | 1.0679 | 11.4 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 200099 | LAUS | 500 | 225 | 0.9574 | 1.0679 | 11.05 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 200099 | LAUS | 500 | 225 | 0.9577 | 1.0679 | 11.02 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 200099 | LAUS | 500 | 225 | 0.9577 | 1.0679 | 11.02 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 200099 | LAUS | 500 | 225 | 1.0044 | 1.0679 | 6.35 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 200075 | BREI | 500 | 225 | 1.021 | 1.0734 | 5.24 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 200075 | BREI | 500 | 225 | 1.0227 | 1.0734 | 5.07 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 200075 | BREI | 500 | 225 | 1.0229 | 1.0734 | 5.05 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 200075 | BREI | 500 | 225 | 1.0229 | 1.0734 | 5.05 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 200026 | HUNTERTN | 500 | 225 | 0.9519 | 1.06 | 10.81 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 200026 | HUNTERTN | 500 | 225 | 0.952 | 1.06 | 10.8 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 200026 | HUNTERTN | 500 | 225 | 0.952 | 1.06 | 10.8 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 200026 | HUNTERTN | 500 | 225 | 0.9538 | 1.06 | 10.62 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 200026 | HUNTERTN | 500 | 225 | 0.9756 | 1.06 | 8.44 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 200016 | 3 MILE I | 500 | 225 | 0.9397 | 1.0655 | 12.58 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 200016 | 3 MILE I | 500 | 225 | 0.943 | 1.0655 | 12.25 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 200016 | 3 MILE I | 500 | 225 | 0.9434 | 1.0655 | 12.21 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 200016 | 3 MILE I | 500 | 225 | 0.9434 | 1.0655 | 12.21 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 200016 | 3 MILE I | 500 | 225 | 0.9953 | 1.0655 | 7.02 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 200009 | JUNI | 500 | 225 | 0.9729 | 1.0687 | 9.58 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 200009 | JUNI | 500 | 225 | 0.9755 | 1.0687 | 9.32 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 200009 | JUNI | 500 | 225 | 0.9757 | 1.0687 | 9.3 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 200009 | JUNI | 500 | 225 | 0.9757 | 1.0687 | 9.3 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 200009 | JUNI | 500 | 225 | 1.016 | 1.0687 | 5.27 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 200008 | HOSE | 500 | 225 | 1.0173 | 1.0723 | 5.5 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 200008 | HOSE | 500 | 225 | 1.0191 | 1.0723 | 5.32 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 200008 | HOSE | 500 | 225 | 1.0192 | 1.0723 | 5.31 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 200008 | HOSE | 500 | 225 | 1.0192 | 1.0723 | 5.31 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 500 | 225 | 0.9872 | 1.05 | 6.28 | Single | 200004 CNASTONE 500 _SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 200001 | ALBU | 500 | 225 | 1.02 | 1.0742 | 5.42 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 200001 | ALBU | 500 | 225 | 1.0218 | 1.0742 | 5.24 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 200001 | ALBU | 500 | 225 | 1.022 | 1.0742 | 5.22 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 200001 | ALBU | 500 | 225 | 1.022 | 1.0742 | 5.22 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 231008 | CRST230 | 230 | 235 | 0.8949 | 1.0174 | 12.25 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 231008 | CRST230 | 230 | 235 | 0.901 | 1.0174 | 11.64 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 231008 | CRST230 | 230 | 235 | 0.9013 | 1.0174 | 11.61 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 231008 | CRST230 | 230 | 235 | 0.9014 | 1.0174 | 11.6 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 231007 | CECIL | 230 | 235 | 0.9067 | 1.0181 | 11.14 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 231007 | CECIL | 230 | 235 | 0.912 | 1.0181 | 10.61 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 231007 | CECIL | 230 | 235 | 0.9124 | 1.0181 | 10.57 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 231007 | CECIL | 230 | 235 | 0.9124 | 1.0181 | 10.57 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 231006 | COLOR_PE | 230 | 235 | 0.8862 | 1.0174 | 13.12 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 231006 | COLOR_PE | 230 | 235 | 0.8928 | 1.0174 | 12.46 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 231006 | COLOR_PE | 230 | 235 | 0.8932 | 1.0174 | 12.42 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 231006 | COLOR_PE | 230 | 235 | 0.8932 | 1.0174 | 12.42 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 214344 | DALEVLLE | 230 | 230 | 0.8989 | 1.0198 | 12.09 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 214344 | DALEVLLE | 230 | 230 | 0.9044 | 1.0198 | 11.54 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 214344 | DALEVLLE | 230 | 230 | 0.9048 | 1.0198 | 11.5 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 214344 | DALEVLLE | 230 | 230 | 0.9048 | 1.0198 | 11.5 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 214219 | NOTTNGH3 | 230 | 230 | 0.8732 | 1.0198 | 14.66 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 214219 | NOTTNGH3 | 230 | 230 | 0.8803 | 1.0198 | 13.95 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 214219 | NOTTNGH3 | 230 | 230 | 0.8807 | 1.0198 | 13.91 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 214219 | NOTTNGH3 | 230 | 230 | 0.8807 | 1.0198 | 13.91 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 214219 | NOTTNGH3 | 230 | 230 | 0.9435 | 1.0198 | 7.63 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 214218 | NOTTNGH2 | 230 | 230 | 0.8731 | 1.0199 | 14.68 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 214218 | NOTTNGH2 | 230 | 230 | 0.8802 | 1.0199 | 13.97 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 214218 | NOTTNGH2 | 230 | 230 | 0.8806 | 1.0199 | 13.93 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 214218 | NOTTNGH2 | 230 | 230 | 0.8806 | 1.0199 | 13.93 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 214218 | NOTTNGH2 | 230 | 230 | 0.9435 | 1.0199 | 7.64 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 214103 | BRADFRDM | 230 | 230 | 0.9456 | 1.0224 | 7.68 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 214103 | BRADFRDM | 230 | 230 | 0.9487 | 1.0224 | 7.37 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 214103 | BRADFRDM | 230 | 230 | 0.949 | 1.0224 | 7.34 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 214103 | BRADFRDM | 230 | 230 | 0.949 | 1.0224 | 7.34 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 214087 | COOPER2 | 230 | 230 | 0.8646 | 0.9944 | 12.98 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 214087 | COOPER2 | 230 | 230 | 0.8697 | 0.9944 | 12.47 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 214087 | COOPER2 | 230 | 230 | 0.8699 | 0.9944 | 12.45 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 214087 | COOPER2 | 230 | 230 | 0.8699 | 0.9944 | 12.45 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 214087 | COOPER2 | 230 | 230 | 0.9135 | 0.9944 | 8.09 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 230 | 230 | 0.8656 | 0.9945 | 12.89 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 230 | 230 | 0.8705 | 0.9945 | 12.4 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 230 | 230 | 0.8708 | 0.9945 | 12.37 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 230 | 230 | 0.8708 | 0.9945 | 12.37 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 230 | 230 | 0.9141 | 0.9945 | 8.04 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 230 | 230 | 0.8491 | 0.9942 | 14.51 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 230 | 230 | 0.8548 | 0.9942 | 13.94 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 230 | 230 | 0.855 | 0.9942 | 13.92 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 230 | 230 | 0.855 | 0.9942 | 13.92 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 230 | 230 | 0.904 | 0.9942 | 9.02 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 230 | 230 | 0.7771 | 1.0026 | 22.55 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 230 | 230 | 0.7869 | 1.0026 | 21.57 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 230 | 230 | 0.7874 | 1.0026 | 21.52 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 230 | 230 | 0.7874 | 1.0026 | 21.52 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 230 | 230 | 0.8686 | 1.0026 | 13.4 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 230 | 230 | 0.873 | 1.02 | 14.7 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 230 | 230 | 0.8801 | 1.02 | 13.99 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 230 | 230 | 0.8805 | 1.02 | 13.95 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 230 | 230 | 0.8805 | 1.02 | 13.95 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 230 | 230 | 0.9434 | 1.02 | 7.66 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 213838 | NEWLNVL3 | 230 | 230 | 0.9502 | 1.0294 | 7.92 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 213838 | NEWLNVL3 | 230 | 230 | 0.9531 | 1.0294 | 7.63 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 213838 | NEWLNVL3 | 230 | 230 | 0.9535 | 1.0294 | 7.59 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 213838 | NEWLNVL3 | 230 | 230 | 0.9535 | 1.0294 | 7.59 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 213834 | NEWLNVIL | 230 | 230 | 0.9503 | 1.0294 | 7.91 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 213834 | NEWLNVIL | 230 | 230 | 0.9533 | 1.0294 | 7.61 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 213834 | NEWLNVIL | 230 | 230 | 0.9536 | 1.0294 | 7.58 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 213834 | NEWLNVIL | 230 | 230 | 0.9536 | 1.0294 | 7.58 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 213833 | NEWLNVI2 | 230 | 230 | 0.9503 | 1.0294 | 7.91 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 213833 | NEWLNVI2 | 230 | 230 | 0.9533 | 1.0294 | 7.61 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 213833 | NEWLNVI2 | 230 | 230 | 0.9536 | 1.0294 | 7.58 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 213833 | NEWLNVI2 | 230 | 230 | 0.9536 | 1.0294 | 7.58 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 213683 | JENNTAP | 230 | 230 | 0.9026 | 1.0181 | 11.55 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 213683 | JENNTAP | 230 | 230 | 0.9078 | 1.0181 | 11.03 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 213683 | JENNTAP | 230 | 230 | 0.9081 | 1.0181 | 11 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 213683 | JENNTAP | 230 | 230 | 0.9081 | 1.0181 | 11 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 213553 | 220-05 TAP | 230 | 230 | 0.899 | 1.0198 | 12.08 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 213553 | 220-05 TAP | 230 | 230 | 0.9044 | 1.0198 | 11.54 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 213553 | 220-05 TAP | 230 | 230 | 0.9048 | 1.0198 | 11.5 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 213553 | 220-05 TAP | 230 | 230 | 0.9048 | 1.0198 | 11.5 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 213520 | CONOWG03 | 230 | 230 | 0.8882 | 1.0174 | 12.92 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 213520 | CONOWG03 | 230 | 230 | 0.8951 | 1.0174 | 12.23 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 213520 | CONOWG03 | 230 | 230 | 0.8955 | 1.0174 | 12.19 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 213520 | CONOWG03 | 230 | 230 | 0.8955 | 1.0174 | 12.19 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 213519 | CONOWG01 | 230 | 230 | 0.8883 | 1.0174 | 12.91 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 213519 | CONOWG01 | 230 | 230 | 0.8952 | 1.0174 | 12.22 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 213519 | CONOWG01 | 230 | 230 | 0.8956 | 1.0174 | 12.18 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 213519 | CONOWG01 | 230 | 230 | 0.8956 | 1.0174 | 12.18 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 213505 | COCHRNVL | 230 | 230 | 0.9429 | 1.0236 | 8.07 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 213505 | COCHRNVL | 230 | 230 | 0.9455 | 1.0236 | 7.81 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 213505 | COCHRNVL | 230 | 230 | 0.9459 | 1.0236 | 7.77 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 213505 | COCHRNVL | 230 | 230 | 0.9459 | 1.0236 | 7.77 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 213502 | CLAY TAP | 230 | 230 | 0.9085 | 1.0188 | 11.03 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 213502 | CLAY TAP | 230 | 230 | 0.9134 | 1.0188 | 10.54 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 213502 | CLAY TAP | 230 | 230 | 0.9138 | 1.0188 | 10.5 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 213502 | CLAY TAP | 230 | 230 | 0.9138 | 1.0188 | 10.5 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 213500 | CLAYNEW | 230 | 230 | 0.895 | 1.0176 | 12.26 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 213500 | CLAYNEW | 230 | 230 | 0.9006 | 1.0176 | 11.7 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 213500 | CLAYNEW | 230 | 230 | 0.9009 | 1.0176 | 11.67 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 213500 | CLAYNEW | 230 | 230 | 0.901 | 1.0176 | 11.66 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 213498 | CLAY | 230 | 230 | 0.8951 | 1.0175 | 12.24 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 213498 | CLAY | 230 | 230 | 0.9006 | 1.0175 | 11.69 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 213498 | CLAY | 230 | 230 | 0.901 | 1.0175 | 11.65 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 213498 | CLAY | 230 | 230 | 0.901 | 1.0175 | 11.65 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 213440 | BRADFRD2 | 230 | 230 | 0.9455 | 1.0224 | 7.69 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 213440 | BRADFRD2 | 230 | 230 | 0.9486 | 1.0224 | 7.38 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 213440 | BRADFRD2 | 230 | 230 | 0.9489 | 1.0224 | 7.35 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 213440 | BRADFRD2 | 230 | 230 | 0.9489 | 1.0224 | 7.35 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 213438 | BRADFRD1 | 230 | 230 | 0.9456 | 1.0224 | 7.68 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 213438 | BRADFRD1 | 230 | 230 | 0.9487 | 1.0224 | 7.37 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 213438 | BRADFRD1 | 230 | 230 | 0.949 | 1.0224 | 7.34 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 213438 | BRADFRD1 | 230 | 230 | 0.949 | 1.0224 | 7.34 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 213437 | BRADFR13 | 230 | 230 | 0.9456 | 1.0224 | 7.68 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 213437 | BRADFR13 | 230 | 230 | 0.9487 | 1.0224 | 7.37 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 213437 | BRADFR13 | 230 | 230 | 0.949 | 1.0224 | 7.34 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 213437 | BRADFR13 | 230 | 230 | 0.949 | 1.0224 | 7.34 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 213436 | BRADFR12 | 230 | 230 | 0.9457 | 1.0224 | 7.67 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 213436 | BRADFR12 | 230 | 230 | 0.9488 | 1.0224 | 7.36 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 213436 | BRADFR12 | 230 | 230 | 0.9491 | 1.0224 | 7.33 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 213436 | BRADFR12 | 230 | 230 | 0.9491 | 1.0224 | 7.33 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208141 | WIGR | 230 | 229 | 0.8024 | 1.0229 | 22.05 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208141 | WIGR | 230 | 229 | 0.8098 | 1.0229 | 21.31 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208141 | WIGR | 230 | 229 | 0.8102 | 1.0229 | 21.27 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208141 | WIGR | 230 | 229 | 0.8102 | 1.0229 | 21.27 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208141 | WIGR | 230 | 229 | 0.8995 | 1.0229 | 12.34 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208136 | WSHO | 230 | 229 | 0.8006 | 1.0241 | 22.35 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208136 | WSHO | 230 | 229 | 0.8083 | 1.0241 | 21.58 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208136 | WSHO | 230 | 229 | 0.8087 | 1.0241 | 21.54 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208136 | WSHO | 230 | 229 | 0.8087 | 1.0241 | 21.54 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208136 | WSHO | 230 | 229 | 0.8997 | 1.0241 | 12.44 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208133 | WHEM TR2 | 230 | 229 | 0.838 | 1.0223 | 18.43 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208133 | WHEM TR2 | 230 | 229 | 0.8478 | 1.0223 | 17.45 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208133 | WHEM TR2 | 230 | 229 | 0.8482 | 1.0223 | 17.41 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208133 | WHEM TR2 | 230 | 229 | 0.8482 | 1.0223 | 17.41 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208133 | WHEM TR2 | 230 | 229 | 0.9286 | 1.0223 | 9.37 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208132 | WHEM TR1 | 230 | 229 | 0.8372 | 1.0222 | 18.5 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208132 | WHEM TR1 | 230 | 229 | 0.8471 | 1.0222 | 17.51 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208132 | WHEM TR1 | 230 | 229 | 0.8474 | 1.0222 | 17.48 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208132 | WHEM TR1 | 230 | 229 | 0.8474 | 1.0222 | 17.48 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208132 | WHEM TR1 | 230 | 229 | 0.928 | 1.0222 | 9.42 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208131 | WHEM | 230 | 229 | 0.8376 | 1.0223 | 18.47 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208131 | WHEM | 230 | 229 | 0.8475 | 1.0223 | 17.48 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208131 | WHEM | 230 | 229 | 0.8478 | 1.0223 | 17.45 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208131 | WHEM | 230 | 229 | 0.8478 | 1.0223 | 17.45 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208131 | WHEM | 230 | 229 | 0.9283 | 1.0223 | 9.4 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208128 | WESC | 230 | 229 | 0.9415 | 1.0335 | 9.2 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208128 | WESC | 230 | 229 | 0.9453 | 1.0335 | 8.82 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208128 | WESC | 230 | 229 | 0.9456 | 1.0335 | 8.79 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208128 | WESC | 230 | 229 | 0.9456 | 1.0335 | 8.79 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208106 | STEE TR3 | 230 | 229 | 0.8056 | 1.0252 | 21.96 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208106 | STEE TR3 | 230 | 229 | 0.8131 | 1.0252 | 21.21 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208106 | STEE TR3 | 230 | 229 | 0.8135 | 1.0252 | 21.17 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208106 | STEE TR3 | 230 | 229 | 0.8135 | 1.0252 | 21.17 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208106 | STEE TR3 | 230 | 229 | 0.904 | 1.0252 | 12.12 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208105 | STEE TR1 | 230 | 229 | 0.8056 | 1.0252 | 21.96 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208105 | STEE TR1 | 230 | 229 | 0.8131 | 1.0252 | 21.21 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208105 | STEE TR1 | 230 | 229 | 0.8135 | 1.0252 | 21.17 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208105 | STEE TR1 | 230 | 229 | 0.8136 | 1.0252 | 21.16 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208105 | STEE TR1 | 230 | 229 | 0.9041 | 1.0252 | 12.11 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208104 | STEE | 230 | 229 | 0.8056 | 1.0252 | 21.96 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208104 | STEE | 230 | 229 | 0.8131 | 1.0252 | 21.21 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208104 | STEE | 230 | 229 | 0.8135 | 1.0252 | 21.17 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208104 | STEE | 230 | 229 | 0.8136 | 1.0252 | 21.16 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208104 | STEE | 230 | 229 | 0.9041 | 1.0252 | 12.11 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208088 | SMAN TR4 | 230 | 229 | 0.7888 | 1.0196 | 23.08 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208088 | SMAN TR4 | 230 | 229 | 0.7978 | 1.0196 | 22.18 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208088 | SMAN TR4 | 230 | 229 | 0.7982 | 1.0196 | 22.14 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208088 | SMAN TR4 | 230 | 229 | 0.7982 | 1.0196 | 22.14 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208088 | SMAN TR4 | 230 | 229 | 0.8929 | 1.0196 | 12.67 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208087 | SMAN TR3 | 230 | 229 | 0.7888 | 1.0196 | 23.08 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208087 | SMAN TR3 | 230 | 229 | 0.7978 | 1.0196 | 22.18 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208087 | SMAN TR3 | 230 | 229 | 0.7982 | 1.0196 | 22.14 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208087 | SMAN TR3 | 230 | 229 | 0.7982 | 1.0196 | 22.14 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208087 | SMAN TR3 | 230 | 229 | 0.8929 | 1.0196 | 12.67 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208083 | SAKRCAPB | 230 | 229 | 0.7945 | 1.0187 | 22.42 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208083 | SAKRCAPB | 230 | 229 | 0.8038 | 1.0187 | 21.49 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208083 | SAKRCAPB | 230 | 229 | 0.8042 | 1.0187 | 21.45 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208083 | SAKRCAPB | 230 | 229 | 0.8042 | 1.0187 | 21.45 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208083 | SAKRCAPB | 230 | 229 | 0.8969 | 1.0187 | 12.18 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208082 | SAKRCAPA | 230 | 229 | 0.7946 | 1.0188 | 22.42 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208082 | SAKRCAPA | 230 | 229 | 0.8039 | 1.0188 | 21.49 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208082 | SAKRCAPA | 230 | 229 | 0.8043 | 1.0188 | 21.45 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208082 | SAKRCAPA | 230 | 229 | 0.8043 | 1.0188 | 21.45 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208082 | SAKRCAPA | 230 | 229 | 0.897 | 1.0188 | 12.18 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208078 | SAKR | 230 | 229 | 0.7945 | 1.0187 | 22.42 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208078 | SAKR | 230 | 229 | 0.8038 | 1.0187 | 21.49 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208078 | SAKR | 230 | 229 | 0.8042 | 1.0187 | 21.45 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208078 | SAKR | 230 | 229 | 0.8042 | 1.0187 | 21.45 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208078 | SAKR | 230 | 229 | 0.8969 | 1.0187 | 12.18 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 230 | 229 | 0.8819 | 1.0199 | 13.8 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 230 | 229 | 0.8901 | 1.0199 | 12.98 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 230 | 229 | 0.8904 | 1.0199 | 12.95 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 230 | 229 | 0.8904 | 1.0199 | 12.95 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208070 | SAHA12TP | 230 | 229 | 0.8816 | 1.0199 | 13.83 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208070 | SAHA12TP | 230 | 229 | 0.8899 | 1.0199 | 13 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208070 | SAHA12TP | 230 | 229 | 0.8901 | 1.0199 | 12.98 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208070 | SAHA12TP | 230 | 229 | 0.8902 | 1.0199 | 12.97 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208067 | SAHA0304 | 230 | 229 | 0.882 | 1.0198 | 13.78 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208067 | SAHA0304 | 230 | 229 | 0.8903 | 1.0198 | 12.95 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208067 | SAHA0304 | 230 | 229 | 0.8906 | 1.0198 | 12.92 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208067 | SAHA0304 | 230 | 229 | 0.8906 | 1.0198 | 12.92 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208066 | SAHA0102 | 230 | 229 | 0.8821 | 1.0198 | 13.77 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208066 | SAHA0102 | 230 | 229 | 0.8904 | 1.0198 | 12.94 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208066 | SAHA0102 | 230 | 229 | 0.8906 | 1.0198 | 12.92 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208066 | SAHA0102 | 230 | 229 | 0.8907 | 1.0198 | 12.91 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 230 | 229 | 0.8559 | 1.0169 | 16.1 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 230 | 229 | 0.8641 | 1.0169 | 15.28 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 230 | 229 | 0.8644 | 1.0169 | 15.25 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 230 | 229 | 0.8644 | 1.0169 | 15.25 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 230 | 229 | 0.9284 | 1.0169 | 8.85 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208045 | LAUS | 230 | 229 | 0.8244 | 1.0128 | 18.84 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208045 | LAUS | 230 | 229 | 0.832 | 1.0128 | 18.08 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208045 | LAUS | 230 | 229 | 0.8324 | 1.0128 | 18.04 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208045 | LAUS | 230 | 229 | 0.8324 | 1.0128 | 18.04 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208045 | LAUS | 230 | 229 | 0.9131 | 1.0128 | 9.97 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208031 | MLWD TR2 | 230 | 229 | 0.846 | 1.017 | 17.1 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208031 | MLWD TR2 | 230 | 229 | 0.8553 | 1.017 | 16.17 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208031 | MLWD TR2 | 230 | 229 | 0.8556 | 1.017 | 16.14 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208031 | MLWD TR2 | 230 | 229 | 0.8556 | 1.017 | 16.14 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208031 | MLWD TR2 | 230 | 229 | 0.9305 | 1.017 | 8.65 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 230 | 229 | 0.8454 | 1.0169 | 17.15 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 230 | 229 | 0.8547 | 1.0169 | 16.22 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 230 | 229 | 0.855 | 1.0169 | 16.19 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 230 | 229 | 0.855 | 1.0169 | 16.19 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 230 | 229 | 0.9301 | 1.0169 | 8.68 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208021 | MANO TR4 | 230 | 229 | 0.8814 | 1.02 | 13.86 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208021 | MANO TR4 | 230 | 229 | 0.8897 | 1.02 | 13.03 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208021 | MANO TR4 | 230 | 229 | 0.8899 | 1.02 | 13.01 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208021 | MANO TR4 | 230 | 229 | 0.8899 | 1.02 | 13.01 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208020 | MANO TR3 | 230 | 229 | 0.8812 | 1.0199 | 13.87 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208020 | MANO TR3 | 230 | 229 | 0.8895 | 1.0199 | 13.04 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208020 | MANO TR3 | 230 | 229 | 0.8897 | 1.0199 | 13.02 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208020 | MANO TR3 | 230 | 229 | 0.8897 | 1.0199 | 13.02 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 230 | 229 | 0.8818 | 1.02 | 13.82 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 230 | 229 | 0.8901 | 1.02 | 12.99 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 230 | 229 | 0.8903 | 1.02 | 12.97 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 230 | 229 | 0.8903 | 1.02 | 12.97 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208004 | JUNI | 230 | 229 | 0.8857 | 1.026 | 14.03 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208004 | JUNI | 230 | 229 | 0.8899 | 1.026 | 13.61 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208004 | JUNI | 230 | 229 | 0.8902 | 1.026 | 13.58 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208004 | JUNI | 230 | 229 | 0.8902 | 1.026 | 13.58 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 207990 | HUMMTPST | 230 | 229 | 0.809 | 1.0253 | 21.63 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 207990 | HUMMTPST | 230 | 229 | 0.8165 | 1.0253 | 20.88 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 207990 | HUMMTPST | 230 | 229 | 0.8169 | 1.0253 | 20.84 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 207990 | HUMMTPST | 230 | 229 | 0.8169 | 1.0253 | 20.84 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 207990 | HUMMTPST | 230 | 229 | 0.9068 | 1.0253 | 11.85 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 207988 | HUMM TR2 | 230 | 229 | 0.8094 | 1.0252 | 21.58 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 207988 | HUMM TR2 | 230 | 229 | 0.8168 | 1.0252 | 20.84 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 207988 | HUMM TR2 | 230 | 229 | 0.8172 | 1.0252 | 20.8 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 207988 | HUMM TR2 | 230 | 229 | 0.8172 | 1.0252 | 20.8 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 207988 | HUMM TR2 | 230 | 229 | 0.907 | 1.0252 | 11.82 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 207987 | HUMM | 230 | 229 | 0.8091 | 1.0253 | 21.62 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 207987 | HUMM | 230 | 229 | 0.8166 | 1.0253 | 20.87 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 207987 | HUMM | 230 | 229 | 0.817 | 1.0253 | 20.83 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 207987 | HUMM | 230 | 229 | 0.817 | 1.0253 | 20.83 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 207987 | HUMM | 230 | 229 | 0.9068 | 1.0253 | 11.85 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 207983 | HOSE | 230 | 229 | 0.9413 | 1.0333 | 9.2 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 207983 | HOSE | 230 | 229 | 0.9451 | 1.0333 | 8.82 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 207983 | HOSE | 230 | 229 | 0.9454 | 1.0333 | 8.79 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 207983 | HOSE | 230 | 229 | 0.9454 | 1.0333 | 8.79 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 207955 | DAUP TR2 | 230 | 229 | 0.8303 | 1.0197 | 18.94 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 207955 | DAUP TR2 | 230 | 229 | 0.8366 | 1.0197 | 18.31 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 207955 | DAUP TR2 | 230 | 229 | 0.837 | 1.0197 | 18.27 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 207955 | DAUP TR2 | 230 | 229 | 0.837 | 1.0197 | 18.27 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 207955 | DAUP TR2 | 230 | 229 | 0.9153 | 1.0197 | 10.44 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 207953 | DAUP TR1 | 230 | 229 | 0.8302 | 1.0197 | 18.95 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 207953 | DAUP TR1 | 230 | 229 | 0.8365 | 1.0197 | 18.32 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 207953 | DAUP TR1 | 230 | 229 | 0.8369 | 1.0197 | 18.28 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 207953 | DAUP TR1 | 230 | 229 | 0.8369 | 1.0197 | 18.28 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 207953 | DAUP TR1 | 230 | 229 | 0.9153 | 1.0197 | 10.44 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 207950 | CUMB | 230 | 229 | 0.8209 | 1.0205 | 19.96 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 207950 | CUMB | 230 | 229 | 0.8274 | 1.0205 | 19.31 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 207950 | CUMB | 230 | 229 | 0.8278 | 1.0205 | 19.27 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 207950 | CUMB | 230 | 229 | 0.8278 | 1.0205 | 19.27 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 207950 | CUMB | 230 | 229 | 0.9083 | 1.0205 | 11.22 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 207944 | COPP | 230 | 229 | 0.8127 | 1.0244 | 21.17 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 207944 | COPP | 230 | 229 | 0.8201 | 1.0244 | 20.43 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 207944 | COPP | 230 | 229 | 0.8205 | 1.0244 | 20.39 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 207944 | COPP | 230 | 229 | 0.8205 | 1.0244 | 20.39 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 207944 | COPP | 230 | 229 | 0.9091 | 1.0244 | 11.53 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 207923 | BRISREAC | 230 | 229 | 0.8046 | 1.0292 | 22.46 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 207923 | BRISREAC | 230 | 229 | 0.8148 | 1.0292 | 21.44 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 207923 | BRISREAC | 230 | 229 | 0.8152 | 1.0292 | 21.4 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 207923 | BRISREAC | 230 | 229 | 0.8152 | 1.0292 | 21.4 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 207923 | BRISREAC | 230 | 229 | 0.9086 | 1.0292 | 12.06 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 207922 | BRIS | 230 | 229 | 0.7993 | 1.0304 | 23.11 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 207922 | BRIS | 230 | 229 | 0.808 | 1.0304 | 22.24 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 207922 | BRIS | 230 | 229 | 0.8084 | 1.0304 | 22.2 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 207922 | BRIS | 230 | 229 | 0.8084 | 1.0304 | 22.2 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 207922 | BRIS | 230 | 229 | 0.9024 | 1.0304 | 12.8 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 207903 | BERK | 230 | 229 | 0.831 | 1.0131 | 18.21 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 207903 | BERK | 230 | 229 | 0.8385 | 1.0131 | 17.46 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 207903 | BERK | 230 | 229 | 0.8389 | 1.0131 | 17.42 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 207903 | BERK | 230 | 229 | 0.8389 | 1.0131 | 17.42 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 207903 | BERK | 230 | 229 | 0.9197 | 1.0131 | 9.34 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 205903 | AA2-115 MAIN | 230 | 227 | 0.9006 | 1.0242 | 12.36 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 205903 | AA2-115 MAIN | 230 | 227 | 0.907 | 1.0242 | 11.72 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 205903 | AA2-115 MAIN | 230 | 227 | 0.9074 | 1.0242 | 11.68 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 205903 | AA2-115 MAIN | 230 | 227 | 0.9074 | 1.0242 | 11.68 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204875 | 27NORTHKIL | 230 | 227 | 0.8702 | 1.0241 | 15.39 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204875 | 27NORTHKIL | 230 | 227 | 0.8766 | 1.0241 | 14.75 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204875 | 27NORTHKIL | 230 | 227 | 0.877 | 1.0241 | 14.71 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204875 | 27NORTHKIL | 230 | 227 | 0.877 | 1.0241 | 14.71 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204709 | 27MIDDJCT8 | 230 | 227 | 0.8045 | 1.0265 | 22.2 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204709 | 27MIDDJCT8 | 230 | 227 | 0.8121 | 1.0265 | 21.44 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204709 | 27MIDDJCT8 | 230 | 227 | 0.8125 | 1.0265 | 21.4 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204709 | 27MIDDJCT8 | 230 | 227 | 0.8125 | 1.0265 | 21.4 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204709 | 27MIDDJCT8 | 230 | 227 | 0.9032 | 1.0265 | 12.33 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204693 | 27BOONETOWN | 230 | 227 | 0.8728 | 1.0088 | 13.6 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204693 | 27BOONETOWN | 230 | 227 | 0.8793 | 1.0088 | 12.95 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204693 | 27BOONETOWN | 230 | 227 | 0.8797 | 1.0088 | 12.91 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204693 | 27BOONETOWN | 230 | 227 | 0.8797 | 1.0088 | 12.91 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204692 | 27WILLOWDR | 230 | 227 | 0.8079 | 1.0256 | 21.77 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204692 | 27WILLOWDR | 230 | 227 | 0.8154 | 1.0256 | 21.02 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204692 | 27WILLOWDR | 230 | 227 | 0.8158 | 1.0256 | 20.98 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204692 | 27WILLOWDR | 230 | 227 | 0.8158 | 1.0256 | 20.98 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204692 | 27WILLOWDR | 230 | 227 | 0.9056 | 1.0256 | 12 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204686 | 27HOSNSACK | 230 | 227 | 0.9413 | 1.0333 | 9.2 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204686 | 27HOSNSACK | 230 | 227 | 0.9451 | 1.0333 | 8.82 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204686 | 27HOSNSACK | 230 | 227 | 0.9454 | 1.0333 | 8.79 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204686 | 27HOSNSACK | 230 | 227 | 0.9454 | 1.0333 | 8.79 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204685 | 27ALBURTIS | 230 | 227 | 0.9471 | 1.0357 | 8.86 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204685 | 27ALBURTIS | 230 | 227 | 0.9507 | 1.0357 | 8.5 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204685 | 27ALBURTIS | 230 | 227 | 0.9509 | 1.0357 | 8.48 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204685 | 27ALBURTIS | 230 | 227 | 0.9509 | 1.0357 | 8.48 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204575 | 27HUNTRST1 | 230 | 227 | 0.8217 | 1.0214 | 19.97 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204575 | 27HUNTRST1 | 230 | 227 | 0.826 | 1.0214 | 19.54 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204575 | 27HUNTRST1 | 230 | 227 | 0.8263 | 1.0214 | 19.51 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204575 | 27HUNTRST1 | 230 | 227 | 0.8263 | 1.0214 | 19.51 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204575 | 27HUNTRST1 | 230 | 227 | 0.9017 | 1.0214 | 11.97 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204519 | 27ONTELAUE | 230 | 227 | 0.8972 | 1.03 | 13.28 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204519 | 27ONTELAUE | 230 | 227 | 0.903 | 1.03 | 12.7 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204519 | 27ONTELAUE | 230 | 227 | 0.9033 | 1.03 | 12.67 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204519 | 27ONTELAUE | 230 | 227 | 0.9033 | 1.03 | 12.67 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204518 | 27IRONWOOD | 230 | 227 | 0.844 | 1.0217 | 17.77 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204518 | 27IRONWOOD | 230 | 227 | 0.8515 | 1.0217 | 17.02 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204518 | 27IRONWOOD | 230 | 227 | 0.8519 | 1.0217 | 16.98 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204518 | 27IRONWOOD | 230 | 227 | 0.852 | 1.0217 | 16.97 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204518 | 27IRONWOOD | 230 | 227 | 0.9388 | 1.0217 | 8.29 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 230 | 227 | 0.7808 | 1.0162 | 23.54 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 230 | 227 | 0.7902 | 1.0162 | 22.6 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 230 | 227 | 0.7906 | 1.0162 | 22.56 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 230 | 227 | 0.7906 | 1.0162 | 22.56 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 230 | 227 | 0.8812 | 1.0162 | 13.5 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204514 | 27TMI | 230 | 227 | 0.8043 | 1.0263 | 22.2 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204514 | 27TMI | 230 | 227 | 0.8118 | 1.0263 | 21.45 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204514 | 27TMI | 230 | 227 | 0.8122 | 1.0263 | 21.41 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204514 | 27TMI | 230 | 227 | 0.8122 | 1.0263 | 21.41 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204514 | 27TMI | 230 | 227 | 0.9024 | 1.0263 | 12.39 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204512 | 27S.RDG | 230 | 227 | 0.8471 | 1.0045 | 15.74 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204512 | 27S.RDG | 230 | 227 | 0.8541 | 1.0045 | 15.04 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204512 | 27S.RDG | 230 | 227 | 0.8545 | 1.0045 | 15 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204512 | 27S.RDG | 230 | 227 | 0.8545 | 1.0045 | 15 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204511 | 27S.LEB | 230 | 227 | 0.8371 | 1.0202 | 18.31 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204511 | 27S.LEB | 230 | 227 | 0.8446 | 1.0202 | 17.56 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204511 | 27S.LEB | 230 | 227 | 0.845 | 1.0202 | 17.52 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204511 | 27S.LEB | 230 | 227 | 0.845 | 1.0202 | 17.52 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204511 | 27S.LEB | 230 | 227 | 0.9322 | 1.0202 | 8.8 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204508 | 27N.TEMPLE | 230 | 227 | 0.8948 | 1.029 | 13.42 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204508 | 27N.TEMPLE | 230 | 227 | 0.9005 | 1.029 | 12.85 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204508 | 27N.TEMPLE | 230 | 227 | 0.9008 | 1.029 | 12.82 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204508 | 27N.TEMPLE | 230 | 227 | 0.9008 | 1.029 | 12.82 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204507 | 27N.LEB | 230 | 227 | 0.8392 | 1.0207 | 18.15 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204507 | 27N.LEB | 230 | 227 | 0.8465 | 1.0207 | 17.42 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204507 | 27N.LEB | 230 | 227 | 0.8469 | 1.0207 | 17.38 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204507 | 27N.LEB | 230 | 227 | 0.8469 | 1.0207 | 17.38 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204507 | 27N.LEB | 230 | 227 | 0.9327 | 1.0207 | 8.8 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204506 | 27N.HERSHY | 230 | 227 | 0.8212 | 1.0244 | 20.32 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204506 | 27N.HERSHY | 230 | 227 | 0.8283 | 1.0244 | 19.61 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204506 | 27N.HERSHY | 230 | 227 | 0.8287 | 1.0244 | 19.57 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204506 | 27N.HERSHY | 230 | 227 | 0.8287 | 1.0244 | 19.57 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204506 | 27N.HERSHY | 230 | 227 | 0.9154 | 1.0244 | 10.9 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204505 | 27N.BOYTWN | 230 | 227 | 0.9077 | 1.0209 | 11.32 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204505 | 27N.BOYTWN | 230 | 227 | 0.9128 | 1.0209 | 10.81 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204505 | 27N.BOYTWN | 230 | 227 | 0.9131 | 1.0209 | 10.78 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204505 | 27N.BOYTWN | 230 | 227 | 0.9131 | 1.0209 | 10.78 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204504 | 27MIDD JCT | 230 | 227 | 0.8045 | 1.0265 | 22.2 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204504 | 27MIDD JCT | 230 | 227 | 0.8121 | 1.0265 | 21.44 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204504 | 27MIDD JCT | 230 | 227 | 0.8125 | 1.0265 | 21.4 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204504 | 27MIDD JCT | 230 | 227 | 0.8125 | 1.0265 | 21.4 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204504 | 27MIDD JCT | 230 | 227 | 0.9032 | 1.0265 | 12.33 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204503 | 27LYONS | 230 | 227 | 0.9056 | 1.0243 | 11.87 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204503 | 27LYONS | 230 | 227 | 0.9106 | 1.0243 | 11.37 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204503 | 27LYONS | 230 | 227 | 0.911 | 1.0243 | 11.33 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204503 | 27LYONS | 230 | 227 | 0.911 | 1.0243 | 11.33 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204502 | 27JACKSON | 230 | 227 | 0.7721 | 1.0136 | 24.15 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204502 | 27JACKSON | 230 | 227 | 0.7792 | 1.0136 | 23.44 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204502 | 27JACKSON | 230 | 227 | 0.7795 | 1.0136 | 23.41 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204502 | 27JACKSON | 230 | 227 | 0.7796 | 1.0136 | 23.4 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204502 | 27JACKSON | 230 | 227 | 0.8723 | 1.0136 | 14.13 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204501 | 27HUNTRSTN | 230 | 227 | 0.9018 | 1.0316 | 12.98 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204501 | 27HUNTRSTN | 230 | 227 | 0.902 | 1.0316 | 12.96 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204501 | 27HUNTRSTN | 230 | 227 | 0.9022 | 1.0316 | 12.94 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204501 | 27HUNTRSTN | 230 | 227 | 0.9022 | 1.0316 | 12.94 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204501 | 27HUNTRSTN | 230 | 227 | 0.9431 | 1.0316 | 8.85 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 200531 | 26YEAGRTWN | 230 | 226 | 0.9154 | 1.0283 | 11.29 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 200531 | 26YEAGRTWN | 230 | 226 | 0.9185 | 1.0283 | 10.98 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 200531 | 26YEAGRTWN | 230 | 226 | 0.9187 | 1.0283 | 10.96 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 200531 | 26YEAGRTWN | 230 | 226 | 0.9187 | 1.0283 | 10.96 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 200513 | 26LEWISTWN | 230 | 226 | 0.9176 | 1.0302 | 11.26 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 200513 | 26LEWISTWN | 230 | 226 | 0.9207 | 1.0302 | 10.95 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 200513 | 26LEWISTWN | 230 | 226 | 0.9209 | 1.0302 | 10.93 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 200513 | 26LEWISTWN | 230 | 226 | 0.9209 | 1.0302 | 10.93 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 213835 | NEWLNVIL | 138 | 230 | 0.9469 | 1.0266 | 7.97 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 213835 | NEWLNVIL | 138 | 230 | 0.9499 | 1.0266 | 7.67 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 213835 | NEWLNVIL | 138 | 230 | 0.9502 | 1.0266 | 7.64 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 213835 | NEWLNVIL | 138 | 230 | 0.9502 | 1.0266 | 7.64 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 213753 | LKNSCTV2 | 138 | 230 | 0.9467 | 1.0264 | 7.97 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 213753 | LKNSCTV2 | 138 | 230 | 0.9497 | 1.0264 | 7.67 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 213753 | LKNSCTV2 | 138 | 230 | 0.95 | 1.0264 | 7.64 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 213753 | LKNSCTV2 | 138 | 230 | 0.95 | 1.0264 | 7.64 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 213752 | LKNSCTV1 | 138 | 230 | 0.9219 | 1.01 | 8.81 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 213752 | LKNSCTV1 | 138 | 230 | 0.9256 | 1.01 | 8.44 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 213752 | LKNSCTV1 | 138 | 230 | 0.9259 | 1.01 | 8.41 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 213752 | LKNSCTV1 | 138 | 230 | 0.9259 | 1.01 | 8.41 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 213435 | BRADFORD | 138 | 230 | 0.9363 | 1.0178 | 8.15 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 213435 | BRADFORD | 138 | 230 | 0.9396 | 1.0178 | 7.82 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 213435 | BRADFORD | 138 | 230 | 0.9399 | 1.0178 | 7.79 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 213435 | BRADFORD | 138 | 230 | 0.94 | 1.0178 | 7.78 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208869 | WHEM CAP | 138 | 229 | 0.8244 | 1.0077 | 18.33 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208869 | WHEM CAP | 138 | 229 | 0.8342 | 1.0077 | 17.35 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208869 | WHEM CAP | 138 | 229 | 0.8345 | 1.0077 | 17.32 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208869 | WHEM CAP | 138 | 229 | 0.8345 | 1.0077 | 17.32 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208869 | WHEM CAP | 138 | 229 | 0.9145 | 1.0077 | 9.32 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208868 | WHEM | 138 | 229 | 0.8244 | 1.0076 | 18.32 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208868 | WHEM | 138 | 229 | 0.8341 | 1.0076 | 17.35 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208868 | WHEM | 138 | 229 | 0.8344 | 1.0076 | 17.32 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208868 | WHEM | 138 | 229 | 0.8345 | 1.0076 | 17.31 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208868 | WHEM | 138 | 229 | 0.9145 | 1.0076 | 9.31 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208764 | SAKR CAP | 138 | 229 | 0.7777 | 1.0034 | 22.57 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208764 | SAKR CAP | 138 | 229 | 0.787 | 1.0034 | 21.64 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208764 | SAKR CAP | 138 | 229 | 0.7874 | 1.0034 | 21.6 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208764 | SAKR CAP | 138 | 229 | 0.7874 | 1.0034 | 21.6 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208764 | SAKR CAP | 138 | 229 | 0.8809 | 1.0034 | 12.25 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208760 | SAKR | 138 | 229 | 0.7777 | 1.0034 | 22.57 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208760 | SAKR | 138 | 229 | 0.7869 | 1.0034 | 21.65 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208760 | SAKR | 138 | 229 | 0.7873 | 1.0034 | 21.61 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208760 | SAKR | 138 | 229 | 0.7873 | 1.0034 | 21.61 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208760 | SAKR | 138 | 229 | 0.8809 | 1.0034 | 12.25 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208751 | RVIL | 138 | 229 | 0.7735 | 1.0008 | 22.73 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208751 | RVIL | 138 | 229 | 0.7829 | 1.0008 | 21.79 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208751 | RVIL | 138 | 229 | 0.7833 | 1.0008 | 21.75 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208751 | RVIL | 138 | 229 | 0.7833 | 1.0008 | 21.75 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208751 | RVIL | 138 | 229 | 0.8776 | 1.0008 | 12.32 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208744 | RTWN 2 | 138 | 229 | 0.8206 | 1.005 | 18.44 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208744 | RTWN 2 | 138 | 229 | 0.8304 | 1.005 | 17.46 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208744 | RTWN 2 | 138 | 229 | 0.8307 | 1.005 | 17.43 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208744 | RTWN 2 | 138 | 229 | 0.8307 | 1.005 | 17.43 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208744 | RTWN 2 | 138 | 229 | 0.9113 | 1.005 | 9.37 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208743 | RTWN 1 | 138 | 229 | 0.8194 | 1.004 | 18.46 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208743 | RTWN 1 | 138 | 229 | 0.8293 | 1.004 | 17.47 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208743 | RTWN 1 | 138 | 229 | 0.8296 | 1.004 | 17.44 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208743 | RTWN 1 | 138 | 229 | 0.8296 | 1.004 | 17.44 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208743 | RTWN 1 | 138 | 229 | 0.9103 | 1.004 | 9.37 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208701 | PRINUGW2 | 138 | 229 | 0.8203 | 1.0048 | 18.45 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208701 | PRINUGW2 | 138 | 229 | 0.8301 | 1.0048 | 17.47 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208701 | PRINUGW2 | 138 | 229 | 0.8304 | 1.0048 | 17.44 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208701 | PRINUGW2 | 138 | 229 | 0.8304 | 1.0048 | 17.44 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208701 | PRINUGW2 | 138 | 229 | 0.9111 | 1.0048 | 9.37 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208700 | PRINUGW1 | 138 | 229 | 0.8186 | 1.0034 | 18.48 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208700 | PRINUGW1 | 138 | 229 | 0.8284 | 1.0034 | 17.5 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208700 | PRINUGW1 | 138 | 229 | 0.8288 | 1.0034 | 17.46 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208700 | PRINUGW1 | 138 | 229 | 0.8288 | 1.0034 | 17.46 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208700 | PRINUGW1 | 138 | 229 | 0.9096 | 1.0034 | 9.38 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208699 | PRINUGS2 | 138 | 229 | 0.7664 | 0.9953 | 22.89 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208699 | PRINUGS2 | 138 | 229 | 0.7756 | 0.9953 | 21.97 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208699 | PRINUGS2 | 138 | 229 | 0.776 | 0.9953 | 21.93 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208699 | PRINUGS2 | 138 | 229 | 0.776 | 0.9953 | 21.93 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208699 | PRINUGS2 | 138 | 229 | 0.8708 | 0.9953 | 12.45 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208698 | PRINUGS1 | 138 | 229 | 0.7662 | 0.9955 | 22.93 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208698 | PRINUGS1 | 138 | 229 | 0.7754 | 0.9955 | 22.01 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208698 | PRINUGS1 | 138 | 229 | 0.7758 | 0.9955 | 21.97 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208698 | PRINUGS1 | 138 | 229 | 0.7758 | 0.9955 | 21.97 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208698 | PRINUGS1 | 138 | 229 | 0.871 | 0.9955 | 12.45 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208695 | PRIN WH2 | 138 | 229 | 0.8197 | 1.0044 | 18.47 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208695 | PRIN WH2 | 138 | 229 | 0.8296 | 1.0044 | 17.48 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208695 | PRIN WH2 | 138 | 229 | 0.8299 | 1.0044 | 17.45 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208695 | PRIN WH2 | 138 | 229 | 0.8299 | 1.0044 | 17.45 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208695 | PRIN WH2 | 138 | 229 | 0.9107 | 1.0044 | 9.37 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208694 | PRIN WH1 | 138 | 229 | 0.8178 | 1.0029 | 18.51 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208694 | PRIN WH1 | 138 | 229 | 0.8277 | 1.0029 | 17.52 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208694 | PRIN WH1 | 138 | 229 | 0.8281 | 1.0029 | 17.48 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208694 | PRIN WH1 | 138 | 229 | 0.8281 | 1.0029 | 17.48 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208694 | PRIN WH1 | 138 | 229 | 0.909 | 1.0029 | 9.39 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208693 | PRIN SA2 | 138 | 229 | 0.7664 | 0.9953 | 22.89 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208693 | PRIN SA2 | 138 | 229 | 0.7756 | 0.9953 | 21.97 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208693 | PRIN SA2 | 138 | 229 | 0.776 | 0.9953 | 21.93 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208693 | PRIN SA2 | 138 | 229 | 0.776 | 0.9953 | 21.93 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208693 | PRIN SA2 | 138 | 229 | 0.8708 | 0.9953 | 12.45 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208692 | PRIN SA1 | 138 | 229 | 0.7662 | 0.9955 | 22.93 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208692 | PRIN SA1 | 138 | 229 | 0.7754 | 0.9955 | 22.01 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208692 | PRIN SA1 | 138 | 229 | 0.7758 | 0.9955 | 21.97 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208692 | PRIN SA1 | 138 | 229 | 0.7758 | 0.9955 | 21.97 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208692 | PRIN SA1 | 138 | 229 | 0.871 | 0.9955 | 12.45 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208677 | PACI 2 | 138 | 229 | 0.7716 | 0.9995 | 22.79 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208677 | PACI 2 | 138 | 229 | 0.7809 | 0.9995 | 21.86 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208677 | PACI 2 | 138 | 229 | 0.7813 | 0.9995 | 21.82 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208677 | PACI 2 | 138 | 229 | 0.7814 | 0.9995 | 21.81 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208677 | PACI 2 | 138 | 229 | 0.876 | 0.9995 | 12.35 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208676 | PACI 1 | 138 | 229 | 0.7707 | 0.999 | 22.83 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208676 | PACI 1 | 138 | 229 | 0.7801 | 0.999 | 21.89 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208676 | PACI 1 | 138 | 229 | 0.7805 | 0.999 | 21.85 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208676 | PACI 1 | 138 | 229 | 0.7805 | 0.999 | 21.85 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208676 | PACI 1 | 138 | 229 | 0.8753 | 0.999 | 12.37 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208661 | NEFF 2 | 138 | 229 | 0.7736 | 1.0008 | 22.72 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208661 | NEFF 2 | 138 | 229 | 0.7829 | 1.0008 | 21.79 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208661 | NEFF 2 | 138 | 229 | 0.7833 | 1.0008 | 21.75 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208661 | NEFF 2 | 138 | 229 | 0.7833 | 1.0008 | 21.75 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208661 | NEFF 2 | 138 | 229 | 0.8776 | 1.0008 | 12.32 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208660 | NEFF 1 | 138 | 229 | 0.7734 | 1.0007 | 22.73 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208660 | NEFF 1 | 138 | 229 | 0.7827 | 1.0007 | 21.8 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208660 | NEFF 1 | 138 | 229 | 0.7831 | 1.0007 | 21.76 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208660 | NEFF 1 | 138 | 229 | 0.7832 | 1.0007 | 21.75 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208660 | NEFF 1 | 138 | 229 | 0.8775 | 1.0007 | 12.32 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208641 | NBRI 2 | 138 | 229 | 0.7668 | 0.9959 | 22.91 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208641 | NBRI 2 | 138 | 229 | 0.776 | 0.9959 | 21.99 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208641 | NBRI 2 | 138 | 229 | 0.7764 | 0.9959 | 21.95 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208641 | NBRI 2 | 138 | 229 | 0.7764 | 0.9959 | 21.95 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208641 | NBRI 2 | 138 | 229 | 0.8715 | 0.9959 | 12.44 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208640 | NBRI 1 | 138 | 229 | 0.7667 | 0.9954 | 22.87 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208640 | NBRI 1 | 138 | 229 | 0.7759 | 0.9954 | 21.95 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208640 | NBRI 1 | 138 | 229 | 0.7763 | 0.9954 | 21.91 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208640 | NBRI 1 | 138 | 229 | 0.7763 | 0.9954 | 21.91 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208640 | NBRI 1 | 138 | 229 | 0.871 | 0.9954 | 12.44 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208521 | LEOL 2 | 138 | 229 | 0.769 | 0.9969 | 22.79 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208521 | LEOL 2 | 138 | 229 | 0.7782 | 0.9969 | 21.87 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208521 | LEOL 2 | 138 | 229 | 0.7786 | 0.9969 | 21.83 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208521 | LEOL 2 | 138 | 229 | 0.7786 | 0.9969 | 21.83 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208521 | LEOL 2 | 138 | 229 | 0.8729 | 0.9969 | 12.4 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208520 | LEOL 1 | 138 | 229 | 0.7708 | 0.9987 | 22.79 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208520 | LEOL 1 | 138 | 229 | 0.78 | 0.9987 | 21.87 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208520 | LEOL 1 | 138 | 229 | 0.7805 | 0.9987 | 21.82 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208520 | LEOL 1 | 138 | 229 | 0.7805 | 0.9987 | 21.82 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208520 | LEOL 1 | 138 | 229 | 0.875 | 0.9987 | 12.37 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208500 | LAPR DC | 138 | 229 | 0.8212 | 1.0054 | 18.42 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208500 | LAPR DC | 138 | 229 | 0.831 | 1.0054 | 17.44 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208500 | LAPR DC | 138 | 229 | 0.8314 | 1.0054 | 17.4 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208500 | LAPR DC | 138 | 229 | 0.8314 | 1.0054 | 17.4 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208500 | LAPR DC | 138 | 229 | 0.9119 | 1.0054 | 9.35 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208498 | LAPR TP2 | 138 | 229 | 0.8212 | 1.0054 | 18.42 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208498 | LAPR TP2 | 138 | 229 | 0.831 | 1.0054 | 17.44 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208498 | LAPR TP2 | 138 | 229 | 0.8314 | 1.0054 | 17.4 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208498 | LAPR TP2 | 138 | 229 | 0.8314 | 1.0054 | 17.4 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208498 | LAPR TP2 | 138 | 229 | 0.9119 | 1.0054 | 9.35 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208497 | LAPR TP1 | 138 | 229 | 0.8213 | 1.0054 | 18.41 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208497 | LAPR TP1 | 138 | 229 | 0.8311 | 1.0054 | 17.43 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208497 | LAPR TP1 | 138 | 229 | 0.8315 | 1.0054 | 17.39 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208497 | LAPR TP1 | 138 | 229 | 0.8315 | 1.0054 | 17.39 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208497 | LAPR TP1 | 138 | 229 | 0.9119 | 1.0054 | 9.35 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208496 | LAPR | 138 | 229 | 0.8211 | 1.0052 | 18.41 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208496 | LAPR | 138 | 229 | 0.8309 | 1.0052 | 17.43 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208496 | LAPR | 138 | 229 | 0.8312 | 1.0052 | 17.4 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208496 | LAPR | 138 | 229 | 0.8312 | 1.0052 | 17.4 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208496 | LAPR | 138 | 229 | 0.9117 | 1.0052 | 9.35 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208376 | EPET 2 | 138 | 229 | 0.772 | 0.9998 | 22.78 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208376 | EPET 2 | 138 | 229 | 0.7813 | 0.9998 | 21.85 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208376 | EPET 2 | 138 | 229 | 0.7817 | 0.9998 | 21.81 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208376 | EPET 2 | 138 | 229 | 0.7818 | 0.9998 | 21.8 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208376 | EPET 2 | 138 | 229 | 0.8763 | 0.9998 | 12.35 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208375 | EPET 1 | 138 | 229 | 0.7713 | 0.9993 | 22.8 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208375 | EPET 1 | 138 | 229 | 0.7806 | 0.9993 | 21.87 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208375 | EPET 1 | 138 | 229 | 0.7811 | 0.9993 | 21.82 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208375 | EPET 1 | 138 | 229 | 0.7811 | 0.9993 | 21.82 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208375 | EPET 1 | 138 | 229 | 0.8758 | 0.9993 | 12.35 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208355 | ELAN 2 | 138 | 229 | 0.7664 | 0.9953 | 22.89 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208355 | ELAN 2 | 138 | 229 | 0.7755 | 0.9953 | 21.98 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208355 | ELAN 2 | 138 | 229 | 0.7759 | 0.9953 | 21.94 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208355 | ELAN 2 | 138 | 229 | 0.776 | 0.9953 | 21.93 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208355 | ELAN 2 | 138 | 229 | 0.8708 | 0.9953 | 12.45 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208354 | ELAN 1 | 138 | 229 | 0.7662 | 0.9955 | 22.93 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208354 | ELAN 1 | 138 | 229 | 0.7753 | 0.9955 | 22.02 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208354 | ELAN 1 | 138 | 229 | 0.7757 | 0.9955 | 21.98 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208354 | ELAN 1 | 138 | 229 | 0.7758 | 0.9955 | 21.97 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208354 | ELAN 1 | 138 | 229 | 0.871 | 0.9955 | 12.45 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208329 | DONV 2 | 138 | 229 | 0.8215 | 1.0056 | 18.41 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208329 | DONV 2 | 138 | 229 | 0.8313 | 1.0056 | 17.43 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208329 | DONV 2 | 138 | 229 | 0.8316 | 1.0056 | 17.4 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208329 | DONV 2 | 138 | 229 | 0.8316 | 1.0056 | 17.4 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208329 | DONV 2 | 138 | 229 | 0.9121 | 1.0056 | 9.35 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208328 | DONV 1 | 138 | 229 | 0.8216 | 1.0056 | 18.4 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208328 | DONV 1 | 138 | 229 | 0.8314 | 1.0056 | 17.42 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208328 | DONV 1 | 138 | 229 | 0.8317 | 1.0056 | 17.39 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208328 | DONV 1 | 138 | 229 | 0.8317 | 1.0056 | 17.39 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208328 | DONV 1 | 138 | 229 | 0.9121 | 1.0056 | 9.35 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208314 | DOGR DC | 138 | 229 | 0.7666 | 0.9957 | 22.91 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208314 | DOGR DC | 138 | 229 | 0.7758 | 0.9957 | 21.99 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208314 | DOGR DC | 138 | 229 | 0.7762 | 0.9957 | 21.95 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208314 | DOGR DC | 138 | 229 | 0.7762 | 0.9957 | 21.95 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208314 | DOGR DC | 138 | 229 | 0.8713 | 0.9957 | 12.44 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208313 | DOGR 2 | 138 | 229 | 0.7666 | 0.9954 | 22.88 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208313 | DOGR 2 | 138 | 229 | 0.7758 | 0.9954 | 21.96 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208313 | DOGR 2 | 138 | 229 | 0.7762 | 0.9954 | 21.92 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208313 | DOGR 2 | 138 | 229 | 0.7762 | 0.9954 | 21.92 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208313 | DOGR 2 | 138 | 229 | 0.871 | 0.9954 | 12.44 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208312 | DOGR 1 | 138 | 229 | 0.7666 | 0.9957 | 22.91 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208312 | DOGR 1 | 138 | 229 | 0.7758 | 0.9957 | 21.99 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208312 | DOGR 1 | 138 | 229 | 0.7762 | 0.9957 | 21.95 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208312 | DOGR 1 | 138 | 229 | 0.7762 | 0.9957 | 21.95 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208312 | DOGR 1 | 138 | 229 | 0.8713 | 0.9957 | 12.44 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208308 | DNLY | 138 | 229 | 0.8188 | 1.0035 | 18.47 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208308 | DNLY | 138 | 229 | 0.8286 | 1.0035 | 17.49 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208308 | DNLY | 138 | 229 | 0.829 | 1.0035 | 17.45 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208308 | DNLY | 138 | 229 | 0.829 | 1.0035 | 17.45 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208308 | DNLY | 138 | 229 | 0.9097 | 1.0035 | 9.38 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208306 | DNLY 2 | 138 | 229 | 0.8204 | 1.0049 | 18.45 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208306 | DNLY 2 | 138 | 229 | 0.8302 | 1.0049 | 17.47 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208306 | DNLY 2 | 138 | 229 | 0.8305 | 1.0049 | 17.44 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208306 | DNLY 2 | 138 | 229 | 0.8306 | 1.0049 | 17.43 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208306 | DNLY 2 | 138 | 229 | 0.9112 | 1.0049 | 9.37 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208305 | DNLY 1 | 138 | 229 | 0.8188 | 1.0035 | 18.47 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208305 | DNLY 1 | 138 | 229 | 0.8286 | 1.0035 | 17.49 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208305 | DNLY 1 | 138 | 229 | 0.829 | 1.0035 | 17.45 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208305 | DNLY 1 | 138 | 229 | 0.829 | 1.0035 | 17.45 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208305 | DNLY 1 | 138 | 229 | 0.9098 | 1.0035 | 9.37 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208304 | DILL TI2 | 138 | 229 | 0.8204 | 1.0048 | 18.44 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208304 | DILL TI2 | 138 | 229 | 0.8302 | 1.0048 | 17.46 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208304 | DILL TI2 | 138 | 229 | 0.8305 | 1.0048 | 17.43 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208304 | DILL TI2 | 138 | 229 | 0.8305 | 1.0048 | 17.43 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208304 | DILL TI2 | 138 | 229 | 0.9112 | 1.0048 | 9.36 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208303 | DILL TI1 | 138 | 229 | 0.8187 | 1.0035 | 18.48 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208303 | DILL TI1 | 138 | 229 | 0.8286 | 1.0035 | 17.49 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208303 | DILL TI1 | 138 | 229 | 0.8289 | 1.0035 | 17.46 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208303 | DILL TI1 | 138 | 229 | 0.8289 | 1.0035 | 17.46 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208303 | DILL TI1 | 138 | 229 | 0.9097 | 1.0035 | 9.38 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208302 | DILL 2 | 138 | 229 | 0.7713 | 0.9993 | 22.8 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208302 | DILL 2 | 138 | 229 | 0.7807 | 0.9993 | 21.86 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208302 | DILL 2 | 138 | 229 | 0.7811 | 0.9993 | 21.82 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208302 | DILL 2 | 138 | 229 | 0.7811 | 0.9993 | 21.82 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208302 | DILL 2 | 138 | 229 | 0.8758 | 0.9993 | 12.35 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208301 | DILL 1 | 138 | 229 | 0.7705 | 0.9988 | 22.83 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208301 | DILL 1 | 138 | 229 | 0.7798 | 0.9988 | 21.9 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208301 | DILL 1 | 138 | 229 | 0.7803 | 0.9988 | 21.85 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208301 | DILL 1 | 138 | 229 | 0.7803 | 0.9988 | 21.85 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208301 | DILL 1 | 138 | 229 | 0.8751 | 0.9988 | 12.37 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208291 | DART DC | 138 | 229 | 0.7683 | 0.9964 | 22.81 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208291 | DART DC | 138 | 229 | 0.7774 | 0.9964 | 21.9 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208291 | DART DC | 138 | 229 | 0.7779 | 0.9964 | 21.85 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208291 | DART DC | 138 | 229 | 0.7779 | 0.9964 | 21.85 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208291 | DART DC | 138 | 229 | 0.8723 | 0.9964 | 12.41 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208290 | DART TP2 | 138 | 229 | 0.7683 | 0.9964 | 22.81 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208290 | DART TP2 | 138 | 229 | 0.7775 | 0.9964 | 21.89 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208290 | DART TP2 | 138 | 229 | 0.7779 | 0.9964 | 21.85 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208290 | DART TP2 | 138 | 229 | 0.7779 | 0.9964 | 21.85 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208290 | DART TP2 | 138 | 229 | 0.8723 | 0.9964 | 12.41 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208289 | DART TP1 | 138 | 229 | 0.7703 | 0.9983 | 22.8 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208289 | DART TP1 | 138 | 229 | 0.7795 | 0.9983 | 21.88 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208289 | DART TP1 | 138 | 229 | 0.7799 | 0.9983 | 21.84 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208289 | DART TP1 | 138 | 229 | 0.7799 | 0.9983 | 21.84 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208289 | DART TP1 | 138 | 229 | 0.8746 | 0.9983 | 12.37 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208288 | DART | 138 | 229 | 0.7664 | 0.9948 | 22.84 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208288 | DART | 138 | 229 | 0.7756 | 0.9948 | 21.92 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208288 | DART | 138 | 229 | 0.776 | 0.9948 | 21.88 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208288 | DART | 138 | 229 | 0.776 | 0.9948 | 21.88 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208288 | DART | 138 | 229 | 0.8704 | 0.9948 | 12.44 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208720 | RED FRONT | 115 | 229 | 0.7786 | 1.0206 | 24.2 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208720 | RED FRONT | 115 | 229 | 0.7875 | 1.0206 | 23.31 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208720 | RED FRONT | 115 | 229 | 0.7878 | 1.0206 | 23.28 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208720 | RED FRONT | 115 | 229 | 0.7878 | 1.0206 | 23.28 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208720 | RED FRONT | 115 | 229 | 0.8815 | 1.0206 | 13.91 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208394 | PPL-BGE TIE | 115 | 229 | 0.8736 | 0.9596 | 8.6 | Tower | BG_P7_GRCTN_RAPHEL_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208393 | FARO DC TIE | 115 | 229 | 0.8882 | 0.9706 | 8.24 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208142 | WIGR-115 | 115 | 229 | 0.7932 | 1.0224 | 22.92 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208142 | WIGR-115 | 115 | 229 | 0.8003 | 1.0224 | 22.21 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208142 | WIGR-115 | 115 | 229 | 0.8007 | 1.0224 | 22.17 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208142 | WIGR-115 | 115 | 229 | 0.8007 | 1.0224 | 22.17 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208142 | WIGR-115 | 115 | 229 | 0.8938 | 1.0224 | 12.86 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 205948 | AE1-129_MAIN | 115 | 227 | 0.782 | 1.0129 | 23.09 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 205948 | AE1-129_MAIN | 115 | 227 | 0.7893 | 1.0129 | 22.36 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 205948 | AE1-129_MAIN | 115 | 227 | 0.7897 | 1.0129 | 22.32 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 205948 | AE1-129_MAIN | 115 | 227 | 0.7897 | 1.0129 | 22.32 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 205948 | AE1-129_MAIN | 115 | 227 | 0.8864 | 1.0129 | 12.65 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 205947 | AE1-129_POI | 115 | 227 | 0.7807 | 1.0129 | 23.22 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 205947 | AE1-129_POI | 115 | 227 | 0.788 | 1.0129 | 22.49 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 205947 | AE1-129_POI | 115 | 227 | 0.7883 | 1.0129 | 22.46 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 205947 | AE1-129_POI | 115 | 227 | 0.7883 | 1.0129 | 22.46 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 205947 | AE1-129_POI | 115 | 227 | 0.8852 | 1.0129 | 12.77 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 205931 | AF2-100 C | 115 | 227 | 0.7697 | 1.0088 | 23.91 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 205931 | AF2-100 C | 115 | 227 | 0.7767 | 1.0088 | 23.21 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 205931 | AF2-100 C | 115 | 227 | 0.777 | 1.0088 | 23.18 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 205931 | AF2-100 C | 115 | 227 | 0.777 | 1.0088 | 23.18 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 205931 | AF2-100 C | 115 | 227 | 0.8705 | 1.0088 | 13.83 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 205930 | AF2-099 C | 115 | 227 | 0.7697 | 1.0088 | 23.91 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 205930 | AF2-099 C | 115 | 227 | 0.7767 | 1.0088 | 23.21 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 205930 | AF2-099 C | 115 | 227 | 0.777 | 1.0088 | 23.18 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 205930 | AF2-099 C | 115 | 227 | 0.777 | 1.0088 | 23.18 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 205930 | AF2-099 C | 115 | 227 | 0.8705 | 1.0088 | 13.83 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 205922 | AF2-268 E | 115 | 227 | 0.8263 | 1.0078 | 18.15 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 205922 | AF2-268 E | 115 | 227 | 0.8305 | 1.0078 | 17.73 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 205922 | AF2-268 E | 115 | 227 | 0.8308 | 1.0078 | 17.7 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 205922 | AF2-268 E | 115 | 227 | 0.8308 | 1.0078 | 17.7 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 205922 | AF2-268 E | 115 | 227 | 0.901 | 1.0078 | 10.68 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 205921 | AF2-151 C | 115 | 227 | 0.7892 | 1.0207 | 23.15 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 205921 | AF2-151 C | 115 | 227 | 0.7955 | 1.0207 | 22.52 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 205921 | AF2-151 C | 115 | 227 | 0.7958 | 1.0207 | 22.49 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 205921 | AF2-151 C | 115 | 227 | 0.7958 | 1.0207 | 22.49 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 205921 | AF2-151 C | 115 | 227 | 0.8886 | 1.0207 | 13.21 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 205920 | AF2-101 C | 115 | 227 | 0.7927 | 1.0246 | 23.19 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 205920 | AF2-101 C | 115 | 227 | 0.7995 | 1.0246 | 22.51 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 205920 | AF2-101 C | 115 | 227 | 0.7999 | 1.0246 | 22.47 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 205920 | AF2-101 C | 115 | 227 | 0.7999 | 1.0246 | 22.47 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 205920 | AF2-101 C | 115 | 227 | 0.8939 | 1.0246 | 13.07 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 205913 | AD1-020 MAIN | 115 | 227 | 0.8308 | 1.0131 | 18.23 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 205913 | AD1-020 MAIN | 115 | 227 | 0.8351 | 1.0131 | 17.8 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 205913 | AD1-020 MAIN | 115 | 227 | 0.8354 | 1.0131 | 17.77 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 205913 | AD1-020 MAIN | 115 | 227 | 0.8354 | 1.0131 | 17.77 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 205913 | AD1-020 MAIN | 115 | 227 | 0.9063 | 1.0131 | 10.68 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 205912 | AD1-020 TAP | 115 | 227 | 0.8308 | 1.0131 | 18.23 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 205912 | AD1-020 TAP | 115 | 227 | 0.8351 | 1.0131 | 17.8 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 205912 | AD1-020 TAP | 115 | 227 | 0.8353 | 1.0131 | 17.78 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 205912 | AD1-020 TAP | 115 | 227 | 0.8353 | 1.0131 | 17.78 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 205912 | AD1-020 TAP | 115 | 227 | 0.9062 | 1.0131 | 10.69 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204715 | 27EISENHOWER | 115 | 227 | 0.7679 | 0.9954 | 22.75 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204715 | 27EISENHOWER | 115 | 227 | 0.7735 | 0.9954 | 22.19 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204715 | 27EISENHOWER | 115 | 227 | 0.7738 | 0.9954 | 22.16 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204715 | 27EISENHOWER | 115 | 227 | 0.7738 | 0.9954 | 22.16 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204715 | 27EISENHOWER | 115 | 227 | 0.861 | 0.9954 | 13.44 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204713 | 27JOHNSCTRL | 115 | 227 | 0.7533 | 0.9966 | 24.33 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204713 | 27JOHNSCTRL | 115 | 227 | 0.7609 | 0.9966 | 23.57 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204713 | 27JOHNSCTRL | 115 | 227 | 0.7612 | 0.9966 | 23.54 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204713 | 27JOHNSCTRL | 115 | 227 | 0.7612 | 0.9966 | 23.54 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204713 | 27JOHNSCTRL | 115 | 227 | 0.8545 | 0.9966 | 14.21 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204701 | 27YORKANAB | 115 | 227 | 0.7792 | 1.0211 | 24.19 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204701 | 27YORKANAB | 115 | 227 | 0.7881 | 1.0211 | 23.3 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204701 | 27YORKANAB | 115 | 227 | 0.7884 | 1.0211 | 23.27 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204701 | 27YORKANAB | 115 | 227 | 0.7884 | 1.0211 | 23.27 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204701 | 27YORKANAB | 115 | 227 | 0.882 | 1.0211 | 13.91 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204700 | 27JACKSON6 | 115 | 227 | 0.7764 | 1.0121 | 23.57 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204700 | 27JACKSON6 | 115 | 227 | 0.7831 | 1.0121 | 22.9 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204700 | 27JACKSON6 | 115 | 227 | 0.7835 | 1.0121 | 22.86 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204700 | 27JACKSON6 | 115 | 227 | 0.7835 | 1.0121 | 22.86 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204700 | 27JACKSON6 | 115 | 227 | 0.8749 | 1.0121 | 13.72 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204687 | 27PROSPECT | 115 | 227 | 0.778 | 1.0203 | 24.23 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204687 | 27PROSPECT | 115 | 227 | 0.7869 | 1.0203 | 23.34 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204687 | 27PROSPECT | 115 | 227 | 0.7872 | 1.0203 | 23.31 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204687 | 27PROSPECT | 115 | 227 | 0.7872 | 1.0203 | 23.31 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204687 | 27PROSPECT | 115 | 227 | 0.881 | 1.0203 | 13.93 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204682 | 27ES3 | 115 | 227 | 0.7732 | 1.0123 | 23.91 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204682 | 27ES3 | 115 | 227 | 0.7805 | 1.0123 | 23.18 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204682 | 27ES3 | 115 | 227 | 0.7808 | 1.0123 | 23.15 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204682 | 27ES3 | 115 | 227 | 0.7809 | 1.0123 | 23.14 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204682 | 27ES3 | 115 | 227 | 0.8781 | 1.0123 | 13.42 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204681 | 27REDFRONT+ | 115 | 227 | 0.7786 | 1.0206 | 24.2 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204681 | 27REDFRONT+ | 115 | 227 | 0.7875 | 1.0206 | 23.31 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204681 | 27REDFRONT+ | 115 | 227 | 0.7878 | 1.0206 | 23.28 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204681 | 27REDFRONT+ | 115 | 227 | 0.7878 | 1.0206 | 23.28 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204681 | 27REDFRONT+ | 115 | 227 | 0.8815 | 1.0206 | 13.91 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204669 | 27TEX E | 115 | 227 | 0.8145 | 1.0207 | 20.62 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204669 | 27TEX E | 115 | 227 | 0.8195 | 1.0207 | 20.12 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204669 | 27TEX E | 115 | 227 | 0.8198 | 1.0207 | 20.09 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204669 | 27TEX E | 115 | 227 | 0.8198 | 1.0207 | 20.09 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204669 | 27TEX E | 115 | 227 | 0.8999 | 1.0207 | 12.08 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204668 | 27TEX E TP | 115 | 227 | 0.815 | 1.0211 | 20.61 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204668 | 27TEX E TP | 115 | 227 | 0.82 | 1.0211 | 20.11 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204668 | 27TEX E TP | 115 | 227 | 0.8203 | 1.0211 | 20.08 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204668 | 27TEX E TP | 115 | 227 | 0.8203 | 1.0211 | 20.08 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204668 | 27TEX E TP | 115 | 227 | 0.9004 | 1.0211 | 12.07 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204660 | 27YK H STA | 115 | 227 | 0.7853 | 1.0202 | 23.49 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204660 | 27YK H STA | 115 | 227 | 0.7926 | 1.0202 | 22.76 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204660 | 27YK H STA | 115 | 227 | 0.7929 | 1.0202 | 22.73 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204660 | 27YK H STA | 115 | 227 | 0.793 | 1.0202 | 22.72 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204660 | 27YK H STA | 115 | 227 | 0.8898 | 1.0202 | 13.04 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204645 | 27PANTHER | 115 | 227 | 0.8835 | 1.0087 | 12.52 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204645 | 27PANTHER | 115 | 227 | 0.8922 | 1.0087 | 11.65 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204645 | 27PANTHER | 115 | 227 | 0.8927 | 1.0087 | 11.6 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204645 | 27PANTHER | 115 | 227 | 0.8927 | 1.0087 | 11.6 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204644 | 27HILL RD | 115 | 227 | 0.8729 | 1.0138 | 14.09 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204644 | 27HILL RD | 115 | 227 | 0.8812 | 1.0138 | 13.26 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204644 | 27HILL RD | 115 | 227 | 0.8817 | 1.0138 | 13.21 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204644 | 27HILL RD | 115 | 227 | 0.8817 | 1.0138 | 13.21 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204598 | 27MIDD JCT | 115 | 227 | 0.791 | 1.0237 | 23.27 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204598 | 27MIDD JCT | 115 | 227 | 0.7983 | 1.0237 | 22.54 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204598 | 27MIDD JCT | 115 | 227 | 0.7987 | 1.0237 | 22.5 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204598 | 27MIDD JCT | 115 | 227 | 0.7987 | 1.0237 | 22.5 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204598 | 27MIDD JCT | 115 | 227 | 0.8954 | 1.0237 | 12.83 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204597 | 27COLLINS | 115 | 227 | 0.7879 | 1.0218 | 23.39 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204597 | 27COLLINS | 115 | 227 | 0.7952 | 1.0218 | 22.66 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204597 | 27COLLINS | 115 | 227 | 0.7956 | 1.0218 | 22.62 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204597 | 27COLLINS | 115 | 227 | 0.7956 | 1.0218 | 22.62 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204597 | 27COLLINS | 115 | 227 | 0.8923 | 1.0218 | 12.95 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204596 | 27MJ5 REAC | 115 | 227 | 0.7925 | 1.0234 | 23.09 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204596 | 27MJ5 REAC | 115 | 227 | 0.8001 | 1.0234 | 22.33 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204596 | 27MJ5 REAC | 115 | 227 | 0.8005 | 1.0234 | 22.29 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204596 | 27MJ5 REAC | 115 | 227 | 0.8005 | 1.0234 | 22.29 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204596 | 27MJ5 REAC | 115 | 227 | 0.8949 | 1.0234 | 12.85 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204595 | 27MJ2 REAC | 115 | 227 | 0.7926 | 1.0234 | 23.08 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204595 | 27MJ2 REAC | 115 | 227 | 0.8002 | 1.0234 | 22.32 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204595 | 27MJ2 REAC | 115 | 227 | 0.8006 | 1.0234 | 22.28 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204595 | 27MJ2 REAC | 115 | 227 | 0.8006 | 1.0234 | 22.28 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204595 | 27MJ2 REAC | 115 | 227 | 0.8949 | 1.0234 | 12.85 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204573 | 27SPRNGWOD | 115 | 227 | 0.7697 | 1.0131 | 24.34 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204573 | 27SPRNGWOD | 115 | 227 | 0.7781 | 1.0131 | 23.5 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204573 | 27SPRNGWOD | 115 | 227 | 0.7784 | 1.0131 | 23.47 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204573 | 27SPRNGWOD | 115 | 227 | 0.7784 | 1.0131 | 23.47 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204573 | 27SPRNGWOD | 115 | 227 | 0.8734 | 1.0131 | 13.97 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204572 | 27RAINTREE | 115 | 227 | 0.7675 | 1.0084 | 24.09 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204572 | 27RAINTREE | 115 | 227 | 0.7748 | 1.0084 | 23.36 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204572 | 27RAINTREE | 115 | 227 | 0.7752 | 1.0084 | 23.32 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204572 | 27RAINTREE | 115 | 227 | 0.7752 | 1.0084 | 23.32 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204572 | 27RAINTREE | 115 | 227 | 0.8724 | 1.0084 | 13.6 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204571 | 27ZIONS VW | 115 | 227 | 0.7732 | 1.0089 | 23.57 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204571 | 27ZIONS VW | 115 | 227 | 0.7805 | 1.0089 | 22.84 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204571 | 27ZIONS VW | 115 | 227 | 0.7808 | 1.0089 | 22.81 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204571 | 27ZIONS VW | 115 | 227 | 0.7808 | 1.0089 | 22.81 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204571 | 27ZIONS VW | 115 | 227 | 0.8779 | 1.0089 | 13.1 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204570 | 27YORKANA | 115 | 227 | 0.7793 | 1.0214 | 24.21 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204570 | 27YORKANA | 115 | 227 | 0.7882 | 1.0214 | 23.32 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204570 | 27YORKANA | 115 | 227 | 0.7886 | 1.0214 | 23.28 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204570 | 27YORKANA | 115 | 227 | 0.7886 | 1.0214 | 23.28 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204570 | 27YORKANA | 115 | 227 | 0.8822 | 1.0214 | 13.92 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204569 | 27YORK INC | 115 | 227 | 0.7671 | 1.0103 | 24.32 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204569 | 27YORK INC | 115 | 227 | 0.7747 | 1.0103 | 23.56 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204569 | 27YORK INC | 115 | 227 | 0.7751 | 1.0103 | 23.52 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204569 | 27YORK INC | 115 | 227 | 0.7751 | 1.0103 | 23.52 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204569 | 27YORK INC | 115 | 227 | 0.8708 | 1.0103 | 13.95 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204568 | 27YOE TAP | 115 | 227 | 0.7717 | 1.0146 | 24.29 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204568 | 27YOE TAP | 115 | 227 | 0.7804 | 1.0146 | 23.42 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204568 | 27YOE TAP | 115 | 227 | 0.7807 | 1.0146 | 23.39 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204568 | 27YOE TAP | 115 | 227 | 0.7807 | 1.0146 | 23.39 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204568 | 27YOE TAP | 115 | 227 | 0.8744 | 1.0146 | 14.02 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204568 | 27YOE TAP | 115 | 227 | 0.9097 | 1.0146 | 10.49 | Line_FB | ME_P2-3_ME-115-032AT_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204567 | 27YOE | 115 | 227 | 0.7724 | 1.0153 | 24.29 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204567 | 27YOE | 115 | 227 | 0.781 | 1.0153 | 23.43 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204567 | 27YOE | 115 | 227 | 0.7813 | 1.0153 | 23.4 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204567 | 27YOE | 115 | 227 | 0.7813 | 1.0153 | 23.4 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204567 | 27YOE | 115 | 227 | 0.8758 | 1.0153 | 13.95 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204566 | 27YK HAVEN | 115 | 227 | 0.7851 | 1.0201 | 23.5 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204566 | 27YK HAVEN | 115 | 227 | 0.7924 | 1.0201 | 22.77 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204566 | 27YK HAVEN | 115 | 227 | 0.7928 | 1.0201 | 22.73 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204566 | 27YK HAVEN | 115 | 227 | 0.7928 | 1.0201 | 22.73 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204566 | 27YK HAVEN | 115 | 227 | 0.8897 | 1.0201 | 13.04 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204565 | 27WINDSOR | 115 | 227 | 0.7665 | 1.0099 | 24.34 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204565 | 27WINDSOR | 115 | 227 | 0.775 | 1.0099 | 23.49 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204565 | 27WINDSOR | 115 | 227 | 0.7753 | 1.0099 | 23.46 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204565 | 27WINDSOR | 115 | 227 | 0.7753 | 1.0099 | 23.46 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204565 | 27WINDSOR | 115 | 227 | 0.8691 | 1.0099 | 14.08 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204565 | 27WINDSOR | 115 | 227 | 0.9097 | 1.0099 | 10.02 | Line_FB | ME_P2-3_ME-115-032AT_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204564 | 27WHITEFRD | 115 | 227 | 0.7671 | 1.0116 | 24.45 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204564 | 27WHITEFRD | 115 | 227 | 0.7752 | 1.0116 | 23.64 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204564 | 27WHITEFRD | 115 | 227 | 0.7755 | 1.0116 | 23.61 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204564 | 27WHITEFRD | 115 | 227 | 0.7755 | 1.0116 | 23.61 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204564 | 27WHITEFRD | 115 | 227 | 0.8711 | 1.0116 | 14.05 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204563 | 27WESTGATE | 115 | 227 | 0.7653 | 1.007 | 24.17 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204563 | 27WESTGATE | 115 | 227 | 0.7726 | 1.007 | 23.44 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204563 | 27WESTGATE | 115 | 227 | 0.773 | 1.007 | 23.4 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204563 | 27WESTGATE | 115 | 227 | 0.773 | 1.007 | 23.4 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204563 | 27WESTGATE | 115 | 227 | 0.8685 | 1.007 | 13.85 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204562 | 27W.HELLAM | 115 | 227 | 0.7736 | 1.0168 | 24.32 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204562 | 27W.HELLAM | 115 | 227 | 0.7822 | 1.0168 | 23.46 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204562 | 27W.HELLAM | 115 | 227 | 0.7825 | 1.0168 | 23.43 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204562 | 27W.HELLAM | 115 | 227 | 0.7826 | 1.0168 | 23.42 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204562 | 27W.HELLAM | 115 | 227 | 0.8769 | 1.0168 | 13.99 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204561 | 27VIOLET H | 115 | 227 | 0.768 | 1.0117 | 24.37 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204561 | 27VIOLET H | 115 | 227 | 0.7762 | 1.0117 | 23.55 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204561 | 27VIOLET H | 115 | 227 | 0.7765 | 1.0117 | 23.52 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204561 | 27VIOLET H | 115 | 227 | 0.7765 | 1.0117 | 23.52 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204561 | 27VIOLET H | 115 | 227 | 0.8719 | 1.0117 | 13.98 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204560 | 27TOLNA | 115 | 227 | 0.7531 | 0.9967 | 24.36 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204560 | 27TOLNA | 115 | 227 | 0.7608 | 0.9967 | 23.59 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204560 | 27TOLNA | 115 | 227 | 0.7611 | 0.9967 | 23.56 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204560 | 27TOLNA | 115 | 227 | 0.7611 | 0.9967 | 23.56 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204560 | 27TOLNA | 115 | 227 | 0.8545 | 0.9967 | 14.22 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204559 | 27TAXVILLE | 115 | 227 | 0.7697 | 1.0088 | 23.91 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204559 | 27TAXVILLE | 115 | 227 | 0.7767 | 1.0088 | 23.21 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204559 | 27TAXVILLE | 115 | 227 | 0.777 | 1.0088 | 23.18 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204559 | 27TAXVILLE | 115 | 227 | 0.777 | 1.0088 | 23.18 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204559 | 27TAXVILLE | 115 | 227 | 0.8705 | 1.0088 | 13.83 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204558 | 27SMITH TP | 115 | 227 | 0.765 | 1.007 | 24.2 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204558 | 27SMITH TP | 115 | 227 | 0.7723 | 1.007 | 23.47 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204558 | 27SMITH TP | 115 | 227 | 0.7727 | 1.007 | 23.43 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204558 | 27SMITH TP | 115 | 227 | 0.7727 | 1.007 | 23.43 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204558 | 27SMITH TP | 115 | 227 | 0.8684 | 1.007 | 13.86 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204557 | 27SMITH ST | 115 | 227 | 0.7636 | 1.0057 | 24.21 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204557 | 27SMITH ST | 115 | 227 | 0.7709 | 1.0057 | 23.48 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204557 | 27SMITH ST | 115 | 227 | 0.7713 | 1.0057 | 23.44 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204557 | 27SMITH ST | 115 | 227 | 0.7713 | 1.0057 | 23.44 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204557 | 27SMITH ST | 115 | 227 | 0.8677 | 1.0057 | 13.8 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204556 | 27ROUND TP | 115 | 227 | 0.7918 | 1.0253 | 23.35 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204556 | 27ROUND TP | 115 | 227 | 0.7984 | 1.0253 | 22.69 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204556 | 27ROUND TP | 115 | 227 | 0.7988 | 1.0253 | 22.65 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204556 | 27ROUND TP | 115 | 227 | 0.7988 | 1.0253 | 22.65 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204556 | 27ROUND TP | 115 | 227 | 0.8934 | 1.0253 | 13.19 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204555 | 27QUEEN ST | 115 | 227 | 0.7688 | 1.0124 | 24.36 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204555 | 27QUEEN ST | 115 | 227 | 0.7771 | 1.0124 | 23.53 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204555 | 27QUEEN ST | 115 | 227 | 0.7774 | 1.0124 | 23.5 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204555 | 27QUEEN ST | 115 | 227 | 0.7775 | 1.0124 | 23.49 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204555 | 27QUEEN ST | 115 | 227 | 0.8726 | 1.0124 | 13.98 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204554 | 27PLEASVIL | 115 | 227 | 0.7676 | 1.0121 | 24.45 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204554 | 27PLEASVIL | 115 | 227 | 0.7756 | 1.0121 | 23.65 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204554 | 27PLEASVIL | 115 | 227 | 0.7759 | 1.0121 | 23.62 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204554 | 27PLEASVIL | 115 | 227 | 0.7759 | 1.0121 | 23.62 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204554 | 27PLEASVIL | 115 | 227 | 0.8717 | 1.0121 | 14.04 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204553 | 27PH GLATR | 115 | 227 | 0.7713 | 1.004 | 23.27 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204553 | 27PH GLATR | 115 | 227 | 0.7774 | 1.004 | 22.66 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204553 | 27PH GLATR | 115 | 227 | 0.7777 | 1.004 | 22.63 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204553 | 27PH GLATR | 115 | 227 | 0.7777 | 1.004 | 22.63 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204553 | 27PH GLATR | 115 | 227 | 0.8673 | 1.004 | 13.67 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204552 | 27P.P.G.I. | 115 | 227 | 0.7962 | 1.0266 | 23.04 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204552 | 27P.P.G.I. | 115 | 227 | 0.8026 | 1.0266 | 22.4 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204552 | 27P.P.G.I. | 115 | 227 | 0.8029 | 1.0266 | 22.37 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204552 | 27P.P.G.I. | 115 | 227 | 0.8029 | 1.0266 | 22.37 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204552 | 27P.P.G.I. | 115 | 227 | 0.8952 | 1.0266 | 13.14 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204551 | 27OXFORD | 115 | 227 | 0.7954 | 1.0073 | 21.19 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204551 | 27OXFORD | 115 | 227 | 0.8005 | 1.0073 | 20.68 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204551 | 27OXFORD | 115 | 227 | 0.8008 | 1.0073 | 20.65 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204551 | 27OXFORD | 115 | 227 | 0.8008 | 1.0073 | 20.65 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204551 | 27OXFORD | 115 | 227 | 0.8823 | 1.0073 | 12.5 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204550 | 27ORRTANNA | 115 | 227 | 0.8263 | 1.0078 | 18.15 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204550 | 27ORRTANNA | 115 | 227 | 0.8305 | 1.0078 | 17.73 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204550 | 27ORRTANNA | 115 | 227 | 0.8308 | 1.0078 | 17.7 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204550 | 27ORRTANNA | 115 | 227 | 0.8308 | 1.0078 | 17.7 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204550 | 27ORRTANNA | 115 | 227 | 0.901 | 1.0078 | 10.68 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204549 | 27NEWBERRY | 115 | 227 | 0.7858 | 1.0207 | 23.49 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204549 | 27NEWBERRY | 115 | 227 | 0.7929 | 1.0207 | 22.78 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204549 | 27NEWBERRY | 115 | 227 | 0.7933 | 1.0207 | 22.74 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204549 | 27NEWBERRY | 115 | 227 | 0.7933 | 1.0207 | 22.74 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204549 | 27NEWBERRY | 115 | 227 | 0.8895 | 1.0207 | 13.12 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204548 | 27N.HANOVR | 115 | 227 | 0.7691 | 0.996 | 22.69 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204548 | 27N.HANOVR | 115 | 227 | 0.7747 | 0.996 | 22.13 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204548 | 27N.HANOVR | 115 | 227 | 0.775 | 0.996 | 22.1 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204548 | 27N.HANOVR | 115 | 227 | 0.775 | 0.996 | 22.1 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204548 | 27N.HANOVR | 115 | 227 | 0.862 | 0.996 | 13.4 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204547 | 27MT ROSE | 115 | 227 | 0.7673 | 1.0116 | 24.43 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204547 | 27MT ROSE | 115 | 227 | 0.7754 | 1.0116 | 23.62 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204547 | 27MT ROSE | 115 | 227 | 0.7758 | 1.0116 | 23.58 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204547 | 27MT ROSE | 115 | 227 | 0.7758 | 1.0116 | 23.58 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204547 | 27MT ROSE | 115 | 227 | 0.8714 | 1.0116 | 14.02 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204546 | 27MOUNTAIN | 115 | 227 | 0.7973 | 1.0272 | 22.99 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204546 | 27MOUNTAIN | 115 | 227 | 0.8036 | 1.0272 | 22.36 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204546 | 27MOUNTAIN | 115 | 227 | 0.804 | 1.0272 | 22.32 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204546 | 27MOUNTAIN | 115 | 227 | 0.804 | 1.0272 | 22.32 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204546 | 27MOUNTAIN | 115 | 227 | 0.896 | 1.0272 | 13.12 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204545 | 27MENGES M | 115 | 227 | 0.7713 | 1.0046 | 23.33 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204545 | 27MENGES M | 115 | 227 | 0.7775 | 1.0046 | 22.71 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204545 | 27MENGES M | 115 | 227 | 0.7778 | 1.0046 | 22.68 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204545 | 27MENGES M | 115 | 227 | 0.7778 | 1.0046 | 22.68 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204545 | 27MENGES M | 115 | 227 | 0.8677 | 1.0046 | 13.69 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 115 | 227 | 0.8305 | 0.9976 | 16.71 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 115 | 227 | 0.8344 | 0.9976 | 16.32 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 115 | 227 | 0.8346 | 0.9976 | 16.3 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 115 | 227 | 0.8346 | 0.9976 | 16.3 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204542 | 27JE BAKER | 115 | 227 | 0.7728 | 1.0102 | 23.74 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204542 | 27JE BAKER | 115 | 227 | 0.7796 | 1.0102 | 23.06 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204542 | 27JE BAKER | 115 | 227 | 0.7799 | 1.0102 | 23.03 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204542 | 27JE BAKER | 115 | 227 | 0.7799 | 1.0102 | 23.03 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204542 | 27JE BAKER | 115 | 227 | 0.8724 | 1.0102 | 13.78 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204541 | 27BAKER TP | 115 | 227 | 0.7731 | 1.0104 | 23.73 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204541 | 27BAKER TP | 115 | 227 | 0.7799 | 1.0104 | 23.05 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204541 | 27BAKER TP | 115 | 227 | 0.7803 | 1.0104 | 23.01 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204541 | 27BAKER TP | 115 | 227 | 0.7803 | 1.0104 | 23.01 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204541 | 27BAKER TP | 115 | 227 | 0.8727 | 1.0104 | 13.77 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204540 | 27JACKSON | 115 | 227 | 0.7761 | 1.012 | 23.59 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204540 | 27JACKSON | 115 | 227 | 0.7828 | 1.012 | 22.92 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204540 | 27JACKSON | 115 | 227 | 0.7831 | 1.012 | 22.89 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204540 | 27JACKSON | 115 | 227 | 0.7832 | 1.012 | 22.88 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204540 | 27JACKSON | 115 | 227 | 0.8747 | 1.012 | 13.73 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204539 | 27HUNTRSTN | 115 | 227 | 0.8305 | 1.0235 | 19.3 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204539 | 27HUNTRSTN | 115 | 227 | 0.835 | 1.0235 | 18.85 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204539 | 27HUNTRSTN | 115 | 227 | 0.8353 | 1.0235 | 18.82 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204539 | 27HUNTRSTN | 115 | 227 | 0.8353 | 1.0235 | 18.82 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204539 | 27HUNTRSTN | 115 | 227 | 0.9097 | 1.0235 | 11.38 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204538 | 27STRABAN | 115 | 227 | 0.8506 | 0.9934 | 14.28 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204538 | 27STRABAN | 115 | 227 | 0.8539 | 0.9934 | 13.95 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204538 | 27STRABAN | 115 | 227 | 0.8541 | 0.9934 | 13.93 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204538 | 27STRABAN | 115 | 227 | 0.8541 | 0.9934 | 13.93 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204537 | 27HILL | 115 | 227 | 0.7543 | 0.9967 | 24.24 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204537 | 27HILL | 115 | 227 | 0.7617 | 0.9967 | 23.5 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204537 | 27HILL | 115 | 227 | 0.762 | 0.9967 | 23.47 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204537 | 27HILL | 115 | 227 | 0.762 | 0.9967 | 23.47 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204537 | 27HILL | 115 | 227 | 0.855 | 0.9967 | 14.17 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204536 | 27HARLEY D | 115 | 227 | 0.767 | 1.0108 | 24.38 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204536 | 27HARLEY D | 115 | 227 | 0.7748 | 1.0108 | 23.6 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204536 | 27HARLEY D | 115 | 227 | 0.7751 | 1.0108 | 23.57 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204536 | 27HARLEY D | 115 | 227 | 0.7751 | 1.0108 | 23.57 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204536 | 27HARLEY D | 115 | 227 | 0.8709 | 1.0108 | 13.99 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204535 | 27HAMILTON | 115 | 227 | 0.7924 | 1.0134 | 22.1 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204535 | 27HAMILTON | 115 | 227 | 0.7981 | 1.0134 | 21.53 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204535 | 27HAMILTON | 115 | 227 | 0.7984 | 1.0134 | 21.5 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204535 | 27HAMILTON | 115 | 227 | 0.7985 | 1.0134 | 21.49 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204535 | 27HAMILTON | 115 | 227 | 0.8838 | 1.0134 | 12.96 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204534 | 27GLADES | 115 | 227 | 0.7683 | 1.0125 | 24.42 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204534 | 27GLADES | 115 | 227 | 0.7766 | 1.0125 | 23.59 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204534 | 27GLADES | 115 | 227 | 0.7769 | 1.0125 | 23.56 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204534 | 27GLADES | 115 | 227 | 0.7769 | 1.0125 | 23.56 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204534 | 27GLADES | 115 | 227 | 0.8721 | 1.0125 | 14.04 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204532 | 27GITTS RN | 115 | 227 | 0.7671 | 0.9954 | 22.83 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204532 | 27GITTS RN | 115 | 227 | 0.7727 | 0.9954 | 22.27 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204532 | 27GITTS RN | 115 | 227 | 0.773 | 0.9954 | 22.24 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204532 | 27GITTS RN | 115 | 227 | 0.7731 | 0.9954 | 22.23 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204532 | 27GITTS RN | 115 | 227 | 0.8606 | 0.9954 | 13.48 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204528 | 27GARDNERS | 115 | 227 | 0.8041 | 1.0205 | 21.64 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204528 | 27GARDNERS | 115 | 227 | 0.8096 | 1.0205 | 21.09 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204528 | 27GARDNERS | 115 | 227 | 0.8099 | 1.0205 | 21.06 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204528 | 27GARDNERS | 115 | 227 | 0.8099 | 1.0205 | 21.06 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204528 | 27GARDNERS | 115 | 227 | 0.8943 | 1.0205 | 12.62 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204527 | 27FAIRVIEW | 115 | 227 | 0.7607 | 0.9901 | 22.94 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204527 | 27FAIRVIEW | 115 | 227 | 0.7664 | 0.9901 | 22.37 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204527 | 27FAIRVIEW | 115 | 227 | 0.7667 | 0.9901 | 22.34 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204527 | 27FAIRVIEW | 115 | 227 | 0.7667 | 0.9901 | 22.34 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204527 | 27FAIRVIEW | 115 | 227 | 0.8544 | 0.9901 | 13.57 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204526 | 27DILLSBRG | 115 | 227 | 0.7892 | 1.0207 | 23.15 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204526 | 27DILLSBRG | 115 | 227 | 0.7955 | 1.0207 | 22.52 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204526 | 27DILLSBRG | 115 | 227 | 0.7958 | 1.0207 | 22.49 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204526 | 27DILLSBRG | 115 | 227 | 0.7958 | 1.0207 | 22.49 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204526 | 27DILLSBRG | 115 | 227 | 0.8886 | 1.0207 | 13.21 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204525 | 27XROADS | 115 | 227 | 0.7558 | 0.9997 | 24.39 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204525 | 27XROADS | 115 | 227 | 0.7637 | 0.9997 | 23.6 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204525 | 27XROADS | 115 | 227 | 0.7641 | 0.9997 | 23.56 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204525 | 27XROADS | 115 | 227 | 0.7641 | 0.9997 | 23.56 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204525 | 27XROADS | 115 | 227 | 0.8577 | 0.9997 | 14.2 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204524 | 27CLY 978 | 115 | 227 | 0.7838 | 1.0192 | 23.54 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204524 | 27CLY 978 | 115 | 227 | 0.7911 | 1.0192 | 22.81 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204524 | 27CLY 978 | 115 | 227 | 0.7914 | 1.0192 | 22.78 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204524 | 27CLY 978 | 115 | 227 | 0.7914 | 1.0192 | 22.78 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204524 | 27CLY 978 | 115 | 227 | 0.8884 | 1.0192 | 13.08 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204523 | 27CLY 975 | 115 | 227 | 0.7838 | 1.0193 | 23.55 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204523 | 27CLY 975 | 115 | 227 | 0.7911 | 1.0193 | 22.82 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204523 | 27CLY 975 | 115 | 227 | 0.7914 | 1.0193 | 22.79 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204523 | 27CLY 975 | 115 | 227 | 0.7914 | 1.0193 | 22.79 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204523 | 27CLY 975 | 115 | 227 | 0.8884 | 1.0193 | 13.09 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204522 | 27CAT TRAC | 115 | 227 | 0.7671 | 1.0117 | 24.46 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204522 | 27CAT TRAC | 115 | 227 | 0.7752 | 1.0117 | 23.65 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204522 | 27CAT TRAC | 115 | 227 | 0.7755 | 1.0117 | 23.62 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204522 | 27CAT TRAC | 115 | 227 | 0.7756 | 1.0117 | 23.61 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204522 | 27CAT TRAC | 115 | 227 | 0.8712 | 1.0117 | 14.05 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204521 | 27BAIR | 115 | 227 | 0.7685 | 1.0066 | 23.81 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204521 | 27BAIR | 115 | 227 | 0.7754 | 1.0066 | 23.12 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204521 | 27BAIR | 115 | 227 | 0.7758 | 1.0066 | 23.08 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204521 | 27BAIR | 115 | 227 | 0.7758 | 1.0066 | 23.08 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204521 | 27BAIR | 115 | 227 | 0.8679 | 1.0066 | 13.87 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204520 | 27ALLEN | 115 | 227 | 0.7927 | 1.0246 | 23.19 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204520 | 27ALLEN | 115 | 227 | 0.7995 | 1.0246 | 22.51 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204520 | 27ALLEN | 115 | 227 | 0.7999 | 1.0246 | 22.47 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204520 | 27ALLEN | 115 | 227 | 0.7999 | 1.0246 | 22.47 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204520 | 27ALLEN | 115 | 227 | 0.8939 | 1.0246 | 13.07 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 203972 | AE1-071-MPT | 115 | 226 | 0.8908 | 1.001 | 11.02 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 203972 | AE1-071-MPT | 115 | 226 | 0.8931 | 1.001 | 10.79 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 203972 | AE1-071-MPT | 115 | 226 | 0.8932 | 1.001 | 10.78 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 203972 | AE1-071-MPT | 115 | 226 | 0.8932 | 1.001 | 10.78 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 203971 | AE1-071-POI | 115 | 226 | 0.8908 | 1.001 | 11.02 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 203971 | AE1-071-POI | 115 | 226 | 0.893 | 1.001 | 10.8 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 203971 | AE1-071-POI | 115 | 226 | 0.8932 | 1.001 | 10.78 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 203971 | AE1-071-POI | 115 | 226 | 0.8932 | 1.001 | 10.78 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 200522 | 26SHADE GP | 115 | 226 | 0.8433 | 0.9937 | 15.04 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 200522 | 26SHADE GP | 115 | 226 | 0.8465 | 0.9937 | 14.72 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 200522 | 26SHADE GP | 115 | 226 | 0.8467 | 0.9937 | 14.7 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 200522 | 26SHADE GP | 115 | 226 | 0.8467 | 0.9937 | 14.7 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 200519 | 26REED TAP | 115 | 226 | 0.8555 | 1.0087 | 15.32 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 200519 | 26REED TAP | 115 | 226 | 0.8591 | 1.0087 | 14.96 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 200519 | 26REED TAP | 115 | 226 | 0.8594 | 1.0087 | 14.93 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 200519 | 26REED TAP | 115 | 226 | 0.8594 | 1.0087 | 14.93 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 200518 | 26REED GAP | 115 | 226 | 0.8553 | 1.0085 | 15.32 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 200518 | 26REED GAP | 115 | 226 | 0.8589 | 1.0085 | 14.96 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 200518 | 26REED GAP | 115 | 226 | 0.8591 | 1.0085 | 14.94 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 200518 | 26REED GAP | 115 | 226 | 0.8591 | 1.0085 | 14.94 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 200512 | 26LEWISTWN | 115 | 226 | 0.8958 | 1.0292 | 13.34 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 200512 | 26LEWISTWN | 115 | 226 | 0.8991 | 1.0292 | 13.01 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 200512 | 26LEWISTWN | 115 | 226 | 0.8994 | 1.0292 | 12.98 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 200512 | 26LEWISTWN | 115 | 226 | 0.8994 | 1.0292 | 12.98 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 200508 | 26HILL VAL | 115 | 226 | 0.835 | 0.9927 | 15.77 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 200508 | 26HILL VAL | 115 | 226 | 0.8384 | 0.9927 | 15.43 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 200508 | 26HILL VAL | 115 | 226 | 0.8386 | 0.9927 | 15.41 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 200508 | 26HILL VAL | 115 | 226 | 0.8386 | 0.9927 | 15.41 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 200504 | 26CARLISLE | 115 | 226 | 0.8786 | 1.0006 | 12.2 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 200504 | 26CARLISLE | 115 | 226 | 0.8813 | 1.0006 | 11.93 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 200504 | 26CARLISLE | 115 | 226 | 0.8815 | 1.0006 | 11.91 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 200504 | 26CARLISLE | 115 | 226 | 0.8815 | 1.0006 | 11.91 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 200502 | 26BLAIN | 115 | 226 | 0.8536 | 1.0072 | 15.36 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 200502 | 26BLAIN | 115 | 226 | 0.8572 | 1.0072 | 15 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 200502 | 26BLAIN | 115 | 226 | 0.8574 | 1.0072 | 14.98 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 200502 | 26BLAIN | 115 | 226 | 0.8574 | 1.0072 | 14.98 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 211354 | ZION | 69 | 229 | 0.8942 | 0.9859 | 9.17 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 211354 | ZION | 69 | 229 | 0.898 | 0.9859 | 8.79 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 211354 | ZION | 69 | 229 | 0.8983 | 0.9859 | 8.76 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 211354 | ZION | 69 | 229 | 0.8983 | 0.9859 | 8.76 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 211301 | UPHA 2 | 69 | 229 | 0.8917 | 0.9837 | 9.2 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 211301 | UPHA 2 | 69 | 229 | 0.8955 | 0.9837 | 8.82 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 211301 | UPHA 2 | 69 | 229 | 0.8958 | 0.9837 | 8.79 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 211301 | UPHA 2 | 69 | 229 | 0.8958 | 0.9837 | 8.79 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 211300 | UPHA 1 | 69 | 229 | 0.8946 | 0.9862 | 9.16 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 211300 | UPHA 1 | 69 | 229 | 0.8984 | 0.9862 | 8.78 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 211300 | UPHA 1 | 69 | 229 | 0.8987 | 0.9862 | 8.75 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 211300 | UPHA 1 | 69 | 229 | 0.8987 | 0.9862 | 8.75 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 211169 | SALL | 69 | 229 | 0.8765 | 0.9707 | 9.42 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 211169 | SALL | 69 | 229 | 0.8804 | 0.9707 | 9.03 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 211169 | SALL | 69 | 229 | 0.8807 | 0.9707 | 9 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 211169 | SALL | 69 | 229 | 0.8807 | 0.9707 | 9 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 211168 | SALL TPH | 69 | 229 | 0.8797 | 0.9733 | 9.36 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 211168 | SALL TPH | 69 | 229 | 0.8836 | 0.9733 | 8.97 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 211168 | SALL TPH | 69 | 229 | 0.8839 | 0.9733 | 8.94 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 211168 | SALL TPH | 69 | 229 | 0.8839 | 0.9733 | 8.94 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 211167 | SALL TP | 69 | 229 | 0.877 | 0.9711 | 9.41 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 211167 | SALL TP | 69 | 229 | 0.8809 | 0.9711 | 9.02 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 211167 | SALL TP | 69 | 229 | 0.8812 | 0.9711 | 8.99 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 211167 | SALL TP | 69 | 229 | 0.8812 | 0.9711 | 8.99 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 211102 | SALI 2 | 69 | 229 | 0.8788 | 0.9726 | 9.38 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 211102 | SALI 2 | 69 | 229 | 0.8827 | 0.9726 | 8.99 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 211102 | SALI 2 | 69 | 229 | 0.883 | 0.9726 | 8.96 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 211102 | SALI 2 | 69 | 229 | 0.883 | 0.9726 | 8.96 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 211101 | SALI 1 | 69 | 229 | 0.8786 | 0.9724 | 9.38 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 211101 | SALI 1 | 69 | 229 | 0.8826 | 0.9724 | 8.98 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 211101 | SALI 1 | 69 | 229 | 0.8828 | 0.9724 | 8.96 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 211101 | SALI 1 | 69 | 229 | 0.8828 | 0.9724 | 8.96 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210926 | MILF NO | 69 | 229 | 0.8912 | 0.9832 | 9.2 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210926 | MILF NO | 69 | 229 | 0.8951 | 0.9832 | 8.81 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210926 | MILF NO | 69 | 229 | 0.8954 | 0.9832 | 8.78 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210926 | MILF NO | 69 | 229 | 0.8954 | 0.9832 | 8.78 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210925 | MILF | 69 | 229 | 0.8912 | 0.9832 | 9.2 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210925 | MILF | 69 | 229 | 0.8951 | 0.9832 | 8.81 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210925 | MILF | 69 | 229 | 0.8954 | 0.9832 | 8.78 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210925 | MILF | 69 | 229 | 0.8954 | 0.9832 | 8.78 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210874 | MACU 1 | 69 | 229 | 0.8935 | 0.9853 | 9.18 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210874 | MACU 1 | 69 | 229 | 0.8973 | 0.9853 | 8.8 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210874 | MACU 1 | 69 | 229 | 0.8976 | 0.9853 | 8.77 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210874 | MACU 1 | 69 | 229 | 0.8976 | 0.9853 | 8.77 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210873 | MACU TP2 | 69 | 229 | 0.8948 | 0.9864 | 9.16 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210873 | MACU TP2 | 69 | 229 | 0.8986 | 0.9864 | 8.78 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210873 | MACU TP2 | 69 | 229 | 0.8989 | 0.9864 | 8.75 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210873 | MACU TP2 | 69 | 229 | 0.8989 | 0.9864 | 8.75 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210857 | MACK TP2 | 69 | 229 | 0.8788 | 0.9726 | 9.38 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210857 | MACK TP2 | 69 | 229 | 0.8828 | 0.9726 | 8.98 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210857 | MACK TP2 | 69 | 229 | 0.883 | 0.9726 | 8.96 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210857 | MACK TP2 | 69 | 229 | 0.883 | 0.9726 | 8.96 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210856 | MACK TP1 | 69 | 229 | 0.8786 | 0.9725 | 9.39 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210856 | MACK TP1 | 69 | 229 | 0.8826 | 0.9725 | 8.99 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210856 | MACK TP1 | 69 | 229 | 0.8829 | 0.9725 | 8.96 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210856 | MACK TP1 | 69 | 229 | 0.8829 | 0.9725 | 8.96 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210855 | MACK 2 | 69 | 229 | 0.8787 | 0.9725 | 9.38 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210855 | MACK 2 | 69 | 229 | 0.8826 | 0.9725 | 8.99 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210855 | MACK 2 | 69 | 229 | 0.8829 | 0.9725 | 8.96 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210855 | MACK 2 | 69 | 229 | 0.8829 | 0.9725 | 8.96 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210854 | MACK 1 | 69 | 229 | 0.8785 | 0.9724 | 9.39 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210854 | MACK 1 | 69 | 229 | 0.8825 | 0.9724 | 8.99 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210854 | MACK 1 | 69 | 229 | 0.8828 | 0.9724 | 8.96 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210854 | MACK 1 | 69 | 229 | 0.8828 | 0.9724 | 8.96 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210794 | LANA 2 | 69 | 229 | 0.8873 | 0.9802 | 9.29 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210794 | LANA 2 | 69 | 229 | 0.8912 | 0.9802 | 8.9 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210794 | LANA 2 | 69 | 229 | 0.8915 | 0.9802 | 8.87 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210794 | LANA 2 | 69 | 229 | 0.8915 | 0.9802 | 8.87 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210793 | LANA 1 | 69 | 229 | 0.8827 | 0.9761 | 9.34 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210793 | LANA 1 | 69 | 229 | 0.8866 | 0.9761 | 8.95 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210793 | LANA 1 | 69 | 229 | 0.8869 | 0.9761 | 8.92 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210793 | LANA 1 | 69 | 229 | 0.8869 | 0.9761 | 8.92 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210792 | ELHE TP1 | 69 | 229 | 0.8762 | 0.9705 | 9.43 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210792 | ELHE TP1 | 69 | 229 | 0.8802 | 0.9705 | 9.03 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210792 | ELHE TP1 | 69 | 229 | 0.8805 | 0.9705 | 9 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210792 | ELHE TP1 | 69 | 229 | 0.8805 | 0.9705 | 9 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210791 | ELHE TP2 | 69 | 229 | 0.8838 | 0.9773 | 9.35 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210791 | ELHE TP2 | 69 | 229 | 0.8878 | 0.9773 | 8.95 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210791 | ELHE TP2 | 69 | 229 | 0.888 | 0.9773 | 8.93 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210791 | ELHE TP2 | 69 | 229 | 0.8881 | 0.9773 | 8.92 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210741 | HOSE | 69 | 229 | 0.897 | 0.9883 | 9.13 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210741 | HOSE | 69 | 229 | 0.9008 | 0.9883 | 8.75 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210741 | HOSE | 69 | 229 | 0.9011 | 0.9883 | 8.72 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210741 | HOSE | 69 | 229 | 0.9011 | 0.9883 | 8.72 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210681 | FOHI | 69 | 229 | 0.8822 | 0.9758 | 9.36 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210681 | FOHI | 69 | 229 | 0.8861 | 0.9758 | 8.97 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210681 | FOHI | 69 | 229 | 0.8864 | 0.9758 | 8.94 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210681 | FOHI | 69 | 229 | 0.8864 | 0.9758 | 8.94 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210680 | FOHI TP2 | 69 | 229 | 0.8822 | 0.9758 | 9.36 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210680 | FOHI TP2 | 69 | 229 | 0.8861 | 0.9758 | 8.97 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210680 | FOHI TP2 | 69 | 229 | 0.8864 | 0.9758 | 8.94 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210680 | FOHI TP2 | 69 | 229 | 0.8864 | 0.9758 | 8.94 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210679 | FOHI TP1 | 69 | 229 | 0.874 | 0.9685 | 9.45 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210679 | FOHI TP1 | 69 | 229 | 0.878 | 0.9685 | 9.05 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210679 | FOHI TP1 | 69 | 229 | 0.8782 | 0.9685 | 9.03 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210679 | FOHI TP1 | 69 | 229 | 0.8782 | 0.9685 | 9.03 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210643 | EMMA TP1 | 69 | 229 | 0.884 | 0.9771 | 9.31 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210643 | EMMA TP1 | 69 | 229 | 0.8879 | 0.9771 | 8.92 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210643 | EMMA TP1 | 69 | 229 | 0.8882 | 0.9771 | 8.89 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210643 | EMMA TP1 | 69 | 229 | 0.8882 | 0.9771 | 8.89 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210642 | EMMA TP2 | 69 | 229 | 0.8842 | 0.9772 | 9.3 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210642 | EMMA TP2 | 69 | 229 | 0.8881 | 0.9772 | 8.91 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210642 | EMMA TP2 | 69 | 229 | 0.8883 | 0.9772 | 8.89 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210642 | EMMA TP2 | 69 | 229 | 0.8884 | 0.9772 | 8.88 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210641 | EMMA 2 | 69 | 229 | 0.8829 | 0.9761 | 9.32 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210641 | EMMA 2 | 69 | 229 | 0.8868 | 0.9761 | 8.93 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210641 | EMMA 2 | 69 | 229 | 0.8871 | 0.9761 | 8.9 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210641 | EMMA 2 | 69 | 229 | 0.8871 | 0.9761 | 8.9 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210640 | EMMA 1 | 69 | 229 | 0.8829 | 0.9761 | 9.32 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210640 | EMMA 1 | 69 | 229 | 0.8868 | 0.9761 | 8.93 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210640 | EMMA 1 | 69 | 229 | 0.8871 | 0.9761 | 8.9 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210640 | EMMA 1 | 69 | 229 | 0.8871 | 0.9761 | 8.9 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210624 | ELHE 2 | 69 | 229 | 0.8819 | 0.9756 | 9.37 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210624 | ELHE 2 | 69 | 229 | 0.8859 | 0.9756 | 8.97 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210624 | ELHE 2 | 69 | 229 | 0.8861 | 0.9756 | 8.95 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210624 | ELHE 2 | 69 | 229 | 0.8861 | 0.9756 | 8.95 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210623 | ELHE 1 | 69 | 229 | 0.8735 | 0.9681 | 9.46 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210623 | ELHE 1 | 69 | 229 | 0.8775 | 0.9681 | 9.06 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210623 | ELHE 1 | 69 | 229 | 0.8778 | 0.9681 | 9.03 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210623 | ELHE 1 | 69 | 229 | 0.8778 | 0.9681 | 9.03 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210589 | EGRE 2 | 69 | 229 | 0.892 | 0.984 | 9.2 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210589 | EGRE 2 | 69 | 229 | 0.8959 | 0.984 | 8.81 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210589 | EGRE 2 | 69 | 229 | 0.8962 | 0.984 | 8.78 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210589 | EGRE 2 | 69 | 229 | 0.8962 | 0.984 | 8.78 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210588 | EGRE 1 | 69 | 229 | 0.8954 | 0.9869 | 9.15 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210588 | EGRE 1 | 69 | 229 | 0.8992 | 0.9869 | 8.77 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210588 | EGRE 1 | 69 | 229 | 0.8995 | 0.9869 | 8.74 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210588 | EGRE 1 | 69 | 229 | 0.8995 | 0.9869 | 8.74 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210587 | EGRETP 2 | 69 | 229 | 0.8927 | 0.9846 | 9.19 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210587 | EGRETP 2 | 69 | 229 | 0.8966 | 0.9846 | 8.8 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210587 | EGRETP 2 | 69 | 229 | 0.8968 | 0.9846 | 8.78 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210587 | EGRETP 2 | 69 | 229 | 0.8968 | 0.9846 | 8.78 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210586 | EGRETP 1 | 69 | 229 | 0.8954 | 0.987 | 9.16 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210586 | EGRETP 1 | 69 | 229 | 0.8993 | 0.987 | 8.77 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210586 | EGRETP 1 | 69 | 229 | 0.8995 | 0.987 | 8.75 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210586 | EGRETP 1 | 69 | 229 | 0.8995 | 0.987 | 8.75 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210470 | BRPR | 69 | 229 | 0.8954 | 0.9869 | 9.15 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210470 | BRPR | 69 | 229 | 0.8992 | 0.9869 | 8.77 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210470 | BRPR | 69 | 229 | 0.8995 | 0.9869 | 8.74 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210470 | BRPR | 69 | 229 | 0.8995 | 0.9869 | 8.74 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210389 | ALPA TP2 | 69 | 229 | 0.88 | 0.9736 | 9.36 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210389 | ALPA TP2 | 69 | 229 | 0.884 | 0.9736 | 8.96 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210389 | ALPA TP2 | 69 | 229 | 0.8842 | 0.9736 | 8.94 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210389 | ALPA TP2 | 69 | 229 | 0.8842 | 0.9736 | 8.94 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210388 | ALPA TP1 | 69 | 229 | 0.8797 | 0.9734 | 9.37 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210388 | ALPA TP1 | 69 | 229 | 0.8837 | 0.9734 | 8.97 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210388 | ALPA TP1 | 69 | 229 | 0.884 | 0.9734 | 8.94 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210388 | ALPA TP1 | 69 | 229 | 0.884 | 0.9734 | 8.94 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210387 | ALPA 2 | 69 | 229 | 0.8795 | 0.9731 | 9.36 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210387 | ALPA 2 | 69 | 229 | 0.8834 | 0.9731 | 8.97 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210387 | ALPA 2 | 69 | 229 | 0.8837 | 0.9731 | 8.94 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210387 | ALPA 2 | 69 | 229 | 0.8837 | 0.9731 | 8.94 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210386 | ALPA 1 | 69 | 229 | 0.879 | 0.9728 | 9.38 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210386 | ALPA 1 | 69 | 229 | 0.883 | 0.9728 | 8.98 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210386 | ALPA 1 | 69 | 229 | 0.8833 | 0.9728 | 8.95 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210386 | ALPA 1 | 69 | 229 | 0.8833 | 0.9728 | 8.95 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210357 | WIND 2 | 69 | 229 | 0.7734 | 0.9775 | 20.41 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210357 | WIND 2 | 69 | 229 | 0.7803 | 0.9775 | 19.72 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210357 | WIND 2 | 69 | 229 | 0.7807 | 0.9775 | 19.68 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210357 | WIND 2 | 69 | 229 | 0.7807 | 0.9775 | 19.68 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210357 | WIND 2 | 69 | 229 | 0.8663 | 0.9775 | 11.12 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210356 | WIND 1 | 69 | 229 | 0.7766 | 0.9798 | 20.32 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210356 | WIND 1 | 69 | 229 | 0.7835 | 0.9798 | 19.63 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210356 | WIND 1 | 69 | 229 | 0.7839 | 0.9798 | 19.59 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210356 | WIND 1 | 69 | 229 | 0.7839 | 0.9798 | 19.59 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210356 | WIND 1 | 69 | 229 | 0.8692 | 0.9798 | 11.06 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210347 | COCO 2 | 69 | 229 | 0.7519 | 0.9711 | 21.92 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210347 | COCO 2 | 69 | 229 | 0.7591 | 0.9711 | 21.2 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210347 | COCO 2 | 69 | 229 | 0.7595 | 0.9711 | 21.16 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210347 | COCO 2 | 69 | 229 | 0.7595 | 0.9711 | 21.16 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210347 | COCO 2 | 69 | 229 | 0.8514 | 0.9711 | 11.97 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210345 | COCO 1 | 69 | 229 | 0.7514 | 0.9706 | 21.92 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210345 | COCO 1 | 69 | 229 | 0.7586 | 0.9706 | 21.2 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210345 | COCO 1 | 69 | 229 | 0.759 | 0.9706 | 21.16 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210345 | COCO 1 | 69 | 229 | 0.759 | 0.9706 | 21.16 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210345 | COCO 1 | 69 | 229 | 0.8509 | 0.9706 | 11.97 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210344 | WHHI TI2 | 69 | 229 | 0.7612 | 0.9862 | 22.5 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210344 | WHHI TI2 | 69 | 229 | 0.7689 | 0.9862 | 21.73 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210344 | WHHI TI2 | 69 | 229 | 0.7693 | 0.9862 | 21.69 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210344 | WHHI TI2 | 69 | 229 | 0.7693 | 0.9862 | 21.69 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210344 | WHHI TI2 | 69 | 229 | 0.8614 | 0.9862 | 12.48 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210343 | WHHI TI1 | 69 | 229 | 0.7612 | 0.9862 | 22.5 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210343 | WHHI TI1 | 69 | 229 | 0.7689 | 0.9862 | 21.73 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210343 | WHHI TI1 | 69 | 229 | 0.7693 | 0.9862 | 21.69 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210343 | WHHI TI1 | 69 | 229 | 0.7693 | 0.9862 | 21.69 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210343 | WHHI TI1 | 69 | 229 | 0.8614 | 0.9862 | 12.48 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210341 | WHHI 2 | 69 | 229 | 0.7595 | 0.985 | 22.55 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210341 | WHHI 2 | 69 | 229 | 0.7673 | 0.985 | 21.77 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210341 | WHHI 2 | 69 | 229 | 0.7677 | 0.985 | 21.73 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210341 | WHHI 2 | 69 | 229 | 0.7677 | 0.985 | 21.73 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210341 | WHHI 2 | 69 | 229 | 0.8601 | 0.985 | 12.49 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210340 | WHHI 1 | 69 | 229 | 0.7595 | 0.985 | 22.55 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210340 | WHHI 1 | 69 | 229 | 0.7672 | 0.985 | 21.78 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210340 | WHHI 1 | 69 | 229 | 0.7676 | 0.985 | 21.74 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210340 | WHHI 1 | 69 | 229 | 0.7677 | 0.985 | 21.73 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210340 | WHHI 1 | 69 | 229 | 0.86 | 0.985 | 12.5 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210339 | WHHI TP2 | 69 | 229 | 0.7572 | 0.9828 | 22.56 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210339 | WHHI TP2 | 69 | 229 | 0.765 | 0.9828 | 21.78 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210339 | WHHI TP2 | 69 | 229 | 0.7654 | 0.9828 | 21.74 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210339 | WHHI TP2 | 69 | 229 | 0.7654 | 0.9828 | 21.74 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210339 | WHHI TP2 | 69 | 229 | 0.8577 | 0.9828 | 12.51 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210338 | WHHI TP1 | 69 | 229 | 0.7597 | 0.9858 | 22.61 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210338 | WHHI TP1 | 69 | 229 | 0.7675 | 0.9858 | 21.83 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210338 | WHHI TP1 | 69 | 229 | 0.7679 | 0.9858 | 21.79 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210338 | WHHI TP1 | 69 | 229 | 0.7679 | 0.9858 | 21.79 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210338 | WHHI TP1 | 69 | 229 | 0.8605 | 0.9858 | 12.53 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210333 | WIGR | 69 | 229 | 0.7649 | 0.9796 | 21.47 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210333 | WIGR | 69 | 229 | 0.7721 | 0.9796 | 20.75 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210333 | WIGR | 69 | 229 | 0.7725 | 0.9796 | 20.71 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210333 | WIGR | 69 | 229 | 0.7725 | 0.9796 | 20.71 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210333 | WIGR | 69 | 229 | 0.8594 | 0.9796 | 12.02 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210332 | WSHO TI2 | 69 | 229 | 0.7612 | 0.9867 | 22.55 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210332 | WSHO TI2 | 69 | 229 | 0.7689 | 0.9867 | 21.78 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210332 | WSHO TI2 | 69 | 229 | 0.7693 | 0.9867 | 21.74 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210332 | WSHO TI2 | 69 | 229 | 0.7693 | 0.9867 | 21.74 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210332 | WSHO TI2 | 69 | 229 | 0.8617 | 0.9867 | 12.5 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210331 | WSHO TI1 | 69 | 229 | 0.7589 | 0.9838 | 22.49 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210331 | WSHO TI1 | 69 | 229 | 0.7666 | 0.9838 | 21.72 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210331 | WSHO TI1 | 69 | 229 | 0.767 | 0.9838 | 21.68 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210331 | WSHO TI1 | 69 | 229 | 0.767 | 0.9838 | 21.68 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210331 | WSHO TI1 | 69 | 229 | 0.859 | 0.9838 | 12.48 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210330 | WSHO | 69 | 229 | 0.7625 | 0.987 | 22.45 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210330 | WSHO | 69 | 229 | 0.7702 | 0.987 | 21.68 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210330 | WSHO | 69 | 229 | 0.7706 | 0.987 | 21.64 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210330 | WSHO | 69 | 229 | 0.7706 | 0.987 | 21.64 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210330 | WSHO | 69 | 229 | 0.8625 | 0.987 | 12.45 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210328 | WCARTI24 | 69 | 229 | 0.7698 | 0.9782 | 20.84 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210328 | WCARTI24 | 69 | 229 | 0.7765 | 0.9782 | 20.17 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210328 | WCARTI24 | 69 | 229 | 0.7769 | 0.9782 | 20.13 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210328 | WCARTI24 | 69 | 229 | 0.7769 | 0.9782 | 20.13 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210328 | WCARTI24 | 69 | 229 | 0.862 | 0.9782 | 11.62 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210327 | WCARUG24 | 69 | 229 | 0.7698 | 0.9782 | 20.84 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210327 | WCARUG24 | 69 | 229 | 0.7765 | 0.9782 | 20.17 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210327 | WCARUG24 | 69 | 229 | 0.7769 | 0.9782 | 20.13 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210327 | WCARUG24 | 69 | 229 | 0.7769 | 0.9782 | 20.13 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210327 | WCARUG24 | 69 | 229 | 0.862 | 0.9782 | 11.62 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210326 | WCARTI13 | 69 | 229 | 0.775 | 0.9826 | 20.76 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210326 | WCARTI13 | 69 | 229 | 0.7816 | 0.9826 | 20.1 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210326 | WCARTI13 | 69 | 229 | 0.782 | 0.9826 | 20.06 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210326 | WCARTI13 | 69 | 229 | 0.782 | 0.9826 | 20.06 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210326 | WCARTI13 | 69 | 229 | 0.8669 | 0.9826 | 11.57 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210325 | WCARUG13 | 69 | 229 | 0.775 | 0.9826 | 20.76 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210325 | WCARUG13 | 69 | 229 | 0.7816 | 0.9826 | 20.1 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210325 | WCARUG13 | 69 | 229 | 0.782 | 0.9826 | 20.06 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210325 | WCARUG13 | 69 | 229 | 0.782 | 0.9826 | 20.06 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210325 | WCARUG13 | 69 | 229 | 0.8669 | 0.9826 | 11.57 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210324 | WCAR 2 | 69 | 229 | 0.7449 | 0.9625 | 21.76 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210324 | WCAR 2 | 69 | 229 | 0.7512 | 0.9625 | 21.13 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210324 | WCAR 2 | 69 | 229 | 0.7516 | 0.9625 | 21.09 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210324 | WCAR 2 | 69 | 229 | 0.7516 | 0.9625 | 21.09 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210324 | WCAR 2 | 69 | 229 | 0.8412 | 0.9625 | 12.13 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210320 | WCAR 1 | 69 | 229 | 0.7452 | 0.9686 | 22.34 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210320 | WCAR 1 | 69 | 229 | 0.7522 | 0.9686 | 21.64 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210320 | WCAR 1 | 69 | 229 | 0.7526 | 0.9686 | 21.6 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210320 | WCAR 1 | 69 | 229 | 0.7526 | 0.9686 | 21.6 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210320 | WCAR 1 | 69 | 229 | 0.8439 | 0.9686 | 12.47 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210317 | WERT 1 | 69 | 229 | 0.7758 | 0.9855 | 20.97 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210317 | WERT 1 | 69 | 229 | 0.7825 | 0.9855 | 20.3 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210317 | WERT 1 | 69 | 229 | 0.7829 | 0.9855 | 20.26 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210317 | WERT 1 | 69 | 229 | 0.7829 | 0.9855 | 20.26 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210317 | WERT 1 | 69 | 229 | 0.8688 | 0.9855 | 11.67 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210316 | WERT 2 | 69 | 229 | 0.7746 | 0.9849 | 21.03 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210316 | WERT 2 | 69 | 229 | 0.7814 | 0.9849 | 20.35 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210316 | WERT 2 | 69 | 229 | 0.7818 | 0.9849 | 20.31 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210316 | WERT 2 | 69 | 229 | 0.7818 | 0.9849 | 20.31 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210316 | WERT 2 | 69 | 229 | 0.8679 | 0.9849 | 11.7 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210312 | WALN UG21 | 69 | 229 | 0.7554 | 0.9774 | 22.2 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210312 | WALN UG21 | 69 | 229 | 0.763 | 0.9774 | 21.44 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210312 | WALN UG21 | 69 | 229 | 0.7634 | 0.9774 | 21.4 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210312 | WALN UG21 | 69 | 229 | 0.7634 | 0.9774 | 21.4 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210312 | WALN UG21 | 69 | 229 | 0.8581 | 0.9774 | 11.93 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210309 | WALNUGH2 | 69 | 229 | 0.7554 | 0.9774 | 22.2 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210309 | WALNUGH2 | 69 | 229 | 0.763 | 0.9774 | 21.44 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210309 | WALNUGH2 | 69 | 229 | 0.7634 | 0.9774 | 21.4 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210309 | WALNUGH2 | 69 | 229 | 0.7634 | 0.9774 | 21.4 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210309 | WALNUGH2 | 69 | 229 | 0.8581 | 0.9774 | 11.93 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210308 | WALNUGH1 | 69 | 229 | 0.7555 | 0.9774 | 22.19 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210308 | WALNUGH1 | 69 | 229 | 0.763 | 0.9774 | 21.44 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210308 | WALNUGH1 | 69 | 229 | 0.7634 | 0.9774 | 21.4 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210308 | WALNUGH1 | 69 | 229 | 0.7635 | 0.9774 | 21.39 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210308 | WALNUGH1 | 69 | 229 | 0.8581 | 0.9774 | 11.93 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210307 | WALNUGD2 | 69 | 229 | 0.7714 | 0.9832 | 21.18 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210307 | WALNUGD2 | 69 | 229 | 0.7785 | 0.9832 | 20.47 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210307 | WALNUGD2 | 69 | 229 | 0.7789 | 0.9832 | 20.43 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210307 | WALNUGD2 | 69 | 229 | 0.7789 | 0.9832 | 20.43 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210307 | WALNUGD2 | 69 | 229 | 0.868 | 0.9832 | 11.52 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210306 | WALNUGD1 | 69 | 229 | 0.7726 | 0.9847 | 21.21 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210306 | WALNUGD1 | 69 | 229 | 0.7797 | 0.9847 | 20.5 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210306 | WALNUGD1 | 69 | 229 | 0.7801 | 0.9847 | 20.46 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210306 | WALNUGD1 | 69 | 229 | 0.7802 | 0.9847 | 20.45 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210306 | WALNUGD1 | 69 | 229 | 0.8694 | 0.9847 | 11.53 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210305 | WALNDATI | 69 | 229 | 0.7717 | 0.9836 | 21.19 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210305 | WALNDATI | 69 | 229 | 0.7788 | 0.9836 | 20.48 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210305 | WALNDATI | 69 | 229 | 0.7792 | 0.9836 | 20.44 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210305 | WALNDATI | 69 | 229 | 0.7792 | 0.9836 | 20.44 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210305 | WALNDATI | 69 | 229 | 0.8684 | 0.9836 | 11.52 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210304 | WALN | 69 | 229 | 0.7725 | 0.9849 | 21.24 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210304 | WALN | 69 | 229 | 0.7797 | 0.9849 | 20.52 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210304 | WALN | 69 | 229 | 0.7801 | 0.9849 | 20.48 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210304 | WALN | 69 | 229 | 0.7801 | 0.9849 | 20.48 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210304 | WALN | 69 | 229 | 0.8695 | 0.9849 | 11.54 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210300 | WALK TP2 | 69 | 229 | 0.8283 | 0.9473 | 11.9 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210300 | WALK TP2 | 69 | 229 | 0.8326 | 0.9473 | 11.47 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210300 | WALK TP2 | 69 | 229 | 0.8329 | 0.9473 | 11.44 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210300 | WALK TP2 | 69 | 229 | 0.8329 | 0.9473 | 11.44 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210298 | WALK | 69 | 229 | 0.8281 | 0.9471 | 11.9 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210298 | WALK | 69 | 229 | 0.8325 | 0.9471 | 11.46 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210298 | WALK | 69 | 229 | 0.8328 | 0.9471 | 11.43 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210298 | WALK | 69 | 229 | 0.8328 | 0.9471 | 11.43 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210292 | TRTE | 69 | 229 | 0.7463 | 0.9737 | 22.74 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210292 | TRTE | 69 | 229 | 0.7541 | 0.9737 | 21.96 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210292 | TRTE | 69 | 229 | 0.7545 | 0.9737 | 21.92 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210292 | TRTE | 69 | 229 | 0.7545 | 0.9737 | 21.92 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210292 | TRTE | 69 | 229 | 0.8477 | 0.9737 | 12.6 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210286 | THOM | 69 | 229 | 0.8292 | 0.9673 | 13.81 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210286 | THOM | 69 | 229 | 0.8335 | 0.9673 | 13.38 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210286 | THOM | 69 | 229 | 0.8338 | 0.9673 | 13.35 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210286 | THOM | 69 | 229 | 0.8338 | 0.9673 | 13.35 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210285 | THOM TP2 | 69 | 229 | 0.8314 | 0.9549 | 12.35 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210285 | THOM TP2 | 69 | 229 | 0.8357 | 0.9549 | 11.92 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210285 | THOM TP2 | 69 | 229 | 0.836 | 0.9549 | 11.89 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210285 | THOM TP2 | 69 | 229 | 0.836 | 0.9549 | 11.89 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210284 | THOM TP1 | 69 | 229 | 0.8292 | 0.9673 | 13.81 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210284 | THOM TP1 | 69 | 229 | 0.8335 | 0.9673 | 13.38 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210284 | THOM TP1 | 69 | 229 | 0.8338 | 0.9673 | 13.35 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210284 | THOM TP1 | 69 | 229 | 0.8338 | 0.9673 | 13.35 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210278 | UPS 2 | 69 | 229 | 0.7583 | 0.9767 | 21.84 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210278 | UPS 2 | 69 | 229 | 0.7656 | 0.9767 | 21.11 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210278 | UPS 2 | 69 | 229 | 0.766 | 0.9767 | 21.07 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210278 | UPS 2 | 69 | 229 | 0.766 | 0.9767 | 21.07 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210278 | UPS 2 | 69 | 229 | 0.8579 | 0.9767 | 11.88 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210277 | UPS TP2 | 69 | 229 | 0.7586 | 0.9769 | 21.83 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210277 | UPS TP2 | 69 | 229 | 0.7658 | 0.9769 | 21.11 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210277 | UPS TP2 | 69 | 229 | 0.7662 | 0.9769 | 21.07 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210277 | UPS TP2 | 69 | 229 | 0.7662 | 0.9769 | 21.07 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210277 | UPS TP2 | 69 | 229 | 0.8581 | 0.9769 | 11.88 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210276 | UPS 1 | 69 | 229 | 0.7583 | 0.9767 | 21.84 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210276 | UPS 1 | 69 | 229 | 0.7655 | 0.9767 | 21.12 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210276 | UPS 1 | 69 | 229 | 0.7659 | 0.9767 | 21.08 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210276 | UPS 1 | 69 | 229 | 0.7659 | 0.9767 | 21.08 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210276 | UPS 1 | 69 | 229 | 0.8579 | 0.9767 | 11.88 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210275 | UPS TP1 | 69 | 229 | 0.7585 | 0.9769 | 21.84 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210275 | UPS TP1 | 69 | 229 | 0.7658 | 0.9769 | 21.11 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210275 | UPS TP1 | 69 | 229 | 0.7662 | 0.9769 | 21.07 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210275 | UPS TP1 | 69 | 229 | 0.7662 | 0.9769 | 21.07 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210275 | UPS TP1 | 69 | 229 | 0.8581 | 0.9769 | 11.88 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210274 | SWAT TP2 | 69 | 229 | 0.7557 | 0.976 | 22.03 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210274 | SWAT TP2 | 69 | 229 | 0.7631 | 0.976 | 21.29 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210274 | SWAT TP2 | 69 | 229 | 0.7635 | 0.976 | 21.25 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210274 | SWAT TP2 | 69 | 229 | 0.7635 | 0.976 | 21.25 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210274 | SWAT TP2 | 69 | 229 | 0.8568 | 0.976 | 11.92 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210273 | SWAT | 69 | 229 | 0.7532 | 0.9743 | 22.11 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210273 | SWAT | 69 | 229 | 0.7606 | 0.9743 | 21.37 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210273 | SWAT | 69 | 229 | 0.761 | 0.9743 | 21.33 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210273 | SWAT | 69 | 229 | 0.761 | 0.9743 | 21.33 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210273 | SWAT | 69 | 229 | 0.8547 | 0.9743 | 11.96 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210272 | SWAT TP1 | 69 | 229 | 0.7551 | 0.9757 | 22.06 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210272 | SWAT TP1 | 69 | 229 | 0.7625 | 0.9757 | 21.32 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210272 | SWAT TP1 | 69 | 229 | 0.7629 | 0.9757 | 21.28 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210272 | SWAT TP1 | 69 | 229 | 0.763 | 0.9757 | 21.27 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210272 | SWAT TP1 | 69 | 229 | 0.8564 | 0.9757 | 11.93 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210266 | SUMM | 69 | 229 | 0.7684 | 0.9845 | 21.61 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210266 | SUMM | 69 | 229 | 0.7754 | 0.9845 | 20.91 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210266 | SUMM | 69 | 229 | 0.7758 | 0.9845 | 20.87 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210266 | SUMM | 69 | 229 | 0.7758 | 0.9845 | 20.87 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210266 | SUMM | 69 | 229 | 0.8647 | 0.9845 | 11.98 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210265 | SUMM TP | 69 | 229 | 0.7689 | 0.9848 | 21.59 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210265 | SUMM TP | 69 | 229 | 0.7758 | 0.9848 | 20.9 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210265 | SUMM TP | 69 | 229 | 0.7762 | 0.9848 | 20.86 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210265 | SUMM TP | 69 | 229 | 0.7762 | 0.9848 | 20.86 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210265 | SUMM TP | 69 | 229 | 0.8651 | 0.9848 | 11.97 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210264 | SUMM TP1 | 69 | 229 | 0.773 | 0.9872 | 21.42 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210264 | SUMM TP1 | 69 | 229 | 0.7799 | 0.9872 | 20.73 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210264 | SUMM TP1 | 69 | 229 | 0.7803 | 0.9872 | 20.69 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210264 | SUMM TP1 | 69 | 229 | 0.7803 | 0.9872 | 20.69 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210264 | SUMM TP1 | 69 | 229 | 0.8683 | 0.9872 | 11.89 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210263 | SUMM TP2 | 69 | 229 | 0.7689 | 0.9848 | 21.59 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210263 | SUMM TP2 | 69 | 229 | 0.7758 | 0.9848 | 20.9 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210263 | SUMM TP2 | 69 | 229 | 0.7762 | 0.9848 | 20.86 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210263 | SUMM TP2 | 69 | 229 | 0.7762 | 0.9848 | 20.86 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210263 | SUMM TP2 | 69 | 229 | 0.8651 | 0.9848 | 11.97 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210258 | SPHI 2 | 69 | 229 | 0.7426 | 0.9707 | 22.81 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210258 | SPHI 2 | 69 | 229 | 0.7504 | 0.9707 | 22.03 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210258 | SPHI 2 | 69 | 229 | 0.7508 | 0.9707 | 21.99 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210258 | SPHI 2 | 69 | 229 | 0.7508 | 0.9707 | 21.99 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210258 | SPHI 2 | 69 | 229 | 0.8444 | 0.9707 | 12.63 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210257 | SPHI 1 | 69 | 229 | 0.7521 | 0.983 | 23.09 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210257 | SPHI 1 | 69 | 229 | 0.7601 | 0.983 | 22.29 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210257 | SPHI 1 | 69 | 229 | 0.7605 | 0.983 | 22.25 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210257 | SPHI 1 | 69 | 229 | 0.7605 | 0.983 | 22.25 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210257 | SPHI 1 | 69 | 229 | 0.8554 | 0.983 | 12.76 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210254 | SPAN 1 | 69 | 229 | 0.7513 | 0.9768 | 22.55 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210254 | SPAN 1 | 69 | 229 | 0.759 | 0.9768 | 21.78 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210254 | SPAN 1 | 69 | 229 | 0.7594 | 0.9768 | 21.74 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210254 | SPAN 1 | 69 | 229 | 0.7594 | 0.9768 | 21.74 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210254 | SPAN 1 | 69 | 229 | 0.8515 | 0.9768 | 12.53 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210252 | SPAN 2 | 69 | 229 | 0.7587 | 0.9861 | 22.74 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210252 | SPAN 2 | 69 | 229 | 0.7665 | 0.9861 | 21.96 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210252 | SPAN 2 | 69 | 229 | 0.7669 | 0.9861 | 21.92 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210252 | SPAN 2 | 69 | 229 | 0.7669 | 0.9861 | 21.92 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210252 | SPAN 2 | 69 | 229 | 0.86 | 0.9861 | 12.61 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210246 | SSDL NO1 | 69 | 229 | 0.7643 | 0.9768 | 21.25 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210246 | SSDL NO1 | 69 | 229 | 0.771 | 0.9768 | 20.58 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210246 | SSDL NO1 | 69 | 229 | 0.7714 | 0.9768 | 20.54 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210246 | SSDL NO1 | 69 | 229 | 0.7714 | 0.9768 | 20.54 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210246 | SSDL NO1 | 69 | 229 | 0.8583 | 0.9768 | 11.85 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210245 | SSDL | 69 | 229 | 0.8404 | 0.975 | 13.46 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210245 | SSDL | 69 | 229 | 0.8446 | 0.975 | 13.04 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210245 | SSDL | 69 | 229 | 0.8449 | 0.975 | 13.01 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210245 | SSDL | 69 | 229 | 0.8449 | 0.975 | 13.01 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210242 | SSDL NO2 | 69 | 229 | 0.7692 | 0.9792 | 21 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210242 | SSDL NO2 | 69 | 229 | 0.7757 | 0.9792 | 20.35 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210242 | SSDL NO2 | 69 | 229 | 0.7761 | 0.9792 | 20.31 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210242 | SSDL NO2 | 69 | 229 | 0.7761 | 0.9792 | 20.31 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210242 | SSDL NO2 | 69 | 229 | 0.8621 | 0.9792 | 11.71 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210237 | SHER 2 | 69 | 229 | 0.7542 | 0.9735 | 21.93 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210237 | SHER 2 | 69 | 229 | 0.7614 | 0.9735 | 21.21 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210237 | SHER 2 | 69 | 229 | 0.7618 | 0.9735 | 21.17 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210237 | SHER 2 | 69 | 229 | 0.7618 | 0.9735 | 21.17 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210237 | SHER 2 | 69 | 229 | 0.8539 | 0.9735 | 11.96 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210236 | SHER 1 | 69 | 229 | 0.7542 | 0.9735 | 21.93 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210236 | SHER 1 | 69 | 229 | 0.7614 | 0.9735 | 21.21 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210236 | SHER 1 | 69 | 229 | 0.7618 | 0.9735 | 21.17 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210236 | SHER 1 | 69 | 229 | 0.7618 | 0.9735 | 21.17 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210236 | SHER 1 | 69 | 229 | 0.8539 | 0.9735 | 11.96 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210230 | SDLE | 69 | 229 | 0.8409 | 0.9754 | 13.45 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210230 | SDLE | 69 | 229 | 0.845 | 0.9754 | 13.04 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210230 | SDLE | 69 | 229 | 0.8453 | 0.9754 | 13.01 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210230 | SDLE | 69 | 229 | 0.8453 | 0.9754 | 13.01 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210229 | SDLE TI | 69 | 229 | 0.7643 | 0.9768 | 21.25 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210229 | SDLE TI | 69 | 229 | 0.771 | 0.9768 | 20.58 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210229 | SDLE TI | 69 | 229 | 0.7714 | 0.9768 | 20.54 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210229 | SDLE TI | 69 | 229 | 0.7714 | 0.9768 | 20.54 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210229 | SDLE TI | 69 | 229 | 0.8583 | 0.9768 | 11.85 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210228 | SDLE TP2 | 69 | 229 | 0.8416 | 0.9761 | 13.45 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210228 | SDLE TP2 | 69 | 229 | 0.8458 | 0.9761 | 13.03 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210228 | SDLE TP2 | 69 | 229 | 0.8461 | 0.9761 | 13 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210228 | SDLE TP2 | 69 | 229 | 0.8461 | 0.9761 | 13 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210227 | SDLE TP1 | 69 | 229 | 0.8409 | 0.9754 | 13.45 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210227 | SDLE TP1 | 69 | 229 | 0.845 | 0.9754 | 13.04 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210227 | SDLE TP1 | 69 | 229 | 0.8453 | 0.9754 | 13.01 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210227 | SDLE TP1 | 69 | 229 | 0.8453 | 0.9754 | 13.01 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210223 | SHLA 2 | 69 | 229 | 0.7542 | 0.9835 | 22.93 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210223 | SHLA 2 | 69 | 229 | 0.7621 | 0.9835 | 22.14 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210223 | SHLA 2 | 69 | 229 | 0.7625 | 0.9835 | 22.1 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210223 | SHLA 2 | 69 | 229 | 0.7625 | 0.9835 | 22.1 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210223 | SHLA 2 | 69 | 229 | 0.8567 | 0.9835 | 12.68 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210222 | SHLA 1 | 69 | 229 | 0.7468 | 0.9742 | 22.74 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210222 | SHLA 1 | 69 | 229 | 0.7546 | 0.9742 | 21.96 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210222 | SHLA 1 | 69 | 229 | 0.755 | 0.9742 | 21.92 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210222 | SHLA 1 | 69 | 229 | 0.755 | 0.9742 | 21.92 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210222 | SHLA 1 | 69 | 229 | 0.8481 | 0.9742 | 12.61 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210216 | RUTH 1 | 69 | 229 | 0.7632 | 0.9814 | 21.82 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210216 | RUTH 1 | 69 | 229 | 0.7707 | 0.9814 | 21.07 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210216 | RUTH 1 | 69 | 229 | 0.7712 | 0.9814 | 21.02 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210216 | RUTH 1 | 69 | 229 | 0.7712 | 0.9814 | 21.02 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210216 | RUTH 1 | 69 | 229 | 0.864 | 0.9814 | 11.74 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210215 | RUTH 2 | 69 | 229 | 0.7746 | 0.9898 | 21.52 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210215 | RUTH 2 | 69 | 229 | 0.7821 | 0.9898 | 20.77 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210215 | RUTH 2 | 69 | 229 | 0.7825 | 0.9898 | 20.73 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210215 | RUTH 2 | 69 | 229 | 0.7825 | 0.9898 | 20.73 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210215 | RUTH 2 | 69 | 229 | 0.8739 | 0.9898 | 11.59 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210209 | ROSS 4 | 69 | 229 | 0.7619 | 0.9866 | 22.47 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210209 | ROSS 4 | 69 | 229 | 0.7696 | 0.9866 | 21.7 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210209 | ROSS 4 | 69 | 229 | 0.77 | 0.9866 | 21.66 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210209 | ROSS 4 | 69 | 229 | 0.77 | 0.9866 | 21.66 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210209 | ROSS 4 | 69 | 229 | 0.862 | 0.9866 | 12.46 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210208 | ROSS 3 | 69 | 229 | 0.7611 | 0.9861 | 22.5 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210208 | ROSS 3 | 69 | 229 | 0.7688 | 0.9861 | 21.73 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210208 | ROSS 3 | 69 | 229 | 0.7692 | 0.9861 | 21.69 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210208 | ROSS 3 | 69 | 229 | 0.7692 | 0.9861 | 21.69 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210208 | ROSS 3 | 69 | 229 | 0.8613 | 0.9861 | 12.48 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210202 | ROSE NO | 69 | 229 | 0.7551 | 0.9772 | 22.21 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210202 | ROSE NO | 69 | 229 | 0.7627 | 0.9772 | 21.45 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210202 | ROSE NO | 69 | 229 | 0.7631 | 0.9772 | 21.41 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210202 | ROSE NO | 69 | 229 | 0.7631 | 0.9772 | 21.41 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210202 | ROSE NO | 69 | 229 | 0.8579 | 0.9772 | 11.93 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210200 | ROSE 2 | 69 | 229 | 0.7575 | 0.9863 | 22.88 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210200 | ROSE 2 | 69 | 229 | 0.7654 | 0.9863 | 22.09 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210200 | ROSE 2 | 69 | 229 | 0.7658 | 0.9863 | 22.05 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210200 | ROSE 2 | 69 | 229 | 0.7658 | 0.9863 | 22.05 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210200 | ROSE 2 | 69 | 229 | 0.8594 | 0.9863 | 12.69 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210199 | ROSE 1 | 69 | 229 | 0.747 | 0.9725 | 22.55 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210199 | ROSE 1 | 69 | 229 | 0.7547 | 0.9725 | 21.78 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210199 | ROSE 1 | 69 | 229 | 0.7551 | 0.9725 | 21.74 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210199 | ROSE 1 | 69 | 229 | 0.7551 | 0.9725 | 21.74 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210199 | ROSE 1 | 69 | 229 | 0.8472 | 0.9725 | 12.53 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210194 | ROCK TP1 | 69 | 229 | 0.7805 | 0.9851 | 20.46 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210194 | ROCK TP1 | 69 | 229 | 0.7874 | 0.9851 | 19.77 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210194 | ROCK TP1 | 69 | 229 | 0.7879 | 0.9851 | 19.72 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210194 | ROCK TP1 | 69 | 229 | 0.7879 | 0.9851 | 19.72 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210194 | ROCK TP1 | 69 | 229 | 0.8737 | 0.9851 | 11.14 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210193 | ROCK TP2 | 69 | 229 | 0.7819 | 0.9858 | 20.39 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210193 | ROCK TP2 | 69 | 229 | 0.7888 | 0.9858 | 19.7 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210193 | ROCK TP2 | 69 | 229 | 0.7892 | 0.9858 | 19.66 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210193 | ROCK TP2 | 69 | 229 | 0.7892 | 0.9858 | 19.66 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210193 | ROCK TP2 | 69 | 229 | 0.8747 | 0.9858 | 11.11 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210192 | ROCK TP | 69 | 229 | 0.7797 | 0.9845 | 20.48 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210192 | ROCK TP | 69 | 229 | 0.7866 | 0.9845 | 19.79 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210192 | ROCK TP | 69 | 229 | 0.787 | 0.9845 | 19.75 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210192 | ROCK TP | 69 | 229 | 0.787 | 0.9845 | 19.75 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210192 | ROCK TP | 69 | 229 | 0.873 | 0.9845 | 11.15 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210186 | RFLD | 69 | 229 | 0.8251 | 0.9648 | 13.97 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210186 | RFLD | 69 | 229 | 0.8295 | 0.9648 | 13.53 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210186 | RFLD | 69 | 229 | 0.8298 | 0.9648 | 13.5 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210186 | RFLD | 69 | 229 | 0.8298 | 0.9648 | 13.5 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210185 | RFLD TP1 | 69 | 229 | 0.8257 | 0.9652 | 13.95 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210185 | RFLD TP1 | 69 | 229 | 0.8301 | 0.9652 | 13.51 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210185 | RFLD TP1 | 69 | 229 | 0.8304 | 0.9652 | 13.48 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210185 | RFLD TP1 | 69 | 229 | 0.8304 | 0.9652 | 13.48 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210182 | REE-HEUG | 69 | 229 | 0.7545 | 0.974 | 21.95 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210182 | REE-HEUG | 69 | 229 | 0.7617 | 0.974 | 21.23 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210182 | REE-HEUG | 69 | 229 | 0.7621 | 0.974 | 21.19 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210182 | REE-HEUG | 69 | 229 | 0.7621 | 0.974 | 21.19 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210182 | REE-HEUG | 69 | 229 | 0.8544 | 0.974 | 11.96 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210181 | REE-HEOH | 69 | 229 | 0.7545 | 0.974 | 21.95 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210181 | REE-HEOH | 69 | 229 | 0.7617 | 0.974 | 21.23 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210181 | REE-HEOH | 69 | 229 | 0.7621 | 0.974 | 21.19 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210181 | REE-HEOH | 69 | 229 | 0.7621 | 0.974 | 21.19 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210181 | REE-HEOH | 69 | 229 | 0.8544 | 0.974 | 11.96 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210180 | REES TP1 | 69 | 229 | 0.7514 | 0.9706 | 21.92 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210180 | REES TP1 | 69 | 229 | 0.7586 | 0.9706 | 21.2 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210180 | REES TP1 | 69 | 229 | 0.759 | 0.9706 | 21.16 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210180 | REES TP1 | 69 | 229 | 0.759 | 0.9706 | 21.16 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210180 | REES TP1 | 69 | 229 | 0.8509 | 0.9706 | 11.97 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210179 | REES TP2 | 69 | 229 | 0.7519 | 0.9711 | 21.92 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210179 | REES TP2 | 69 | 229 | 0.7591 | 0.9711 | 21.2 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210179 | REES TP2 | 69 | 229 | 0.7595 | 0.9711 | 21.16 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210179 | REES TP2 | 69 | 229 | 0.7595 | 0.9711 | 21.16 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210179 | REES TP2 | 69 | 229 | 0.8514 | 0.9711 | 11.97 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210173 | RALS | 69 | 229 | 0.7509 | 0.9685 | 21.76 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210173 | RALS | 69 | 229 | 0.7582 | 0.9685 | 21.03 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210173 | RALS | 69 | 229 | 0.7585 | 0.9685 | 21 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210173 | RALS | 69 | 229 | 0.7586 | 0.9685 | 20.99 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210173 | RALS | 69 | 229 | 0.8464 | 0.9685 | 12.21 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210172 | RALS TP | 69 | 229 | 0.7531 | 0.9704 | 21.73 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210172 | RALS TP | 69 | 229 | 0.7603 | 0.9704 | 21.01 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210172 | RALS TP | 69 | 229 | 0.7607 | 0.9704 | 20.97 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210172 | RALS TP | 69 | 229 | 0.7607 | 0.9704 | 20.97 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210172 | RALS TP | 69 | 229 | 0.8485 | 0.9704 | 12.19 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210166 | QUOA | 69 | 229 | 0.7456 | 0.9732 | 22.76 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210166 | QUOA | 69 | 229 | 0.7534 | 0.9732 | 21.98 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210166 | QUOA | 69 | 229 | 0.7538 | 0.9732 | 21.94 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210166 | QUOA | 69 | 229 | 0.7538 | 0.9732 | 21.94 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210166 | QUOA | 69 | 229 | 0.847 | 0.9732 | 12.62 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210160 | PURI | 69 | 229 | 0.7452 | 0.9728 | 22.76 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210160 | PURI | 69 | 229 | 0.753 | 0.9728 | 21.98 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210160 | PURI | 69 | 229 | 0.7534 | 0.9728 | 21.94 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210160 | PURI | 69 | 229 | 0.7534 | 0.9728 | 21.94 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210160 | PURI | 69 | 229 | 0.8467 | 0.9728 | 12.61 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210154 | PENN 2 | 69 | 229 | 0.7674 | 0.9837 | 21.63 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210154 | PENN 2 | 69 | 229 | 0.7743 | 0.9837 | 20.94 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210154 | PENN 2 | 69 | 229 | 0.7747 | 0.9837 | 20.9 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210154 | PENN 2 | 69 | 229 | 0.7747 | 0.9837 | 20.9 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210154 | PENN 2 | 69 | 229 | 0.8638 | 0.9837 | 11.99 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210153 | PENN 1 | 69 | 229 | 0.7718 | 0.9864 | 21.46 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210153 | PENN 1 | 69 | 229 | 0.7787 | 0.9864 | 20.77 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210153 | PENN 1 | 69 | 229 | 0.7791 | 0.9864 | 20.73 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210153 | PENN 1 | 69 | 229 | 0.7792 | 0.9864 | 20.72 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210153 | PENN 1 | 69 | 229 | 0.8673 | 0.9864 | 11.91 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210141 | PROG TP2 | 69 | 229 | 0.7697 | 0.9746 | 20.49 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210141 | PROG TP2 | 69 | 229 | 0.7766 | 0.9746 | 19.8 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210141 | PROG TP2 | 69 | 229 | 0.777 | 0.9746 | 19.76 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210141 | PROG TP2 | 69 | 229 | 0.777 | 0.9746 | 19.76 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210141 | PROG TP2 | 69 | 229 | 0.8629 | 0.9746 | 11.17 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210140 | PROG TP1 | 69 | 229 | 0.7738 | 0.9777 | 20.39 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210140 | PROG TP1 | 69 | 229 | 0.7807 | 0.9777 | 19.7 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210140 | PROG TP1 | 69 | 229 | 0.7811 | 0.9777 | 19.66 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210140 | PROG TP1 | 69 | 229 | 0.7812 | 0.9777 | 19.65 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210140 | PROG TP1 | 69 | 229 | 0.8668 | 0.9777 | 11.09 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210136 | OBER 2 | 69 | 229 | 0.7549 | 0.9765 | 22.16 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210136 | OBER 2 | 69 | 229 | 0.7624 | 0.9765 | 21.41 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210136 | OBER 2 | 69 | 229 | 0.7628 | 0.9765 | 21.37 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210136 | OBER 2 | 69 | 229 | 0.7628 | 0.9765 | 21.37 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210136 | OBER 2 | 69 | 229 | 0.8571 | 0.9765 | 11.94 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210133 | AMP1 TP1 | 69 | 229 | 0.7552 | 0.9768 | 22.16 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210133 | AMP1 TP1 | 69 | 229 | 0.7627 | 0.9768 | 21.41 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210133 | AMP1 TP1 | 69 | 229 | 0.7631 | 0.9768 | 21.37 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210133 | AMP1 TP1 | 69 | 229 | 0.7631 | 0.9768 | 21.37 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210133 | AMP1 TP1 | 69 | 229 | 0.8575 | 0.9768 | 11.93 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210132 | OBER 1 | 69 | 229 | 0.7551 | 0.9763 | 22.12 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210132 | OBER 1 | 69 | 229 | 0.7626 | 0.9763 | 21.37 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210132 | OBER 1 | 69 | 229 | 0.763 | 0.9763 | 21.33 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210132 | OBER 1 | 69 | 229 | 0.763 | 0.9763 | 21.33 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210132 | OBER 1 | 69 | 229 | 0.857 | 0.9763 | 11.93 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210127 | NOTT 1 | 69 | 229 | 0.7422 | 0.9659 | 22.37 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210127 | NOTT 1 | 69 | 229 | 0.7493 | 0.9659 | 21.66 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210127 | NOTT 1 | 69 | 229 | 0.7497 | 0.9659 | 21.62 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210127 | NOTT 1 | 69 | 229 | 0.7497 | 0.9659 | 21.62 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210127 | NOTT 1 | 69 | 229 | 0.8412 | 0.9659 | 12.47 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210126 | NOTT TP1 | 69 | 229 | 0.7451 | 0.9678 | 22.27 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210126 | NOTT TP1 | 69 | 229 | 0.7521 | 0.9678 | 21.57 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210126 | NOTT TP1 | 69 | 229 | 0.7525 | 0.9678 | 21.53 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210126 | NOTT TP1 | 69 | 229 | 0.7525 | 0.9678 | 21.53 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210126 | NOTT TP1 | 69 | 229 | 0.8436 | 0.9678 | 12.42 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210125 | NOTT 2 | 69 | 229 | 0.7453 | 0.9628 | 21.75 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210125 | NOTT 2 | 69 | 229 | 0.7517 | 0.9628 | 21.11 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210125 | NOTT 2 | 69 | 229 | 0.752 | 0.9628 | 21.08 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210125 | NOTT 2 | 69 | 229 | 0.752 | 0.9628 | 21.08 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210125 | NOTT 2 | 69 | 229 | 0.8416 | 0.9628 | 12.12 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210124 | NOTT TP2 | 69 | 229 | 0.7469 | 0.9639 | 21.7 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210124 | NOTT TP2 | 69 | 229 | 0.7533 | 0.9639 | 21.06 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210124 | NOTT TP2 | 69 | 229 | 0.7537 | 0.9639 | 21.02 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210124 | NOTT TP2 | 69 | 229 | 0.7537 | 0.9639 | 21.02 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210124 | NOTT TP2 | 69 | 229 | 0.843 | 0.9639 | 12.09 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210117 | NHAR TP2 | 69 | 229 | 0.7731 | 0.983 | 20.99 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210117 | NHAR TP2 | 69 | 229 | 0.7801 | 0.983 | 20.29 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210117 | NHAR TP2 | 69 | 229 | 0.7806 | 0.983 | 20.24 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210117 | NHAR TP2 | 69 | 229 | 0.7806 | 0.983 | 20.24 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210117 | NHAR TP2 | 69 | 229 | 0.8688 | 0.983 | 11.42 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210116 | NHAR TP1 | 69 | 229 | 0.774 | 0.9841 | 21.01 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210116 | NHAR TP1 | 69 | 229 | 0.7811 | 0.9841 | 20.3 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210116 | NHAR TP1 | 69 | 229 | 0.7815 | 0.9841 | 20.26 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210116 | NHAR TP1 | 69 | 229 | 0.7815 | 0.9841 | 20.26 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210116 | NHAR TP1 | 69 | 229 | 0.8699 | 0.9841 | 11.42 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210113 | NEWV 2 | 69 | 229 | 0.7472 | 0.9643 | 21.71 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210113 | NEWV 2 | 69 | 229 | 0.7536 | 0.9643 | 21.07 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210113 | NEWV 2 | 69 | 229 | 0.754 | 0.9643 | 21.03 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210113 | NEWV 2 | 69 | 229 | 0.754 | 0.9643 | 21.03 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210113 | NEWV 2 | 69 | 229 | 0.8433 | 0.9643 | 12.1 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210111 | NEWV 1 | 69 | 229 | 0.7453 | 0.9681 | 22.28 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210111 | NEWV 1 | 69 | 229 | 0.7523 | 0.9681 | 21.58 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210111 | NEWV 1 | 69 | 229 | 0.7527 | 0.9681 | 21.54 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210111 | NEWV 1 | 69 | 229 | 0.7527 | 0.9681 | 21.54 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210111 | NEWV 1 | 69 | 229 | 0.8438 | 0.9681 | 12.43 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210105 | NEWP | 69 | 229 | 0.839 | 0.9705 | 13.15 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210105 | NEWP | 69 | 229 | 0.8431 | 0.9705 | 12.74 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210105 | NEWP | 69 | 229 | 0.8435 | 0.9705 | 12.7 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210105 | NEWP | 69 | 229 | 0.8435 | 0.9705 | 12.7 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210104 | NEWP TP2 | 69 | 229 | 0.839 | 0.9705 | 13.15 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210104 | NEWP TP2 | 69 | 229 | 0.8431 | 0.9705 | 12.74 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210104 | NEWP TP2 | 69 | 229 | 0.8435 | 0.9705 | 12.7 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210104 | NEWP TP2 | 69 | 229 | 0.8435 | 0.9705 | 12.7 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210103 | NEWP TP1 | 69 | 229 | 0.84 | 0.9751 | 13.51 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210103 | NEWP TP1 | 69 | 229 | 0.8442 | 0.9751 | 13.09 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210103 | NEWP TP1 | 69 | 229 | 0.8445 | 0.9751 | 13.06 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210103 | NEWP TP1 | 69 | 229 | 0.8445 | 0.9751 | 13.06 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210098 | NEKI | 69 | 229 | 0.7797 | 0.9853 | 20.56 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210098 | NEKI | 69 | 229 | 0.7863 | 0.9853 | 19.9 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210098 | NEKI | 69 | 229 | 0.7867 | 0.9853 | 19.86 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210098 | NEKI | 69 | 229 | 0.7867 | 0.9853 | 19.86 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210098 | NEKI | 69 | 229 | 0.8706 | 0.9853 | 11.47 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210097 | NEBL TP2 | 69 | 229 | 0.8438 | 0.9777 | 13.39 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210097 | NEBL TP2 | 69 | 229 | 0.848 | 0.9777 | 12.97 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210097 | NEBL TP2 | 69 | 229 | 0.8483 | 0.9777 | 12.94 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210097 | NEBL TP2 | 69 | 229 | 0.8483 | 0.9777 | 12.94 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210096 | NEBL TP1 | 69 | 229 | 0.8437 | 0.9776 | 13.39 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210096 | NEBL TP1 | 69 | 229 | 0.8478 | 0.9776 | 12.98 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210096 | NEBL TP1 | 69 | 229 | 0.8481 | 0.9776 | 12.95 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210096 | NEBL TP1 | 69 | 229 | 0.8481 | 0.9776 | 12.95 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210094 | NEBL | 69 | 229 | 0.8437 | 0.9776 | 13.39 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210094 | NEBL | 69 | 229 | 0.8478 | 0.9776 | 12.98 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210094 | NEBL | 69 | 229 | 0.8481 | 0.9776 | 12.95 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210094 | NEBL | 69 | 229 | 0.8481 | 0.9776 | 12.95 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210092 | NCAD | 69 | 229 | 0.7566 | 0.9855 | 22.89 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210092 | NCAD | 69 | 229 | 0.7644 | 0.9855 | 22.11 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210092 | NCAD | 69 | 229 | 0.7648 | 0.9855 | 22.07 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210092 | NCAD | 69 | 229 | 0.7648 | 0.9855 | 22.07 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210092 | NCAD | 69 | 229 | 0.8584 | 0.9855 | 12.71 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210091 | NCAD TP | 69 | 229 | 0.7574 | 0.9862 | 22.88 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210091 | NCAD TP | 69 | 229 | 0.7652 | 0.9862 | 22.1 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210091 | NCAD TP | 69 | 229 | 0.7656 | 0.9862 | 22.06 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210091 | NCAD TP | 69 | 229 | 0.7656 | 0.9862 | 22.06 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210091 | NCAD TP | 69 | 229 | 0.8592 | 0.9862 | 12.7 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210085 | MORO | 69 | 229 | 0.7402 | 0.9591 | 21.89 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210085 | MORO | 69 | 229 | 0.7465 | 0.9591 | 21.26 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210085 | MORO | 69 | 229 | 0.7469 | 0.9591 | 21.22 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210085 | MORO | 69 | 229 | 0.7469 | 0.9591 | 21.22 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210085 | MORO | 69 | 229 | 0.8372 | 0.9591 | 12.19 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210078 | MOAL 2 | 69 | 229 | 0.7616 | 0.9865 | 22.49 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210078 | MOAL 2 | 69 | 229 | 0.7693 | 0.9865 | 21.72 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210078 | MOAL 2 | 69 | 229 | 0.7697 | 0.9865 | 21.68 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210078 | MOAL 2 | 69 | 229 | 0.7697 | 0.9865 | 21.68 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210078 | MOAL 2 | 69 | 229 | 0.8618 | 0.9865 | 12.47 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210077 | MOAL 1 | 69 | 229 | 0.7615 | 0.9864 | 22.49 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210077 | MOAL 1 | 69 | 229 | 0.7692 | 0.9864 | 21.72 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210077 | MOAL 1 | 69 | 229 | 0.7696 | 0.9864 | 21.68 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210077 | MOAL 1 | 69 | 229 | 0.7696 | 0.9864 | 21.68 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210077 | MOAL 1 | 69 | 229 | 0.8617 | 0.9864 | 12.47 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210076 | MOAL TP4 | 69 | 229 | 0.7624 | 0.987 | 22.46 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210076 | MOAL TP4 | 69 | 229 | 0.7701 | 0.987 | 21.69 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210076 | MOAL TP4 | 69 | 229 | 0.7706 | 0.987 | 21.64 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210076 | MOAL TP4 | 69 | 229 | 0.7706 | 0.987 | 21.64 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210076 | MOAL TP4 | 69 | 229 | 0.8625 | 0.987 | 12.45 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210075 | MOAL TP3 | 69 | 229 | 0.7624 | 0.987 | 22.46 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210075 | MOAL TP3 | 69 | 229 | 0.7701 | 0.987 | 21.69 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210075 | MOAL TP3 | 69 | 229 | 0.7705 | 0.987 | 21.65 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210075 | MOAL TP3 | 69 | 229 | 0.7705 | 0.987 | 21.65 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210075 | MOAL TP3 | 69 | 229 | 0.8624 | 0.987 | 12.46 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210069 | MIFF | 69 | 229 | 0.8291 | 0.9441 | 11.5 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210069 | MIFF | 69 | 229 | 0.8335 | 0.9441 | 11.06 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210069 | MIFF | 69 | 229 | 0.8338 | 0.9441 | 11.03 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210069 | MIFF | 69 | 229 | 0.8338 | 0.9441 | 11.03 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210068 | WALK TP1 | 69 | 229 | 0.8292 | 0.9674 | 13.82 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210068 | WALK TP1 | 69 | 229 | 0.8335 | 0.9674 | 13.39 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210068 | WALK TP1 | 69 | 229 | 0.8338 | 0.9674 | 13.36 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210068 | WALK TP1 | 69 | 229 | 0.8338 | 0.9674 | 13.36 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210067 | MIFF TP2 | 69 | 229 | 0.8291 | 0.9441 | 11.5 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210067 | MIFF TP2 | 69 | 229 | 0.8334 | 0.9441 | 11.07 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210067 | MIFF TP2 | 69 | 229 | 0.8338 | 0.9441 | 11.03 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210067 | MIFF TP2 | 69 | 229 | 0.8338 | 0.9441 | 11.03 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210064 | MTON 1 | 69 | 229 | 0.7535 | 0.9709 | 21.74 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210064 | MTON 1 | 69 | 229 | 0.7604 | 0.9709 | 21.05 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210064 | MTON 1 | 69 | 229 | 0.7608 | 0.9709 | 21.01 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210064 | MTON 1 | 69 | 229 | 0.7608 | 0.9709 | 21.01 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210064 | MTON 1 | 69 | 229 | 0.8497 | 0.9709 | 12.12 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210062 | MTON 2 | 69 | 229 | 0.7578 | 0.9713 | 21.35 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210062 | MTON 2 | 69 | 229 | 0.7643 | 0.9713 | 20.7 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210062 | MTON 2 | 69 | 229 | 0.7647 | 0.9713 | 20.66 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210062 | MTON 2 | 69 | 229 | 0.7647 | 0.9713 | 20.66 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210062 | MTON 2 | 69 | 229 | 0.8523 | 0.9713 | 11.9 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210056 | MEISTIRI | 69 | 229 | 0.8257 | 0.9652 | 13.95 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210056 | MEISTIRI | 69 | 229 | 0.8301 | 0.9652 | 13.51 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210056 | MEISTIRI | 69 | 229 | 0.8304 | 0.9652 | 13.48 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210056 | MEISTIRI | 69 | 229 | 0.8304 | 0.9652 | 13.48 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210049 | MTON TP1 | 69 | 229 | 0.7537 | 0.971 | 21.73 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210049 | MTON TP1 | 69 | 229 | 0.7606 | 0.971 | 21.04 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210049 | MTON TP1 | 69 | 229 | 0.761 | 0.971 | 21 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210049 | MTON TP1 | 69 | 229 | 0.761 | 0.971 | 21 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210049 | MTON TP1 | 69 | 229 | 0.8498 | 0.971 | 12.12 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210048 | MTON TP2 | 69 | 229 | 0.7579 | 0.9714 | 21.35 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210048 | MTON TP2 | 69 | 229 | 0.7644 | 0.9714 | 20.7 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210048 | MTON TP2 | 69 | 229 | 0.7648 | 0.9714 | 20.66 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210048 | MTON TP2 | 69 | 229 | 0.7648 | 0.9714 | 20.66 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210048 | MTON TP2 | 69 | 229 | 0.8524 | 0.9714 | 11.9 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210046 | SMEC TP2 | 69 | 229 | 0.7649 | 0.9797 | 21.48 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210046 | SMEC TP2 | 69 | 229 | 0.7721 | 0.9797 | 20.76 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210046 | SMEC TP2 | 69 | 229 | 0.7725 | 0.9797 | 20.72 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210046 | SMEC TP2 | 69 | 229 | 0.7725 | 0.9797 | 20.72 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210046 | SMEC TP2 | 69 | 229 | 0.8595 | 0.9797 | 12.02 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210045 | SMEC TP1 | 69 | 229 | 0.7634 | 0.9786 | 21.52 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210045 | SMEC TP1 | 69 | 229 | 0.7707 | 0.9786 | 20.79 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210045 | SMEC TP1 | 69 | 229 | 0.7711 | 0.9786 | 20.75 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210045 | SMEC TP1 | 69 | 229 | 0.7711 | 0.9786 | 20.75 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210045 | SMEC TP1 | 69 | 229 | 0.8582 | 0.9786 | 12.04 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210043 | SMEC | 69 | 229 | 0.7634 | 0.9786 | 21.52 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210043 | SMEC | 69 | 229 | 0.7707 | 0.9786 | 20.79 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210043 | SMEC | 69 | 229 | 0.7711 | 0.9786 | 20.75 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210043 | SMEC | 69 | 229 | 0.7711 | 0.9786 | 20.75 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210043 | SMEC | 69 | 229 | 0.8582 | 0.9786 | 12.04 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210041 | MECH 4 | 69 | 229 | 0.7538 | 0.971 | 21.72 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210041 | MECH 4 | 69 | 229 | 0.761 | 0.971 | 21 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210041 | MECH 4 | 69 | 229 | 0.7614 | 0.971 | 20.96 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210041 | MECH 4 | 69 | 229 | 0.7614 | 0.971 | 20.96 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210041 | MECH 4 | 69 | 229 | 0.8492 | 0.971 | 12.18 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210040 | MECH 3 | 69 | 229 | 0.7598 | 0.976 | 21.62 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210040 | MECH 3 | 69 | 229 | 0.7671 | 0.976 | 20.89 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210040 | MECH 3 | 69 | 229 | 0.7674 | 0.976 | 20.86 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210040 | MECH 3 | 69 | 229 | 0.7674 | 0.976 | 20.86 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210040 | MECH 3 | 69 | 229 | 0.855 | 0.976 | 12.1 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210034 | MCAL TP1 | 69 | 229 | 0.8285 | 0.967 | 13.85 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210034 | MCAL TP1 | 69 | 229 | 0.8328 | 0.967 | 13.42 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210034 | MCAL TP1 | 69 | 229 | 0.8331 | 0.967 | 13.39 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210034 | MCAL TP1 | 69 | 229 | 0.8331 | 0.967 | 13.39 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210033 | MCAL | 69 | 229 | 0.8286 | 0.9671 | 13.85 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210033 | MCAL | 69 | 229 | 0.8329 | 0.9671 | 13.42 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210033 | MCAL | 69 | 229 | 0.8332 | 0.9671 | 13.39 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210033 | MCAL | 69 | 229 | 0.8332 | 0.9671 | 13.39 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210021 | LING 2 | 69 | 229 | 0.7692 | 0.9843 | 21.51 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210021 | LING 2 | 69 | 229 | 0.7767 | 0.9843 | 20.76 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210021 | LING 2 | 69 | 229 | 0.7771 | 0.9843 | 20.72 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210021 | LING 2 | 69 | 229 | 0.7771 | 0.9843 | 20.72 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210021 | LING 2 | 69 | 229 | 0.8684 | 0.9843 | 11.59 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210020 | LING 1 | 69 | 229 | 0.7694 | 0.9843 | 21.49 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210020 | LING 1 | 69 | 229 | 0.7769 | 0.9843 | 20.74 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210020 | LING 1 | 69 | 229 | 0.7773 | 0.9843 | 20.7 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210020 | LING 1 | 69 | 229 | 0.7773 | 0.9843 | 20.7 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210020 | LING 1 | 69 | 229 | 0.8685 | 0.9843 | 11.58 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210019 | LING TP2 | 69 | 229 | 0.7732 | 0.987 | 21.38 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210019 | LING TP2 | 69 | 229 | 0.7806 | 0.987 | 20.64 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210019 | LING TP2 | 69 | 229 | 0.7811 | 0.987 | 20.59 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210019 | LING TP2 | 69 | 229 | 0.7811 | 0.987 | 20.59 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210019 | LING TP2 | 69 | 229 | 0.8717 | 0.987 | 11.53 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210018 | LING TP1 | 69 | 229 | 0.7733 | 0.987 | 21.37 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210018 | LING TP1 | 69 | 229 | 0.7807 | 0.987 | 20.63 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210018 | LING TP1 | 69 | 229 | 0.7812 | 0.987 | 20.58 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210018 | LING TP1 | 69 | 229 | 0.7812 | 0.987 | 20.58 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210018 | LING TP1 | 69 | 229 | 0.8717 | 0.987 | 11.53 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210011 | LAWN 1 | 69 | 229 | 0.7597 | 0.9795 | 21.98 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210011 | LAWN 1 | 69 | 229 | 0.7673 | 0.9795 | 21.22 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210011 | LAWN 1 | 69 | 229 | 0.7677 | 0.9795 | 21.18 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210011 | LAWN 1 | 69 | 229 | 0.7677 | 0.9795 | 21.18 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210011 | LAWN 1 | 69 | 229 | 0.8613 | 0.9795 | 11.82 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210010 | LAWN 2 | 69 | 229 | 0.774 | 0.9901 | 21.61 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210010 | LAWN 2 | 69 | 229 | 0.7816 | 0.9901 | 20.85 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210010 | LAWN 2 | 69 | 229 | 0.782 | 0.9901 | 20.81 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210010 | LAWN 2 | 69 | 229 | 0.782 | 0.9901 | 20.81 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210010 | LAWN 2 | 69 | 229 | 0.8739 | 0.9901 | 11.62 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210004 | LAPU | 69 | 229 | 0.753 | 0.9703 | 21.73 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210004 | LAPU | 69 | 229 | 0.7602 | 0.9703 | 21.01 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210004 | LAPU | 69 | 229 | 0.7606 | 0.9703 | 20.97 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210004 | LAPU | 69 | 229 | 0.7606 | 0.9703 | 20.97 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210004 | LAPU | 69 | 229 | 0.8484 | 0.9703 | 12.19 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210003 | LAPU TP | 69 | 229 | 0.753 | 0.9704 | 21.74 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210003 | LAPU TP | 69 | 229 | 0.7602 | 0.9704 | 21.02 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210003 | LAPU TP | 69 | 229 | 0.7606 | 0.9704 | 20.98 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210003 | LAPU TP | 69 | 229 | 0.7606 | 0.9704 | 20.98 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 210003 | LAPU TP | 69 | 229 | 0.8485 | 0.9704 | 12.19 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209998 | JUNINPCC | 69 | 229 | 0.8434 | 0.9769 | 13.35 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209998 | JUNINPCC | 69 | 229 | 0.8475 | 0.9769 | 12.94 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209998 | JUNINPCC | 69 | 229 | 0.8478 | 0.9769 | 12.91 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209998 | JUNINPCC | 69 | 229 | 0.8478 | 0.9769 | 12.91 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209997 | JUNI | 69 | 229 | 0.8441 | 0.978 | 13.39 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209997 | JUNI | 69 | 229 | 0.8483 | 0.978 | 12.97 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209997 | JUNI | 69 | 229 | 0.8486 | 0.978 | 12.94 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209997 | JUNI | 69 | 229 | 0.8486 | 0.978 | 12.94 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209991 | IBM | 69 | 229 | 0.7794 | 0.9853 | 20.59 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209991 | IBM | 69 | 229 | 0.786 | 0.9853 | 19.93 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209991 | IBM | 69 | 229 | 0.7864 | 0.9853 | 19.89 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209991 | IBM | 69 | 229 | 0.7864 | 0.9853 | 19.89 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209991 | IBM | 69 | 229 | 0.8704 | 0.9853 | 11.49 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209985 | HUMM | 69 | 229 | 0.7591 | 0.9772 | 21.81 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209985 | HUMM | 69 | 229 | 0.7663 | 0.9772 | 21.09 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209985 | HUMM | 69 | 229 | 0.7667 | 0.9772 | 21.05 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209985 | HUMM | 69 | 229 | 0.7668 | 0.9772 | 21.04 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209985 | HUMM | 69 | 229 | 0.8585 | 0.9772 | 11.87 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209977 | HEME 2 | 69 | 229 | 0.7542 | 0.9735 | 21.93 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209977 | HEME 2 | 69 | 229 | 0.7614 | 0.9735 | 21.21 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209977 | HEME 2 | 69 | 229 | 0.7618 | 0.9735 | 21.17 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209977 | HEME 2 | 69 | 229 | 0.7618 | 0.9735 | 21.17 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209977 | HEME 2 | 69 | 229 | 0.8539 | 0.9735 | 11.96 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209976 | HEME 1 | 69 | 229 | 0.7542 | 0.9735 | 21.93 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209976 | HEME 1 | 69 | 229 | 0.7614 | 0.9735 | 21.21 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209976 | HEME 1 | 69 | 229 | 0.7618 | 0.9735 | 21.17 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209976 | HEME 1 | 69 | 229 | 0.7618 | 0.9735 | 21.17 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209976 | HEME 1 | 69 | 229 | 0.854 | 0.9735 | 11.95 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209966 | HERS 2 | 69 | 229 | 0.7545 | 0.974 | 21.95 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209966 | HERS 2 | 69 | 229 | 0.7617 | 0.974 | 21.23 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209966 | HERS 2 | 69 | 229 | 0.7621 | 0.974 | 21.19 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209966 | HERS 2 | 69 | 229 | 0.7621 | 0.974 | 21.19 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209966 | HERS 2 | 69 | 229 | 0.8544 | 0.974 | 11.96 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209965 | HERS 1 | 69 | 229 | 0.7545 | 0.974 | 21.95 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209965 | HERS 1 | 69 | 229 | 0.7617 | 0.974 | 21.23 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209965 | HERS 1 | 69 | 229 | 0.7621 | 0.974 | 21.19 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209965 | HERS 1 | 69 | 229 | 0.7621 | 0.974 | 21.19 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209965 | HERS 1 | 69 | 229 | 0.8544 | 0.974 | 11.96 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209959 | PAXT IPP TP | 69 | 229 | 0.7557 | 0.9774 | 22.17 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209959 | PAXT IPP TP | 69 | 229 | 0.7633 | 0.9774 | 21.41 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209959 | PAXT IPP TP | 69 | 229 | 0.7637 | 0.9774 | 21.37 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209959 | PAXT IPP TP | 69 | 229 | 0.7637 | 0.9774 | 21.37 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209959 | PAXT IPP TP | 69 | 229 | 0.8583 | 0.9774 | 11.91 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209957 | HAR UG11 | 69 | 229 | 0.7554 | 0.9774 | 22.2 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209957 | HAR UG11 | 69 | 229 | 0.763 | 0.9774 | 21.44 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209957 | HAR UG11 | 69 | 229 | 0.7634 | 0.9774 | 21.4 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209957 | HAR UG11 | 69 | 229 | 0.7634 | 0.9774 | 21.4 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209957 | HAR UG11 | 69 | 229 | 0.8581 | 0.9774 | 11.93 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209956 | NHARR TP2 | 69 | 229 | 0.7523 | 0.9747 | 22.24 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209956 | NHARR TP2 | 69 | 229 | 0.7599 | 0.9747 | 21.48 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209956 | NHARR TP2 | 69 | 229 | 0.7603 | 0.9747 | 21.44 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209956 | NHARR TP2 | 69 | 229 | 0.7603 | 0.9747 | 21.44 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209956 | NHARR TP2 | 69 | 229 | 0.8552 | 0.9747 | 11.95 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209953 | HAMP2 | 69 | 229 | 0.749 | 0.9811 | 23.21 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209953 | HAMP2 | 69 | 229 | 0.757 | 0.9811 | 22.41 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209953 | HAMP2 | 69 | 229 | 0.7574 | 0.9811 | 22.37 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209953 | HAMP2 | 69 | 229 | 0.7574 | 0.9811 | 22.37 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209953 | HAMP2 | 69 | 229 | 0.853 | 0.9811 | 12.81 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209952 | HAMP TP2 | 69 | 229 | 0.752 | 0.9829 | 23.09 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209952 | HAMP TP2 | 69 | 229 | 0.76 | 0.9829 | 22.29 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209952 | HAMP TP2 | 69 | 229 | 0.7604 | 0.9829 | 22.25 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209952 | HAMP TP2 | 69 | 229 | 0.7605 | 0.9829 | 22.24 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209952 | HAMP TP2 | 69 | 229 | 0.8553 | 0.9829 | 12.76 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209951 | HAMP TP1 | 69 | 229 | 0.743 | 0.9711 | 22.81 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209951 | HAMP TP1 | 69 | 229 | 0.7509 | 0.9711 | 22.02 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209951 | HAMP TP1 | 69 | 229 | 0.7513 | 0.9711 | 21.98 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209951 | HAMP TP1 | 69 | 229 | 0.7513 | 0.9711 | 21.98 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209951 | HAMP TP1 | 69 | 229 | 0.8448 | 0.9711 | 12.63 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209950 | HAMP1 | 69 | 229 | 0.7406 | 0.9696 | 22.9 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209950 | HAMP1 | 69 | 229 | 0.7484 | 0.9696 | 22.12 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209950 | HAMP1 | 69 | 229 | 0.7489 | 0.9696 | 22.07 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209950 | HAMP1 | 69 | 229 | 0.7489 | 0.9696 | 22.07 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209950 | HAMP1 | 69 | 229 | 0.8428 | 0.9696 | 12.68 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209946 | HALI | 69 | 229 | 0.7783 | 0.9808 | 20.25 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209946 | HALI | 69 | 229 | 0.7851 | 0.9808 | 19.57 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209946 | HALI | 69 | 229 | 0.7855 | 0.9808 | 19.53 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209946 | HALI | 69 | 229 | 0.7855 | 0.9808 | 19.53 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209946 | HALI | 69 | 229 | 0.8706 | 0.9808 | 11.02 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209943 | GIBL | 69 | 229 | 0.7554 | 0.9774 | 22.2 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209943 | GIBL | 69 | 229 | 0.763 | 0.9774 | 21.44 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209943 | GIBL | 69 | 229 | 0.7634 | 0.9774 | 21.4 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209943 | GIBL | 69 | 229 | 0.7634 | 0.9774 | 21.4 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209943 | GIBL | 69 | 229 | 0.8581 | 0.9774 | 11.93 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209942 | NHARR TP1 | 69 | 229 | 0.7554 | 0.9772 | 22.18 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209942 | NHARR TP1 | 69 | 229 | 0.7629 | 0.9772 | 21.43 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209942 | NHARR TP1 | 69 | 229 | 0.7634 | 0.9772 | 21.38 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209942 | NHARR TP1 | 69 | 229 | 0.7634 | 0.9772 | 21.38 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209942 | NHARR TP1 | 69 | 229 | 0.858 | 0.9772 | 11.92 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209940 | GRPA | 69 | 229 | 0.8371 | 0.9726 | 13.55 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209940 | GRPA | 69 | 229 | 0.8413 | 0.9726 | 13.13 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209940 | GRPA | 69 | 229 | 0.8416 | 0.9726 | 13.1 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209940 | GRPA | 69 | 229 | 0.8416 | 0.9726 | 13.1 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209939 | GRPA TP2 | 69 | 229 | 0.8416 | 0.9761 | 13.45 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209939 | GRPA TP2 | 69 | 229 | 0.8457 | 0.9761 | 13.04 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209939 | GRPA TP2 | 69 | 229 | 0.846 | 0.9761 | 13.01 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209939 | GRPA TP2 | 69 | 229 | 0.846 | 0.9761 | 13.01 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209938 | GRPA TP1 | 69 | 229 | 0.8421 | 0.9764 | 13.43 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209938 | GRPA TP1 | 69 | 229 | 0.8462 | 0.9764 | 13.02 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209938 | GRPA TP1 | 69 | 229 | 0.8465 | 0.9764 | 12.99 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209938 | GRPA TP1 | 69 | 229 | 0.8466 | 0.9764 | 12.98 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209926 | FRY 4 | 69 | 229 | 0.7584 | 0.9748 | 21.64 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209926 | FRY 4 | 69 | 229 | 0.7656 | 0.9748 | 20.92 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209926 | FRY 4 | 69 | 229 | 0.766 | 0.9748 | 20.88 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209926 | FRY 4 | 69 | 229 | 0.766 | 0.9748 | 20.88 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209926 | FRY 4 | 69 | 229 | 0.8536 | 0.9748 | 12.12 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209920 | FRY 3 | 69 | 229 | 0.752 | 0.9695 | 21.75 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209920 | FRY 3 | 69 | 229 | 0.7593 | 0.9695 | 21.02 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209920 | FRY 3 | 69 | 229 | 0.7596 | 0.9695 | 20.99 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209920 | FRY 3 | 69 | 229 | 0.7596 | 0.9695 | 20.99 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209920 | FRY 3 | 69 | 229 | 0.8475 | 0.9695 | 12.2 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209914 | FRSW | 69 | 229 | 0.7699 | 0.9783 | 20.84 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209914 | FRSW | 69 | 229 | 0.7766 | 0.9783 | 20.17 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209914 | FRSW | 69 | 229 | 0.777 | 0.9783 | 20.13 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209914 | FRSW | 69 | 229 | 0.777 | 0.9783 | 20.13 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209914 | FRSW | 69 | 229 | 0.8621 | 0.9783 | 11.62 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209907 | ENOL 2 | 69 | 229 | 0.7694 | 0.9851 | 21.57 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209907 | ENOL 2 | 69 | 229 | 0.7763 | 0.9851 | 20.88 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209907 | ENOL 2 | 69 | 229 | 0.7767 | 0.9851 | 20.84 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209907 | ENOL 2 | 69 | 229 | 0.7767 | 0.9851 | 20.84 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209907 | ENOL 2 | 69 | 229 | 0.8655 | 0.9851 | 11.96 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209906 | ENOL 1 | 69 | 229 | 0.7732 | 0.9874 | 21.42 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209906 | ENOL 1 | 69 | 229 | 0.7802 | 0.9874 | 20.72 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209906 | ENOL 1 | 69 | 229 | 0.7806 | 0.9874 | 20.68 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209906 | ENOL 1 | 69 | 229 | 0.7806 | 0.9874 | 20.68 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209906 | ENOL 1 | 69 | 229 | 0.8685 | 0.9874 | 11.89 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209905 | ENOL TP2 | 69 | 229 | 0.7715 | 0.9858 | 21.43 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209905 | ENOL TP2 | 69 | 229 | 0.7784 | 0.9858 | 20.74 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209905 | ENOL TP2 | 69 | 229 | 0.7788 | 0.9858 | 20.7 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209905 | ENOL TP2 | 69 | 229 | 0.7788 | 0.9858 | 20.7 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209905 | ENOL TP2 | 69 | 229 | 0.8668 | 0.9858 | 11.9 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209904 | ENOL TP1 | 69 | 229 | 0.7745 | 0.9875 | 21.3 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209904 | ENOL TP1 | 69 | 229 | 0.7813 | 0.9875 | 20.62 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209904 | ENOL TP1 | 69 | 229 | 0.7817 | 0.9875 | 20.58 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209904 | ENOL TP1 | 69 | 229 | 0.7818 | 0.9875 | 20.57 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209904 | ENOL TP1 | 69 | 229 | 0.8691 | 0.9875 | 11.84 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209892 | EBEN | 69 | 229 | 0.7553 | 0.9759 | 22.06 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209892 | EBEN | 69 | 229 | 0.7627 | 0.9759 | 21.32 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209892 | EBEN | 69 | 229 | 0.7631 | 0.9759 | 21.28 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209892 | EBEN | 69 | 229 | 0.7631 | 0.9759 | 21.28 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209892 | EBEN | 69 | 229 | 0.8566 | 0.9759 | 11.93 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209886 | DUKE 1 | 69 | 229 | 0.7564 | 0.9749 | 21.85 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209886 | DUKE 1 | 69 | 229 | 0.7636 | 0.9749 | 21.13 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209886 | DUKE 1 | 69 | 229 | 0.764 | 0.9749 | 21.09 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209886 | DUKE 1 | 69 | 229 | 0.764 | 0.9749 | 21.09 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209886 | DUKE 1 | 69 | 229 | 0.8558 | 0.9749 | 11.91 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209885 | DUKE 2 | 69 | 229 | 0.7567 | 0.9752 | 21.85 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209885 | DUKE 2 | 69 | 229 | 0.7639 | 0.9752 | 21.13 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209885 | DUKE 2 | 69 | 229 | 0.7643 | 0.9752 | 21.09 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209885 | DUKE 2 | 69 | 229 | 0.7643 | 0.9752 | 21.09 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209885 | DUKE 2 | 69 | 229 | 0.8561 | 0.9752 | 11.91 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209884 | DUKE TP1 | 69 | 229 | 0.7575 | 0.9759 | 21.84 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209884 | DUKE TP1 | 69 | 229 | 0.7647 | 0.9759 | 21.12 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209884 | DUKE TP1 | 69 | 229 | 0.7651 | 0.9759 | 21.08 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209884 | DUKE TP1 | 69 | 229 | 0.7651 | 0.9759 | 21.08 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209884 | DUKE TP1 | 69 | 229 | 0.8569 | 0.9759 | 11.9 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209883 | DUKE TP2 | 69 | 229 | 0.7576 | 0.976 | 21.84 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209883 | DUKE TP2 | 69 | 229 | 0.7649 | 0.976 | 21.11 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209883 | DUKE TP2 | 69 | 229 | 0.7653 | 0.976 | 21.07 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209883 | DUKE TP2 | 69 | 229 | 0.7653 | 0.976 | 21.07 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209883 | DUKE TP2 | 69 | 229 | 0.8571 | 0.976 | 11.89 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209877 | DEVO 2 | 69 | 229 | 0.7671 | 0.9727 | 20.56 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209877 | DEVO 2 | 69 | 229 | 0.774 | 0.9727 | 19.87 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209877 | DEVO 2 | 69 | 229 | 0.7744 | 0.9727 | 19.83 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209877 | DEVO 2 | 69 | 229 | 0.7744 | 0.9727 | 19.83 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209877 | DEVO 2 | 69 | 229 | 0.8607 | 0.9727 | 11.2 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209876 | DEVO 1 | 69 | 229 | 0.772 | 0.9764 | 20.44 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209876 | DEVO 1 | 69 | 229 | 0.7789 | 0.9764 | 19.75 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209876 | DEVO 1 | 69 | 229 | 0.7793 | 0.9764 | 19.71 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209876 | DEVO 1 | 69 | 229 | 0.7793 | 0.9764 | 19.71 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209876 | DEVO 1 | 69 | 229 | 0.8652 | 0.9764 | 11.12 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209869 | DAUPTIJU | 69 | 229 | 0.7732 | 0.9772 | 20.4 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209869 | DAUPTIJU | 69 | 229 | 0.7801 | 0.9772 | 19.71 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209869 | DAUPTIJU | 69 | 229 | 0.7805 | 0.9772 | 19.67 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209869 | DAUPTIJU | 69 | 229 | 0.7805 | 0.9772 | 19.67 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209869 | DAUPTIJU | 69 | 229 | 0.8663 | 0.9772 | 11.09 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209868 | PAXT TP1 | 69 | 229 | 0.7742 | 0.9877 | 21.35 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209868 | PAXT TP1 | 69 | 229 | 0.7817 | 0.9877 | 20.6 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209868 | PAXT TP1 | 69 | 229 | 0.7821 | 0.9877 | 20.56 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209868 | PAXT TP1 | 69 | 229 | 0.7821 | 0.9877 | 20.56 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209868 | PAXT TP1 | 69 | 229 | 0.8725 | 0.9877 | 11.52 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209867 | PAXT TP2 | 69 | 229 | 0.7742 | 0.9877 | 21.35 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209867 | PAXT TP2 | 69 | 229 | 0.7816 | 0.9877 | 20.61 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209867 | PAXT TP2 | 69 | 229 | 0.782 | 0.9877 | 20.57 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209867 | PAXT TP2 | 69 | 229 | 0.782 | 0.9877 | 20.57 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209867 | PAXT TP2 | 69 | 229 | 0.8725 | 0.9877 | 11.52 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209866 | DAUP | 69 | 229 | 0.7883 | 0.9878 | 19.95 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209866 | DAUP | 69 | 229 | 0.795 | 0.9878 | 19.28 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209866 | DAUP | 69 | 229 | 0.7954 | 0.9878 | 19.24 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209866 | DAUP | 69 | 229 | 0.7954 | 0.9878 | 19.24 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209866 | DAUP | 69 | 229 | 0.879 | 0.9878 | 10.88 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209864 | MBRG | 69 | 229 | 0.7728 | 0.9769 | 20.41 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209864 | MBRG | 69 | 229 | 0.7798 | 0.9769 | 19.71 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209864 | MBRG | 69 | 229 | 0.7802 | 0.9769 | 19.67 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209864 | MBRG | 69 | 229 | 0.7802 | 0.9769 | 19.67 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209864 | MBRG | 69 | 229 | 0.866 | 0.9769 | 11.09 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209853 | CUMB CC | 69 | 229 | 0.7793 | 0.9852 | 20.59 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209853 | CUMB CC | 69 | 229 | 0.7859 | 0.9852 | 19.93 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209853 | CUMB CC | 69 | 229 | 0.7863 | 0.9852 | 19.89 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209853 | CUMB CC | 69 | 229 | 0.7863 | 0.9852 | 19.89 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209853 | CUMB CC | 69 | 229 | 0.8703 | 0.9852 | 11.49 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209852 | CUMB | 69 | 229 | 0.7799 | 0.9854 | 20.55 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209852 | CUMB | 69 | 229 | 0.7865 | 0.9854 | 19.89 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209852 | CUMB | 69 | 229 | 0.7869 | 0.9854 | 19.85 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209852 | CUMB | 69 | 229 | 0.7869 | 0.9854 | 19.85 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209852 | CUMB | 69 | 229 | 0.8707 | 0.9854 | 11.47 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209846 | COPP HA1 | 69 | 229 | 0.7731 | 0.9873 | 21.42 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209846 | COPP HA1 | 69 | 229 | 0.7805 | 0.9873 | 20.68 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209846 | COPP HA1 | 69 | 229 | 0.7809 | 0.9873 | 20.64 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209846 | COPP HA1 | 69 | 229 | 0.7809 | 0.9873 | 20.64 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209846 | COPP HA1 | 69 | 229 | 0.8718 | 0.9873 | 11.55 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209845 | COPP HA2 | 69 | 229 | 0.7758 | 0.9895 | 21.37 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209845 | COPP HA2 | 69 | 229 | 0.7833 | 0.9895 | 20.62 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209845 | COPP HA2 | 69 | 229 | 0.7837 | 0.9895 | 20.58 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209845 | COPP HA2 | 69 | 229 | 0.7837 | 0.9895 | 20.58 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209845 | COPP HA2 | 69 | 229 | 0.8742 | 0.9895 | 11.53 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209844 | COPP HU1 | 69 | 229 | 0.7575 | 0.9759 | 21.84 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209844 | COPP HU1 | 69 | 229 | 0.7647 | 0.9759 | 21.12 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209844 | COPP HU1 | 69 | 229 | 0.7651 | 0.9759 | 21.08 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209844 | COPP HU1 | 69 | 229 | 0.7651 | 0.9759 | 21.08 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209844 | COPP HU1 | 69 | 229 | 0.8569 | 0.9759 | 11.9 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209843 | COPP HU2 | 69 | 229 | 0.7576 | 0.976 | 21.84 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209843 | COPP HU2 | 69 | 229 | 0.7649 | 0.976 | 21.11 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209843 | COPP HU2 | 69 | 229 | 0.7653 | 0.976 | 21.07 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209843 | COPP HU2 | 69 | 229 | 0.7653 | 0.976 | 21.07 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209843 | COPP HU2 | 69 | 229 | 0.8571 | 0.976 | 11.89 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209842 | COPP DA1 | 69 | 229 | 0.7754 | 0.9885 | 21.31 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209842 | COPP DA1 | 69 | 229 | 0.7828 | 0.9885 | 20.57 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209842 | COPP DA1 | 69 | 229 | 0.7832 | 0.9885 | 20.53 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209842 | COPP DA1 | 69 | 229 | 0.7833 | 0.9885 | 20.52 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209842 | COPP DA1 | 69 | 229 | 0.8735 | 0.9885 | 11.5 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209841 | COPP DA2 | 69 | 229 | 0.7754 | 0.9885 | 21.31 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209841 | COPP DA2 | 69 | 229 | 0.7828 | 0.9885 | 20.57 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209841 | COPP DA2 | 69 | 229 | 0.7832 | 0.9885 | 20.53 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209841 | COPP DA2 | 69 | 229 | 0.7832 | 0.9885 | 20.53 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209841 | COPP DA2 | 69 | 229 | 0.8735 | 0.9885 | 11.5 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209840 | COPP | 69 | 229 | 0.7759 | 0.9889 | 21.3 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209840 | COPP | 69 | 229 | 0.7833 | 0.9889 | 20.56 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209840 | COPP | 69 | 229 | 0.7837 | 0.9889 | 20.52 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209840 | COPP | 69 | 229 | 0.7838 | 0.9889 | 20.51 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209840 | COPP | 69 | 229 | 0.8739 | 0.9889 | 11.5 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209834 | COSR | 69 | 229 | 0.7723 | 0.9829 | 21.06 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209834 | COSR | 69 | 229 | 0.7794 | 0.9829 | 20.35 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209834 | COSR | 69 | 229 | 0.7798 | 0.9829 | 20.31 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209834 | COSR | 69 | 229 | 0.7798 | 0.9829 | 20.31 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209834 | COSR | 69 | 229 | 0.8684 | 0.9829 | 11.45 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209827 | COPA 2 | 69 | 229 | 0.7684 | 0.9737 | 20.53 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209827 | COPA 2 | 69 | 229 | 0.7753 | 0.9737 | 19.84 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209827 | COPA 2 | 69 | 229 | 0.7757 | 0.9737 | 19.8 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209827 | COPA 2 | 69 | 229 | 0.7757 | 0.9737 | 19.8 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209827 | COPA 2 | 69 | 229 | 0.8618 | 0.9737 | 11.19 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209826 | COPA 1 | 69 | 229 | 0.7725 | 0.9768 | 20.43 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209826 | COPA 1 | 69 | 229 | 0.7795 | 0.9768 | 19.73 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209826 | COPA 1 | 69 | 229 | 0.7799 | 0.9768 | 19.69 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209826 | COPA 1 | 69 | 229 | 0.7799 | 0.9768 | 19.69 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209826 | COPA 1 | 69 | 229 | 0.8657 | 0.9768 | 11.11 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209820 | CHRO 2 | 69 | 229 | 0.7718 | 0.983 | 21.12 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209820 | CHRO 2 | 69 | 229 | 0.7789 | 0.983 | 20.41 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209820 | CHRO 2 | 69 | 229 | 0.7793 | 0.983 | 20.37 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209820 | CHRO 2 | 69 | 229 | 0.7793 | 0.983 | 20.37 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209820 | CHRO 2 | 69 | 229 | 0.8682 | 0.983 | 11.48 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209819 | CHRO 1 | 69 | 229 | 0.773 | 0.9845 | 21.15 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209819 | CHRO 1 | 69 | 229 | 0.7801 | 0.9845 | 20.44 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209819 | CHRO 1 | 69 | 229 | 0.7806 | 0.9845 | 20.39 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209819 | CHRO 1 | 69 | 229 | 0.7806 | 0.9845 | 20.39 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209819 | CHRO 1 | 69 | 229 | 0.8696 | 0.9845 | 11.49 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209813 | CCTY 1 | 69 | 229 | 0.7554 | 0.9773 | 22.19 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209813 | CCTY 1 | 69 | 229 | 0.7629 | 0.9773 | 21.44 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209813 | CCTY 1 | 69 | 229 | 0.7634 | 0.9773 | 21.39 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209813 | CCTY 1 | 69 | 229 | 0.7634 | 0.9773 | 21.39 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209813 | CCTY 1 | 69 | 229 | 0.858 | 0.9773 | 11.93 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209812 | CCTY TP2 | 69 | 229 | 0.7714 | 0.9832 | 21.18 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209812 | CCTY TP2 | 69 | 229 | 0.7785 | 0.9832 | 20.47 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209812 | CCTY TP2 | 69 | 229 | 0.7789 | 0.9832 | 20.43 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209812 | CCTY TP2 | 69 | 229 | 0.7789 | 0.9832 | 20.43 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209812 | CCTY TP2 | 69 | 229 | 0.868 | 0.9832 | 11.52 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209811 | CCTY TP1 | 69 | 229 | 0.7726 | 0.9847 | 21.21 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209811 | CCTY TP1 | 69 | 229 | 0.7797 | 0.9847 | 20.5 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209811 | CCTY TP1 | 69 | 229 | 0.7801 | 0.9847 | 20.46 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209811 | CCTY TP1 | 69 | 229 | 0.7802 | 0.9847 | 20.45 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209811 | CCTY TP1 | 69 | 229 | 0.8694 | 0.9847 | 11.53 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209804 | CEDA TP2 | 69 | 229 | 0.7555 | 0.9775 | 22.2 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209804 | CEDA TP2 | 69 | 229 | 0.7631 | 0.9775 | 21.44 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209804 | CEDA TP2 | 69 | 229 | 0.7635 | 0.9775 | 21.4 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209804 | CEDA TP2 | 69 | 229 | 0.7635 | 0.9775 | 21.4 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209804 | CEDA TP2 | 69 | 229 | 0.8582 | 0.9775 | 11.93 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209803 | CEDA TP1 | 69 | 229 | 0.7551 | 0.9772 | 22.21 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209803 | CEDA TP1 | 69 | 229 | 0.7627 | 0.9772 | 21.45 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209803 | CEDA TP1 | 69 | 229 | 0.7631 | 0.9772 | 21.41 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209803 | CEDA TP1 | 69 | 229 | 0.7631 | 0.9772 | 21.41 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209803 | CEDA TP1 | 69 | 229 | 0.8579 | 0.9772 | 11.93 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209798 | CASY 2 | 69 | 229 | 0.7448 | 0.968 | 22.32 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209798 | CASY 2 | 69 | 229 | 0.7518 | 0.968 | 21.62 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209798 | CASY 2 | 69 | 229 | 0.7522 | 0.968 | 21.58 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209798 | CASY 2 | 69 | 229 | 0.7522 | 0.968 | 21.58 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209798 | CASY 2 | 69 | 229 | 0.8435 | 0.968 | 12.45 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209797 | CASY 1 | 69 | 229 | 0.7448 | 0.968 | 22.32 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209797 | CASY 1 | 69 | 229 | 0.7518 | 0.968 | 21.62 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209797 | CASY 1 | 69 | 229 | 0.7522 | 0.968 | 21.58 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209797 | CASY 1 | 69 | 229 | 0.7522 | 0.968 | 21.58 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209797 | CASY 1 | 69 | 229 | 0.8435 | 0.968 | 12.45 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209792 | CABA TP2 | 69 | 229 | 0.7765 | 0.9836 | 20.71 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209792 | CABA TP2 | 69 | 229 | 0.7831 | 0.9836 | 20.05 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209792 | CABA TP2 | 69 | 229 | 0.7835 | 0.9836 | 20.01 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209792 | CABA TP2 | 69 | 229 | 0.7835 | 0.9836 | 20.01 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209792 | CABA TP2 | 69 | 229 | 0.8681 | 0.9836 | 11.55 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209790 | CABA TP4 | 69 | 229 | 0.7731 | 0.9806 | 20.75 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209790 | CABA TP4 | 69 | 229 | 0.7798 | 0.9806 | 20.08 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209790 | CABA TP4 | 69 | 229 | 0.7801 | 0.9806 | 20.05 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209790 | CABA TP4 | 69 | 229 | 0.7801 | 0.9806 | 20.05 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209790 | CABA TP4 | 69 | 229 | 0.8649 | 0.9806 | 11.57 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209789 | CABA T1 | 69 | 229 | 0.7728 | 0.9803 | 20.75 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209789 | CABA T1 | 69 | 229 | 0.7794 | 0.9803 | 20.09 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209789 | CABA T1 | 69 | 229 | 0.7798 | 0.9803 | 20.05 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209789 | CABA T1 | 69 | 229 | 0.7798 | 0.9803 | 20.05 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209789 | CABA T1 | 69 | 229 | 0.8646 | 0.9803 | 11.57 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209788 | CABA T2 | 69 | 229 | 0.7762 | 0.9833 | 20.71 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209788 | CABA T2 | 69 | 229 | 0.7828 | 0.9833 | 20.05 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209788 | CABA T2 | 69 | 229 | 0.7832 | 0.9833 | 20.01 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209788 | CABA T2 | 69 | 229 | 0.7832 | 0.9833 | 20.01 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209788 | CABA T2 | 69 | 229 | 0.8678 | 0.9833 | 11.55 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209787 | CARLUG24 | 69 | 229 | 0.7698 | 0.9782 | 20.84 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209787 | CARLUG24 | 69 | 229 | 0.7765 | 0.9782 | 20.17 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209787 | CARLUG24 | 69 | 229 | 0.7769 | 0.9782 | 20.13 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209787 | CARLUG24 | 69 | 229 | 0.7769 | 0.9782 | 20.13 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209787 | CARLUG24 | 69 | 229 | 0.862 | 0.9782 | 11.62 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209786 | CARLTI24 | 69 | 229 | 0.745 | 0.9626 | 21.76 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209786 | CARLTI24 | 69 | 229 | 0.7514 | 0.9626 | 21.12 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209786 | CARLTI24 | 69 | 229 | 0.7518 | 0.9626 | 21.08 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209786 | CARLTI24 | 69 | 229 | 0.7518 | 0.9626 | 21.08 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209786 | CARLTI24 | 69 | 229 | 0.8414 | 0.9626 | 12.12 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209785 | CARLUG13 | 69 | 229 | 0.775 | 0.9826 | 20.76 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209785 | CARLUG13 | 69 | 229 | 0.7816 | 0.9826 | 20.1 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209785 | CARLUG13 | 69 | 229 | 0.782 | 0.9826 | 20.06 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209785 | CARLUG13 | 69 | 229 | 0.782 | 0.9826 | 20.06 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209785 | CARLUG13 | 69 | 229 | 0.8669 | 0.9826 | 11.57 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209784 | CARLTI13 | 69 | 229 | 0.7451 | 0.9685 | 22.34 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209784 | CARLTI13 | 69 | 229 | 0.7521 | 0.9685 | 21.64 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209784 | CARLTI13 | 69 | 229 | 0.7525 | 0.9685 | 21.6 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209784 | CARLTI13 | 69 | 229 | 0.7525 | 0.9685 | 21.6 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209784 | CARLTI13 | 69 | 229 | 0.8438 | 0.9685 | 12.47 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209782 | CARL 2 | 69 | 229 | 0.7698 | 0.9782 | 20.84 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209782 | CARL 2 | 69 | 229 | 0.7765 | 0.9782 | 20.17 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209782 | CARL 2 | 69 | 229 | 0.7769 | 0.9782 | 20.13 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209782 | CARL 2 | 69 | 229 | 0.7769 | 0.9782 | 20.13 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209782 | CARL 2 | 69 | 229 | 0.862 | 0.9782 | 11.62 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209781 | CARL 1 | 69 | 229 | 0.7748 | 0.9825 | 20.77 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209781 | CARL 1 | 69 | 229 | 0.7814 | 0.9825 | 20.11 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209781 | CARL 1 | 69 | 229 | 0.7818 | 0.9825 | 20.07 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209781 | CARL 1 | 69 | 229 | 0.7818 | 0.9825 | 20.07 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209781 | CARL 1 | 69 | 229 | 0.8667 | 0.9825 | 11.58 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209780 | CARL TP4 | 69 | 229 | 0.7788 | 0.9846 | 20.58 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209780 | CARL TP4 | 69 | 229 | 0.7854 | 0.9846 | 19.92 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209780 | CARL TP4 | 69 | 229 | 0.7857 | 0.9846 | 19.89 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209780 | CARL TP4 | 69 | 229 | 0.7857 | 0.9846 | 19.89 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209780 | CARL TP4 | 69 | 229 | 0.8698 | 0.9846 | 11.48 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209779 | CARL TP3 | 69 | 229 | 0.7794 | 0.9853 | 20.59 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209779 | CARL TP3 | 69 | 229 | 0.786 | 0.9853 | 19.93 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209779 | CARL TP3 | 69 | 229 | 0.7864 | 0.9853 | 19.89 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209779 | CARL TP3 | 69 | 229 | 0.7864 | 0.9853 | 19.89 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209779 | CARL TP3 | 69 | 229 | 0.8704 | 0.9853 | 11.49 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209778 | SDLE TI2 | 69 | 229 | 0.7692 | 0.9792 | 21 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209778 | SDLE TI2 | 69 | 229 | 0.7757 | 0.9792 | 20.35 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209778 | SDLE TI2 | 69 | 229 | 0.7761 | 0.9792 | 20.31 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209778 | SDLE TI2 | 69 | 229 | 0.7761 | 0.9792 | 20.31 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209778 | SDLE TI2 | 69 | 229 | 0.8621 | 0.9792 | 11.71 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209777 | CARL TI | 69 | 229 | 0.7698 | 0.9782 | 20.84 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209777 | CARL TI | 69 | 229 | 0.7765 | 0.9782 | 20.17 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209777 | CARL TI | 69 | 229 | 0.7769 | 0.9782 | 20.13 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209777 | CARL TI | 69 | 229 | 0.7769 | 0.9782 | 20.13 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209777 | CARL TI | 69 | 229 | 0.862 | 0.9782 | 11.62 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209769 | CAPA D | 69 | 229 | 0.7724 | 0.9846 | 21.22 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209769 | CAPA D | 69 | 229 | 0.7796 | 0.9846 | 20.5 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209769 | CAPA D | 69 | 229 | 0.78 | 0.9846 | 20.46 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209769 | CAPA D | 69 | 229 | 0.78 | 0.9846 | 20.46 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209769 | CAPA D | 69 | 229 | 0.8693 | 0.9846 | 11.53 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209768 | CAPA C | 69 | 229 | 0.7554 | 0.9773 | 22.19 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209768 | CAPA C | 69 | 229 | 0.7629 | 0.9773 | 21.44 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209768 | CAPA C | 69 | 229 | 0.7634 | 0.9773 | 21.39 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209768 | CAPA C | 69 | 229 | 0.7634 | 0.9773 | 21.39 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209768 | CAPA C | 69 | 229 | 0.858 | 0.9773 | 11.93 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209767 | CAPA B | 69 | 229 | 0.7554 | 0.9774 | 22.2 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209767 | CAPA B | 69 | 229 | 0.763 | 0.9774 | 21.44 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209767 | CAPA B | 69 | 229 | 0.7634 | 0.9774 | 21.4 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209767 | CAPA B | 69 | 229 | 0.7634 | 0.9774 | 21.4 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209767 | CAPA B | 69 | 229 | 0.8581 | 0.9774 | 11.93 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209766 | CAPA A | 69 | 229 | 0.7712 | 0.9831 | 21.19 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209766 | CAPA A | 69 | 229 | 0.7783 | 0.9831 | 20.48 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209766 | CAPA A | 69 | 229 | 0.7787 | 0.9831 | 20.44 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209766 | CAPA A | 69 | 229 | 0.7787 | 0.9831 | 20.44 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209766 | CAPA A | 69 | 229 | 0.8678 | 0.9831 | 11.53 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209765 | CAPAUGCC | 69 | 229 | 0.7554 | 0.9773 | 22.19 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209765 | CAPAUGCC | 69 | 229 | 0.7629 | 0.9773 | 21.44 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209765 | CAPAUGCC | 69 | 229 | 0.7634 | 0.9773 | 21.39 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209765 | CAPAUGCC | 69 | 229 | 0.7634 | 0.9773 | 21.39 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209765 | CAPAUGCC | 69 | 229 | 0.858 | 0.9773 | 11.93 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209764 | CAPAUGD2 | 69 | 229 | 0.7714 | 0.9832 | 21.18 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209764 | CAPAUGD2 | 69 | 229 | 0.7785 | 0.9832 | 20.47 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209764 | CAPAUGD2 | 69 | 229 | 0.7789 | 0.9832 | 20.43 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209764 | CAPAUGD2 | 69 | 229 | 0.7789 | 0.9832 | 20.43 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209764 | CAPAUGD2 | 69 | 229 | 0.868 | 0.9832 | 11.52 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209763 | CAPAUGD1 | 69 | 229 | 0.7726 | 0.9847 | 21.21 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209763 | CAPAUGD1 | 69 | 229 | 0.7797 | 0.9847 | 20.5 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209763 | CAPAUGD1 | 69 | 229 | 0.7801 | 0.9847 | 20.46 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209763 | CAPAUGD1 | 69 | 229 | 0.7802 | 0.9847 | 20.45 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209763 | CAPAUGD1 | 69 | 229 | 0.8694 | 0.9847 | 11.53 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209757 | BENV 2 | 69 | 229 | 0.8416 | 0.9761 | 13.45 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209757 | BENV 2 | 69 | 229 | 0.8458 | 0.9761 | 13.03 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209757 | BENV 2 | 69 | 229 | 0.8461 | 0.9761 | 13 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209757 | BENV 2 | 69 | 229 | 0.8461 | 0.9761 | 13 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209756 | BENV 1 | 69 | 229 | 0.8392 | 0.9742 | 13.5 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209756 | BENV 1 | 69 | 229 | 0.8434 | 0.9742 | 13.08 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209756 | BENV 1 | 69 | 229 | 0.8437 | 0.9742 | 13.05 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209756 | BENV 1 | 69 | 229 | 0.8437 | 0.9742 | 13.05 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209755 | BENV TP2 | 69 | 229 | 0.8433 | 0.9774 | 13.41 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209755 | BENV TP2 | 69 | 229 | 0.8474 | 0.9774 | 13 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209755 | BENV TP2 | 69 | 229 | 0.8477 | 0.9774 | 12.97 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209755 | BENV TP2 | 69 | 229 | 0.8477 | 0.9774 | 12.97 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209754 | BENV TP1 | 69 | 229 | 0.8432 | 0.9772 | 13.4 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209754 | BENV TP1 | 69 | 229 | 0.8473 | 0.9772 | 12.99 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209754 | BENV TP1 | 69 | 229 | 0.8476 | 0.9772 | 12.96 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209754 | BENV TP1 | 69 | 229 | 0.8476 | 0.9772 | 12.96 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209741 | AMP2 2 | 69 | 229 | 0.7551 | 0.9758 | 22.07 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209741 | AMP2 2 | 69 | 229 | 0.7625 | 0.9758 | 21.33 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209741 | AMP2 2 | 69 | 229 | 0.7629 | 0.9758 | 21.29 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209741 | AMP2 2 | 69 | 229 | 0.7629 | 0.9758 | 21.29 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209741 | AMP2 2 | 69 | 229 | 0.8565 | 0.9758 | 11.93 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209740 | AMP2 1 | 69 | 229 | 0.7549 | 0.9757 | 22.08 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209740 | AMP2 1 | 69 | 229 | 0.7623 | 0.9757 | 21.34 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209740 | AMP2 1 | 69 | 229 | 0.7627 | 0.9757 | 21.3 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209740 | AMP2 1 | 69 | 229 | 0.7628 | 0.9757 | 21.29 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209740 | AMP2 1 | 69 | 229 | 0.8563 | 0.9757 | 11.94 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209739 | AMP2 TP2 | 69 | 229 | 0.7553 | 0.9759 | 22.06 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209739 | AMP2 TP2 | 69 | 229 | 0.7627 | 0.9759 | 21.32 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209739 | AMP2 TP2 | 69 | 229 | 0.7631 | 0.9759 | 21.28 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209739 | AMP2 TP2 | 69 | 229 | 0.7631 | 0.9759 | 21.28 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209739 | AMP2 TP2 | 69 | 229 | 0.8566 | 0.9759 | 11.93 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209738 | AMP2 TP1 | 69 | 229 | 0.7551 | 0.9758 | 22.07 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209738 | AMP2 TP1 | 69 | 229 | 0.7625 | 0.9758 | 21.33 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209738 | AMP2 TP1 | 69 | 229 | 0.7629 | 0.9758 | 21.29 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209738 | AMP2 TP1 | 69 | 229 | 0.7629 | 0.9758 | 21.29 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209738 | AMP2 TP1 | 69 | 229 | 0.8565 | 0.9758 | 11.93 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209733 | AMP1 TP2 | 69 | 229 | 0.755 | 0.9766 | 22.16 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209733 | AMP1 TP2 | 69 | 229 | 0.7625 | 0.9766 | 21.41 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209733 | AMP1 TP2 | 69 | 229 | 0.7629 | 0.9766 | 21.37 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209733 | AMP1 TP2 | 69 | 229 | 0.7629 | 0.9766 | 21.37 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209733 | AMP1 TP2 | 69 | 229 | 0.8572 | 0.9766 | 11.94 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209732 | AMP1 2 | 69 | 229 | 0.7549 | 0.9766 | 22.17 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209732 | AMP1 2 | 69 | 229 | 0.7624 | 0.9766 | 21.42 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209732 | AMP1 2 | 69 | 229 | 0.7629 | 0.9766 | 21.37 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209732 | AMP1 2 | 69 | 229 | 0.7629 | 0.9766 | 21.37 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209732 | AMP1 2 | 69 | 229 | 0.8572 | 0.9766 | 11.94 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209731 | AMP1 1 | 69 | 229 | 0.7552 | 0.9768 | 22.16 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209731 | AMP1 1 | 69 | 229 | 0.7627 | 0.9768 | 21.41 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209731 | AMP1 1 | 69 | 229 | 0.7631 | 0.9768 | 21.37 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209731 | AMP1 1 | 69 | 229 | 0.7631 | 0.9768 | 21.37 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209731 | AMP1 1 | 69 | 229 | 0.8574 | 0.9768 | 11.94 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209065 | AE2-060 MAIN | 69 | 229 | 0.8304 | 0.9439 | 11.35 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209065 | AE2-060 MAIN | 69 | 229 | 0.8347 | 0.9439 | 10.92 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209065 | AE2-060 MAIN | 69 | 229 | 0.835 | 0.9439 | 10.89 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209065 | AE2-060 MAIN | 69 | 229 | 0.835 | 0.9439 | 10.89 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209064 | AE2-060 TAP | 69 | 229 | 0.8302 | 0.9439 | 11.37 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209064 | AE2-060 TAP | 69 | 229 | 0.8346 | 0.9439 | 10.93 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209064 | AE2-060 TAP | 69 | 229 | 0.8349 | 0.9439 | 10.9 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 209064 | AE2-060 TAP | 69 | 229 | 0.8349 | 0.9439 | 10.9 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208921 | SAHA 693 | 69 | 229 | 0.8562 | 0.9893 | 13.31 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208921 | SAHA 693 | 69 | 229 | 0.8646 | 0.9893 | 12.47 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208921 | SAHA 693 | 69 | 229 | 0.8648 | 0.9893 | 12.45 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208921 | SAHA 693 | 69 | 229 | 0.8648 | 0.9893 | 12.45 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208919 | SAHA 692 | 69 | 229 | 0.8562 | 0.9893 | 13.31 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208919 | SAHA 692 | 69 | 229 | 0.8646 | 0.9893 | 12.47 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208919 | SAHA 692 | 69 | 229 | 0.8648 | 0.9893 | 12.45 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208919 | SAHA 692 | 69 | 229 | 0.8648 | 0.9893 | 12.45 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208899 | WYET TP1 | 69 | 229 | 0.8038 | 0.9795 | 17.57 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208899 | WYET TP1 | 69 | 229 | 0.8138 | 0.9795 | 16.57 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208899 | WYET TP1 | 69 | 229 | 0.8141 | 0.9795 | 16.54 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208899 | WYET TP1 | 69 | 229 | 0.8141 | 0.9795 | 16.54 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208899 | WYET TP1 | 69 | 229 | 0.8933 | 0.9795 | 8.62 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208898 | WYET | 69 | 229 | 0.8038 | 0.9794 | 17.56 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208898 | WYET | 69 | 229 | 0.8137 | 0.9794 | 16.57 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208898 | WYET | 69 | 229 | 0.814 | 0.9794 | 16.54 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208898 | WYET | 69 | 229 | 0.814 | 0.9794 | 16.54 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208898 | WYET | 69 | 229 | 0.8932 | 0.9794 | 8.62 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208896 | WYETH 2 | 69 | 229 | 0.809 | 0.9831 | 17.41 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208896 | WYETH 2 | 69 | 229 | 0.8188 | 0.9831 | 16.43 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208896 | WYETH 2 | 69 | 229 | 0.8191 | 0.9831 | 16.4 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208896 | WYETH 2 | 69 | 229 | 0.8191 | 0.9831 | 16.4 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208896 | WYETH 2 | 69 | 229 | 0.8975 | 0.9831 | 8.56 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208891 | WEWI 1 | 69 | 229 | 0.8395 | 0.9839 | 14.44 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208891 | WEWI 1 | 69 | 229 | 0.8482 | 0.9839 | 13.57 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208891 | WEWI 1 | 69 | 229 | 0.8485 | 0.9839 | 13.54 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208891 | WEWI 1 | 69 | 229 | 0.8485 | 0.9839 | 13.54 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208884 | WNHO | 69 | 229 | 0.7457 | 0.9837 | 23.8 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208884 | WNHO | 69 | 229 | 0.7545 | 0.9837 | 22.92 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208884 | WNHO | 69 | 229 | 0.7549 | 0.9837 | 22.88 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208884 | WNHO | 69 | 229 | 0.7549 | 0.9837 | 22.88 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208884 | WNHO | 69 | 229 | 0.8545 | 0.9837 | 12.92 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208882 | WYOM 2 | 69 | 229 | 0.8003 | 0.9834 | 18.31 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208882 | WYOM 2 | 69 | 229 | 0.808 | 0.9834 | 17.54 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208882 | WYOM 2 | 69 | 229 | 0.8084 | 0.9834 | 17.5 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208882 | WYOM 2 | 69 | 229 | 0.8084 | 0.9834 | 17.5 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208882 | WYOM 2 | 69 | 229 | 0.89 | 0.9834 | 9.34 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208881 | WYOM 1 | 69 | 229 | 0.7995 | 0.9827 | 18.32 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208881 | WYOM 1 | 69 | 229 | 0.8072 | 0.9827 | 17.55 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208881 | WYOM 1 | 69 | 229 | 0.8076 | 0.9827 | 17.51 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208881 | WYOM 1 | 69 | 229 | 0.8076 | 0.9827 | 17.51 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208881 | WYOM 1 | 69 | 229 | 0.8893 | 0.9827 | 9.34 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208880 | WYET TP2 | 69 | 229 | 0.8091 | 0.9831 | 17.4 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208880 | WYET TP2 | 69 | 229 | 0.8189 | 0.9831 | 16.42 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208880 | WYET TP2 | 69 | 229 | 0.8192 | 0.9831 | 16.39 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208880 | WYET TP2 | 69 | 229 | 0.8192 | 0.9831 | 16.39 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208880 | WYET TP2 | 69 | 229 | 0.8976 | 0.9831 | 8.55 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208878 | WLAN TP2 | 69 | 229 | 0.8432 | 0.9823 | 13.91 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208878 | WLAN TP2 | 69 | 229 | 0.8518 | 0.9823 | 13.05 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208878 | WLAN TP2 | 69 | 229 | 0.8521 | 0.9823 | 13.02 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208878 | WLAN TP2 | 69 | 229 | 0.8521 | 0.9823 | 13.02 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208877 | WLAN TP1 | 69 | 229 | 0.8432 | 0.9822 | 13.9 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208877 | WLAN TP1 | 69 | 229 | 0.8518 | 0.9822 | 13.04 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208877 | WLAN TP1 | 69 | 229 | 0.8521 | 0.9822 | 13.01 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208877 | WLAN TP1 | 69 | 229 | 0.8521 | 0.9822 | 13.01 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208875 | WLAN 2 | 69 | 229 | 0.8413 | 0.9808 | 13.95 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208875 | WLAN 2 | 69 | 229 | 0.8499 | 0.9808 | 13.09 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208875 | WLAN 2 | 69 | 229 | 0.8502 | 0.9808 | 13.06 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208875 | WLAN 2 | 69 | 229 | 0.8502 | 0.9808 | 13.06 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208874 | WLAN 1 | 69 | 229 | 0.8412 | 0.9807 | 13.95 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208874 | WLAN 1 | 69 | 229 | 0.8498 | 0.9807 | 13.09 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208874 | WLAN 1 | 69 | 229 | 0.8501 | 0.9807 | 13.06 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208874 | WLAN 1 | 69 | 229 | 0.8501 | 0.9807 | 13.06 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208867 | WHEM | 69 | 229 | 0.816 | 0.9885 | 17.25 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208867 | WHEM | 69 | 229 | 0.8258 | 0.9885 | 16.27 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208867 | WHEM | 69 | 229 | 0.8261 | 0.9885 | 16.24 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208867 | WHEM | 69 | 229 | 0.8261 | 0.9885 | 16.24 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208867 | WHEM | 69 | 229 | 0.9036 | 0.9885 | 8.49 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208866 | WEWI 2 | 69 | 229 | 0.838 | 0.983 | 14.5 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208866 | WEWI 2 | 69 | 229 | 0.8468 | 0.983 | 13.62 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208866 | WEWI 2 | 69 | 229 | 0.847 | 0.983 | 13.6 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208866 | WEWI 2 | 69 | 229 | 0.847 | 0.983 | 13.6 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208865 | WEWI TP2 | 69 | 229 | 0.8389 | 0.9837 | 14.48 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208865 | WEWI TP2 | 69 | 229 | 0.8477 | 0.9837 | 13.6 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208865 | WEWI TP2 | 69 | 229 | 0.8479 | 0.9837 | 13.58 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208865 | WEWI TP2 | 69 | 229 | 0.8479 | 0.9837 | 13.58 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208860 | WERN | 69 | 229 | 0.7962 | 0.9797 | 18.35 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208860 | WERN | 69 | 229 | 0.8039 | 0.9797 | 17.58 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208860 | WERN | 69 | 229 | 0.8044 | 0.9797 | 17.53 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208860 | WERN | 69 | 229 | 0.8044 | 0.9797 | 17.53 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208860 | WERN | 69 | 229 | 0.8862 | 0.9797 | 9.35 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208857 | AE1-226 TAP | 69 | 229 | 0.8642 | 0.9691 | 10.49 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208857 | AE1-226 TAP | 69 | 229 | 0.8713 | 0.9691 | 9.78 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208857 | AE1-226 TAP | 69 | 229 | 0.8715 | 0.9691 | 9.76 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208857 | AE1-226 TAP | 69 | 229 | 0.8715 | 0.9691 | 9.76 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208856 | AE1-226 GEN | 69 | 229 | 0.8643 | 0.9692 | 10.49 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208856 | AE1-226 GEN | 69 | 229 | 0.8714 | 0.9692 | 9.78 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208856 | AE1-226 GEN | 69 | 229 | 0.8716 | 0.9692 | 9.76 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208856 | AE1-226 GEN | 69 | 229 | 0.8716 | 0.9692 | 9.76 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208853 | WARW | 69 | 229 | 0.7472 | 0.9794 | 23.22 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208853 | WARW | 69 | 229 | 0.756 | 0.9794 | 22.34 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208853 | WARW | 69 | 229 | 0.7564 | 0.9794 | 22.3 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208853 | WARW | 69 | 229 | 0.7564 | 0.9794 | 22.3 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208853 | WARW | 69 | 229 | 0.8537 | 0.9794 | 12.57 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208852 | WARW 2 | 69 | 229 | 0.7472 | 0.9794 | 23.22 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208852 | WARW 2 | 69 | 229 | 0.756 | 0.9794 | 22.34 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208852 | WARW 2 | 69 | 229 | 0.7564 | 0.9794 | 22.3 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208852 | WARW 2 | 69 | 229 | 0.7564 | 0.9794 | 22.3 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208852 | WARW 2 | 69 | 229 | 0.8537 | 0.9794 | 12.57 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208851 | CHWA TP2 | 69 | 229 | 0.8613 | 0.9666 | 10.53 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208851 | CHWA TP2 | 69 | 229 | 0.8685 | 0.9666 | 9.81 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208851 | CHWA TP2 | 69 | 229 | 0.8688 | 0.9666 | 9.78 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208851 | CHWA TP2 | 69 | 229 | 0.8688 | 0.9666 | 9.78 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208849 | WAKE TP2 | 69 | 229 | 0.8608 | 0.9674 | 10.66 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208849 | WAKE TP2 | 69 | 229 | 0.868 | 0.9674 | 9.94 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208849 | WAKE TP2 | 69 | 229 | 0.8683 | 0.9674 | 9.91 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208849 | WAKE TP2 | 69 | 229 | 0.8683 | 0.9674 | 9.91 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208847 | WAKE TP | 69 | 229 | 0.8619 | 0.9672 | 10.53 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208847 | WAKE TP | 69 | 229 | 0.8691 | 0.9672 | 9.81 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208847 | WAKE TP | 69 | 229 | 0.8694 | 0.9672 | 9.78 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208847 | WAKE TP | 69 | 229 | 0.8694 | 0.9672 | 9.78 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208845 | WAKE | 69 | 229 | 0.8577 | 0.9636 | 10.59 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208845 | WAKE | 69 | 229 | 0.865 | 0.9636 | 9.86 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208845 | WAKE | 69 | 229 | 0.8652 | 0.9636 | 9.84 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208845 | WAKE | 69 | 229 | 0.8652 | 0.9636 | 9.84 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208843 | TWVA 2 | 69 | 229 | 0.7592 | 0.9622 | 20.3 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208843 | TWVA 2 | 69 | 229 | 0.7671 | 0.9622 | 19.51 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208843 | TWVA 2 | 69 | 229 | 0.7675 | 0.9622 | 19.47 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208843 | TWVA 2 | 69 | 229 | 0.7675 | 0.9622 | 19.47 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208843 | TWVA 2 | 69 | 229 | 0.8562 | 0.9622 | 10.6 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208842 | TWVA TW7 | 69 | 229 | 0.7935 | 0.9857 | 19.22 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208842 | TWVA TW7 | 69 | 229 | 0.8013 | 0.9857 | 18.44 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208842 | TWVA TW7 | 69 | 229 | 0.8017 | 0.9857 | 18.4 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208842 | TWVA TW7 | 69 | 229 | 0.8017 | 0.9857 | 18.4 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208842 | TWVA TW7 | 69 | 229 | 0.8846 | 0.9857 | 10.11 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208841 | TWVA TW6 | 69 | 229 | 0.7935 | 0.9857 | 19.22 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208841 | TWVA TW6 | 69 | 229 | 0.8012 | 0.9857 | 18.45 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208841 | TWVA TW6 | 69 | 229 | 0.8016 | 0.9857 | 18.41 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208841 | TWVA TW6 | 69 | 229 | 0.8017 | 0.9857 | 18.4 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208841 | TWVA TW6 | 69 | 229 | 0.8846 | 0.9857 | 10.11 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208838 | TWVA 1 | 69 | 229 | 0.7935 | 0.9857 | 19.22 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208838 | TWVA 1 | 69 | 229 | 0.8012 | 0.9857 | 18.45 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208838 | TWVA 1 | 69 | 229 | 0.8016 | 0.9857 | 18.41 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208838 | TWVA 1 | 69 | 229 | 0.8016 | 0.9857 | 18.41 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208838 | TWVA 1 | 69 | 229 | 0.8846 | 0.9857 | 10.11 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208833 | TEHI TP1 | 69 | 229 | 0.7444 | 0.9755 | 23.11 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208833 | TEHI TP1 | 69 | 229 | 0.7533 | 0.9755 | 22.22 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208833 | TEHI TP1 | 69 | 229 | 0.7537 | 0.9755 | 22.18 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208833 | TEHI TP1 | 69 | 229 | 0.7537 | 0.9755 | 22.18 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208833 | TEHI TP1 | 69 | 229 | 0.8495 | 0.9755 | 12.6 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208832 | TEHI TP2 | 69 | 229 | 0.7423 | 0.9829 | 24.06 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208832 | TEHI TP2 | 69 | 229 | 0.7511 | 0.9829 | 23.18 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208832 | TEHI TP2 | 69 | 229 | 0.7514 | 0.9829 | 23.15 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208832 | TEHI TP2 | 69 | 229 | 0.7515 | 0.9829 | 23.14 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208832 | TEHI TP2 | 69 | 229 | 0.8521 | 0.9829 | 13.08 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208831 | TEHI TI | 69 | 229 | 0.7455 | 0.9764 | 23.09 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208831 | TEHI TI | 69 | 229 | 0.7543 | 0.9764 | 22.21 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208831 | TEHI TI | 69 | 229 | 0.7547 | 0.9764 | 22.17 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208831 | TEHI TI | 69 | 229 | 0.7547 | 0.9764 | 22.17 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208831 | TEHI TI | 69 | 229 | 0.8506 | 0.9764 | 12.58 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208829 | TEHI 2 | 69 | 229 | 0.7419 | 0.9825 | 24.06 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208829 | TEHI 2 | 69 | 229 | 0.7506 | 0.9825 | 23.19 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208829 | TEHI 2 | 69 | 229 | 0.751 | 0.9825 | 23.15 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208829 | TEHI 2 | 69 | 229 | 0.751 | 0.9825 | 23.15 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208829 | TEHI 2 | 69 | 229 | 0.8517 | 0.9825 | 13.08 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208826 | TEHI 1 | 69 | 229 | 0.7434 | 0.9746 | 23.12 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208826 | TEHI 1 | 69 | 229 | 0.7522 | 0.9746 | 22.24 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208826 | TEHI 1 | 69 | 229 | 0.7526 | 0.9746 | 22.2 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208826 | TEHI 1 | 69 | 229 | 0.7526 | 0.9746 | 22.2 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208826 | TEHI 1 | 69 | 229 | 0.8484 | 0.9746 | 12.62 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208825 | STRAMLTI | 69 | 229 | 0.8329 | 0.9763 | 14.34 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208825 | STRAMLTI | 69 | 229 | 0.8417 | 0.9763 | 13.46 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208825 | STRAMLTI | 69 | 229 | 0.842 | 0.9763 | 13.43 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208825 | STRAMLTI | 69 | 229 | 0.842 | 0.9763 | 13.43 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208823 | STRA TP2 | 69 | 229 | 0.8329 | 0.9763 | 14.34 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208823 | STRA TP2 | 69 | 229 | 0.8417 | 0.9763 | 13.46 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208823 | STRA TP2 | 69 | 229 | 0.842 | 0.9763 | 13.43 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208823 | STRA TP2 | 69 | 229 | 0.842 | 0.9763 | 13.43 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208822 | STRA TP1 | 69 | 229 | 0.8314 | 0.9766 | 14.52 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208822 | STRA TP1 | 69 | 229 | 0.8403 | 0.9766 | 13.63 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208822 | STRA TP1 | 69 | 229 | 0.8405 | 0.9766 | 13.61 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208822 | STRA TP1 | 69 | 229 | 0.8406 | 0.9766 | 13.6 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208820 | STRA | 69 | 229 | 0.8251 | 0.9717 | 14.66 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208820 | STRA | 69 | 229 | 0.8341 | 0.9717 | 13.76 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208820 | STRA | 69 | 229 | 0.8344 | 0.9717 | 13.73 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208820 | STRA | 69 | 229 | 0.8344 | 0.9717 | 13.73 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208819 | STRA NO | 69 | 229 | 0.8329 | 0.9763 | 14.34 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208819 | STRA NO | 69 | 229 | 0.8417 | 0.9763 | 13.46 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208819 | STRA NO | 69 | 229 | 0.842 | 0.9763 | 13.43 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208819 | STRA NO | 69 | 229 | 0.842 | 0.9763 | 13.43 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208814 | STHI TPR | 69 | 229 | 0.8001 | 0.9828 | 18.27 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208814 | STHI TPR | 69 | 229 | 0.8078 | 0.9828 | 17.5 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208814 | STHI TPR | 69 | 229 | 0.8082 | 0.9828 | 17.46 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208814 | STHI TPR | 69 | 229 | 0.8082 | 0.9828 | 17.46 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208814 | STHI TPR | 69 | 229 | 0.8896 | 0.9828 | 9.32 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208813 | STHI TP2 | 69 | 229 | 0.8001 | 0.9842 | 18.41 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208813 | STHI TP2 | 69 | 229 | 0.8079 | 0.9842 | 17.63 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208813 | STHI TP2 | 69 | 229 | 0.8083 | 0.9842 | 17.59 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208813 | STHI TP2 | 69 | 229 | 0.8083 | 0.9842 | 17.59 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208813 | STHI TP2 | 69 | 229 | 0.8904 | 0.9842 | 9.38 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208809 | STHI 2 | 69 | 229 | 0.7983 | 0.9827 | 18.44 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208809 | STHI 2 | 69 | 229 | 0.806 | 0.9827 | 17.67 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208809 | STHI 2 | 69 | 229 | 0.8064 | 0.9827 | 17.63 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208809 | STHI 2 | 69 | 229 | 0.8064 | 0.9827 | 17.63 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208809 | STHI 2 | 69 | 229 | 0.8887 | 0.9827 | 9.4 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208808 | STHI 1 | 69 | 229 | 0.7967 | 0.9803 | 18.36 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208808 | STHI 1 | 69 | 229 | 0.8044 | 0.9803 | 17.59 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208808 | STHI 1 | 69 | 229 | 0.8048 | 0.9803 | 17.55 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208808 | STHI 1 | 69 | 229 | 0.8048 | 0.9803 | 17.55 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208808 | STHI 1 | 69 | 229 | 0.8867 | 0.9803 | 9.36 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208800 | SPRI 2 | 69 | 229 | 0.8027 | 0.9852 | 18.25 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208800 | SPRI 2 | 69 | 229 | 0.8103 | 0.9852 | 17.49 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208800 | SPRI 2 | 69 | 229 | 0.8107 | 0.9852 | 17.45 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208800 | SPRI 2 | 69 | 229 | 0.8107 | 0.9852 | 17.45 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208800 | SPRI 2 | 69 | 229 | 0.8921 | 0.9852 | 9.31 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208799 | SPRI 1 | 69 | 229 | 0.8023 | 0.9849 | 18.26 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208799 | SPRI 1 | 69 | 229 | 0.8099 | 0.9849 | 17.5 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208799 | SPRI 1 | 69 | 229 | 0.8103 | 0.9849 | 17.46 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208799 | SPRI 1 | 69 | 229 | 0.8103 | 0.9849 | 17.46 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208799 | SPRI 1 | 69 | 229 | 0.8917 | 0.9849 | 9.32 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208794 | SMAN TP1 | 69 | 229 | 0.7942 | 0.9729 | 17.87 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208794 | SMAN TP1 | 69 | 229 | 0.8044 | 0.9729 | 16.85 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208794 | SMAN TP1 | 69 | 229 | 0.8048 | 0.9729 | 16.81 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208794 | SMAN TP1 | 69 | 229 | 0.8048 | 0.9729 | 16.81 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208794 | SMAN TP1 | 69 | 229 | 0.8855 | 0.9729 | 8.74 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208793 | SMAN TR2 | 69 | 229 | 0.751 | 0.9892 | 23.82 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208793 | SMAN TR2 | 69 | 229 | 0.7597 | 0.9892 | 22.95 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208793 | SMAN TR2 | 69 | 229 | 0.7601 | 0.9892 | 22.91 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208793 | SMAN TR2 | 69 | 229 | 0.7601 | 0.9892 | 22.91 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208793 | SMAN TR2 | 69 | 229 | 0.8567 | 0.9892 | 13.25 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208792 | SMAN TR1 | 69 | 229 | 0.751 | 0.9892 | 23.82 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208792 | SMAN TR1 | 69 | 229 | 0.7597 | 0.9892 | 22.95 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208792 | SMAN TR1 | 69 | 229 | 0.7601 | 0.9892 | 22.91 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208792 | SMAN TR1 | 69 | 229 | 0.7601 | 0.9892 | 22.91 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208792 | SMAN TR1 | 69 | 229 | 0.8567 | 0.9892 | 13.25 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208790 | SMAN | 69 | 229 | 0.751 | 0.9892 | 23.82 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208790 | SMAN | 69 | 229 | 0.7597 | 0.9892 | 22.95 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208790 | SMAN | 69 | 229 | 0.7601 | 0.9892 | 22.91 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208790 | SMAN | 69 | 229 | 0.7601 | 0.9892 | 22.91 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208790 | SMAN | 69 | 229 | 0.8567 | 0.9892 | 13.25 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208784 | SLIT TP | 69 | 229 | 0.7486 | 0.9876 | 23.9 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208784 | SLIT TP | 69 | 229 | 0.7574 | 0.9876 | 23.02 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208784 | SLIT TP | 69 | 229 | 0.7578 | 0.9876 | 22.98 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208784 | SLIT TP | 69 | 229 | 0.7578 | 0.9876 | 22.98 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208784 | SLIT TP | 69 | 229 | 0.8548 | 0.9876 | 13.28 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208782 | SLIT | 69 | 229 | 0.7459 | 0.9858 | 23.99 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208782 | SLIT | 69 | 229 | 0.7547 | 0.9858 | 23.11 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208782 | SLIT | 69 | 229 | 0.7551 | 0.9858 | 23.07 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208782 | SLIT | 69 | 229 | 0.7551 | 0.9858 | 23.07 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208782 | SLIT | 69 | 229 | 0.8526 | 0.9858 | 13.32 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208776 | SISP 2 | 69 | 229 | 0.8084 | 0.9824 | 17.4 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208776 | SISP 2 | 69 | 229 | 0.8182 | 0.9824 | 16.42 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208776 | SISP 2 | 69 | 229 | 0.8185 | 0.9824 | 16.39 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208776 | SISP 2 | 69 | 229 | 0.8185 | 0.9824 | 16.39 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208776 | SISP 2 | 69 | 229 | 0.8969 | 0.9824 | 8.55 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208774 | SISP 1 | 69 | 229 | 0.7982 | 0.9757 | 17.75 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208774 | SISP 1 | 69 | 229 | 0.8083 | 0.9757 | 16.74 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208774 | SISP 1 | 69 | 229 | 0.8086 | 0.9757 | 16.71 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208774 | SISP 1 | 69 | 229 | 0.8086 | 0.9757 | 16.71 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208774 | SISP 1 | 69 | 229 | 0.8888 | 0.9757 | 8.69 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208770 | SHIL 1 | 69 | 229 | 0.8379 | 0.9961 | 15.82 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208770 | SHIL 1 | 69 | 229 | 0.8449 | 0.9961 | 15.12 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208770 | SHIL 1 | 69 | 229 | 0.8453 | 0.9961 | 15.08 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208770 | SHIL 1 | 69 | 229 | 0.8453 | 0.9961 | 15.08 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208766 | SHIL 2 | 69 | 229 | 0.8004 | 0.983 | 18.26 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208766 | SHIL 2 | 69 | 229 | 0.8081 | 0.983 | 17.49 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208766 | SHIL 2 | 69 | 229 | 0.8085 | 0.983 | 17.45 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208766 | SHIL 2 | 69 | 229 | 0.8085 | 0.983 | 17.45 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208766 | SHIL 2 | 69 | 229 | 0.8898 | 0.983 | 9.32 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208763 | SAKR TR2 | 69 | 229 | 0.7582 | 0.9867 | 22.85 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208763 | SAKR TR2 | 69 | 229 | 0.7671 | 0.9867 | 21.96 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208763 | SAKR TR2 | 69 | 229 | 0.7675 | 0.9867 | 21.92 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208763 | SAKR TR2 | 69 | 229 | 0.7675 | 0.9867 | 21.92 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208763 | SAKR TR2 | 69 | 229 | 0.8629 | 0.9867 | 12.38 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208762 | SAKR TR1 | 69 | 229 | 0.7582 | 0.9867 | 22.85 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208762 | SAKR TR1 | 69 | 229 | 0.7671 | 0.9867 | 21.96 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208762 | SAKR TR1 | 69 | 229 | 0.7675 | 0.9867 | 21.92 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208762 | SAKR TR1 | 69 | 229 | 0.7675 | 0.9867 | 21.92 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208762 | SAKR TR1 | 69 | 229 | 0.8629 | 0.9867 | 12.38 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208759 | SAKR | 69 | 229 | 0.7582 | 0.9867 | 22.85 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208759 | SAKR | 69 | 229 | 0.7671 | 0.9867 | 21.96 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208759 | SAKR | 69 | 229 | 0.7675 | 0.9867 | 21.92 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208759 | SAKR | 69 | 229 | 0.7675 | 0.9867 | 21.92 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208759 | SAKR | 69 | 229 | 0.8629 | 0.9867 | 12.38 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208738 | ROBE TP1 | 69 | 229 | 0.7971 | 0.9807 | 18.36 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208738 | ROBE TP1 | 69 | 229 | 0.8048 | 0.9807 | 17.59 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208738 | ROBE TP1 | 69 | 229 | 0.8052 | 0.9807 | 17.55 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208738 | ROBE TP1 | 69 | 229 | 0.8052 | 0.9807 | 17.55 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208738 | ROBE TP1 | 69 | 229 | 0.8871 | 0.9807 | 9.36 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208737 | ROBE TP2 | 69 | 229 | 0.7952 | 0.9847 | 18.95 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208737 | ROBE TP2 | 69 | 229 | 0.8032 | 0.9847 | 18.15 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208737 | ROBE TP2 | 69 | 229 | 0.8036 | 0.9847 | 18.11 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208737 | ROBE TP2 | 69 | 229 | 0.8036 | 0.9847 | 18.11 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208737 | ROBE TP2 | 69 | 229 | 0.8884 | 0.9847 | 9.63 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208735 | ROBE | 69 | 229 | 0.7953 | 0.9849 | 18.96 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208735 | ROBE | 69 | 229 | 0.8033 | 0.9849 | 18.16 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208735 | ROBE | 69 | 229 | 0.8038 | 0.9849 | 18.11 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208735 | ROBE | 69 | 229 | 0.8038 | 0.9849 | 18.11 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208735 | ROBE | 69 | 229 | 0.8886 | 0.9849 | 9.63 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208734 | ROBE DC | 69 | 229 | 0.7952 | 0.9847 | 18.95 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208734 | ROBE DC | 69 | 229 | 0.8032 | 0.9847 | 18.15 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208734 | ROBE DC | 69 | 229 | 0.8036 | 0.9847 | 18.11 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208734 | ROBE DC | 69 | 229 | 0.8036 | 0.9847 | 18.11 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208734 | ROBE DC | 69 | 229 | 0.8885 | 0.9847 | 9.62 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208728 | RHEE | 69 | 229 | 0.7577 | 0.9772 | 21.95 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208728 | RHEE | 69 | 229 | 0.765 | 0.9772 | 21.22 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208728 | RHEE | 69 | 229 | 0.7654 | 0.9772 | 21.18 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208728 | RHEE | 69 | 229 | 0.7654 | 0.9772 | 21.18 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208728 | RHEE | 69 | 229 | 0.8579 | 0.9772 | 11.93 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208726 | REAM TP2 | 69 | 229 | 0.7891 | 0.9823 | 19.32 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208726 | REAM TP2 | 69 | 229 | 0.797 | 0.9823 | 18.53 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208726 | REAM TP2 | 69 | 229 | 0.7974 | 0.9823 | 18.49 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208726 | REAM TP2 | 69 | 229 | 0.7974 | 0.9823 | 18.49 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208726 | REAM TP2 | 69 | 229 | 0.8809 | 0.9823 | 10.14 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208725 | REAM TP1 | 69 | 229 | 0.7912 | 0.9841 | 19.29 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208725 | REAM TP1 | 69 | 229 | 0.799 | 0.9841 | 18.51 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208725 | REAM TP1 | 69 | 229 | 0.7994 | 0.9841 | 18.47 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208725 | REAM TP1 | 69 | 229 | 0.7994 | 0.9841 | 18.47 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208725 | REAM TP1 | 69 | 229 | 0.8828 | 0.9841 | 10.13 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208723 | REIN | 69 | 229 | 0.7943 | 0.9782 | 18.39 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208723 | REIN | 69 | 229 | 0.802 | 0.9782 | 17.62 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208723 | REIN | 69 | 229 | 0.8024 | 0.9782 | 17.58 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208723 | REIN | 69 | 229 | 0.8025 | 0.9782 | 17.57 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208723 | REIN | 69 | 229 | 0.8845 | 0.9782 | 9.37 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208721 | REAM 1 | 69 | 229 | 0.7912 | 0.9841 | 19.29 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208721 | REAM 1 | 69 | 229 | 0.799 | 0.9841 | 18.51 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208721 | REAM 1 | 69 | 229 | 0.7994 | 0.9841 | 18.47 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208721 | REAM 1 | 69 | 229 | 0.7994 | 0.9841 | 18.47 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208721 | REAM 1 | 69 | 229 | 0.8828 | 0.9841 | 10.13 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208717 | REAM 2 | 69 | 229 | 0.7891 | 0.9823 | 19.32 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208717 | REAM 2 | 69 | 229 | 0.797 | 0.9823 | 18.53 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208717 | REAM 2 | 69 | 229 | 0.7974 | 0.9823 | 18.49 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208717 | REAM 2 | 69 | 229 | 0.7974 | 0.9823 | 18.49 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208717 | REAM 2 | 69 | 229 | 0.8809 | 0.9823 | 10.14 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208712 | QVIL | 69 | 229 | 0.8471 | 0.9602 | 11.31 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208712 | QVIL | 69 | 229 | 0.8549 | 0.9602 | 10.53 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208712 | QVIL | 69 | 229 | 0.8551 | 0.9602 | 10.51 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208712 | QVIL | 69 | 229 | 0.8551 | 0.9602 | 10.51 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208711 | ATGL TP2 | 69 | 229 | 0.8318 | 0.9479 | 11.61 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208711 | ATGL TP2 | 69 | 229 | 0.8398 | 0.9479 | 10.81 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208711 | ATGL TP2 | 69 | 229 | 0.84 | 0.9479 | 10.79 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208711 | ATGL TP2 | 69 | 229 | 0.84 | 0.9479 | 10.79 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208708 | QVIL 14 | 69 | 229 | 0.8471 | 0.9602 | 11.31 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208708 | QVIL 14 | 69 | 229 | 0.8549 | 0.9602 | 10.53 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208708 | QVIL 14 | 69 | 229 | 0.8551 | 0.9602 | 10.51 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208708 | QVIL 14 | 69 | 229 | 0.8551 | 0.9602 | 10.51 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208707 | QVIL 13 | 69 | 229 | 0.8597 | 0.9664 | 10.67 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208707 | QVIL 13 | 69 | 229 | 0.8672 | 0.9664 | 9.92 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208707 | QVIL 13 | 69 | 229 | 0.8674 | 0.9664 | 9.9 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208707 | QVIL 13 | 69 | 229 | 0.8674 | 0.9664 | 9.9 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208686 | COCA TP | 69 | 229 | 0.7896 | 0.983 | 19.34 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208686 | COCA TP | 69 | 229 | 0.7975 | 0.983 | 18.55 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208686 | COCA TP | 69 | 229 | 0.7979 | 0.983 | 18.51 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208686 | COCA TP | 69 | 229 | 0.7979 | 0.983 | 18.51 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208686 | COCA TP | 69 | 229 | 0.8815 | 0.983 | 10.15 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208685 | PEFA | 69 | 229 | 0.7882 | 0.9817 | 19.35 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208685 | PEFA | 69 | 229 | 0.7961 | 0.9817 | 18.56 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208685 | PEFA | 69 | 229 | 0.7965 | 0.9817 | 18.52 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208685 | PEFA | 69 | 229 | 0.7965 | 0.9817 | 18.52 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208685 | PEFA | 69 | 229 | 0.8801 | 0.9817 | 10.16 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208674 | ODEC | 69 | 229 | 0.8585 | 0.9643 | 10.58 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208674 | ODEC | 69 | 229 | 0.8657 | 0.9643 | 9.86 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208674 | ODEC | 69 | 229 | 0.8659 | 0.9643 | 9.84 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208674 | ODEC | 69 | 229 | 0.866 | 0.9643 | 9.83 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208673 | CHWA ODEC | 69 | 229 | 0.8585 | 0.9643 | 10.58 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208673 | CHWA ODEC | 69 | 229 | 0.8657 | 0.9643 | 9.86 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208673 | CHWA ODEC | 69 | 229 | 0.8659 | 0.9643 | 9.84 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208673 | CHWA ODEC | 69 | 229 | 0.866 | 0.9643 | 9.83 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208671 | NMAN | 69 | 229 | 0.7456 | 0.9854 | 23.98 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208671 | NMAN | 69 | 229 | 0.7543 | 0.9854 | 23.11 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208671 | NMAN | 69 | 229 | 0.7547 | 0.9854 | 23.07 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208671 | NMAN | 69 | 229 | 0.7547 | 0.9854 | 23.07 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208671 | NMAN | 69 | 229 | 0.852 | 0.9854 | 13.34 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208666 | LAUS | 69 | 229 | 0.7985 | 0.9891 | 19.06 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208666 | LAUS | 69 | 229 | 0.8062 | 0.9891 | 18.29 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208666 | LAUS | 69 | 229 | 0.8066 | 0.9891 | 18.25 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208666 | LAUS | 69 | 229 | 0.8066 | 0.9891 | 18.25 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208666 | LAUS | 69 | 229 | 0.8888 | 0.9891 | 10.03 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208657 | NCOL TP2 | 69 | 229 | 0.8116 | 0.9854 | 17.38 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208657 | NCOL TP2 | 69 | 229 | 0.8214 | 0.9854 | 16.4 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208657 | NCOL TP2 | 69 | 229 | 0.8217 | 0.9854 | 16.37 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208657 | NCOL TP2 | 69 | 229 | 0.8217 | 0.9854 | 16.37 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208657 | NCOL TP2 | 69 | 229 | 0.8999 | 0.9854 | 8.55 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208656 | NCOL TP1 | 69 | 229 | 0.8144 | 0.9873 | 17.29 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208656 | NCOL TP1 | 69 | 229 | 0.8242 | 0.9873 | 16.31 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208656 | NCOL TP1 | 69 | 229 | 0.8245 | 0.9873 | 16.28 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208656 | NCOL TP1 | 69 | 229 | 0.8245 | 0.9873 | 16.28 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208656 | NCOL TP1 | 69 | 229 | 0.9023 | 0.9873 | 8.5 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208652 | NCOL 2 | 69 | 229 | 0.8098 | 0.9841 | 17.43 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208652 | NCOL 2 | 69 | 229 | 0.8196 | 0.9841 | 16.45 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208652 | NCOL 2 | 69 | 229 | 0.82 | 0.9841 | 16.41 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208652 | NCOL 2 | 69 | 229 | 0.82 | 0.9841 | 16.41 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208652 | NCOL 2 | 69 | 229 | 0.8985 | 0.9841 | 8.56 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208651 | NCOL 1 | 69 | 229 | 0.8142 | 0.9871 | 17.29 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208651 | NCOL 1 | 69 | 229 | 0.8239 | 0.9871 | 16.32 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208651 | NCOL 1 | 69 | 229 | 0.8242 | 0.9871 | 16.29 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208651 | NCOL 1 | 69 | 229 | 0.8242 | 0.9871 | 16.29 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208651 | NCOL 1 | 69 | 229 | 0.902 | 0.9871 | 8.51 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208637 | LAND TP2 | 69 | 229 | 0.7399 | 0.9816 | 24.17 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208637 | LAND TP2 | 69 | 229 | 0.7486 | 0.9816 | 23.3 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208637 | LAND TP2 | 69 | 229 | 0.749 | 0.9816 | 23.26 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208637 | LAND TP2 | 69 | 229 | 0.749 | 0.9816 | 23.26 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208637 | LAND TP2 | 69 | 229 | 0.8473 | 0.9816 | 13.43 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208635 | NAST | 69 | 229 | 0.7366 | 0.9785 | 24.19 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208635 | NAST | 69 | 229 | 0.7451 | 0.9785 | 23.34 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208635 | NAST | 69 | 229 | 0.7455 | 0.9785 | 23.3 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208635 | NAST | 69 | 229 | 0.7455 | 0.9785 | 23.3 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208635 | NAST | 69 | 229 | 0.8438 | 0.9785 | 13.47 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208626 | MONE | 69 | 229 | 0.8528 | 0.9771 | 12.43 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208626 | MONE | 69 | 229 | 0.8606 | 0.9771 | 11.65 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208626 | MONE | 69 | 229 | 0.8609 | 0.9771 | 11.62 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208626 | MONE | 69 | 229 | 0.8609 | 0.9771 | 11.62 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208621 | MOJO 1 | 69 | 229 | 0.7364 | 0.9784 | 24.2 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208621 | MOJO 1 | 69 | 229 | 0.745 | 0.9784 | 23.34 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208621 | MOJO 1 | 69 | 229 | 0.7453 | 0.9784 | 23.31 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208621 | MOJO 1 | 69 | 229 | 0.7454 | 0.9784 | 23.3 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208621 | MOJO 1 | 69 | 229 | 0.8437 | 0.9784 | 13.47 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208620 | MOJO TP2 | 69 | 229 | 0.7362 | 0.979 | 24.28 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208620 | MOJO TP2 | 69 | 229 | 0.7448 | 0.979 | 23.42 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208620 | MOJO TP2 | 69 | 229 | 0.7452 | 0.979 | 23.38 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208620 | MOJO TP2 | 69 | 229 | 0.7452 | 0.979 | 23.38 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208620 | MOJO TP2 | 69 | 229 | 0.8441 | 0.979 | 13.49 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208618 | MOJO 2 | 69 | 229 | 0.7359 | 0.9788 | 24.29 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208618 | MOJO 2 | 69 | 229 | 0.7445 | 0.9788 | 23.43 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208618 | MOJO 2 | 69 | 229 | 0.7449 | 0.9788 | 23.39 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208618 | MOJO 2 | 69 | 229 | 0.7449 | 0.9788 | 23.39 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208618 | MOJO 2 | 69 | 229 | 0.8438 | 0.9788 | 13.5 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208612 | MMMA 2 | 69 | 229 | 0.7298 | 0.9816 | 25.18 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208612 | MMMA 2 | 69 | 229 | 0.7368 | 0.9816 | 24.48 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208612 | MMMA 2 | 69 | 229 | 0.7372 | 0.9816 | 24.44 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208612 | MMMA 2 | 69 | 229 | 0.7372 | 0.9816 | 24.44 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208612 | MMMA 2 | 69 | 229 | 0.8454 | 0.9816 | 13.62 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208611 | MMMA 1 | 69 | 229 | 0.7298 | 0.9816 | 25.18 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208611 | MMMA 1 | 69 | 229 | 0.7368 | 0.9816 | 24.48 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208611 | MMMA 1 | 69 | 229 | 0.7372 | 0.9816 | 24.44 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208611 | MMMA 1 | 69 | 229 | 0.7372 | 0.9816 | 24.44 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208611 | MMMA 1 | 69 | 229 | 0.8454 | 0.9816 | 13.62 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208605 | MLWDSTTI | 69 | 229 | 0.8397 | 0.9841 | 14.44 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208605 | MLWDSTTI | 69 | 229 | 0.8484 | 0.9841 | 13.57 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208605 | MLWDSTTI | 69 | 229 | 0.8487 | 0.9841 | 13.54 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208605 | MLWDSTTI | 69 | 229 | 0.8487 | 0.9841 | 13.54 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208604 | MLWD | 69 | 229 | 0.8443 | 0.9892 | 14.49 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208604 | MLWD | 69 | 229 | 0.8529 | 0.9892 | 13.63 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208604 | MLWD | 69 | 229 | 0.8532 | 0.9892 | 13.6 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208604 | MLWD | 69 | 229 | 0.8532 | 0.9892 | 13.6 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208598 | MIUN 2 | 69 | 229 | 0.84 | 0.9807 | 14.07 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208598 | MIUN 2 | 69 | 229 | 0.8487 | 0.9807 | 13.2 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208598 | MIUN 2 | 69 | 229 | 0.849 | 0.9807 | 13.17 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208598 | MIUN 2 | 69 | 229 | 0.849 | 0.9807 | 13.17 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208597 | MIUN 1 | 69 | 229 | 0.8401 | 0.9807 | 14.06 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208597 | MIUN 1 | 69 | 229 | 0.8488 | 0.9807 | 13.19 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208597 | MIUN 1 | 69 | 229 | 0.849 | 0.9807 | 13.17 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208597 | MIUN 1 | 69 | 229 | 0.849 | 0.9807 | 13.17 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208591 | MILL TP2 | 69 | 229 | 0.8404 | 0.981 | 14.06 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208591 | MILL TP2 | 69 | 229 | 0.849 | 0.981 | 13.2 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208591 | MILL TP2 | 69 | 229 | 0.8493 | 0.981 | 13.17 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208591 | MILL TP2 | 69 | 229 | 0.8493 | 0.981 | 13.17 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208590 | MILL TP1 | 69 | 229 | 0.8404 | 0.981 | 14.06 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208590 | MILL TP1 | 69 | 229 | 0.8491 | 0.981 | 13.19 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208590 | MILL TP1 | 69 | 229 | 0.8494 | 0.981 | 13.16 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208590 | MILL TP1 | 69 | 229 | 0.8494 | 0.981 | 13.16 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208587 | MILL 2 | 69 | 229 | 0.84 | 0.9807 | 14.07 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208587 | MILL 2 | 69 | 229 | 0.8487 | 0.9807 | 13.2 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208587 | MILL 2 | 69 | 229 | 0.849 | 0.9807 | 13.17 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208587 | MILL 2 | 69 | 229 | 0.849 | 0.9807 | 13.17 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208586 | MILL 1 | 69 | 229 | 0.8401 | 0.9807 | 14.06 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208586 | MILL 1 | 69 | 229 | 0.8488 | 0.9807 | 13.19 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208586 | MILL 1 | 69 | 229 | 0.849 | 0.9807 | 13.17 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208586 | MILL 1 | 69 | 229 | 0.849 | 0.9807 | 13.17 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208578 | MGTN 2 | 69 | 229 | 0.7671 | 0.9679 | 20.08 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208578 | MGTN 2 | 69 | 229 | 0.775 | 0.9679 | 19.29 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208578 | MGTN 2 | 69 | 229 | 0.7754 | 0.9679 | 19.25 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208578 | MGTN 2 | 69 | 229 | 0.7754 | 0.9679 | 19.25 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208578 | MGTN 2 | 69 | 229 | 0.8629 | 0.9679 | 10.5 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208577 | MGTN 1 | 69 | 229 | 0.7935 | 0.9857 | 19.22 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208577 | MGTN 1 | 69 | 229 | 0.8012 | 0.9857 | 18.45 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208577 | MGTN 1 | 69 | 229 | 0.8016 | 0.9857 | 18.41 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208577 | MGTN 1 | 69 | 229 | 0.8017 | 0.9857 | 18.4 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208577 | MGTN 1 | 69 | 229 | 0.8846 | 0.9857 | 10.11 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208566 | MCGO | 69 | 229 | 0.7905 | 0.9701 | 17.96 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208566 | MCGO | 69 | 229 | 0.8008 | 0.9701 | 16.93 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208566 | MCGO | 69 | 229 | 0.8011 | 0.9701 | 16.9 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208566 | MCGO | 69 | 229 | 0.8011 | 0.9701 | 16.9 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208566 | MCGO | 69 | 229 | 0.8823 | 0.9701 | 8.78 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208560 | MARI TP2 | 69 | 229 | 0.8099 | 0.9838 | 17.39 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208560 | MARI TP2 | 69 | 229 | 0.8197 | 0.9838 | 16.41 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208560 | MARI TP2 | 69 | 229 | 0.82 | 0.9838 | 16.38 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208560 | MARI TP2 | 69 | 229 | 0.82 | 0.9838 | 16.38 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208560 | MARI TP2 | 69 | 229 | 0.8983 | 0.9838 | 8.55 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208559 | MARI TP1 | 69 | 229 | 0.8044 | 0.9799 | 17.55 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208559 | MARI TP1 | 69 | 229 | 0.8143 | 0.9799 | 16.56 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208559 | MARI TP1 | 69 | 229 | 0.8146 | 0.9799 | 16.53 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208559 | MARI TP1 | 69 | 229 | 0.8147 | 0.9799 | 16.52 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208559 | MARI TP1 | 69 | 229 | 0.8938 | 0.9799 | 8.61 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208557 | MARI | 69 | 229 | 0.8043 | 0.9799 | 17.56 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208557 | MARI | 69 | 229 | 0.8142 | 0.9799 | 16.57 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208557 | MARI | 69 | 229 | 0.8145 | 0.9799 | 16.54 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208557 | MARI | 69 | 229 | 0.8146 | 0.9799 | 16.53 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208557 | MARI | 69 | 229 | 0.8937 | 0.9799 | 8.62 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208551 | MANO | 69 | 229 | 0.8562 | 0.9893 | 13.31 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208551 | MANO | 69 | 229 | 0.8645 | 0.9893 | 12.48 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208551 | MANO | 69 | 229 | 0.8648 | 0.9893 | 12.45 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208551 | MANO | 69 | 229 | 0.8648 | 0.9893 | 12.45 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208543 | LITI 2 | 69 | 229 | 0.7446 | 0.9777 | 23.31 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208543 | LITI 2 | 69 | 229 | 0.7535 | 0.9777 | 22.42 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208543 | LITI 2 | 69 | 229 | 0.7539 | 0.9777 | 22.38 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208543 | LITI 2 | 69 | 229 | 0.7539 | 0.9777 | 22.38 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208543 | LITI 2 | 69 | 229 | 0.8517 | 0.9777 | 12.6 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208542 | LITI 1 | 69 | 229 | 0.7476 | 0.9869 | 23.93 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208542 | LITI 1 | 69 | 229 | 0.7564 | 0.9869 | 23.05 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208542 | LITI 1 | 69 | 229 | 0.7568 | 0.9869 | 23.01 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208542 | LITI 1 | 69 | 229 | 0.7568 | 0.9869 | 23.01 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208542 | LITI 1 | 69 | 229 | 0.8539 | 0.9869 | 13.3 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208535 | LINC 1 | 69 | 229 | 0.7321 | 0.9678 | 23.57 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208535 | LINC 1 | 69 | 229 | 0.7408 | 0.9678 | 22.7 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208535 | LINC 1 | 69 | 229 | 0.7411 | 0.9678 | 22.67 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208535 | LINC 1 | 69 | 229 | 0.7412 | 0.9678 | 22.66 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208535 | LINC 1 | 69 | 229 | 0.8399 | 0.9678 | 12.79 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208533 | LINC 2 | 69 | 229 | 0.7321 | 0.9678 | 23.57 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208533 | LINC 2 | 69 | 229 | 0.7407 | 0.9678 | 22.71 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208533 | LINC 2 | 69 | 229 | 0.7411 | 0.9678 | 22.67 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208533 | LINC 2 | 69 | 229 | 0.7411 | 0.9678 | 22.67 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208533 | LINC 2 | 69 | 229 | 0.8399 | 0.9678 | 12.79 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208528 | LETO | 69 | 229 | 0.8323 | 0.9882 | 15.59 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208528 | LETO | 69 | 229 | 0.8415 | 0.9882 | 14.67 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208528 | LETO | 69 | 229 | 0.8418 | 0.9882 | 14.64 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208528 | LETO | 69 | 229 | 0.8418 | 0.9882 | 14.64 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208514 | LAWF TP | 69 | 229 | 0.8169 | 0.9885 | 17.16 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208514 | LAWF TP | 69 | 229 | 0.8266 | 0.9885 | 16.19 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208514 | LAWF TP | 69 | 229 | 0.8269 | 0.9885 | 16.16 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208514 | LAWF TP | 69 | 229 | 0.8269 | 0.9885 | 16.16 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208514 | LAWF TP | 69 | 229 | 0.9041 | 0.9885 | 8.44 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208513 | LAWF | 69 | 229 | 0.8169 | 0.9884 | 17.15 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208513 | LAWF | 69 | 229 | 0.8265 | 0.9884 | 16.19 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208513 | LAWF | 69 | 229 | 0.8269 | 0.9884 | 16.15 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208513 | LAWF | 69 | 229 | 0.8269 | 0.9884 | 16.15 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208513 | LAWF | 69 | 229 | 0.9041 | 0.9884 | 8.43 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208509 | LAVI 1 | 69 | 229 | 0.7955 | 0.9795 | 18.4 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208509 | LAVI 1 | 69 | 229 | 0.8033 | 0.9795 | 17.62 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208509 | LAVI 1 | 69 | 229 | 0.8037 | 0.9795 | 17.58 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208509 | LAVI 1 | 69 | 229 | 0.8037 | 0.9795 | 17.58 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208509 | LAVI 1 | 69 | 229 | 0.8857 | 0.9795 | 9.38 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208507 | LAVI 1 TP | 69 | 229 | 0.7954 | 0.979 | 18.36 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208507 | LAVI 1 TP | 69 | 229 | 0.8031 | 0.979 | 17.59 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208507 | LAVI 1 TP | 69 | 229 | 0.8035 | 0.979 | 17.55 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208507 | LAVI 1 TP | 69 | 229 | 0.8035 | 0.979 | 17.55 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208507 | LAVI 1 TP | 69 | 229 | 0.8854 | 0.979 | 9.36 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208504 | LAVI 2 | 69 | 229 | 0.7901 | 0.9812 | 19.11 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208504 | LAVI 2 | 69 | 229 | 0.7983 | 0.9812 | 18.29 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208504 | LAVI 2 | 69 | 229 | 0.7987 | 0.9812 | 18.25 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208504 | LAVI 2 | 69 | 229 | 0.7987 | 0.9812 | 18.25 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208504 | LAVI 2 | 69 | 229 | 0.8843 | 0.9812 | 9.69 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208490 | LAPI TP2 | 69 | 229 | 0.8017 | 0.9845 | 18.28 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208490 | LAPI TP2 | 69 | 229 | 0.8093 | 0.9845 | 17.52 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208490 | LAPI TP2 | 69 | 229 | 0.8097 | 0.9845 | 17.48 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208490 | LAPI TP2 | 69 | 229 | 0.8097 | 0.9845 | 17.48 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208490 | LAPI TP2 | 69 | 229 | 0.8912 | 0.9845 | 9.33 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208489 | LAPI TP1 | 69 | 229 | 0.8016 | 0.9839 | 18.23 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208489 | LAPI TP1 | 69 | 229 | 0.8093 | 0.9839 | 17.46 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208489 | LAPI TP1 | 69 | 229 | 0.8097 | 0.9839 | 17.42 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208489 | LAPI TP1 | 69 | 229 | 0.8097 | 0.9839 | 17.42 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208489 | LAPI TP1 | 69 | 229 | 0.8909 | 0.9839 | 9.3 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208488 | LAPI | 69 | 229 | 0.8016 | 0.9839 | 18.23 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208488 | LAPI | 69 | 229 | 0.8093 | 0.9839 | 17.46 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208488 | LAPI | 69 | 229 | 0.8097 | 0.9839 | 17.42 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208488 | LAPI | 69 | 229 | 0.8097 | 0.9839 | 17.42 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208488 | LAPI | 69 | 229 | 0.8909 | 0.9839 | 9.3 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208480 | LAND 2 | 69 | 229 | 0.8048 | 0.9796 | 17.48 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208480 | LAND 2 | 69 | 229 | 0.8147 | 0.9796 | 16.49 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208480 | LAND 2 | 69 | 229 | 0.815 | 0.9796 | 16.46 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208480 | LAND 2 | 69 | 229 | 0.815 | 0.9796 | 16.46 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208480 | LAND 2 | 69 | 229 | 0.8937 | 0.9796 | 8.59 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208479 | LAND 1 | 69 | 229 | 0.7937 | 0.9726 | 17.89 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208479 | LAND 1 | 69 | 229 | 0.8039 | 0.9726 | 16.87 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208479 | LAND 1 | 69 | 229 | 0.8042 | 0.9726 | 16.84 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208479 | LAND 1 | 69 | 229 | 0.8043 | 0.9726 | 16.83 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208479 | LAND 1 | 69 | 229 | 0.8851 | 0.9726 | 8.75 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208473 | KINZ TP | 69 | 229 | 0.7558 | 0.9922 | 23.64 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208473 | KINZ TP | 69 | 229 | 0.7647 | 0.9922 | 22.75 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208473 | KINZ TP | 69 | 229 | 0.7651 | 0.9922 | 22.71 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208473 | KINZ TP | 69 | 229 | 0.7651 | 0.9922 | 22.71 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208473 | KINZ TP | 69 | 229 | 0.8641 | 0.9922 | 12.81 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208471 | KINZ 2 | 69 | 229 | 0.8279 | 0.9449 | 11.7 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208471 | KINZ 2 | 69 | 229 | 0.836 | 0.9449 | 10.89 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208471 | KINZ 2 | 69 | 229 | 0.8362 | 0.9449 | 10.87 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208471 | KINZ 2 | 69 | 229 | 0.8362 | 0.9449 | 10.87 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208470 | KINZ TP2 | 69 | 229 | 0.7713 | 0.9709 | 19.96 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208470 | KINZ TP2 | 69 | 229 | 0.7791 | 0.9709 | 19.18 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208470 | KINZ TP2 | 69 | 229 | 0.7796 | 0.9709 | 19.13 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208470 | KINZ TP2 | 69 | 229 | 0.7796 | 0.9709 | 19.13 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208470 | KINZ TP2 | 69 | 229 | 0.8665 | 0.9709 | 10.44 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208469 | KINZ 1 | 69 | 229 | 0.8469 | 0.9562 | 10.93 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208469 | KINZ 1 | 69 | 229 | 0.8546 | 0.9562 | 10.16 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208469 | KINZ 1 | 69 | 229 | 0.8549 | 0.9562 | 10.13 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208469 | KINZ 1 | 69 | 229 | 0.8549 | 0.9562 | 10.13 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208466 | KELG 2 | 69 | 229 | 0.8033 | 0.9784 | 17.51 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208466 | KELG 2 | 69 | 229 | 0.8132 | 0.9784 | 16.52 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208466 | KELG 2 | 69 | 229 | 0.8135 | 0.9784 | 16.49 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208466 | KELG 2 | 69 | 229 | 0.8135 | 0.9784 | 16.49 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208466 | KELG 2 | 69 | 229 | 0.8924 | 0.9784 | 8.6 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208465 | KELG 1 | 69 | 229 | 0.791 | 0.9705 | 17.95 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208465 | KELG 1 | 69 | 229 | 0.8012 | 0.9705 | 16.93 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208465 | KELG 1 | 69 | 229 | 0.8016 | 0.9705 | 16.89 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208465 | KELG 1 | 69 | 229 | 0.8016 | 0.9705 | 16.89 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208465 | KELG 1 | 69 | 229 | 0.8827 | 0.9705 | 8.78 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208464 | HWMT 2 | 69 | 229 | 0.7367 | 0.9757 | 23.9 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208464 | HWMT 2 | 69 | 229 | 0.7453 | 0.9757 | 23.04 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208464 | HWMT 2 | 69 | 229 | 0.7457 | 0.9757 | 23 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208464 | HWMT 2 | 69 | 229 | 0.7457 | 0.9757 | 23 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208464 | HWMT 2 | 69 | 229 | 0.8405 | 0.9757 | 13.52 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208463 | HWMT 1 | 69 | 229 | 0.7375 | 0.9764 | 23.89 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208463 | HWMT 1 | 69 | 229 | 0.746 | 0.9764 | 23.04 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208463 | HWMT 1 | 69 | 229 | 0.7464 | 0.9764 | 23 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208463 | HWMT 1 | 69 | 229 | 0.7464 | 0.9764 | 23 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208463 | HWMT 1 | 69 | 229 | 0.8414 | 0.9764 | 13.5 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208456 | HONY TIE | 69 | 229 | 0.7718 | 0.9712 | 19.94 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208456 | HONY TIE | 69 | 229 | 0.7796 | 0.9712 | 19.16 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208456 | HONY TIE | 69 | 229 | 0.78 | 0.9712 | 19.12 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208456 | HONY TIE | 69 | 229 | 0.78 | 0.9712 | 19.12 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208456 | HONY TIE | 69 | 229 | 0.8668 | 0.9712 | 10.44 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208455 | HWMT TP2 | 69 | 229 | 0.7417 | 0.9804 | 23.87 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208455 | HWMT TP2 | 69 | 229 | 0.7503 | 0.9804 | 23.01 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208455 | HWMT TP2 | 69 | 229 | 0.7507 | 0.9804 | 22.97 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208455 | HWMT TP2 | 69 | 229 | 0.7507 | 0.9804 | 22.97 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208455 | HWMT TP2 | 69 | 229 | 0.8462 | 0.9804 | 13.42 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208454 | HWMT TP1 | 69 | 229 | 0.7421 | 0.9807 | 23.86 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208454 | HWMT TP1 | 69 | 229 | 0.7507 | 0.9807 | 23 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208454 | HWMT TP1 | 69 | 229 | 0.7511 | 0.9807 | 22.96 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208454 | HWMT TP1 | 69 | 229 | 0.7511 | 0.9807 | 22.96 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208454 | HWMT TP1 | 69 | 229 | 0.8466 | 0.9807 | 13.41 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208452 | HONY TP | 69 | 229 | 0.7713 | 0.9709 | 19.96 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208452 | HONY TP | 69 | 229 | 0.7791 | 0.9709 | 19.18 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208452 | HONY TP | 69 | 229 | 0.7795 | 0.9709 | 19.14 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208452 | HONY TP | 69 | 229 | 0.7795 | 0.9709 | 19.14 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208452 | HONY TP | 69 | 229 | 0.8664 | 0.9709 | 10.45 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208451 | HONY | 69 | 229 | 0.764 | 0.9657 | 20.17 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208451 | HONY | 69 | 229 | 0.7718 | 0.9657 | 19.39 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208451 | HONY | 69 | 229 | 0.7723 | 0.9657 | 19.34 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208451 | HONY | 69 | 229 | 0.7723 | 0.9657 | 19.34 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208451 | HONY | 69 | 229 | 0.8603 | 0.9657 | 10.54 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208448 | HONY 2 | 69 | 229 | 0.764 | 0.9657 | 20.17 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208448 | HONY 2 | 69 | 229 | 0.7718 | 0.9657 | 19.39 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208448 | HONY 2 | 69 | 229 | 0.7723 | 0.9657 | 19.34 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208448 | HONY 2 | 69 | 229 | 0.7723 | 0.9657 | 19.34 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208448 | HONY 2 | 69 | 229 | 0.8603 | 0.9657 | 10.54 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208437 | HEMP 2 | 69 | 229 | 0.8144 | 0.9872 | 17.28 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208437 | HEMP 2 | 69 | 229 | 0.8241 | 0.9872 | 16.31 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208437 | HEMP 2 | 69 | 229 | 0.8244 | 0.9872 | 16.28 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208437 | HEMP 2 | 69 | 229 | 0.8244 | 0.9872 | 16.28 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208437 | HEMP 2 | 69 | 229 | 0.9022 | 0.9872 | 8.5 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208436 | HEMP 1 | 69 | 229 | 0.8149 | 0.9878 | 17.29 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208436 | HEMP 1 | 69 | 229 | 0.8247 | 0.9878 | 16.31 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208436 | HEMP 1 | 69 | 229 | 0.825 | 0.9878 | 16.28 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208436 | HEMP 1 | 69 | 229 | 0.825 | 0.9878 | 16.28 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208436 | HEMP 1 | 69 | 229 | 0.9028 | 0.9878 | 8.5 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208429 | HEID | 69 | 229 | 0.7352 | 0.9775 | 24.23 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208429 | HEID | 69 | 229 | 0.7437 | 0.9775 | 23.38 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208429 | HEID | 69 | 229 | 0.7441 | 0.9775 | 23.34 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208429 | HEID | 69 | 229 | 0.7441 | 0.9775 | 23.34 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208429 | HEID | 69 | 229 | 0.8423 | 0.9775 | 13.52 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208423 | GRIN TP2 | 69 | 229 | 0.8126 | 0.986 | 17.34 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208423 | GRIN TP2 | 69 | 229 | 0.8224 | 0.986 | 16.36 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208423 | GRIN TP2 | 69 | 229 | 0.8227 | 0.986 | 16.33 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208423 | GRIN TP2 | 69 | 229 | 0.8227 | 0.986 | 16.33 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208423 | GRIN TP2 | 69 | 229 | 0.9008 | 0.986 | 8.52 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208422 | GRIN TP1 | 69 | 229 | 0.8139 | 0.9871 | 17.32 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208422 | GRIN TP1 | 69 | 229 | 0.8237 | 0.9871 | 16.34 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208422 | GRIN TP1 | 69 | 229 | 0.824 | 0.9871 | 16.31 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208422 | GRIN TP1 | 69 | 229 | 0.824 | 0.9871 | 16.31 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208422 | GRIN TP1 | 69 | 229 | 0.9019 | 0.9871 | 8.52 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208421 | GRIN 2 | 69 | 229 | 0.8127 | 0.986 | 17.33 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208421 | GRIN 2 | 69 | 229 | 0.8224 | 0.986 | 16.36 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208421 | GRIN 2 | 69 | 229 | 0.8227 | 0.986 | 16.33 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208421 | GRIN 2 | 69 | 229 | 0.8228 | 0.986 | 16.32 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208421 | GRIN 2 | 69 | 229 | 0.9008 | 0.986 | 8.52 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208420 | GRIN 1 | 69 | 229 | 0.8132 | 0.9864 | 17.32 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208420 | GRIN 1 | 69 | 229 | 0.8229 | 0.9864 | 16.35 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208420 | GRIN 1 | 69 | 229 | 0.8232 | 0.9864 | 16.32 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208420 | GRIN 1 | 69 | 229 | 0.8232 | 0.9864 | 16.32 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208420 | GRIN 1 | 69 | 229 | 0.9012 | 0.9864 | 8.52 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208413 | GREE 2 | 69 | 229 | 0.8292 | 0.9728 | 14.36 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208413 | GREE 2 | 69 | 229 | 0.838 | 0.9728 | 13.48 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208413 | GREE 2 | 69 | 229 | 0.8382 | 0.9728 | 13.46 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208413 | GREE 2 | 69 | 229 | 0.8382 | 0.9728 | 13.46 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208412 | GREE 1 | 69 | 229 | 0.8317 | 0.9776 | 14.59 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208412 | GREE 1 | 69 | 229 | 0.8407 | 0.9776 | 13.69 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208412 | GREE 1 | 69 | 229 | 0.841 | 0.9776 | 13.66 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208412 | GREE 1 | 69 | 229 | 0.841 | 0.9776 | 13.66 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208408 | LAND TP1 | 69 | 229 | 0.7401 | 0.9812 | 24.11 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208408 | LAND TP1 | 69 | 229 | 0.7487 | 0.9812 | 23.25 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208408 | LAND TP1 | 69 | 229 | 0.7491 | 0.9812 | 23.21 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208408 | LAND TP1 | 69 | 229 | 0.7491 | 0.9812 | 23.21 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208408 | LAND TP1 | 69 | 229 | 0.847 | 0.9812 | 13.42 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208406 | FULL TP1 | 69 | 229 | 0.749 | 0.9877 | 23.87 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208406 | FULL TP1 | 69 | 229 | 0.7577 | 0.9877 | 23 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208406 | FULL TP1 | 69 | 229 | 0.758 | 0.9877 | 22.97 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208406 | FULL TP1 | 69 | 229 | 0.7581 | 0.9877 | 22.96 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208406 | FULL TP1 | 69 | 229 | 0.8549 | 0.9877 | 13.28 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208404 | FULL | 69 | 229 | 0.7488 | 0.9876 | 23.88 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208404 | FULL | 69 | 229 | 0.7575 | 0.9876 | 23.01 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208404 | FULL | 69 | 229 | 0.7579 | 0.9876 | 22.97 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208404 | FULL | 69 | 229 | 0.7579 | 0.9876 | 22.97 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208404 | FULL | 69 | 229 | 0.8548 | 0.9876 | 13.28 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208400 | FRKZ13TI | 69 | 229 | 0.8647 | 0.9696 | 10.49 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208400 | FRKZ13TI | 69 | 229 | 0.8718 | 0.9696 | 9.78 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208400 | FRKZ13TI | 69 | 229 | 0.8721 | 0.9696 | 9.75 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208400 | FRKZ13TI | 69 | 229 | 0.8721 | 0.9696 | 9.75 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208399 | FRKZ14TI | 69 | 229 | 0.8647 | 0.9696 | 10.49 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208399 | FRKZ14TI | 69 | 229 | 0.8718 | 0.9696 | 9.78 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208399 | FRKZ14TI | 69 | 229 | 0.8721 | 0.9696 | 9.75 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208399 | FRKZ14TI | 69 | 229 | 0.8721 | 0.9696 | 9.75 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208396 | FARO | 69 | 229 | 0.8647 | 0.9696 | 10.49 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208396 | FARO | 69 | 229 | 0.8718 | 0.9696 | 9.78 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208396 | FARO | 69 | 229 | 0.8721 | 0.9696 | 9.75 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208396 | FARO | 69 | 229 | 0.8721 | 0.9696 | 9.75 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208395 | FARO FF | 69 | 229 | 0.8644 | 0.9693 | 10.49 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208395 | FARO FF | 69 | 229 | 0.8715 | 0.9693 | 9.78 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208395 | FARO FF | 69 | 229 | 0.8717 | 0.9693 | 9.76 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208395 | FARO FF | 69 | 229 | 0.8718 | 0.9693 | 9.75 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208390 | EPHR TP2 | 69 | 229 | 0.7304 | 0.9666 | 23.62 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208390 | EPHR TP2 | 69 | 229 | 0.739 | 0.9666 | 22.76 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208390 | EPHR TP2 | 69 | 229 | 0.7394 | 0.9666 | 22.72 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208390 | EPHR TP2 | 69 | 229 | 0.7394 | 0.9666 | 22.72 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208390 | EPHR TP2 | 69 | 229 | 0.8385 | 0.9666 | 12.81 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208389 | EPHR TP1 | 69 | 229 | 0.7457 | 0.9778 | 23.21 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208389 | EPHR TP1 | 69 | 229 | 0.7545 | 0.9778 | 22.33 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208389 | EPHR TP1 | 69 | 229 | 0.7548 | 0.9778 | 22.3 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208389 | EPHR TP1 | 69 | 229 | 0.7549 | 0.9778 | 22.29 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208389 | EPHR TP1 | 69 | 229 | 0.852 | 0.9778 | 12.58 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208387 | EPHR 2 | 69 | 229 | 0.7262 | 0.9634 | 23.72 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208387 | EPHR 2 | 69 | 229 | 0.7348 | 0.9634 | 22.86 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208387 | EPHR 2 | 69 | 229 | 0.7351 | 0.9634 | 22.83 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208387 | EPHR 2 | 69 | 229 | 0.7351 | 0.9634 | 22.83 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208387 | EPHR 2 | 69 | 229 | 0.8347 | 0.9634 | 12.87 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208386 | EPHR 1 | 69 | 229 | 0.7416 | 0.9749 | 23.33 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208386 | EPHR 1 | 69 | 229 | 0.7503 | 0.9749 | 22.46 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208386 | EPHR 1 | 69 | 229 | 0.7507 | 0.9749 | 22.42 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208386 | EPHR 1 | 69 | 229 | 0.7507 | 0.9749 | 22.42 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208386 | EPHR 1 | 69 | 229 | 0.8484 | 0.9749 | 12.65 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208372 | ENGL | 69 | 229 | 0.8374 | 0.9805 | 14.31 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208372 | ENGL | 69 | 229 | 0.8461 | 0.9805 | 13.44 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208372 | ENGL | 69 | 229 | 0.8464 | 0.9805 | 13.41 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208372 | ENGL | 69 | 229 | 0.8464 | 0.9805 | 13.41 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208367 | ELIZ DC | 69 | 229 | 0.7303 | 0.982 | 25.17 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208367 | ELIZ DC | 69 | 229 | 0.7373 | 0.982 | 24.47 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208367 | ELIZ DC | 69 | 229 | 0.7377 | 0.982 | 24.43 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208367 | ELIZ DC | 69 | 229 | 0.7377 | 0.982 | 24.43 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208367 | ELIZ DC | 69 | 229 | 0.8458 | 0.982 | 13.62 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208366 | ELIZ TP1 | 69 | 229 | 0.7578 | 0.9772 | 21.94 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208366 | ELIZ TP1 | 69 | 229 | 0.7651 | 0.9772 | 21.21 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208366 | ELIZ TP1 | 69 | 229 | 0.7655 | 0.9772 | 21.17 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208366 | ELIZ TP1 | 69 | 229 | 0.7655 | 0.9772 | 21.17 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208366 | ELIZ TP1 | 69 | 229 | 0.858 | 0.9772 | 11.92 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208365 | ELIZ 2 | 69 | 229 | 0.7303 | 0.982 | 25.17 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208365 | ELIZ 2 | 69 | 229 | 0.7373 | 0.982 | 24.47 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208365 | ELIZ 2 | 69 | 229 | 0.7376 | 0.982 | 24.44 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208365 | ELIZ 2 | 69 | 229 | 0.7377 | 0.982 | 24.43 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208365 | ELIZ 2 | 69 | 229 | 0.8458 | 0.982 | 13.62 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208364 | ELIZ 1 | 69 | 229 | 0.7577 | 0.9772 | 21.95 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208364 | ELIZ 1 | 69 | 229 | 0.765 | 0.9772 | 21.22 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208364 | ELIZ 1 | 69 | 229 | 0.7654 | 0.9772 | 21.18 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208364 | ELIZ 1 | 69 | 229 | 0.7654 | 0.9772 | 21.18 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208364 | ELIZ 1 | 69 | 229 | 0.8579 | 0.9772 | 11.93 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208347 | EELI | 69 | 229 | 0.7366 | 0.9817 | 24.51 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208347 | EELI | 69 | 229 | 0.7436 | 0.9817 | 23.81 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208347 | EELI | 69 | 229 | 0.744 | 0.9817 | 23.77 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208347 | EELI | 69 | 229 | 0.744 | 0.9817 | 23.77 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208347 | EELI | 69 | 229 | 0.849 | 0.9817 | 13.27 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208344 | ELIZ TP2 | 69 | 229 | 0.7337 | 0.9818 | 24.81 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208344 | ELIZ TP2 | 69 | 229 | 0.7407 | 0.9818 | 24.11 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208344 | ELIZ TP2 | 69 | 229 | 0.741 | 0.9818 | 24.08 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208344 | ELIZ TP2 | 69 | 229 | 0.7411 | 0.9818 | 24.07 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208344 | ELIZ TP2 | 69 | 229 | 0.8475 | 0.9818 | 13.43 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208343 | EELI TP2 | 69 | 229 | 0.7366 | 0.9817 | 24.51 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208343 | EELI TP2 | 69 | 229 | 0.7436 | 0.9817 | 23.81 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208343 | EELI TP2 | 69 | 229 | 0.744 | 0.9817 | 23.77 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208343 | EELI TP2 | 69 | 229 | 0.744 | 0.9817 | 23.77 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208343 | EELI TP2 | 69 | 229 | 0.8489 | 0.9817 | 13.28 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208342 | EELI TP1 | 69 | 229 | 0.7579 | 0.9772 | 21.93 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208342 | EELI TP1 | 69 | 229 | 0.7652 | 0.9772 | 21.2 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208342 | EELI TP1 | 69 | 229 | 0.7656 | 0.9772 | 21.16 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208342 | EELI TP1 | 69 | 229 | 0.7656 | 0.9772 | 21.16 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208342 | EELI TP1 | 69 | 229 | 0.858 | 0.9772 | 11.92 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208341 | EARL TP2 | 69 | 229 | 0.756 | 0.9915 | 23.55 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208341 | EARL TP2 | 69 | 229 | 0.7649 | 0.9915 | 22.66 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208341 | EARL TP2 | 69 | 229 | 0.7653 | 0.9915 | 22.62 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208341 | EARL TP2 | 69 | 229 | 0.7653 | 0.9915 | 22.62 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208341 | EARL TP2 | 69 | 229 | 0.8639 | 0.9915 | 12.76 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208340 | EARL TP1 | 69 | 229 | 0.7443 | 0.9846 | 24.03 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208340 | EARL TP1 | 69 | 229 | 0.753 | 0.9846 | 23.16 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208340 | EARL TP1 | 69 | 229 | 0.7534 | 0.9846 | 23.12 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208340 | EARL TP1 | 69 | 229 | 0.7534 | 0.9846 | 23.12 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208340 | EARL TP1 | 69 | 229 | 0.8541 | 0.9846 | 13.05 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208338 | EARL 2 | 69 | 229 | 0.7558 | 0.9922 | 23.64 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208338 | EARL 2 | 69 | 229 | 0.7647 | 0.9922 | 22.75 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208338 | EARL 2 | 69 | 229 | 0.7651 | 0.9922 | 22.71 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208338 | EARL 2 | 69 | 229 | 0.7651 | 0.9922 | 22.71 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208338 | EARL 2 | 69 | 229 | 0.8641 | 0.9922 | 12.81 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208337 | EARL 1 | 69 | 229 | 0.7448 | 0.9856 | 24.08 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208337 | EARL 1 | 69 | 229 | 0.7535 | 0.9856 | 23.21 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208337 | EARL 1 | 69 | 229 | 0.7539 | 0.9856 | 23.17 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208337 | EARL 1 | 69 | 229 | 0.7539 | 0.9856 | 23.17 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208337 | EARL 1 | 69 | 229 | 0.8549 | 0.9856 | 13.07 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208323 | DONG TP | 69 | 229 | 0.751 | 0.9892 | 23.82 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208323 | DONG TP | 69 | 229 | 0.7597 | 0.9892 | 22.95 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208323 | DONG TP | 69 | 229 | 0.7601 | 0.9892 | 22.91 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208323 | DONG TP | 69 | 229 | 0.7601 | 0.9892 | 22.91 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208323 | DONG TP | 69 | 229 | 0.8567 | 0.9892 | 13.25 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208322 | SMAN TP2 | 69 | 229 | 0.805 | 0.9798 | 17.48 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208322 | SMAN TP2 | 69 | 229 | 0.8149 | 0.9798 | 16.49 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208322 | SMAN TP2 | 69 | 229 | 0.8152 | 0.9798 | 16.46 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208322 | SMAN TP2 | 69 | 229 | 0.8152 | 0.9798 | 16.46 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208322 | SMAN TP2 | 69 | 229 | 0.8939 | 0.9798 | 8.59 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208320 | DONG 2 | 69 | 229 | 0.7331 | 0.9766 | 24.35 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208320 | DONG 2 | 69 | 229 | 0.7417 | 0.9766 | 23.49 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208320 | DONG 2 | 69 | 229 | 0.7421 | 0.9766 | 23.45 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208320 | DONG 2 | 69 | 229 | 0.7421 | 0.9766 | 23.45 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208320 | DONG 2 | 69 | 229 | 0.8412 | 0.9766 | 13.54 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208319 | DONG 1 | 69 | 229 | 0.7337 | 0.9765 | 24.28 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208319 | DONG 1 | 69 | 229 | 0.7423 | 0.9765 | 23.42 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208319 | DONG 1 | 69 | 229 | 0.7427 | 0.9765 | 23.38 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208319 | DONG 1 | 69 | 229 | 0.7427 | 0.9765 | 23.38 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208319 | DONG 1 | 69 | 229 | 0.8413 | 0.9765 | 13.52 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208280 | COCA 2 | 69 | 229 | 0.7879 | 0.9816 | 19.37 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208280 | COCA 2 | 69 | 229 | 0.7958 | 0.9816 | 18.58 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208280 | COCA 2 | 69 | 229 | 0.7962 | 0.9816 | 18.54 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208280 | COCA 2 | 69 | 229 | 0.7962 | 0.9816 | 18.54 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208280 | COCA 2 | 69 | 229 | 0.8799 | 0.9816 | 10.17 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208279 | COCA 1 | 69 | 229 | 0.7889 | 0.9825 | 19.36 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208279 | COCA 1 | 69 | 229 | 0.7968 | 0.9825 | 18.57 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208279 | COCA 1 | 69 | 229 | 0.7972 | 0.9825 | 18.53 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208279 | COCA 1 | 69 | 229 | 0.7972 | 0.9825 | 18.53 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208279 | COCA 1 | 69 | 229 | 0.8809 | 0.9825 | 10.16 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208278 | COCA NO | 69 | 229 | 0.7457 | 0.9778 | 23.21 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208278 | COCA NO | 69 | 229 | 0.7545 | 0.9778 | 22.33 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208278 | COCA NO | 69 | 229 | 0.7549 | 0.9778 | 22.29 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208278 | COCA NO | 69 | 229 | 0.7549 | 0.9778 | 22.29 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208278 | COCA NO | 69 | 229 | 0.852 | 0.9778 | 12.58 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208273 | CHWA TP | 69 | 229 | 0.8585 | 0.9643 | 10.58 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208273 | CHWA TP | 69 | 229 | 0.8658 | 0.9643 | 9.85 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208273 | CHWA TP | 69 | 229 | 0.866 | 0.9643 | 9.83 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208273 | CHWA TP | 69 | 229 | 0.866 | 0.9643 | 9.83 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208272 | CHWA | 69 | 229 | 0.8585 | 0.9643 | 10.58 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208272 | CHWA | 69 | 229 | 0.8657 | 0.9643 | 9.86 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208272 | CHWA | 69 | 229 | 0.8659 | 0.9643 | 9.84 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208272 | CHWA | 69 | 229 | 0.866 | 0.9643 | 9.83 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208261 | BUIR TP2 | 69 | 229 | 0.8539 | 0.9636 | 10.97 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208261 | BUIR TP2 | 69 | 229 | 0.8614 | 0.9636 | 10.22 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208261 | BUIR TP2 | 69 | 229 | 0.8616 | 0.9636 | 10.2 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208261 | BUIR TP2 | 69 | 229 | 0.8616 | 0.9636 | 10.2 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208259 | BUIR TP | 69 | 229 | 0.8576 | 0.9632 | 10.56 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208259 | BUIR TP | 69 | 229 | 0.8649 | 0.9632 | 9.83 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208259 | BUIR TP | 69 | 229 | 0.8652 | 0.9632 | 9.8 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208259 | BUIR TP | 69 | 229 | 0.8652 | 0.9632 | 9.8 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208258 | BUIR | 69 | 229 | 0.8554 | 0.9613 | 10.59 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208258 | BUIR | 69 | 229 | 0.8628 | 0.9613 | 9.85 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208258 | BUIR | 69 | 229 | 0.8631 | 0.9613 | 9.82 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208258 | BUIR | 69 | 229 | 0.8631 | 0.9613 | 9.82 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208251 | BUCK | 69 | 229 | 0.8576 | 0.9632 | 10.56 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208251 | BUCK | 69 | 229 | 0.865 | 0.9632 | 9.82 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208251 | BUCK | 69 | 229 | 0.8653 | 0.9632 | 9.79 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208251 | BUCK | 69 | 229 | 0.8653 | 0.9632 | 9.79 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208250 | BUCK 2 | 69 | 229 | 0.8524 | 0.9629 | 11.05 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208250 | BUCK 2 | 69 | 229 | 0.8599 | 0.9629 | 10.3 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208250 | BUCK 2 | 69 | 229 | 0.8602 | 0.9629 | 10.27 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208250 | BUCK 2 | 69 | 229 | 0.8602 | 0.9629 | 10.27 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208249 | BUCK 1 | 69 | 229 | 0.8576 | 0.9632 | 10.56 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208249 | BUCK 1 | 69 | 229 | 0.865 | 0.9632 | 9.82 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208249 | BUCK 1 | 69 | 229 | 0.8653 | 0.9632 | 9.79 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208249 | BUCK 1 | 69 | 229 | 0.8653 | 0.9632 | 9.79 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208246 | BREC NO | 69 | 229 | 0.7963 | 0.9876 | 19.13 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208246 | BREC NO | 69 | 229 | 0.804 | 0.9876 | 18.36 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208246 | BREC NO | 69 | 229 | 0.8044 | 0.9876 | 18.32 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208246 | BREC NO | 69 | 229 | 0.8044 | 0.9876 | 18.32 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208246 | BREC NO | 69 | 229 | 0.887 | 0.9876 | 10.06 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208244 | BREC | 69 | 229 | 0.7435 | 0.9751 | 23.16 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208244 | BREC | 69 | 229 | 0.7524 | 0.9751 | 22.27 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208244 | BREC | 69 | 229 | 0.7528 | 0.9751 | 22.23 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208244 | BREC | 69 | 229 | 0.7528 | 0.9751 | 22.23 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208244 | BREC | 69 | 229 | 0.849 | 0.9751 | 12.61 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208240 | BERK CC | 69 | 229 | 0.8015 | 0.9838 | 18.23 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208240 | BERK CC | 69 | 229 | 0.8092 | 0.9838 | 17.46 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208240 | BERK CC | 69 | 229 | 0.8096 | 0.9838 | 17.42 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208240 | BERK CC | 69 | 229 | 0.8096 | 0.9838 | 17.42 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208240 | BERK CC | 69 | 229 | 0.8908 | 0.9838 | 9.3 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208239 | SHIL TP2 | 69 | 229 | 0.8028 | 0.9849 | 18.21 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208239 | SHIL TP2 | 69 | 229 | 0.8104 | 0.9849 | 17.45 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208239 | SHIL TP2 | 69 | 229 | 0.8108 | 0.9849 | 17.41 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208239 | SHIL TP2 | 69 | 229 | 0.8109 | 0.9849 | 17.4 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208239 | SHIL TP2 | 69 | 229 | 0.8919 | 0.9849 | 9.3 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208237 | BERK 5 | 69 | 229 | 0.8028 | 0.9847 | 18.19 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208237 | BERK 5 | 69 | 229 | 0.8104 | 0.9847 | 17.43 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208237 | BERK 5 | 69 | 229 | 0.8108 | 0.9847 | 17.39 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208237 | BERK 5 | 69 | 229 | 0.8108 | 0.9847 | 17.39 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208237 | BERK 5 | 69 | 229 | 0.8918 | 0.9847 | 9.29 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208236 | BERK | 69 | 229 | 0.8028 | 0.9848 | 18.2 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208236 | BERK | 69 | 229 | 0.8105 | 0.9848 | 17.43 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208236 | BERK | 69 | 229 | 0.8109 | 0.9848 | 17.39 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208236 | BERK | 69 | 229 | 0.8109 | 0.9848 | 17.39 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208236 | BERK | 69 | 229 | 0.8919 | 0.9848 | 9.29 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208230 | BEMA TP2 | 69 | 229 | 0.8003 | 0.9835 | 18.32 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208230 | BEMA TP2 | 69 | 229 | 0.808 | 0.9835 | 17.55 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208230 | BEMA TP2 | 69 | 229 | 0.8084 | 0.9835 | 17.51 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208230 | BEMA TP2 | 69 | 229 | 0.8084 | 0.9835 | 17.51 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208230 | BEMA TP2 | 69 | 229 | 0.89 | 0.9835 | 9.35 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208229 | BEMA TP1 | 69 | 229 | 0.7996 | 0.9828 | 18.32 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208229 | BEMA TP1 | 69 | 229 | 0.8073 | 0.9828 | 17.55 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208229 | BEMA TP1 | 69 | 229 | 0.8077 | 0.9828 | 17.51 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208229 | BEMA TP1 | 69 | 229 | 0.8077 | 0.9828 | 17.51 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208229 | BEMA TP1 | 69 | 229 | 0.8893 | 0.9828 | 9.35 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208225 | BEMA 2 | 69 | 229 | 0.8003 | 0.9834 | 18.31 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208225 | BEMA 2 | 69 | 229 | 0.808 | 0.9834 | 17.54 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208225 | BEMA 2 | 69 | 229 | 0.8084 | 0.9834 | 17.5 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208225 | BEMA 2 | 69 | 229 | 0.8084 | 0.9834 | 17.5 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208225 | BEMA 2 | 69 | 229 | 0.89 | 0.9834 | 9.34 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208224 | BEMA 1 | 69 | 229 | 0.7996 | 0.9828 | 18.32 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208224 | BEMA 1 | 69 | 229 | 0.8073 | 0.9828 | 17.55 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208224 | BEMA 1 | 69 | 229 | 0.8077 | 0.9828 | 17.51 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208224 | BEMA 1 | 69 | 229 | 0.8077 | 0.9828 | 17.51 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208224 | BEMA 1 | 69 | 229 | 0.8893 | 0.9828 | 9.35 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208218 | ATGL TP | 69 | 229 | 0.8525 | 0.9607 | 10.82 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208218 | ATGL TP | 69 | 229 | 0.8601 | 0.9607 | 10.06 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208218 | ATGL TP | 69 | 229 | 0.8603 | 0.9607 | 10.04 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208218 | ATGL TP | 69 | 229 | 0.8604 | 0.9607 | 10.03 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208216 | ATGL 14 | 69 | 229 | 0.8277 | 0.9445 | 11.68 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208216 | ATGL 14 | 69 | 229 | 0.8358 | 0.9445 | 10.87 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208216 | ATGL 14 | 69 | 229 | 0.8361 | 0.9445 | 10.84 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208216 | ATGL 14 | 69 | 229 | 0.8361 | 0.9445 | 10.84 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208215 | ATGL 13 | 69 | 229 | 0.8525 | 0.9607 | 10.82 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208215 | ATGL 13 | 69 | 229 | 0.8601 | 0.9607 | 10.06 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208215 | ATGL 13 | 69 | 229 | 0.8604 | 0.9607 | 10.03 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208215 | ATGL 13 | 69 | 229 | 0.8604 | 0.9607 | 10.03 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208212 | DONG TP2 | 69 | 229 | 0.8124 | 0.9857 | 17.33 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208212 | DONG TP2 | 69 | 229 | 0.8221 | 0.9857 | 16.36 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208212 | DONG TP2 | 69 | 229 | 0.8224 | 0.9857 | 16.33 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208212 | DONG TP2 | 69 | 229 | 0.8225 | 0.9857 | 16.32 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208212 | DONG TP2 | 69 | 229 | 0.9005 | 0.9857 | 8.52 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208211 | DONG TP1 | 69 | 229 | 0.8085 | 0.9831 | 17.46 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208211 | DONG TP1 | 69 | 229 | 0.8184 | 0.9831 | 16.47 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208211 | DONG TP1 | 69 | 229 | 0.8187 | 0.9831 | 16.44 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208211 | DONG TP1 | 69 | 229 | 0.8187 | 0.9831 | 16.44 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208211 | DONG TP1 | 69 | 229 | 0.8973 | 0.9831 | 8.58 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208209 | ARMA TP | 69 | 229 | 0.8116 | 0.9851 | 17.35 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208209 | ARMA TP | 69 | 229 | 0.8214 | 0.9851 | 16.37 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208209 | ARMA TP | 69 | 229 | 0.8217 | 0.9851 | 16.34 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208209 | ARMA TP | 69 | 229 | 0.8217 | 0.9851 | 16.34 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208209 | ARMA TP | 69 | 229 | 0.8998 | 0.9851 | 8.53 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208208 | ARMA 2 | 69 | 229 | 0.809 | 0.9831 | 17.41 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208208 | ARMA 2 | 69 | 229 | 0.8188 | 0.9831 | 16.43 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208208 | ARMA 2 | 69 | 229 | 0.8192 | 0.9831 | 16.39 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208208 | ARMA 2 | 69 | 229 | 0.8192 | 0.9831 | 16.39 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208208 | ARMA 2 | 69 | 229 | 0.8975 | 0.9831 | 8.56 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208207 | ARMA 1 | 69 | 229 | 0.8038 | 0.9795 | 17.57 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208207 | ARMA 1 | 69 | 229 | 0.8138 | 0.9795 | 16.57 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208207 | ARMA 1 | 69 | 229 | 0.8141 | 0.9795 | 16.54 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208207 | ARMA 1 | 69 | 229 | 0.8141 | 0.9795 | 16.54 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208207 | ARMA 1 | 69 | 229 | 0.8932 | 0.9795 | 8.63 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208206 | ARMA TP2 | 69 | 229 | 0.8067 | 0.9817 | 17.5 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208206 | ARMA TP2 | 69 | 229 | 0.8166 | 0.9817 | 16.51 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208206 | ARMA TP2 | 69 | 229 | 0.8169 | 0.9817 | 16.48 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208206 | ARMA TP2 | 69 | 229 | 0.817 | 0.9817 | 16.47 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208206 | ARMA TP2 | 69 | 229 | 0.8958 | 0.9817 | 8.59 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208108 | STEE 2 | 69 | 229 | 0.854 | 1.0819 | 22.79 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208108 | STEE 2 | 69 | 229 | 0.8619 | 1.0819 | 22 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208108 | STEE 2 | 69 | 229 | 0.8623 | 1.0819 | 21.96 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208108 | STEE 2 | 69 | 229 | 0.8623 | 1.0819 | 21.96 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208108 | STEE 2 | 69 | 229 | 0.9562 | 1.0819 | 12.57 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208107 | STEE | 69 | 229 | 0.8137 | 1.0319 | 21.82 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208107 | STEE | 69 | 229 | 0.8212 | 1.0319 | 21.07 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208107 | STEE | 69 | 229 | 0.8216 | 1.0319 | 21.03 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208107 | STEE | 69 | 229 | 0.8216 | 1.0319 | 21.03 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 208107 | STEE | 69 | 229 | 0.9115 | 1.0319 | 12.04 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 205953 | AE1-196_MAIN | 69 | 227 | 0.7786 | 1.0052 | 22.66 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 205953 | AE1-196_MAIN | 69 | 227 | 0.7858 | 1.0052 | 21.94 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 205953 | AE1-196_MAIN | 69 | 227 | 0.7861 | 1.0052 | 21.91 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 205953 | AE1-196_MAIN | 69 | 227 | 0.7861 | 1.0052 | 21.91 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 205953 | AE1-196_MAIN | 69 | 227 | 0.8799 | 1.0052 | 12.53 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 205952 | AE1-196_POI | 69 | 227 | 0.7782 | 1.0051 | 22.69 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 205952 | AE1-196_POI | 69 | 227 | 0.7854 | 1.0051 | 21.97 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 205952 | AE1-196_POI | 69 | 227 | 0.7858 | 1.0051 | 21.93 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 205952 | AE1-196_POI | 69 | 227 | 0.7858 | 1.0051 | 21.93 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 205952 | AE1-196_POI | 69 | 227 | 0.8796 | 1.0051 | 12.55 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 205943 | AE1-185 GEN | 69 | 227 | 0.7829 | 1.0098 | 22.69 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 205943 | AE1-185 GEN | 69 | 227 | 0.79 | 1.0098 | 21.98 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 205943 | AE1-185 GEN | 69 | 227 | 0.7903 | 1.0098 | 21.95 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 205943 | AE1-185 GEN | 69 | 227 | 0.7903 | 1.0098 | 21.95 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 205943 | AE1-185 GEN | 69 | 227 | 0.8831 | 1.0098 | 12.67 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 205942 | AE1-185 TAP | 69 | 227 | 0.7828 | 1.0096 | 22.68 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 205942 | AE1-185 TAP | 69 | 227 | 0.7898 | 1.0096 | 21.98 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 205942 | AE1-185 TAP | 69 | 227 | 0.7902 | 1.0096 | 21.94 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 205942 | AE1-185 TAP | 69 | 227 | 0.7902 | 1.0096 | 21.94 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 205942 | AE1-185 TAP | 69 | 227 | 0.883 | 1.0096 | 12.66 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 205938 | AD2-115 MAIN | 69 | 227 | 0.8738 | 1.0019 | 12.81 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 205938 | AD2-115 MAIN | 69 | 227 | 0.8796 | 1.0019 | 12.23 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 205938 | AD2-115 MAIN | 69 | 227 | 0.88 | 1.0019 | 12.19 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 205938 | AD2-115 MAIN | 69 | 227 | 0.88 | 1.0019 | 12.19 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 205937 | AD2-115 TAP | 69 | 227 | 0.8735 | 1.0019 | 12.84 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 205937 | AD2-115 TAP | 69 | 227 | 0.8794 | 1.0019 | 12.25 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 205937 | AD2-115 TAP | 69 | 227 | 0.8797 | 1.0019 | 12.22 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 205937 | AD2-115 TAP | 69 | 227 | 0.8797 | 1.0019 | 12.22 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 205936 | AD2-116_POI | 69 | 227 | 0.7758 | 1.0037 | 22.79 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 205936 | AD2-116_POI | 69 | 227 | 0.783 | 1.0037 | 22.07 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 205936 | AD2-116_POI | 69 | 227 | 0.7834 | 1.0037 | 22.03 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 205936 | AD2-116_POI | 69 | 227 | 0.7834 | 1.0037 | 22.03 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 205936 | AD2-116_POI | 69 | 227 | 0.8775 | 1.0037 | 12.62 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 205935 | AD2-116_MAIN | 69 | 227 | 0.7761 | 1.0037 | 22.76 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 205935 | AD2-116_MAIN | 69 | 227 | 0.7833 | 1.0037 | 22.04 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 205935 | AD2-116_MAIN | 69 | 227 | 0.7836 | 1.0037 | 22.01 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 205935 | AD2-116_MAIN | 69 | 227 | 0.7836 | 1.0037 | 22.01 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 205935 | AD2-116_MAIN | 69 | 227 | 0.8777 | 1.0037 | 12.6 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 205928 | AF2-431 E | 69 | 227 | 0.8641 | 0.9942 | 13.01 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 205928 | AF2-431 E | 69 | 227 | 0.87 | 0.9942 | 12.42 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 205928 | AF2-431 E | 69 | 227 | 0.8704 | 0.9942 | 12.38 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 205928 | AF2-431 E | 69 | 227 | 0.8704 | 0.9942 | 12.38 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 205927 | AF2-430 E | 69 | 227 | 0.8616 | 0.9957 | 13.41 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 205927 | AF2-430 E | 69 | 227 | 0.8677 | 0.9957 | 12.8 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 205927 | AF2-430 E | 69 | 227 | 0.8681 | 0.9957 | 12.76 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 205927 | AF2-430 E | 69 | 227 | 0.8681 | 0.9957 | 12.76 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 205925 | AF2-428 E | 69 | 227 | 0.8583 | 0.9979 | 13.96 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 205925 | AF2-428 E | 69 | 227 | 0.8646 | 0.9979 | 13.33 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 205925 | AF2-428 E | 69 | 227 | 0.865 | 0.9979 | 13.29 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 205925 | AF2-428 E | 69 | 227 | 0.865 | 0.9979 | 13.29 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 205924 | AF2-281 E | 69 | 227 | 0.8362 | 0.9748 | 13.86 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 205924 | AF2-281 E | 69 | 227 | 0.8427 | 0.9748 | 13.21 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 205924 | AF2-281 E | 69 | 227 | 0.8431 | 0.9748 | 13.17 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 205924 | AF2-281 E | 69 | 227 | 0.8431 | 0.9748 | 13.17 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 205923 | AF2-272 E | 69 | 227 | 0.8553 | 1.0036 | 14.83 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 205923 | AF2-272 E | 69 | 227 | 0.8619 | 1.0036 | 14.17 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 205923 | AF2-272 E | 69 | 227 | 0.8623 | 1.0036 | 14.13 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 205923 | AF2-272 E | 69 | 227 | 0.8623 | 1.0036 | 14.13 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204876 | 27NORTHKLL | 69 | 227 | 0.8571 | 1.0059 | 14.88 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204876 | 27NORTHKLL | 69 | 227 | 0.8636 | 1.0059 | 14.23 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204876 | 27NORTHKLL | 69 | 227 | 0.864 | 1.0059 | 14.19 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204876 | 27NORTHKLL | 69 | 227 | 0.864 | 1.0059 | 14.19 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204874 | 27DUKE | 69 | 227 | 0.8493 | 0.9829 | 13.36 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204874 | 27DUKE | 69 | 227 | 0.8554 | 0.9829 | 12.75 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204874 | 27DUKE | 69 | 227 | 0.8558 | 0.9829 | 12.71 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204874 | 27DUKE | 69 | 227 | 0.8558 | 0.9829 | 12.71 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204873 | 27PEACHST | 69 | 227 | 0.8441 | 0.9888 | 14.47 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204873 | 27PEACHST | 69 | 227 | 0.8507 | 0.9888 | 13.81 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204873 | 27PEACHST | 69 | 227 | 0.8511 | 0.9888 | 13.77 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204873 | 27PEACHST | 69 | 227 | 0.8511 | 0.9888 | 13.77 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204872 | 27SHOEMKRSVL | 69 | 227 | 0.8438 | 0.9875 | 14.37 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204872 | 27SHOEMKRSVL | 69 | 227 | 0.8506 | 0.9875 | 13.69 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204872 | 27SHOEMKRSVL | 69 | 227 | 0.851 | 0.9875 | 13.65 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204872 | 27SHOEMKRSVL | 69 | 227 | 0.851 | 0.9875 | 13.65 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204871 | 27WESTSHORE | 69 | 227 | 0.8373 | 0.9907 | 15.34 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204871 | 27WESTSHORE | 69 | 227 | 0.8441 | 0.9907 | 14.66 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204871 | 27WESTSHORE | 69 | 227 | 0.8445 | 0.9907 | 14.62 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204871 | 27WESTSHORE | 69 | 227 | 0.8445 | 0.9907 | 14.62 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204870 | 27VANREED | 69 | 227 | 0.8456 | 0.9927 | 14.71 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204870 | 27VANREED | 69 | 227 | 0.8522 | 0.9927 | 14.05 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204870 | 27VANREED | 69 | 227 | 0.8526 | 0.9927 | 14.01 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204870 | 27VANREED | 69 | 227 | 0.8526 | 0.9927 | 14.01 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204869 | 27KUTZUNIV | 69 | 227 | 0.8644 | 0.9944 | 13 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204869 | 27KUTZUNIV | 69 | 227 | 0.8702 | 0.9944 | 12.42 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204869 | 27KUTZUNIV | 69 | 227 | 0.8706 | 0.9944 | 12.38 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204869 | 27KUTZUNIV | 69 | 227 | 0.8706 | 0.9944 | 12.38 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204868 | 27CAMBLEE | 69 | 227 | 0.8482 | 0.9934 | 14.52 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204868 | 27CAMBLEE | 69 | 227 | 0.8546 | 0.9934 | 13.88 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204868 | 27CAMBLEE | 69 | 227 | 0.855 | 0.9934 | 13.84 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204868 | 27CAMBLEE | 69 | 227 | 0.855 | 0.9934 | 13.84 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204867 | 27HUFFCHURCH | 69 | 227 | 0.8611 | 0.9942 | 13.31 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204867 | 27HUFFCHURCH | 69 | 227 | 0.8672 | 0.9942 | 12.7 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204867 | 27HUFFCHURCH | 69 | 227 | 0.8675 | 0.9942 | 12.67 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204867 | 27HUFFCHURCH | 69 | 227 | 0.8675 | 0.9942 | 12.67 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204865 | 27WR_V4-052 | 69 | 227 | 0.8417 | 0.9992 | 15.75 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204865 | 27WR_V4-052 | 69 | 227 | 0.8487 | 0.9992 | 15.05 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204865 | 27WR_V4-052 | 69 | 227 | 0.8491 | 0.9992 | 15.01 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204865 | 27WR_V4-052 | 69 | 227 | 0.8491 | 0.9992 | 15.01 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204863 | 27STATE ST | 69 | 227 | 0.8475 | 0.9897 | 14.22 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204863 | 27STATE ST | 69 | 227 | 0.8543 | 0.9897 | 13.54 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204863 | 27STATE ST | 69 | 227 | 0.8547 | 0.9897 | 13.5 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204863 | 27STATE ST | 69 | 227 | 0.8548 | 0.9897 | 13.49 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204862 | 27W.RDG | 69 | 227 | 0.8417 | 0.9992 | 15.75 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204862 | 27W.RDG | 69 | 227 | 0.8487 | 0.9992 | 15.05 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204862 | 27W.RDG | 69 | 227 | 0.8491 | 0.9992 | 15.01 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204862 | 27W.RDG | 69 | 227 | 0.8491 | 0.9992 | 15.01 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204861 | 27W.BOYTWN | 69 | 227 | 0.8583 | 0.9979 | 13.96 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204861 | 27W.BOYTWN | 69 | 227 | 0.8646 | 0.9979 | 13.33 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204861 | 27W.BOYTWN | 69 | 227 | 0.865 | 0.9979 | 13.29 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204861 | 27W.BOYTWN | 69 | 227 | 0.865 | 0.9979 | 13.29 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204859 | 27U.CORSTK | 69 | 227 | 0.8445 | 1.0025 | 15.8 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204859 | 27U.CORSTK | 69 | 227 | 0.8515 | 1.0025 | 15.1 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204859 | 27U.CORSTK | 69 | 227 | 0.8519 | 1.0025 | 15.06 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204859 | 27U.CORSTK | 69 | 227 | 0.8519 | 1.0025 | 15.06 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204858 | 27ST PETRS | 69 | 227 | 0.8575 | 0.9941 | 13.66 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204858 | 27ST PETRS | 69 | 227 | 0.8638 | 0.9941 | 13.03 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204858 | 27ST PETRS | 69 | 227 | 0.8642 | 0.9941 | 12.99 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204858 | 27ST PETRS | 69 | 227 | 0.8642 | 0.9941 | 12.99 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204857 | 27SPG VAL | 69 | 227 | 0.8352 | 0.9878 | 15.26 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204857 | 27SPG VAL | 69 | 227 | 0.842 | 0.9878 | 14.58 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204857 | 27SPG VAL | 69 | 227 | 0.8424 | 0.9878 | 14.54 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204857 | 27SPG VAL | 69 | 227 | 0.8424 | 0.9878 | 14.54 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204856 | 27ROYAL TP | 69 | 227 | 0.8497 | 0.9942 | 14.45 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204856 | 27ROYAL TP | 69 | 227 | 0.8561 | 0.9942 | 13.81 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204856 | 27ROYAL TP | 69 | 227 | 0.8565 | 0.9942 | 13.77 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204856 | 27ROYAL TP | 69 | 227 | 0.8565 | 0.9942 | 13.77 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204855 | 27ROYAL GR | 69 | 227 | 0.8496 | 0.9942 | 14.46 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204855 | 27ROYAL GR | 69 | 227 | 0.8561 | 0.9942 | 13.81 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204855 | 27ROYAL GR | 69 | 227 | 0.8565 | 0.9942 | 13.77 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204855 | 27ROYAL GR | 69 | 227 | 0.8565 | 0.9942 | 13.77 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204853 | 27ROSEDALE | 69 | 227 | 0.8411 | 0.99 | 14.89 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204853 | 27ROSEDALE | 69 | 227 | 0.8477 | 0.99 | 14.23 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204853 | 27ROSEDALE | 69 | 227 | 0.8481 | 0.99 | 14.19 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204853 | 27ROSEDALE | 69 | 227 | 0.8481 | 0.99 | 14.19 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204852 | 27RNGROCKS | 69 | 227 | 0.8575 | 0.9958 | 13.83 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204852 | 27RNGROCKS | 69 | 227 | 0.8638 | 0.9958 | 13.2 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204852 | 27RNGROCKS | 69 | 227 | 0.8641 | 0.9958 | 13.17 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204852 | 27RNGROCKS | 69 | 227 | 0.8642 | 0.9958 | 13.16 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204851 | 27RIVRVIEW | 69 | 227 | 0.8445 | 0.992 | 14.75 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204851 | 27RIVRVIEW | 69 | 227 | 0.8511 | 0.992 | 14.09 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204851 | 27RIVRVIEW | 69 | 227 | 0.8514 | 0.992 | 14.06 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204851 | 27RIVRVIEW | 69 | 227 | 0.8515 | 0.992 | 14.05 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204850 | 27LYONSTAP | 69 | 227 | 0.8767 | 1.0041 | 12.74 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204850 | 27LYONSTAP | 69 | 227 | 0.8824 | 1.0041 | 12.17 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204850 | 27LYONSTAP | 69 | 227 | 0.8827 | 1.0041 | 12.14 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204850 | 27LYONSTAP | 69 | 227 | 0.8827 | 1.0041 | 12.14 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204849 | 27PINE LNE | 69 | 227 | 0.8395 | 0.9912 | 15.17 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204849 | 27PINE LNE | 69 | 227 | 0.8462 | 0.9912 | 14.5 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204849 | 27PINE LNE | 69 | 227 | 0.8466 | 0.9912 | 14.46 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204849 | 27PINE LNE | 69 | 227 | 0.8466 | 0.9912 | 14.46 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204848 | 27OUTR STA | 69 | 227 | 0.8355 | 0.9879 | 15.24 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204848 | 27OUTR STA | 69 | 227 | 0.8423 | 0.9879 | 14.56 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204848 | 27OUTR STA | 69 | 227 | 0.8427 | 0.9879 | 14.52 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204848 | 27OUTR STA | 69 | 227 | 0.8427 | 0.9879 | 14.52 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204847 | 27MUHLENBG | 69 | 227 | 0.8359 | 0.9876 | 15.17 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204847 | 27MUHLENBG | 69 | 227 | 0.8426 | 0.9876 | 14.5 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204847 | 27MUHLENBG | 69 | 227 | 0.843 | 0.9876 | 14.46 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204847 | 27MUHLENBG | 69 | 227 | 0.843 | 0.9876 | 14.46 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204846 | 27MOSELEM | 69 | 227 | 0.8616 | 0.9957 | 13.41 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204846 | 27MOSELEM | 69 | 227 | 0.8677 | 0.9957 | 12.8 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204846 | 27MOSELEM | 69 | 227 | 0.8681 | 0.9957 | 12.76 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204846 | 27MOSELEM | 69 | 227 | 0.8681 | 0.9957 | 12.76 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204845 | 27MG IND T | 69 | 227 | 0.8352 | 0.9877 | 15.25 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204845 | 27MG IND T | 69 | 227 | 0.842 | 0.9877 | 14.57 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204845 | 27MG IND T | 69 | 227 | 0.8424 | 0.9877 | 14.53 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204845 | 27MG IND T | 69 | 227 | 0.8424 | 0.9877 | 14.53 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204844 | 27MG IND | 69 | 227 | 0.8351 | 0.9876 | 15.25 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204844 | 27MG IND | 69 | 227 | 0.8419 | 0.9876 | 14.57 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204844 | 27MG IND | 69 | 227 | 0.8423 | 0.9876 | 14.53 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204844 | 27MG IND | 69 | 227 | 0.8423 | 0.9876 | 14.53 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204843 | 27MC-KN GP | 69 | 227 | 0.8371 | 0.9917 | 15.46 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204843 | 27MC-KN GP | 69 | 227 | 0.844 | 0.9917 | 14.77 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204843 | 27MC-KN GP | 69 | 227 | 0.8444 | 0.9917 | 14.73 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204843 | 27MC-KN GP | 69 | 227 | 0.8444 | 0.9917 | 14.73 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204842 | 27LYNNVILE | 69 | 227 | 0.8362 | 0.9748 | 13.86 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204842 | 27LYNNVILE | 69 | 227 | 0.8427 | 0.9748 | 13.21 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204842 | 27LYNNVILE | 69 | 227 | 0.8431 | 0.9748 | 13.17 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204842 | 27LYNNVILE | 69 | 227 | 0.8431 | 0.9748 | 13.17 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204841 | 27LORANE | 69 | 227 | 0.8403 | 0.9977 | 15.74 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204841 | 27LORANE | 69 | 227 | 0.8473 | 0.9977 | 15.04 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204841 | 27LORANE | 69 | 227 | 0.8477 | 0.9977 | 15 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204841 | 27LORANE | 69 | 227 | 0.8477 | 0.9977 | 15 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204839 | 27LINC 822 | 69 | 227 | 0.8379 | 0.9961 | 15.82 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204839 | 27LINC 822 | 69 | 227 | 0.8449 | 0.9961 | 15.12 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204839 | 27LINC 822 | 69 | 227 | 0.8453 | 0.9961 | 15.08 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204839 | 27LINC 822 | 69 | 227 | 0.8453 | 0.9961 | 15.08 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204838 | 27LINC 821 | 69 | 227 | 0.8371 | 0.9957 | 15.86 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204838 | 27LINC 821 | 69 | 227 | 0.8441 | 0.9957 | 15.16 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204838 | 27LINC 821 | 69 | 227 | 0.8445 | 0.9957 | 15.12 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204838 | 27LINC 821 | 69 | 227 | 0.8445 | 0.9957 | 15.12 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204836 | 27LEESPORT | 69 | 227 | 0.8433 | 0.9878 | 14.45 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204836 | 27LEESPORT | 69 | 227 | 0.8499 | 0.9878 | 13.79 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204836 | 27LEESPORT | 69 | 227 | 0.8503 | 0.9878 | 13.75 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204836 | 27LEESPORT | 69 | 227 | 0.8503 | 0.9878 | 13.75 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204835 | 27KUTZTOWN | 69 | 227 | 0.8623 | 0.9928 | 13.05 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204835 | 27KUTZTOWN | 69 | 227 | 0.8682 | 0.9928 | 12.46 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204835 | 27KUTZTOWN | 69 | 227 | 0.8685 | 0.9928 | 12.43 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204835 | 27KUTZTOWN | 69 | 227 | 0.8685 | 0.9928 | 12.43 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204834 | 27CABOTIND | 69 | 227 | 0.8645 | 1.0006 | 13.61 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204834 | 27CABOTIND | 69 | 227 | 0.8707 | 1.0006 | 12.99 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204834 | 27CABOTIND | 69 | 227 | 0.8711 | 1.0006 | 12.95 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204834 | 27CABOTIND | 69 | 227 | 0.8711 | 1.0006 | 12.95 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204833 | 27GLENSIDE | 69 | 227 | 0.8392 | 0.9939 | 15.47 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204833 | 27GLENSIDE | 69 | 227 | 0.846 | 0.9939 | 14.79 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204833 | 27GLENSIDE | 69 | 227 | 0.8464 | 0.9939 | 14.75 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204833 | 27GLENSIDE | 69 | 227 | 0.8464 | 0.9939 | 14.75 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204832 | 27FRIEDNBG | 69 | 227 | 0.8492 | 0.9938 | 14.46 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204832 | 27FRIEDNBG | 69 | 227 | 0.8556 | 0.9938 | 13.82 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204832 | 27FRIEDNBG | 69 | 227 | 0.856 | 0.9938 | 13.78 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204832 | 27FRIEDNBG | 69 | 227 | 0.856 | 0.9938 | 13.78 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204831 | 27FLYING H | 69 | 227 | 0.8428 | 1.0018 | 15.9 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204831 | 27FLYING H | 69 | 227 | 0.8498 | 1.0018 | 15.2 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204831 | 27FLYING H | 69 | 227 | 0.8502 | 1.0018 | 15.16 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204831 | 27FLYING H | 69 | 227 | 0.8502 | 1.0018 | 15.16 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204830 | 27EXIDE | 69 | 227 | 0.8358 | 0.9889 | 15.31 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204830 | 27EXIDE | 69 | 227 | 0.8426 | 0.9889 | 14.63 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204830 | 27EXIDE | 69 | 227 | 0.843 | 0.9889 | 14.59 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204830 | 27EXIDE | 69 | 227 | 0.843 | 0.9889 | 14.59 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204829 | 27E.TOPTON | 69 | 227 | 0.8646 | 0.9952 | 13.06 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204829 | 27E.TOPTON | 69 | 227 | 0.8705 | 0.9952 | 12.47 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204829 | 27E.TOPTON | 69 | 227 | 0.8709 | 0.9952 | 12.43 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204829 | 27E.TOPTON | 69 | 227 | 0.8709 | 0.9952 | 12.43 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204828 | 27E PENN | 69 | 227 | 0.8754 | 1.0029 | 12.75 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204828 | 27E PENN | 69 | 227 | 0.8811 | 1.0029 | 12.18 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204828 | 27E PENN | 69 | 227 | 0.8814 | 1.0029 | 12.15 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204828 | 27E PENN | 69 | 227 | 0.8814 | 1.0029 | 12.15 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204826 | 27CONTY LN | 69 | 227 | 0.8643 | 1.0005 | 13.62 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204826 | 27CONTY LN | 69 | 227 | 0.8705 | 1.0005 | 13 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204826 | 27CONTY LN | 69 | 227 | 0.8709 | 1.0005 | 12.96 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204826 | 27CONTY LN | 69 | 227 | 0.8709 | 1.0005 | 12.96 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204825 | 27CLOUSER | 69 | 227 | 0.8581 | 0.9976 | 13.95 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204825 | 27CLOUSER | 69 | 227 | 0.8644 | 0.9976 | 13.32 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204825 | 27CLOUSER | 69 | 227 | 0.8648 | 0.9976 | 13.28 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204825 | 27CLOUSER | 69 | 227 | 0.8648 | 0.9976 | 13.28 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204824 | 27CARSONIA | 69 | 227 | 0.841 | 0.9974 | 15.64 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204824 | 27CARSONIA | 69 | 227 | 0.8479 | 0.9974 | 14.95 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204824 | 27CARSONIA | 69 | 227 | 0.8483 | 0.9974 | 14.91 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204824 | 27CARSONIA | 69 | 227 | 0.8483 | 0.9974 | 14.91 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204823 | 27CAR TECH | 69 | 227 | 0.8374 | 0.9902 | 15.28 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204823 | 27CAR TECH | 69 | 227 | 0.8442 | 0.9902 | 14.6 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204823 | 27CAR TECH | 69 | 227 | 0.8446 | 0.9902 | 14.56 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204823 | 27CAR TECH | 69 | 227 | 0.8446 | 0.9902 | 14.56 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204822 | 27BIRDFERO | 69 | 227 | 0.8388 | 0.9948 | 15.6 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204822 | 27BIRDFERO | 69 | 227 | 0.8457 | 0.9948 | 14.91 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204822 | 27BIRDFERO | 69 | 227 | 0.8461 | 0.9948 | 14.87 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204822 | 27BIRDFERO | 69 | 227 | 0.8461 | 0.9948 | 14.87 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204821 | 27BIRDBORO | 69 | 227 | 0.8381 | 0.9939 | 15.58 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204821 | 27BIRDBORO | 69 | 227 | 0.845 | 0.9939 | 14.89 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204821 | 27BIRDBORO | 69 | 227 | 0.8454 | 0.9939 | 14.85 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204821 | 27BIRDBORO | 69 | 227 | 0.8454 | 0.9939 | 14.85 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204820 | 27BERNVILL | 69 | 227 | 0.8553 | 1.0036 | 14.83 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204820 | 27BERNVILL | 69 | 227 | 0.8619 | 1.0036 | 14.17 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204820 | 27BERNVILL | 69 | 227 | 0.8623 | 1.0036 | 14.13 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204820 | 27BERNVILL | 69 | 227 | 0.8623 | 1.0036 | 14.13 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204819 | 27BERN CH | 69 | 227 | 0.8458 | 0.993 | 14.72 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204819 | 27BERN CH | 69 | 227 | 0.8523 | 0.993 | 14.07 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204819 | 27BERN CH | 69 | 227 | 0.8527 | 0.993 | 14.03 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204819 | 27BERN CH | 69 | 227 | 0.8527 | 0.993 | 14.03 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204818 | 27BERK 835 | 69 | 227 | 0.8484 | 0.9936 | 14.52 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204818 | 27BERK 835 | 69 | 227 | 0.8549 | 0.9936 | 13.87 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204818 | 27BERK 835 | 69 | 227 | 0.8553 | 0.9936 | 13.83 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204818 | 27BERK 835 | 69 | 227 | 0.8553 | 0.9936 | 13.83 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204817 | 27BERK 24 | 69 | 227 | 0.8487 | 0.9932 | 14.45 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204817 | 27BERK 24 | 69 | 227 | 0.8551 | 0.9932 | 13.81 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204817 | 27BERK 24 | 69 | 227 | 0.8555 | 0.9932 | 13.77 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204817 | 27BERK 24 | 69 | 227 | 0.8555 | 0.9932 | 13.77 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204816 | 27BARTO | 69 | 227 | 0.863 | 0.9976 | 13.46 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204816 | 27BARTO | 69 | 227 | 0.8691 | 0.9976 | 12.85 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204816 | 27BARTO | 69 | 227 | 0.8695 | 0.9976 | 12.81 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204816 | 27BARTO | 69 | 227 | 0.8695 | 0.9976 | 12.81 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204815 | 27BALDY | 69 | 227 | 0.8641 | 0.9942 | 13.01 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204815 | 27BALDY | 69 | 227 | 0.87 | 0.9942 | 12.42 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204815 | 27BALDY | 69 | 227 | 0.8704 | 0.9942 | 12.38 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204815 | 27BALDY | 69 | 227 | 0.8704 | 0.9942 | 12.38 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204814 | 27LUCENT | 69 | 227 | 0.8356 | 0.9885 | 15.29 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204814 | 27LUCENT | 69 | 227 | 0.8424 | 0.9885 | 14.61 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204814 | 27LUCENT | 69 | 227 | 0.8428 | 0.9885 | 14.57 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204814 | 27LUCENT | 69 | 227 | 0.8428 | 0.9885 | 14.57 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204813 | 27ARMORCST | 69 | 227 | 0.8381 | 0.9939 | 15.58 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204813 | 27ARMORCST | 69 | 227 | 0.845 | 0.9939 | 14.89 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204813 | 27ARMORCST | 69 | 227 | 0.8454 | 0.9939 | 14.85 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204813 | 27ARMORCST | 69 | 227 | 0.8454 | 0.9939 | 14.85 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204812 | 27ALTN CMT | 69 | 227 | 0.8547 | 0.9932 | 13.85 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204812 | 27ALTN CMT | 69 | 227 | 0.8611 | 0.9932 | 13.21 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204812 | 27ALTN CMT | 69 | 227 | 0.8614 | 0.9932 | 13.18 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204812 | 27ALTN CMT | 69 | 227 | 0.8615 | 0.9932 | 13.17 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204811 | 27ADAMSTWN | 69 | 227 | 0.836 | 0.9953 | 15.93 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204811 | 27ADAMSTWN | 69 | 227 | 0.843 | 0.9953 | 15.23 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204811 | 27ADAMSTWN | 69 | 227 | 0.8434 | 0.9953 | 15.19 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204811 | 27ADAMSTWN | 69 | 227 | 0.8434 | 0.9953 | 15.19 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204789 | 27BELLEVANS | 69 | 227 | 0.7873 | 0.9864 | 19.91 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204789 | 27BELLEVANS | 69 | 227 | 0.7945 | 0.9864 | 19.19 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204789 | 27BELLEVANS | 69 | 227 | 0.7949 | 0.9864 | 19.15 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204789 | 27BELLEVANS | 69 | 227 | 0.7949 | 0.9864 | 19.15 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204788 | 27HERSHEYB | 69 | 227 | 0.7889 | 0.9869 | 19.8 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204788 | 27HERSHEYB | 69 | 227 | 0.7961 | 0.9869 | 19.08 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204788 | 27HERSHEYB | 69 | 227 | 0.7965 | 0.9869 | 19.04 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204788 | 27HERSHEYB | 69 | 227 | 0.7965 | 0.9869 | 19.04 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204787 | 27REHRERSBRG | 69 | 227 | 0.7739 | 0.9707 | 19.68 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204787 | 27REHRERSBRG | 69 | 227 | 0.7811 | 0.9707 | 18.96 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204787 | 27REHRERSBRG | 69 | 227 | 0.7815 | 0.9707 | 18.92 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204787 | 27REHRERSBRG | 69 | 227 | 0.7815 | 0.9707 | 18.92 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204786 | 27REHRERBRG+ | 69 | 227 | 0.7788 | 0.9748 | 19.6 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204786 | 27REHRERBRG+ | 69 | 227 | 0.7861 | 0.9748 | 18.87 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204786 | 27REHRERBRG+ | 69 | 227 | 0.7865 | 0.9748 | 18.83 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204786 | 27REHRERBRG+ | 69 | 227 | 0.7865 | 0.9748 | 18.83 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204785 | 27GLRA_Q45 | 69 | 227 | 0.8121 | 1.0036 | 19.15 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204785 | 27GLRA_Q45 | 69 | 227 | 0.8196 | 1.0036 | 18.4 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204785 | 27GLRA_Q45 | 69 | 227 | 0.82 | 1.0036 | 18.36 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204785 | 27GLRA_Q45 | 69 | 227 | 0.82 | 1.0036 | 18.36 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204784 | 27LMR_E02 | 69 | 227 | 0.8121 | 1.0036 | 19.15 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204784 | 27LMR_E02 | 69 | 227 | 0.8196 | 1.0036 | 18.4 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204784 | 27LMR_E02 | 69 | 227 | 0.82 | 1.0036 | 18.36 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204784 | 27LMR_E02 | 69 | 227 | 0.82 | 1.0036 | 18.36 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204782 | 27W.LEB | 69 | 227 | 0.8004 | 0.994 | 19.36 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204782 | 27W.LEB | 69 | 227 | 0.808 | 0.994 | 18.6 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204782 | 27W.LEB | 69 | 227 | 0.8085 | 0.994 | 18.55 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204782 | 27W.LEB | 69 | 227 | 0.8085 | 0.994 | 18.55 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204781 | 27TURFCLUB | 69 | 227 | 0.8059 | 1.0094 | 20.35 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204781 | 27TURFCLUB | 69 | 227 | 0.8132 | 1.0094 | 19.62 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204781 | 27TURFCLUB | 69 | 227 | 0.8136 | 1.0094 | 19.58 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204781 | 27TURFCLUB | 69 | 227 | 0.8136 | 1.0094 | 19.58 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204781 | 27TURFCLUB | 69 | 227 | 0.9053 | 1.0094 | 10.41 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204780 | 27THRD&GRN | 69 | 227 | 0.8109 | 1.0021 | 19.12 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204780 | 27THRD&GRN | 69 | 227 | 0.8184 | 1.0021 | 18.37 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204780 | 27THRD&GRN | 69 | 227 | 0.8188 | 1.0021 | 18.33 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204780 | 27THRD&GRN | 69 | 227 | 0.8189 | 1.0021 | 18.32 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204779 | 27SWAT HIL | 69 | 227 | 0.7925 | 0.9862 | 19.37 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204779 | 27SWAT HIL | 69 | 227 | 0.7997 | 0.9862 | 18.65 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204779 | 27SWAT HIL | 69 | 227 | 0.8001 | 0.9862 | 18.61 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204779 | 27SWAT HIL | 69 | 227 | 0.8001 | 0.9862 | 18.61 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204778 | 27STOUCHBG | 69 | 227 | 0.8037 | 0.9967 | 19.3 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204778 | 27STOUCHBG | 69 | 227 | 0.8113 | 0.9967 | 18.54 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204778 | 27STOUCHBG | 69 | 227 | 0.8118 | 0.9967 | 18.49 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204778 | 27STOUCHBG | 69 | 227 | 0.8118 | 0.9967 | 18.49 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204777 | 27OLMSTED | 69 | 227 | 0.7975 | 0.9917 | 19.42 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204777 | 27OLMSTED | 69 | 227 | 0.8048 | 0.9917 | 18.69 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204777 | 27OLMSTED | 69 | 227 | 0.8052 | 0.9917 | 18.65 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204777 | 27OLMSTED | 69 | 227 | 0.8052 | 0.9917 | 18.65 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204776 | 27MYERSTWN | 69 | 227 | 0.8033 | 0.9961 | 19.28 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204776 | 27MYERSTWN | 69 | 227 | 0.8109 | 0.9961 | 18.52 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204776 | 27MYERSTWN | 69 | 227 | 0.8114 | 0.9961 | 18.47 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204776 | 27MYERSTWN | 69 | 227 | 0.8114 | 0.9961 | 18.47 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204775 | 27MILLARDS | 69 | 227 | 0.7894 | 0.9872 | 19.78 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204775 | 27MILLARDS | 69 | 227 | 0.7967 | 0.9872 | 19.05 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204775 | 27MILLARDS | 69 | 227 | 0.7971 | 0.9872 | 19.01 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204775 | 27MILLARDS | 69 | 227 | 0.7971 | 0.9872 | 19.01 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204774 | 27MILL ST | 69 | 227 | 0.7961 | 0.9916 | 19.55 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204774 | 27MILL ST | 69 | 227 | 0.8034 | 0.9916 | 18.82 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204774 | 27MILL ST | 69 | 227 | 0.8038 | 0.9916 | 18.78 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204774 | 27MILL ST | 69 | 227 | 0.8038 | 0.9916 | 18.78 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204774 | 27MILL ST | 69 | 227 | 0.8912 | 0.9916 | 10.04 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204773 | 27MIDDLETN | 69 | 227 | 0.7979 | 0.9926 | 19.47 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204773 | 27MIDDLETN | 69 | 227 | 0.8052 | 0.9926 | 18.74 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204773 | 27MIDDLETN | 69 | 227 | 0.8056 | 0.9926 | 18.7 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204773 | 27MIDDLETN | 69 | 227 | 0.8056 | 0.9926 | 18.7 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204773 | 27MIDDLETN | 69 | 227 | 0.8926 | 0.9926 | 10 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204772 | 27LICKDALE | 69 | 227 | 0.7896 | 0.9906 | 20.1 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204772 | 27LICKDALE | 69 | 227 | 0.7969 | 0.9906 | 19.37 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204772 | 27LICKDALE | 69 | 227 | 0.7973 | 0.9906 | 19.33 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204772 | 27LICKDALE | 69 | 227 | 0.7973 | 0.9906 | 19.33 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204772 | 27LICKDALE | 69 | 227 | 0.8901 | 0.9906 | 10.05 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204769 | 27INDTNGAP | 69 | 227 | 0.7951 | 0.9974 | 20.23 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204769 | 27INDTNGAP | 69 | 227 | 0.8024 | 0.9974 | 19.5 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204769 | 27INDTNGAP | 69 | 227 | 0.8028 | 0.9974 | 19.46 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204769 | 27INDTNGAP | 69 | 227 | 0.8028 | 0.9974 | 19.46 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204769 | 27INDTNGAP | 69 | 227 | 0.8953 | 0.9974 | 10.21 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204768 | 27GRANTVLE | 69 | 227 | 0.8064 | 1.0089 | 20.25 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204768 | 27GRANTVLE | 69 | 227 | 0.8138 | 1.0089 | 19.51 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204768 | 27GRANTVLE | 69 | 227 | 0.8142 | 1.0089 | 19.47 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204768 | 27GRANTVLE | 69 | 227 | 0.8142 | 1.0089 | 19.47 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204768 | 27GRANTVLE | 69 | 227 | 0.9047 | 1.0089 | 10.42 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204767 | 27FTH& GRN | 69 | 227 | 0.812 | 1.0029 | 19.09 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204767 | 27FTH& GRN | 69 | 227 | 0.8196 | 1.0029 | 18.33 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204767 | 27FTH& GRN | 69 | 227 | 0.82 | 1.0029 | 18.29 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204767 | 27FTH& GRN | 69 | 227 | 0.82 | 1.0029 | 18.29 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204766 | 27FRYSTOWN | 69 | 227 | 0.7777 | 0.9739 | 19.62 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204766 | 27FRYSTOWN | 69 | 227 | 0.7849 | 0.9739 | 18.9 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204766 | 27FRYSTOWN | 69 | 227 | 0.7853 | 0.9739 | 18.86 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204766 | 27FRYSTOWN | 69 | 227 | 0.7853 | 0.9739 | 18.86 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204765 | 27CLEONA | 69 | 227 | 0.8036 | 0.9967 | 19.31 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204765 | 27CLEONA | 69 | 227 | 0.8112 | 0.9967 | 18.55 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204765 | 27CLEONA | 69 | 227 | 0.8116 | 0.9967 | 18.51 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204765 | 27CLEONA | 69 | 227 | 0.8116 | 0.9967 | 18.51 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204764 | 27CMPBLTWN | 69 | 227 | 0.789 | 0.9875 | 19.85 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204764 | 27CMPBLTWN | 69 | 227 | 0.7962 | 0.9875 | 19.13 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204764 | 27CMPBLTWN | 69 | 227 | 0.7966 | 0.9875 | 19.09 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204764 | 27CMPBLTWN | 69 | 227 | 0.7967 | 0.9875 | 19.08 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204764 | 27CMPBLTWN | 69 | 227 | 0.8866 | 0.9875 | 10.09 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204763 | 27CAMP TAP | 69 | 227 | 0.7935 | 0.992 | 19.85 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204763 | 27CAMP TAP | 69 | 227 | 0.8007 | 0.992 | 19.13 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204763 | 27CAMP TAP | 69 | 227 | 0.8011 | 0.992 | 19.09 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204763 | 27CAMP TAP | 69 | 227 | 0.8011 | 0.992 | 19.09 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204763 | 27CAMP TAP | 69 | 227 | 0.8907 | 0.992 | 10.13 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204762 | 27BAYER | 69 | 227 | 0.8043 | 0.9969 | 19.26 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204762 | 27BAYER | 69 | 227 | 0.8119 | 0.9969 | 18.5 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204762 | 27BAYER | 69 | 227 | 0.8124 | 0.9969 | 18.45 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204762 | 27BAYER | 69 | 227 | 0.8124 | 0.9969 | 18.45 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204761 | 27BROAD ST | 69 | 227 | 0.7996 | 0.9933 | 19.37 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204761 | 27BROAD ST | 69 | 227 | 0.8073 | 0.9933 | 18.6 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204761 | 27BROAD ST | 69 | 227 | 0.8077 | 0.9933 | 18.56 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204761 | 27BROAD ST | 69 | 227 | 0.8077 | 0.9933 | 18.56 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204760 | 27ANNVILLE | 69 | 227 | 0.7953 | 0.9911 | 19.58 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204760 | 27ANNVILLE | 69 | 227 | 0.8027 | 0.9911 | 18.84 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204760 | 27ANNVILLE | 69 | 227 | 0.8031 | 0.9911 | 18.8 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204760 | 27ANNVILLE | 69 | 227 | 0.8031 | 0.9911 | 18.8 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204759 | 27ALCOA | 69 | 227 | 0.8048 | 0.9973 | 19.25 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204759 | 27ALCOA | 69 | 227 | 0.8125 | 0.9973 | 18.48 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204759 | 27ALCOA | 69 | 227 | 0.8129 | 0.9973 | 18.44 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204759 | 27ALCOA | 69 | 227 | 0.8129 | 0.9973 | 18.44 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204758 | 27WOOD ST | 69 | 227 | 0.7977 | 0.9923 | 19.46 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204758 | 27WOOD ST | 69 | 227 | 0.805 | 0.9923 | 18.73 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204758 | 27WOOD ST | 69 | 227 | 0.8054 | 0.9923 | 18.69 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204758 | 27WOOD ST | 69 | 227 | 0.8054 | 0.9923 | 18.69 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204757 | 27WOODTP86 | 69 | 227 | 0.7978 | 0.9924 | 19.46 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204757 | 27WOODTP86 | 69 | 227 | 0.8051 | 0.9924 | 18.73 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204757 | 27WOODTP86 | 69 | 227 | 0.8055 | 0.9924 | 18.69 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204757 | 27WOODTP86 | 69 | 227 | 0.8055 | 0.9924 | 18.69 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204756 | 27WOODTP72 | 69 | 227 | 0.7976 | 0.9925 | 19.49 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204756 | 27WOODTP72 | 69 | 227 | 0.8049 | 0.9925 | 18.76 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204756 | 27WOODTP72 | 69 | 227 | 0.8053 | 0.9925 | 18.72 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204756 | 27WOODTP72 | 69 | 227 | 0.8053 | 0.9925 | 18.72 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204756 | 27WOODTP72 | 69 | 227 | 0.8923 | 0.9925 | 10.02 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204724 | 27LEHI CEM | 69 | 227 | 0.7757 | 1.0036 | 22.79 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204724 | 27LEHI CEM | 69 | 227 | 0.7829 | 1.0036 | 22.07 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204724 | 27LEHI CEM | 69 | 227 | 0.7832 | 1.0036 | 22.04 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204724 | 27LEHI CEM | 69 | 227 | 0.7833 | 1.0036 | 22.03 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204724 | 27LEHI CEM | 69 | 227 | 0.8774 | 1.0036 | 12.62 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204723 | 27HOKES | 69 | 227 | 0.776 | 1.0039 | 22.79 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204723 | 27HOKES | 69 | 227 | 0.7832 | 1.0039 | 22.07 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204723 | 27HOKES | 69 | 227 | 0.7835 | 1.0039 | 22.04 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204723 | 27HOKES | 69 | 227 | 0.7835 | 1.0039 | 22.04 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204723 | 27HOKES | 69 | 227 | 0.8777 | 1.0039 | 12.62 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204722 | 27GRANTLEY | 69 | 227 | 0.7671 | 0.998 | 23.09 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204722 | 27GRANTLEY | 69 | 227 | 0.7744 | 0.998 | 22.36 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204722 | 27GRANTLEY | 69 | 227 | 0.7748 | 0.998 | 22.32 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204722 | 27GRANTLEY | 69 | 227 | 0.7748 | 0.998 | 22.32 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204722 | 27GRANTLEY | 69 | 227 | 0.8691 | 0.998 | 12.89 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204721 | 27YORK INT | 69 | 227 | 0.7668 | 0.9978 | 23.1 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204721 | 27YORK INT | 69 | 227 | 0.7742 | 0.9978 | 22.36 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204721 | 27YORK INT | 69 | 227 | 0.7745 | 0.9978 | 22.33 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204721 | 27YORK INT | 69 | 227 | 0.7745 | 0.9978 | 22.33 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204721 | 27YORK INT | 69 | 227 | 0.8689 | 0.9978 | 12.89 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204712 | 27FREDRCKS | 69 | 227 | 0.7903 | 0.9889 | 19.86 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204712 | 27FREDRCKS | 69 | 227 | 0.7976 | 0.9889 | 19.13 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204712 | 27FREDRCKS | 69 | 227 | 0.798 | 0.9889 | 19.09 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204712 | 27FREDRCKS | 69 | 227 | 0.798 | 0.9889 | 19.09 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204708 | 27NCORNWAL | 69 | 227 | 0.8009 | 0.9943 | 19.34 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204708 | 27NCORNWAL | 69 | 227 | 0.8086 | 0.9943 | 18.57 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204708 | 27NCORNWAL | 69 | 227 | 0.809 | 0.9943 | 18.53 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204708 | 27NCORNWAL | 69 | 227 | 0.809 | 0.9943 | 18.53 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204707 | 27WESENBRG | 69 | 227 | 0.8417 | 0.9778 | 13.61 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204707 | 27WESENBRG | 69 | 227 | 0.848 | 0.9778 | 12.98 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204707 | 27WESENBRG | 69 | 227 | 0.8483 | 0.9778 | 12.95 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204707 | 27WESENBRG | 69 | 227 | 0.8484 | 0.9778 | 12.94 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204705 | 27PAINTSKY | 69 | 227 | 0.8439 | 1.002 | 15.81 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204705 | 27PAINTSKY | 69 | 227 | 0.8509 | 1.002 | 15.11 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204705 | 27PAINTSKY | 69 | 227 | 0.8513 | 1.002 | 15.07 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204705 | 27PAINTSKY | 69 | 227 | 0.8513 | 1.002 | 15.07 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204702 | 27MIDDCRK | 69 | 227 | 0.8599 | 0.9973 | 13.74 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204702 | 27MIDDCRK | 69 | 227 | 0.8661 | 0.9973 | 13.12 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204702 | 27MIDDCRK | 69 | 227 | 0.8665 | 0.9973 | 13.08 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204702 | 27MIDDCRK | 69 | 227 | 0.8665 | 0.9973 | 13.08 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204679 | 27PC_Q59Y356 | 69 | 227 | 0.8389 | 0.9953 | 15.64 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204679 | 27PC_Q59Y356 | 69 | 227 | 0.8459 | 0.9953 | 14.94 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204679 | 27PC_Q59Y356 | 69 | 227 | 0.8463 | 0.9953 | 14.9 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204679 | 27PC_Q59Y356 | 69 | 227 | 0.8463 | 0.9953 | 14.9 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204643 | 27HILL RD | 69 | 227 | 0.8468 | 0.9883 | 14.15 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204643 | 27HILL RD | 69 | 227 | 0.8537 | 0.9883 | 13.46 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204643 | 27HILL RD | 69 | 227 | 0.8542 | 0.9883 | 13.41 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204643 | 27HILL RD | 69 | 227 | 0.8542 | 0.9883 | 13.41 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204613 | 27TITUS804 | 69 | 227 | 0.8479 | 1.0063 | 15.84 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204613 | 27TITUS804 | 69 | 227 | 0.8549 | 1.0063 | 15.14 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204613 | 27TITUS804 | 69 | 227 | 0.8553 | 1.0063 | 15.1 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204613 | 27TITUS804 | 69 | 227 | 0.8553 | 1.0063 | 15.1 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204612 | 27TITUS803 | 69 | 227 | 0.8479 | 1.0063 | 15.84 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204612 | 27TITUS803 | 69 | 227 | 0.8549 | 1.0063 | 15.14 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204612 | 27TITUS803 | 69 | 227 | 0.8553 | 1.0063 | 15.1 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204612 | 27TITUS803 | 69 | 227 | 0.8553 | 1.0063 | 15.1 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204611 | 27TITUS802 | 69 | 227 | 0.8479 | 1.0063 | 15.84 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204611 | 27TITUS802 | 69 | 227 | 0.8549 | 1.0063 | 15.14 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204611 | 27TITUS802 | 69 | 227 | 0.8553 | 1.0063 | 15.1 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204611 | 27TITUS802 | 69 | 227 | 0.8553 | 1.0063 | 15.1 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204609 | 27S.RDG | 69 | 227 | 0.8479 | 1.0063 | 15.84 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204609 | 27S.RDG | 69 | 227 | 0.8549 | 1.0063 | 15.14 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204609 | 27S.RDG | 69 | 227 | 0.8553 | 1.0063 | 15.1 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204609 | 27S.RDG | 69 | 227 | 0.8553 | 1.0063 | 15.1 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204608 | 27S.HAMBRG | 69 | 227 | 0.8475 | 0.9896 | 14.21 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204608 | 27S.HAMBRG | 69 | 227 | 0.8543 | 0.9896 | 13.53 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204608 | 27S.HAMBRG | 69 | 227 | 0.8547 | 0.9896 | 13.49 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204608 | 27S.HAMBRG | 69 | 227 | 0.8547 | 0.9896 | 13.49 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204607 | 27N.TEMPLE | 69 | 227 | 0.8505 | 0.995 | 14.45 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204607 | 27N.TEMPLE | 69 | 227 | 0.8569 | 0.995 | 13.81 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204607 | 27N.TEMPLE | 69 | 227 | 0.8573 | 0.995 | 13.77 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204607 | 27N.TEMPLE | 69 | 227 | 0.8573 | 0.995 | 13.77 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204606 | 27N.BOYTWN | 69 | 227 | 0.8685 | 1.0037 | 13.52 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204606 | 27N.BOYTWN | 69 | 227 | 0.8746 | 1.0037 | 12.91 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204606 | 27N.BOYTWN | 69 | 227 | 0.8749 | 1.0037 | 12.88 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204606 | 27N.BOYTWN | 69 | 227 | 0.875 | 1.0037 | 12.87 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204605 | 27LYONS | 69 | 227 | 0.8768 | 1.0041 | 12.73 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204605 | 27LYONS | 69 | 227 | 0.8825 | 1.0041 | 12.16 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204605 | 27LYONS | 69 | 227 | 0.8828 | 1.0041 | 12.13 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204605 | 27LYONS | 69 | 227 | 0.8828 | 1.0041 | 12.13 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204604 | 27S.LEB | 69 | 227 | 0.8132 | 1.0037 | 19.05 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204604 | 27S.LEB | 69 | 227 | 0.8208 | 1.0037 | 18.29 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204604 | 27S.LEB | 69 | 227 | 0.8212 | 1.0037 | 18.25 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204604 | 27S.LEB | 69 | 227 | 0.8212 | 1.0037 | 18.25 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204603 | 27N.LEB | 69 | 227 | 0.8121 | 1.0036 | 19.15 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204603 | 27N.LEB | 69 | 227 | 0.8196 | 1.0036 | 18.4 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204603 | 27N.LEB | 69 | 227 | 0.82 | 1.0036 | 18.36 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204603 | 27N.LEB | 69 | 227 | 0.82 | 1.0036 | 18.36 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204602 | 27N.HERSHY | 69 | 227 | 0.8074 | 1.0091 | 20.17 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204602 | 27N.HERSHY | 69 | 227 | 0.8146 | 1.0091 | 19.45 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204602 | 27N.HERSHY | 69 | 227 | 0.815 | 1.0091 | 19.41 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204602 | 27N.HERSHY | 69 | 227 | 0.8151 | 1.0091 | 19.4 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204602 | 27N.HERSHY | 69 | 227 | 0.9049 | 1.0091 | 10.42 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204601 | 27MIDD JCT | 69 | 227 | 0.7977 | 0.9895 | 19.18 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204601 | 27MIDD JCT | 69 | 227 | 0.805 | 0.9895 | 18.45 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204601 | 27MIDD JCT | 69 | 227 | 0.8054 | 0.9895 | 18.41 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204601 | 27MIDD JCT | 69 | 227 | 0.8054 | 0.9895 | 18.41 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204600 | 27LARA | 69 | 227 | 0.834 | 0.9917 | 15.77 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204600 | 27LARA | 69 | 227 | 0.8411 | 0.9917 | 15.06 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204600 | 27LARA | 69 | 227 | 0.8415 | 0.9917 | 15.02 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204600 | 27LARA | 69 | 227 | 0.8415 | 0.9917 | 15.02 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204579 | 27VIOLET H | 69 | 227 | 0.7651 | 0.9974 | 23.23 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204579 | 27VIOLET H | 69 | 227 | 0.7726 | 0.9974 | 22.48 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204579 | 27VIOLET H | 69 | 227 | 0.7729 | 0.9974 | 22.45 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204579 | 27VIOLET H | 69 | 227 | 0.7729 | 0.9974 | 22.45 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204579 | 27VIOLET H | 69 | 227 | 0.8673 | 0.9974 | 13.01 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204578 | 27SMITH ST | 69 | 227 | 0.7797 | 1.0134 | 23.37 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204578 | 27SMITH ST | 69 | 227 | 0.787 | 1.0134 | 22.64 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204578 | 27SMITH ST | 69 | 227 | 0.7874 | 1.0134 | 22.6 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204578 | 27SMITH ST | 69 | 227 | 0.7874 | 1.0134 | 22.6 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204578 | 27SMITH ST | 69 | 227 | 0.8829 | 1.0134 | 13.05 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204577 | 27JACKSON1 | 69 | 227 | 0.7826 | 1.0106 | 22.8 | Line_FB | PJM_500_BG_P4_5_CNSTN_B_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204577 | 27JACKSON1 | 69 | 227 | 0.7896 | 1.0106 | 22.1 | Line_FB | PECO_P4_PEACH235_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204577 | 27JACKSON1 | 69 | 227 | 0.7899 | 1.0106 | 22.07 | Single | PECO_P1-2_5012_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204577 | 27JACKSON1 | 69 | 227 | 0.7899 | 1.0106 | 22.07 | Line_FB | PJM_500_BG_P4_5_CNSTN_C_SRT-A | NO | Related to 2022 Window 3, pending window outcome
N/A | 204577 | 27JACKSON1 | 69 | 227 | 0.8821 | 1.0106 | 12.85 | Line_FB | PECO_P4_PEACH245_SRT-A | NO | Related to 2022 Window 3, pending window outcome
| Note | APS and Dominion zones as a whole are quarantined pending Window 3 outcome and are not included in above results
Related to Window 3, pending window outcome