## Winter GenDeliv
| Note | APS and Dominion zones as a whole are quarantined pending Window 3 outcome and are not included in above results
Related to 2022 Window 3, pending window outcome
2028 RTEP PJM Generation Deliverability Result (Winter)
FG # | Fr Bus | Name | To Bus | Name | CKT | KVs | Areas | Rating | FN DC Flow | FN AC Flow | FN DC % | FN AC % | Cont Label | Cont Type | Conductor/Transformer Rating (MVA) | PJM Accepting Proposals | Reason For Exclusion | Comments
2023W1-GD-W912 | 270737 | ELWOOD ; R | 270769 | GOODINGS ;2R | 1 | 345 | 222 | 1781 | 2079 | 2061 | 116.73 | 115.72 | COMED_P4_116-45-L11613__SRT-A | Breaker | 1602/1921/2051/2325 (WN/WE/WSTE/WLD) | YES
2023W1-GD-W229 | 271680 | HAUMESSER; B | 272756 | W DEKALB ;3T | 1 | 138 | 222 | 472 | 534.1 | 532.6 | 113.17 106.25 | 112.84 105.92 | COMED_P1-2_345-L15502_B-R_SRT-A | Single | 472/472/476/495 (WN/WE/WSTE/WLD) | YES
2023W1-GD-W945 | 271680 | HAUMESSER; B | 272756 | W DEKALB ;3T | 1 | 138 | 222 | 472 | 530.5 | 528.9 | 112.4 105.57 | 112.06 105.23 | COMED_P4_111-45-L11124__SRT-A | Breaker | 472/472/476/495 (WN/WE/WSTE/WLD) | YES
2023W1-GD-W1387 | 271680 | HAUMESSER; B | 272756 | W DEKALB ;3T | 1 | 138 | 222 | 472 | 530.5 | 528.9 | 112.4 105.57 | 112.06 105.23 | COMED_P2-2_111_EJ-345B__1_SRT-A | Bus | 472/472/476/495 (WN/WE/WSTE/WLD) | YES
2023W1-GD-W946 | 271680 | HAUMESSER; B | 272756 | W DEKALB ;3T | 1 | 138 | 222 | 472 | 529.8 | 528.6 | 112.25 105.4 | 111.99 105.14 | COMED_P4_155-45-BT2-34__SRT-A | Breaker | 472/472/476/495 (WN/WE/WSTE/WLD) | YES
2023W1-GD-W955 | 271680 | HAUMESSER; B | 272756 | W DEKALB ;3T | 1 | 138 | 222 | 472 | 524.9 | 523.7 | 111.2 104.96 | 110.94 104.7 | COMED_P4_155-45-BT34-5__SRT-A | Breaker | 472/472/476/495 (WN/WE/WSTE/WLD) | YES
2023W1-GD-W972 | 271680 | HAUMESSER; B | 272756 | W DEKALB ;3T | 1 | 138 | 222 | 472 | 518.6 | 516.8 | 109.87 102.33 | 109.49 101.96 | COMED_P4_006-45-BT3-4___SRT-A | Breaker | 472/472/476/495 (WN/WE/WSTE/WLD) | YES
2023W1-GD-W268 | 272756 | W DEKALB ;3T | 271428 | ESS H452 ;RT | 1 | 138 | 222 | 472 | 512.9 | 513.1 | 108.66 101.74 | 108.7 101.78 | COMED_P1-2_345-L15502_B-R_SRT-A | Single | 452/472/476/495 (WN/WE/WSTE/WLD) | YES
2023W1-GD-W273 | 271680 | HAUMESSER; B | 272756 | W DEKALB ;3T | 1 | 138 | 222 | 472 | 512.4 | 511.2 | 108.57 | 108.3 | COMED_P1-2_345-L0627__B-R_SRT-A | Single | 472/472/476/495 (WN/WE/WSTE/WLD) | YES
2023W1-GD-W1397 | 272756 | W DEKALB ;3T | 271428 | ESS H452 ;RT | 1 | 138 | 222 | 472 | 509.3 | 509.4 | 107.9 101.07 | 107.93 101.1 | COMED_P2-2_111_EJ-345B__1_SRT-A | Bus | 452/472/476/495 (WN/WE/WSTE/WLD) | YES
2023W1-GD-W988 | 272756 | W DEKALB ;3T | 271428 | ESS H452 ;RT | 1 | 138 | 222 | 472 | 509.3 | 509.4 | 107.9 101.07 | 107.93 101.1 | COMED_P4_111-45-L11124__SRT-A | Breaker | 452/472/476/495 (WN/WE/WSTE/WLD) | YES
2023W1-GD-W993 | 272756 | W DEKALB ;3T | 271428 | ESS H452 ;RT | 1 | 138 | 222 | 472 | 508.6 | 509.1 | 107.75 100.9 | 107.86 101.01 | COMED_P4_155-45-BT2-34__SRT-A | Breaker | 452/472/476/495 (WN/WE/WSTE/WLD) | YES
2023W1-GD-W292 | 271680 | HAUMESSER; B | 272756 | W DEKALB ;3T | 1 | 138 | 222 | 472 | 507.8 | 506.7 | 107.57 | 107.36 | COMED_P1-2_345-L15501_B-R_SRT-A | Single | 472/472/476/495 (WN/WE/WSTE/WLD) | YES
2023W1-GD-W1006 | 272756 | W DEKALB ;3T | 271428 | ESS H452 ;RT | 1 | 138 | 222 | 472 | 503.6 | 504.1 | 106.7 | 106.81 | COMED_P4_155-45-BT34-5__SRT-A | Breaker | 452/472/476/495 (WN/WE/WSTE/WLD) | YES
2023W1-GD-W326 | 232012 | HOPE CREEK | 232013 | SILVER RUN | 1 | 230 | 225 | 1150 | 1241.4 | 1212.1 | 107.95 | 105.4 | PJM500_PS_P1-2_5015_SRT-A | Single | 940/1150 (WN/WE) | NO | Addressed by Baseline Upgrade
2023W1-GD-W1025 | 272756 | W DEKALB ;3T | 271428 | ESS H452 ;RT | 1 | 138 | 222 | 472 | 497.3 | 497.5 | 105.37 | 105.4 | COMED_P4_006-45-BT3-4___SRT-A | Breaker | 452/472/476/495 (WN/WE/WSTE/WLD) | YES
2023W1-GD-W1031 | 232012 | HOPE CREEK | 232013 | SILVER RUN | 1 | 230 | 225 | 1150 | 1239 | 1209.3 | 107.74 | 105.16 | PJM500_PS_P2-3_HOPC_3-4_SRT-A | Breaker | 940/1150 (WN/WE) | NO | Addressed by Baseline Upgrade
2023W1-GD-W1047 | 270828 | NELSON ; B | 270730 | ELECT JCT; B | 1 | 345 | 222 | 1856 | 1933.3 | 1937 | 104.17 | 104.37 | COMED_P4_006-45-BT3-8___SRT-A | Breaker | 2091/2381/2445/2648 (WN/WE/WSTE/WLD) | NO | Substation Equipment Exclusion
2023W1-GD-W1048 | 270828 | NELSON ; B | 270730 | ELECT JCT; B | 1 | 345 | 222 | 1856 | 1934.3 | 1936.3 | 104.22 | 104.33 | COMED_P4_006-45-BT3-4___SRT-A | Breaker | 2091/2381/2445/2648 (WN/WE/WSTE/WLD) | NO | Substation Equipment Exclusion
2023W1-GD-W341 | 272756 | W DEKALB ;3T | 271428 | ESS H452 ;RT | 1 | 138 | 222 | 472 | 491.2 | 491.8 | 104.06 | 104.19 | COMED_P1-2_345-L0627__B-R_SRT-A | Single | 452/472/476/495 (WN/WE/WSTE/WLD) | YES
2023W1-GD-W343 | 270828 | NELSON ; B | 270730 | ELECT JCT; B | 1 | 345 | 222 | 1856 | 1927.4 | 1931.1 | 103.85 | 104.05 | COMED_P1-2_345-L0627__B-R_SRT-A | Single | 2091/2381/2445/2648 (WN/WE/WSTE/WLD) | NO | Substation Equipment Exclusion
2023W1-GD-W1060 | 232012 | HOPE CREEK | 232013 | SILVER RUN | 1 | 230 | 225 | 1150 | 1220.3 | 1191.1 | 106.11 | 103.58 | PJM500_DPL_P4_2_REDLION-HOPE AT50_SRT-A | Breaker | 940/1150 (WN/WE) | NO | Addressed by Baseline Upgrade
2023W1-GD-W354 | 272756 | W DEKALB ;3T | 271428 | ESS H452 ;RT | 1 | 138 | 222 | 472 | 486.5 | 487.4 | 103.07 | 103.25 | COMED_P1-2_345-L15501_B-R_SRT-A | Single | 452/472/476/495 (WN/WE/WSTE/WLD) | YES
2023W1-GD-W1069 | 232012 | HOPE CREEK | 232013 | SILVER RUN | 1 | 230 | 225 | 1150 | 1210.2 | 1181.3 | 105.23 | 102.72 | PJM500_DPL_P4_2_REDLION-HOPE AT51_SRT-A | Breaker | 940/1150 (WN/WE) | NO | Addressed by Baseline Upgrade
2023W1-GD-W363 | 271680 | HAUMESSER; B | 272756 | W DEKALB ;3T | 1 | 138 | 222 | 472 | 482.5 | 484 | 102.22 | 102.54 | COMED_P1-2_138-L15627_R-R_SRT-A | Single | 472/472/476/495 (WN/WE/WSTE/WLD) | YES
2023W1-GD-W375 | 271680 | HAUMESSER; B | 272756 | W DEKALB ;3T | 1 | 138 | 222 | 472 | 479.2 | 479.6 | 101.52 | 101.61 | COMED_P1-2_345-L92805__B-R_SRT-A | Single | 472/472/476/495 (WN/WE/WSTE/WLD) | YES
2023W1-GD-W390 | 271241 | CRESCENT ; R | 348935 | 4CORBIN | 1 | 138 | 222/357 | 229 | 221.1 | 230 | 96.56 | 100.45 | EXT_348921 4PRINCETN TP 138 348923 4EKEWANEE N 138 1 _SRT-W | Single | 252/298/300/313 (WN/WE/WSTE/WLD) | NO | Below 200 kV Exclusion
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 1792.2 | 1913.7 | 290.46 | 310.16 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 1779.7 | 1913.7 | 288.45 | 310.16 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 1792.4 | 1902.6 | 290.51 | 308.36 | PECO_P4_PEACH235_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 1780 | 1902.6 | 288.49 | 308.36 | PECO_P4_PEACH235_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 1792 | 1902 | 290.43 | 308.27 | PECO_P1-2_5012_SRT-A | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 1779.5 | 1902 | 288.41 | 308.27 | PECO_P1-2_5012_SRT-A | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 1779.5 | 1902 | 288.41 | 308.27 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 1791.9 | 1902 | 290.43 | 308.27 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 1764.7 | 1901.5 | 276.16 | 297.58 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 1765 | 1890.3 | 276.21 | 295.83 | PECO_P4_PEACH235_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 1764.5 | 1889.8 | 276.13 | 295.74 | PECO_P1-2_5012_SRT-A | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 1764.5 | 1889.8 | 276.13 | 295.74 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 1737.5 | 1882.4 | 271.9 | 294.58 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 1737.7 | 1871 | 271.95 | 292.81 | PECO_P4_PEACH235_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 1737.2 | 1870.5 | 271.87 | 292.72 | PECO_P1-2_5012_SRT-A | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 1737.2 | 1870.5 | 271.87 | 292.72 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 1704.4 | 1767.6 | 276.24 | 286.49 | PECO_P4_PEACH245_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 1692 | 1767.6 | 274.22 | 286.49 | PECO_P4_PEACH245_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 1676.9 | 1754.9 | 262.43 | 274.63 | PECO_P4_PEACH245_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 1649.7 | 1734.6 | 258.17 | 271.45 | PECO_P4_PEACH245_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200004 | CNASTONE | 1 | 500 | 225 | 3464 | 7731.2 | 7510.3 | 223.19 | 216.81 | Base Case | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200065 | PCHBTM2S | 200064 | PCHBTM1S | Z1 | 500 | 225 | 3277 | 7166.5 | 6915.9 | 218.69 | 211.04 | PECO_P4_PEACH255_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200065 | PCHBTM2S | 200064 | PCHBTM1S | Z2 | 500 | 225 | 3022 | 6516.5 | 6298.3 | 215.64 | 208.41 | PECO_P4_PEACH025_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200065 | PCHBTM2S | 200064 | PCHBTM1S | Z2 | 500 | 225 | 3022 | 6240.5 | 6025.7 | 206.5 | 199.39 | PECO_P1-2_PBTIE1_SRT-A | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 205912 | AD1-020 TAP | 204544 | 27LINCOLN | 1 | 115 | 227 | 334 | 651.8 | 664.2 | 195.14 | 198.88 | PJM_500_BG_P1_5011_SRT-A | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204539 | 27HUNTRSTN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 334 | 654.3 | 662.4 | 195.9 | 198.32 | PJM_500_BG_P1_5011_SRT-A | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 235463 | 01TANEY | 1 | 138 | 227/201 | 317 | 644.5 | 627.5 | 203.3 | 197.96 | PJM_500_BG_P1_5011_SRT-A | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200004 | CNASTONE | 1 | 500 | 225 | 4030 | 8206.9 | 7975.1 | 203.64 | 197.89 | PECO_P4_NOTTI55_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200004 | CNASTONE | 1 | 500 | 225 | 4030 | 8198.8 | 7967.6 | 203.44 | 197.71 | PECO_P2-2_NOTT230B_SRT-A | Bus |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200004 | CNASTONE | 1 | 500 | 225 | 4030 | 8199.8 | 7967.1 | 203.47 | 197.69 | PECO_P4_NOTTI785_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200004 | CNASTONE | 1 | 500 | 225 | 4030 | 8188.9 | 7959.2 | 203.2 | 197.5 | PECO_P4_NOTTI85_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200004 | CNASTONE | 1 | 500 | 225 | 4030 | 8186.4 | 7957.7 | 203.14 | 197.46 | PECO_P1-2_220-08_SRT-A | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200004 | CNASTONE | 1 | 500 | 225 | 4030 | 8183.8 | 7955.8 | 203.07 | 197.42 | PECO_P4_COOPR125_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200004 | CNASTONE | 1 | 500 | 225 | 4030 | 8170 | 7947.4 | 202.73 | 197.21 | PECO_P1-2_220-93_SRT-A | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 1787.1 | 1747.1 | 201.02 | 196.53 | PECO_P1-2_5012_SRT-A | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 205912 | AD1-020 TAP | 204544 | 27LINCOLN | 1 | 115 | 227 | 334 | 644.9 | 656.2 | 193.07 | 196.47 | PJM_500_BG_P4_5_CNSTN_J_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 205912 | AD1-020 TAP | 204544 | 27LINCOLN | 1 | 115 | 227 | 334 | 644.5 | 655.8 | 192.96 | 196.34 | PEPCO_P4_PP40_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 235463 | 01TANEY | 1 | 138 | 227/201 | 317 | 638.8 | 621.7 | 201.5 | 196.13 | PJM_500_BG_P4_5_CNSTN_J_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 235463 | 01TANEY | 1 | 138 | 227/201 | 317 | 638.3 | 621.4 | 201.36 | 196.02 | PEPCO_P4_PP40_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204539 | 27HUNTRSTN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 334 | 647.4 | 654.4 | 193.83 | 195.94 | PJM_500_BG_P4_5_CNSTN_J_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204539 | 27HUNTRSTN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 334 | 647 | 654 | 193.71 | 195.8 | PEPCO_P4_PP40_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 1744.3 | 1754.7 | 194.46 | 195.62 | PECO_P1-2_5012_SRT-A | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200004 | CNASTONE | 1 | 500 | 225 | 4030 | 8049.8 | 7845.3 | 199.75 | 194.67 | PJM_500_BG_P4_5_CNSTN_M_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200004 | CNASTONE | 1 | 500 | 225 | 4030 | 8049.8 | 7844.8 | 199.75 | 194.66 | PJM_500_BG_P1_5013_SRT-A | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 1772.5 | 1730.2 | 199.38 | 194.62 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 1772.3 | 1730.1 | 199.36 | 194.61 | PECO_P4_PEACH235_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 1725.1 | 1743.8 | 192.32 | 194.41 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 1765.6 | 1728.2 | 198.6 | 194.4 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200004 | CNASTONE | 1 | 500 | 225 | 4030 | 8032.2 | 7820.7 | 199.31 | 194.06 | PL_05_P71_000906_SRT-A | Tower |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200003 | BRIGHTON | 1 | 500 | 225 | 3183 | 6004.6 | 6167.1 | 188.65 | 193.75 | BG_P7_CNSTN_NWEST2_SRT-A | Tower |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200004 | CNASTONE | 1 | 500 | 225 | 4030 | 7979 | 7790.2 | 197.99 | 193.3 | AP_P1-2_PE-500-001_SRT-W | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200004 | CNASTONE | 1 | 500 | 225 | 4030 | 7979 | 7790.2 | 197.99 | 193.3 | AP_P1-2_WP-500-DRT17_SRT-W | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 1721.9 | 1729.2 | 191.96 | 192.78 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 1721.7 | 1729.2 | 191.94 | 192.77 | PECO_P4_PEACH235_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200004 | CNASTONE | 1 | 500 | 225 | 4030 | 7983.2 | 7753.5 | 198.09 | 192.39 | PL_04_P71_001014_SRT-A | Tower |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200003 | BRIGHTON | 1 | 500 | 225 | 3183 | 5938.2 | 6113.6 | 186.56 | 192.07 | BG_P7_GRCTN_RAPHEL_SRT-A | Tower |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 204538 | 27STRABAN | 1 | 115 | 227 | 371 | 688.7 | 711.6 | 185.64 | 191.8 | PJM_500_BG_P1_5011_SRT-A | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200004 | CNASTONE | 1 | 500 | 225 | 4030 | 7939.7 | 7722.1 | 197.01 | 191.61 | PL_05_P22_000674_SRT-A | Bus |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200004 | CNASTONE | 1 | 500 | 225 | 4030 | 7938.5 | 7716.9 | 196.98 | 191.49 | AP_P2-2_WP-500-DRT16_SRT-W | Bus |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200004 | CNASTONE | 1 | 500 | 225 | 4030 | 7912.4 | 7688.8 | 196.34 | 190.79 | PL_04_P22_102817_SRT-A | Bus |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200004 | CNASTONE | 1 | 500 | 225 | 4030 | 7910.5 | 7686.3 | 196.29 | 190.73 | PL_04_P71_000904_SRT-A | Tower |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200004 | CNASTONE | 1 | 500 | 225 | 4030 | 7909.7 | 7685.6 | 196.27 | 190.71 | PL_04_P71_001822_SRT-A | Tower |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200004 | CNASTONE | 1 | 500 | 225 | 4030 | 7877.6 | 7655.1 | 195.48 | 189.95 | AP_P2-2_WP-500-DRT17_SRT-W | Bus |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 204538 | 27STRABAN | 1 | 115 | 227 | 371 | 683 | 704.6 | 184.1 | 189.91 | PJM_500_BG_P4_5_CNSTN_J_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 204538 | 27STRABAN | 1 | 115 | 227 | 371 | 682.6 | 704 | 183.99 | 189.77 | PEPCO_P4_PP40_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200004 | CNASTONE | 1 | 500 | 225 | 4030 | 7844.6 | 7623.6 | 194.65 | 189.17 | PL_04_P71_000907_SRT-A | Tower |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200003 | BRIGHTON | 1 | 500 | 225 | 3183 | 5831 | 5995.2 | 183.19 | 188.35 | BG_P7_NEAST_RPHLRD_SRT-A | Tower |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 1706.5 | 1666.4 | 191.95 | 187.45 | PECO_P4_PEACH245_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204538 | 27STRABAN | 204529 | 27GERMANTN | 1 | 115 | 227 | 371 | 667.3 | 694.7 | 179.86 | 187.24 | PJM_500_BG_P1_5011_SRT-A | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204550 | 27ORRTANNA | 204544 | 27LINCOLN | 1 | 115 | 227 | 189 | 352.7 | 352.6 | 186.62 | 186.56 | ME_P1-2_ME-115-068_SRT-A | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204550 | 27ORRTANNA | 204544 | 27LINCOLN | 1 | 115 | 227 | 189 | 354.5 | 351.8 | 187.57 | 186.14 | ME_P1-2_ME-115-067_SRT-A | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204538 | 27STRABAN | 204529 | 27GERMANTN | 1 | 115 | 227 | 371 | 661.6 | 687.6 | 178.32 | 185.35 | PJM_500_BG_P4_5_CNSTN_J_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204538 | 27STRABAN | 204529 | 27GERMANTN | 1 | 115 | 227 | 371 | 661.1 | 687.1 | 178.21 | 185.21 | PEPCO_P4_PP40_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200065 | PCHBTM2S | 200064 | PCHBTM1S | Z1 | 500 | 225 | 3277 | 6240.5 | 6025.7 | 190.43 | 183.88 | PECO_P1-2_PBTIE2_SRT-A | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200003 | BRIGHTON | 1 | 500 | 225 | 3183 | 5719.4 | 5835.5 | 179.69 | 183.33 | PJM_500_BG_P4_5_CNSTN_13_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200003 | BRIGHTON | 1 | 500 | 225 | 3183 | 5716.8 | 5832.8 | 179.6 | 183.25 | PJM_500_BG_P4_5_CNSTN_6_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200065 | PCHBTM2S | 200064 | PCHBTM1S | Z2 | 500 | 225 | 3022 | 5695.3 | 5508.5 | 188.46 | 182.28 | PECO_P4_PEACH015_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 1643.2 | 1634.2 | 183.19 | 182.18 | PECO_P4_PEACH245_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204550 | 27ORRTANNA | 204544 | 27LINCOLN | 1 | 115 | 227 | 189 | 341.9 | 344.2 | 180.91 | 182.14 | ME_P2-3_ME-115-035A_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200003 | BRIGHTON | 1 | 500 | 225 | 2901 | 5196.5 | 5268.5 | 179.13 | 181.61 | Base Case | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204550 | 27ORRTANNA | 204544 | 27LINCOLN | 1 | 115 | 227 | 189 | 341 | 340.3 | 180.44 | 180.04 | ME_P2-3_ME-115-013B_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204550 | 27ORRTANNA | 204544 | 27LINCOLN | 1 | 115 | 227 | 189 | 340.5 | 339.7 | 180.14 | 179.71 | ME_P2-3_ME-115-013A_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204550 | 27ORRTANNA | 204544 | 27LINCOLN | 1 | 115 | 227 | 189 | 337.6 | 339.6 | 178.61 | 179.71 | ME_P2-3_ME-115-035B_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200003 | BRIGHTON | 1 | 500 | 225 | 3183 | 5567.2 | 5715.2 | 174.9 | 179.55 | AP_P2-3_PE-500-016_SRT-W | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200003 | BRIGHTON | 1 | 500 | 225 | 3183 | 5569.2 | 5714.6 | 174.97 | 179.53 | AP_P2-3_PE-500-015_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200003 | BRIGHTON | 1 | 500 | 225 | 3183 | 5600.8 | 5701.6 | 175.96 | 179.13 | BG_P7_GRNITE_HIRDG_SRT-A | Tower |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200065 | PCHBTM2S | 200064 | PCHBTM1S | Z1 | 500 | 225 | 3277 | 6076.6 | 5864.3 | 185.43 | 178.95 | PECO_P4_PEACH055_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200003 | BRIGHTON | 1 | 500 | 225 | 3183 | 5545.7 | 5687.5 | 174.23 | 178.69 | AP_P2-3_WP-500-DRT19_SRT-W | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200003 | BRIGHTON | 1 | 500 | 225 | 3183 | 5545.7 | 5687.2 | 174.23 | 178.67 | AP_P1-2_PE-500-004_SRT-W | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200003 | BRIGHTON | 1 | 500 | 225 | 3183 | 5545.7 | 5687.2 | 174.23 | 178.67 | AP_P1-2_WP-500-006_SRT-A | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200003 | BRIGHTON | 1 | 500 | 225 | 3183 | 5541.1 | 5686.4 | 174.09 | 178.65 | AP_P1-2_WP-500-DRT17_SRT-W | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200003 | BRIGHTON | 1 | 500 | 225 | 3183 | 5541.1 | 5686.4 | 174.09 | 178.65 | AP_P1-2_PE-500-001_SRT-W | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200065 | PCHBTM2S | 200064 | PCHBTM1S | Z2 | 500 | 225 | 3022 | 5577 | 5395.5 | 184.55 | 178.54 | PECO_P4_PEACH205_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 205912 | AD1-020 TAP | 204544 | 27LINCOLN | 1 | 115 | 227 | 263 | 472.4 | 468.1 | 179.61 | 177.98 | Base Case | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204539 | 27HUNTRSTN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 263 | 474.9 | 467.2 | 180.58 | 177.65 | Base Case | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200065 | PCHBTM2S | 200064 | PCHBTM1S | Z1 | 500 | 225 | 3277 | 6017 | 5812.4 | 183.61 | 177.37 | PECO_P4_PEACH045_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200003 | BRIGHTON | 1 | 500 | 225 | 3183 | 5539.5 | 5637.9 | 174.04 | 177.12 | BG_P7_NWEST_GRNITE_SRT-A | Tower |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200003 | BRIGHTON | 1 | 500 | 225 | 3183 | 5520.4 | 5603 | 173.44 | 176.03 | AP_P1-2_WP-500-008_SRT-A | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200003 | BRIGHTON | 1 | 500 | 225 | 3183 | 5504.6 | 5598.5 | 172.94 | 175.89 | PJM_500_BG_P2_CNSTN_230-S_SRT-A | Bus |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200003 | BRIGHTON | 1 | 500 | 225 | 3183 | 5503.6 | 5597.6 | 172.91 | 175.86 | PJM_500_BG_P2_CNSTN_230-N_SRT-A | Bus |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 235463 | 01TANEY | 1 | 138 | 227/201 | 250 | 442.3 | 438.2 | 176.93 | 175.28 | Base Case | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200003 | BRIGHTON | 1 | 500 | 225 | 3183 | 5489.9 | 5577.8 | 172.47 | 175.24 | AP_P2-2_WP-500-DRT16_SRT-W | Bus |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204550 | 27ORRTANNA | 204544 | 27LINCOLN | 1 | 115 | 227 | 189 | 333.9 | 330.3 | 176.66 | 174.77 | ME_P2-3_ME-115-0102-A_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204550 | 27ORRTANNA | 204544 | 27LINCOLN | 1 | 115 | 227 | 189 | 333.9 | 330.3 | 176.66 | 174.77 | ME_P2-2_ME-115-0102-4_SRT-A | Bus |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 221090 | GLENARM2 | 221089 | WINDYED1 | 1 | 115 | 232 | 222 | 374.7 | 383.7 | 168.79 | 172.86 | BG_P7_GRCTN_RAPHEL_SRT-A | Tower |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200003 | BRIGHTON | 1 | 500 | 225 | 3183 | 5414.2 | 5490.8 | 170.1 | 172.5 | AP_P2-2_WP-500-DRT17_SRT-W | Bus |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 903 | 1482.1 | 1553.1 | 164.13 | 171.99 | PECO_P1-2_5012_SRT-A | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 911 | 1609.4 | 1559.5 | 176.66 | 171.18 | PECO_P1-2_5012_SRT-A | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200003 | BRIGHTON | 1 | 500 | 225 | 3183 | 5367.1 | 5445.7 | 168.62 | 171.09 | AP_P2-2_WP-500-DRT15_SRT-W | Bus |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 911 | 1596 | 1547.6 | 175.2 | 169.88 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 911 | 1598.4 | 1547.2 | 175.46 | 169.84 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 911 | 1598.3 | 1547.2 | 175.44 | 169.83 | PECO_P4_PEACH235_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 903 | 1460.4 | 1531.1 | 161.73 | 169.56 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204539 | 27HUNTRSTN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 334 | 570 | 565 | 170.66 | 169.15 | PECO_P1-2_5012_SRT-A | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 204538 | 27STRABAN | 1 | 115 | 227 | 291 | 486.6 | 490.8 | 167.22 | 168.65 | Base Case | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 205912 | AD1-020 TAP | 204544 | 27LINCOLN | 1 | 115 | 227 | 334 | 567.4 | 562.2 | 169.89 | 168.32 | PECO_P1-2_5012_SRT-A | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 903 | 1458.5 | 1519.1 | 161.52 | 168.23 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 903 | 1458.4 | 1519 | 161.5 | 168.21 | PECO_P4_PEACH235_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200065 | PCHBTM2S | 200064 | PCHBTM1S | Z1 | 500 | 225 | 3277 | 5693.9 | 5507.3 | 173.75 | 168.06 | PECO_P4_PEACH225_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204539 | 27HUNTRSTN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 334 | 563.6 | 558.8 | 168.75 | 167.31 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204539 | 27HUNTRSTN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 334 | 563.6 | 558.7 | 168.74 | 167.29 | PECO_P4_PEACH235_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204539 | 27HUNTRSTN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 334 | 563.3 | 558.4 | 168.65 | 167.19 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 205912 | AD1-020 TAP | 204544 | 27LINCOLN | 1 | 115 | 227 | 334 | 561.1 | 555.5 | 167.98 | 166.32 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 205912 | AD1-020 TAP | 204544 | 27LINCOLN | 1 | 115 | 227 | 334 | 561 | 555.5 | 167.98 | 166.31 | PECO_P4_PEACH235_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 205912 | AD1-020 TAP | 204544 | 27LINCOLN | 1 | 115 | 227 | 334 | 560.7 | 555 | 167.89 | 166.18 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204538 | 27STRABAN | 204529 | 27GERMANTN | 1 | 115 | 227 | 291 | 465.2 | 474.3 | 159.85 | 162.99 | Base Case | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 911 | 1528.6 | 1484.8 | 167.8 | 162.99 | PECO_P4_PEACH245_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208078 | SAKR | 208030 | MLWD TR1 | 1 | 230 | 229 | 903 | 1381.4 | 1465.8 | 152.98 | 162.32 | PECO_P1-2_5012_SRT-A | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 205912 | AD1-020 TAP | 204544 | 27LINCOLN | 1 | 115 | 227 | 334 | 541.2 | 538.8 | 162.02 | 161.32 | ME_P1-2_ME-115-061_SRT-A | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204539 | 27HUNTRSTN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 334 | 543.9 | 537.9 | 162.83 | 161.06 | ME_P1-2_ME-115-061_SRT-A | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 221090 | GLENARM2 | 221089 | WINDYED1 | 1 | 115 | 232 | 222 | 344.7 | 356 | 155.27 | 160.36 | BG_P7_NEAST_RPHLRD_SRT-A | Tower |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 204538 | 27STRABAN | 1 | 115 | 227 | 371 | 593.7 | 594.3 | 160.03 | 160.2 | PECO_P1-2_5012_SRT-A | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 963.4 | 980.6 | 156.14 | 158.94 | PJM_500_BG_P1_5011_SRT-A | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 950.9 | 980.6 | 154.12 | 158.94 | PJM_500_BG_P1_5011_SRT-A | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208078 | SAKR | 208030 | MLWD TR1 | 1 | 230 | 229 | 903 | 1353.8 | 1432.8 | 149.92 | 158.67 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 903 | 1395.5 | 1431.4 | 154.54 | 158.51 | PECO_P4_PEACH245_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204514 | 27TMI | 204502 | 27JACKSON | 1 | 230 | 227 | 781 | 1163.2 | 1235.1 | 148.94 | 158.14 | PECO_P1-2_5012_SRT-A | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 204538 | 27STRABAN | 1 | 115 | 227 | 371 | 586.4 | 586.5 | 158.06 | 158.09 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 204538 | 27STRABAN | 1 | 115 | 227 | 371 | 586.4 | 586.5 | 158.05 | 158.09 | PECO_P4_PEACH235_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 204538 | 27STRABAN | 1 | 115 | 227 | 371 | 586 | 586 | 157.96 | 157.96 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208078 | SAKR | 208030 | MLWD TR1 | 1 | 230 | 229 | 903 | 1352.2 | 1424.6 | 149.74 | 157.76 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208078 | SAKR | 208030 | MLWD TR1 | 1 | 230 | 229 | 903 | 1352.1 | 1424.5 | 149.73 | 157.75 | PECO_P4_PEACH235_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 2401.5 | 2376.1 | 159.25 | 157.57 | DVP_P4-2: 514T595_SRT-SW | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220972 | GRANITE1 | 220953 | HOWARD12 | 1 | 230 | 232 | 772 | 1249.2 | 1211.7 | 161.82 | 156.96 | PJM_500_BG_P1_5011_SRT-A | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 2385.8 | 2360.2 | 158.21 | 156.51 | DVP_P4-2: 51482_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 235463 | 01TANEY | 1 | 138 | 227/201 | 317 | 549.4 | 496 | 173.32 | 156.45 | PECO_P1-2_5012_SRT-A | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 2385.8 | 2358.7 | 158.21 | 156.42 | AP_P1-2_PE-500-407T_SRT-W | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 2385.8 | 2358.7 | 158.21 | 156.42 | DVP_P1-2: LN 514_SRT-A | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204528 | 27GARDNERS | 200504 | 26CARLISLE | 1 | 115 | 226/227 | 190 | 280.1 | 296.9 | 147.4 | 156.24 | PN_P2-3_PN-115-0331-B_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204538 | 27STRABAN | 204529 | 27GERMANTN | 1 | 115 | 227 | 371 | 572.3 | 578 | 154.25 | 155.8 | PECO_P1-2_5012_SRT-A | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204514 | 27TMI | 204502 | 27JACKSON | 1 | 230 | 227 | 781 | 1149.1 | 1216.3 | 147.13 | 155.74 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204514 | 27TMI | 204502 | 27JACKSON | 1 | 230 | 227 | 781 | 1149.9 | 1215.3 | 147.23 | 155.6 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204514 | 27TMI | 204502 | 27JACKSON | 1 | 230 | 227 | 781 | 1149.8 | 1215.2 | 147.22 | 155.59 | PECO_P4_PEACH235_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 205912 | AD1-020 TAP | 204544 | 27LINCOLN | 1 | 115 | 227 | 334 | 522.6 | 519.3 | 156.47 | 155.47 | ME_P2-2_ME-115-0102A-8_SRT-A | Bus |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204539 | 27HUNTRSTN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 334 | 524.9 | 518 | 157.16 | 155.08 | ME_P2-2_ME-115-0102A-8_SRT-A | Bus |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 205912 | AD1-020 TAP | 204544 | 27LINCOLN | 1 | 115 | 227 | 334 | 520 | 517.7 | 155.67 | 154.99 | ME_P1-2_ME-115-062_SRT-A | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204528 | 27GARDNERS | 200504 | 26CARLISLE | 1 | 115 | 226/227 | 190 | 278.7 | 294.1 | 146.7 | 154.8 | PN_P2-3_PN-115-58B_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204528 | 27GARDNERS | 200504 | 26CARLISLE | 1 | 115 | 226/227 | 190 | 280 | 294 | 147.38 | 154.75 | PN_P2-2_PN-115-030_SRT-A | Bus |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204528 | 27GARDNERS | 200504 | 26CARLISLE | 1 | 115 | 226/227 | 190 | 280 | 294 | 147.38 | 154.75 | PN_P1-3_PN-115-040_SRT-A | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204539 | 27HUNTRSTN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 334 | 522.7 | 516.8 | 156.48 | 154.74 | ME_P1-2_ME-115-062_SRT-A | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 205912 | AD1-020 TAP | 204544 | 27LINCOLN | 1 | 115 | 227 | 334 | 512.5 | 516.8 | 153.45 | 154.72 | BG_P7_GRCTN_RAPHEL_SRT-A | Tower |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204528 | 27GARDNERS | 200504 | 26CARLISLE | 1 | 115 | 226/227 | 190 | 278.4 | 294 | 146.51 | 154.72 | PN_P1-2_PN-115-094_SRT-A | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204528 | 27GARDNERS | 200504 | 26CARLISLE | 1 | 115 | 226/227 | 190 | 277.1 | 293.9 | 145.82 | 154.67 | PN_P1-2_PN-115-094_A_SRT-A | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204539 | 27HUNTRSTN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 334 | 515.1 | 515.6 | 154.21 | 154.39 | BG_P7_GRCTN_RAPHEL_SRT-A | Tower |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 205912 | AD1-020 TAP | 204544 | 27LINCOLN | 1 | 115 | 227 | 334 | 511.4 | 514.8 | 153.11 | 154.14 | BG_P7_CNSTN_NWEST2_SRT-A | Tower |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 221058 | DOLFD T1 | 221055 | HARRIS1A | 1 | 115 | 232 | 201 | 309.5 | 309.8 | 153.97 | 154.11 | BG_P7_NWEST_GRNITE_SRT-A | Tower |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 235463 | 01TANEY | 1 | 138 | 227/201 | 317 | 489.5 | 488.3 | 154.43 | 154.03 | BG_P7_GRCTN_RAPHEL_SRT-A | Tower |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204539 | 27HUNTRSTN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 334 | 513.9 | 513.7 | 153.87 | 153.8 | BG_P7_CNSTN_NWEST2_SRT-A | Tower |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 203981 | AD2-062_POI | 235188 | 01GREENE | 1 | 138 | 226/201 | 317 | 514.3 | 487.4 | 162.25 | 153.77 | PJM_500_BG_P1_5011_SRT-A | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204538 | 27STRABAN | 204529 | 27GERMANTN | 1 | 115 | 227 | 371 | 564.9 | 570.3 | 152.28 | 153.72 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204538 | 27STRABAN | 204529 | 27GERMANTN | 1 | 115 | 227 | 371 | 564.9 | 570.3 | 152.27 | 153.72 | PECO_P4_PEACH235_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 1366.7 | 1366 | 153.74 | 153.65 | PJM_500_BG_P4_5_CNSTN_15_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204538 | 27STRABAN | 204529 | 27GERMANTN | 1 | 115 | 227 | 371 | 564.6 | 569.8 | 152.18 | 153.59 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 235463 | 01TANEY | 1 | 138 | 227/201 | 317 | 490.3 | 486.8 | 154.68 | 153.57 | AP_P1-2_PE-500-001_SRT-W | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 235463 | 01TANEY | 1 | 138 | 227/201 | 317 | 490.3 | 486.8 | 154.68 | 153.57 | AP_P1-2_WP-500-DRT17_SRT-W | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 235463 | 01TANEY | 1 | 138 | 227/201 | 317 | 542.1 | 486.5 | 171.02 | 153.46 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 235463 | 01TANEY | 1 | 138 | 227/201 | 317 | 542.1 | 486.4 | 171.01 | 153.44 | PECO_P4_PEACH235_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 235463 | 01TANEY | 1 | 138 | 227/201 | 317 | 488.3 | 486.3 | 154.03 | 153.4 | BG_P7_CNSTN_NWEST2_SRT-A | Tower |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 235463 | 01TANEY | 1 | 138 | 227/201 | 317 | 490 | 485.7 | 154.59 | 153.22 | AP_P1-2_PE-500-004_SRT-W | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 235463 | 01TANEY | 1 | 138 | 227/201 | 317 | 541.8 | 485.5 | 170.9 | 153.15 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200532 | 26ROXBURY | 203981 | AD2-062_POI | 1 | 138 | 226 | 317 | 513.8 | 485 | 162.07 | 152.99 | PJM_500_BG_P1_5011_SRT-A | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 203981 | AD2-062_POI | 235188 | 01GREENE | 1 | 138 | 226/201 | 317 | 510.8 | 483.3 | 161.15 | 152.48 | PJM_500_BG_P4_5_CNSTN_J_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 1349.6 | 1354.5 | 151.81 | 152.36 | BG_P7_GRCTN_CNSTN_SRT-A | Tower |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 203981 | AD2-062_POI | 235188 | 01GREENE | 1 | 138 | 226/201 | 317 | 510.3 | 483 | 160.97 | 152.35 | PEPCO_P4_PP40_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 205912 | AD1-020 TAP | 204544 | 27LINCOLN | 1 | 115 | 227 | 334 | 505 | 508.1 | 151.2 | 152.12 | BG_P7_NEAST_RPHLRD_SRT-A | Tower |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220973 | GRANITE6 | 220954 | HOWARD32 | 1 | 230 | 232 | 772 | 1207.1 | 1172.6 | 156.36 | 151.89 | PJM_500_BG_P1_5011_SRT-A | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204539 | 27HUNTRSTN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 334 | 507.6 | 507 | 151.96 | 151.78 | BG_P7_NEAST_RPHLRD_SRT-A | Tower |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 205912 | AD1-020 TAP | 204544 | 27LINCOLN | 1 | 115 | 227 | 334 | 507.5 | 506.7 | 151.94 | 151.7 | PN_P1-3_PN-115-118_SRT-A | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200532 | 26ROXBURY | 203981 | AD2-062_POI | 1 | 138 | 226 | 317 | 510.3 | 480.9 | 160.97 | 151.7 | PJM_500_BG_P4_5_CNSTN_J_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200532 | 26ROXBURY | 203981 | AD2-062_POI | 1 | 138 | 226 | 317 | 509.7 | 480.5 | 160.79 | 151.58 | PEPCO_P4_PP40_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204539 | 27HUNTRSTN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 334 | 510 | 505.7 | 152.7 | 151.42 | PN_P1-3_PN-115-118_SRT-A | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 235463 | 01TANEY | 1 | 138 | 227/201 | 317 | 481.1 | 479.4 | 151.76 | 151.25 | BG_P7_NEAST_RPHLRD_SRT-A | Tower |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 935.9 | 966.2 | 146.46 | 151.2 | PJM_500_BG_P1_5011_SRT-A | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220972 | GRANITE1 | 220953 | HOWARD12 | 1 | 230 | 232 | 772 | 1191.1 | 1160.5 | 154.29 | 150.33 | PEPCO_P4_PP40_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 925.4 | 927.3 | 149.99 | 150.29 | PECO_P1-2_5014_SRT-A | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 937.9 | 927.3 | 152 | 150.29 | PECO_P1-2_5014_SRT-A | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220972 | GRANITE1 | 1 | 230 | 232 | 829 | 1284.2 | 1244.3 | 154.91 | 150.1 | PJM_500_BG_P1_5011_SRT-A | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 221092 | FIVE.FOR | 221096 | ROCKRGE1 | 1 | 115 | 232 | 293 | 429 | 439.2 | 146.41 | 149.9 | BG_P7_GRCTN_RAPHEL_SRT-A | Tower |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204528 | 27GARDNERS | 200504 | 26CARLISLE | 1 | 115 | 226/227 | 190 | 272.7 | 284.1 | 143.51 | 149.54 | PN_P2-3_PN-230-0014-12_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220972 | GRANITE1 | 220953 | HOWARD12 | 1 | 230 | 232 | 772 | 1185.2 | 1154.2 | 153.52 | 149.51 | PJM_500_BG_P4_5_CNSTN_J_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204528 | 27GARDNERS | 200504 | 26CARLISLE | 1 | 115 | 226/227 | 190 | 264.1 | 283.7 | 138.98 | 149.34 | PJM_500_BG_P1_5011_SRT-A | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204529 | 27GERMANTN | 204530 | 27GERMANTN | 1 | 115/138 | 227 | 453 | 644.5 | 676.3 | 142.26 | 149.28 | PJM_500_BG_P1_5011_SRT-A | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204528 | 27GARDNERS | 200504 | 26CARLISLE | 1 | 115 | 226/227 | 190 | 272.7 | 283.3 | 143.5 | 149.12 | PN_P2-3_PN-230-0014-11_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204528 | 27GARDNERS | 200504 | 26CARLISLE | 1 | 115 | 226/227 | 190 | 272.7 | 283.3 | 143.5 | 149.11 | PN_P1-3_PN-230-020A_SRT-A | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208020 | MANO TR3 | 208019 | MANO | 1 | 230 | 229 | 793 | 1065.6 | 1182.4 | 134.37 | 149.11 | PECO_P1-2_5012_SRT-A | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204528 | 27GARDNERS | 200504 | 26CARLISLE | 1 | 115 | 226/227 | 190 | 272.5 | 283.3 | 143.43 | 149.1 | PN_P2-2_PN-115-031_SRT-A | Bus |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 521 | 778.7 | 775.6 | 149.47 | 148.87 | Base Case | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 521 | 766.3 | 775.6 | 147.08 | 148.87 | Base Case | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220980 | RAPHAEL | 220965 | NEAST339 | 1 | 230 | 232 | 1340 | 1990.8 | 1988.9 | 148.56 | 148.43 | BG_P1_2315_SRT-A | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208031 | MLWD TR2 | 1 | 230 | 229 | 911 | 1254.6 | 1351.2 | 137.72 | 148.32 | PECO_P1-2_5012_SRT-A | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208078 | SAKR | 208030 | MLWD TR1 | 1 | 230 | 229 | 903 | 1287.8 | 1338 | 142.61 | 148.17 | PECO_P4_PEACH245_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204529 | 27GERMANTN | 204530 | 27GERMANTN | 1 | 115/138 | 227 | 453 | 638.8 | 669.3 | 141.01 | 147.74 | PJM_500_BG_P4_5_CNSTN_J_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204529 | 27GERMANTN | 204530 | 27GERMANTN | 1 | 115/138 | 227 | 453 | 638.3 | 668.8 | 140.91 | 147.63 | PEPCO_P4_PP40_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 204538 | 27STRABAN | 1 | 115 | 227 | 371 | 533.8 | 547.6 | 143.88 | 147.59 | BG_P7_GRCTN_RAPHEL_SRT-A | Tower |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 920.6 | 910.6 | 149.21 | 147.59 | PECO_P4_PEACH205_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 908.2 | 910.6 | 147.19 | 147.59 | PECO_P4_PEACH205_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 908.7 | 941.8 | 142.2 | 147.39 | PJM_500_BG_P1_5011_SRT-A | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220973 | GRANITE6 | 1 | 230 | 232 | 829 | 1259.5 | 1221.2 | 151.93 | 147.31 | PJM_500_BG_P1_5011_SRT-A | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 207922 | BRIS | 204515 | 27YORKANA | 1 | 230 | 227/229 | 1031 | 1430.3 | 1518.6 | 138.73 | 147.29 | PECO_P1-2_5012_SRT-A | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 221057 | DOLFD T0 | 221056 | HARRIS0A | 1 | 115 | 232 | 201 | 295.4 | 295.5 | 146.99 | 147.02 | BG_P7_NWEST_GRNITE_SRT-A | Tower |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220980 | RAPHAEL | 220979 | NEAST317 | 1 | 230 | 232 | 1340 | 1971.1 | 1969.9 | 147.09 | 147.01 | BG_P1_2337_SRT-A | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 204538 | 27STRABAN | 1 | 115 | 227 | 371 | 532.5 | 545.4 | 143.54 | 147 | BG_P7_CNSTN_NWEST2_SRT-A | Tower |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220980 | RAPHAEL | 220965 | NEAST339 | 1 | 230 | 232 | 1340 | 1968.3 | 1968.5 | 146.89 | 146.91 | BG_P4_5_NEAST_17_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220980 | RAPHAEL | 220965 | NEAST339 | 1 | 230 | 232 | 1340 | 1970.4 | 1968.5 | 147.05 | 146.91 | BG_P4_5_NEAST_15_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 2239.8 | 2211.7 | 148.53 | 146.66 | AP_P2-3_PE-500-019C_SRT-W | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 207922 | BRIS | 204515 | 27YORKANA | 1 | 230 | 227/229 | 1031 | 1422.7 | 1511.6 | 137.99 | 146.62 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204528 | 27GARDNERS | 200504 | 26CARLISLE | 1 | 115 | 226/227 | 190 | 259.3 | 278.3 | 136.48 | 146.47 | PJM_500_BG_P4_5_CNSTN_J_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 205912 | AD1-020 TAP | 204544 | 27LINCOLN | 1 | 115 | 227 | 334 | 492.3 | 488.5 | 147.41 | 146.25 | AP_P2-2_WP-500-DRT16_SRT-W | Bus |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 521 | 751.3 | 761.4 | 144.19 | 146.15 | Base Case | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220973 | GRANITE6 | 220954 | HOWARD32 | 1 | 230 | 232 | 772 | 1154.8 | 1127.7 | 149.58 | 146.07 | PEPCO_P4_PP40_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204539 | 27HUNTRSTN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 334 | 494.9 | 487.4 | 148.17 | 145.94 | AP_P2-2_WP-500-DRT16_SRT-W | Bus |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 203981 | AD2-062_POI | 235188 | 01GREENE | 1 | 138 | 226/201 | 250 | 366.1 | 364.3 | 146.43 | 145.71 | Base Case | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 207922 | BRIS | 204515 | 27YORKANA | 1 | 230 | 227/229 | 1031 | 1419 | 1501.8 | 137.63 | 145.67 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 207922 | BRIS | 204515 | 27YORKANA | 1 | 230 | 227/229 | 1031 | 1418.8 | 1501.8 | 137.62 | 145.66 | PECO_P4_PEACH235_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220980 | RAPHAEL | 220979 | NEAST317 | 1 | 230 | 232 | 1340 | 1952.2 | 1951.1 | 145.69 | 145.6 | BG_P4_5_NEAST_37_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220980 | RAPHAEL | 220979 | NEAST317 | 1 | 230 | 232 | 1340 | 1952.2 | 1951.1 | 145.69 | 145.6 | BG_P4_5_NEAST_39_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 205912 | AD1-020 TAP | 204544 | 27LINCOLN | 1 | 115 | 227 | 334 | 488.1 | 486.2 | 146.13 | 145.55 | BG_P7_GRNITE_HIRDG_SRT-A | Tower |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204514 | 27TMI | 204502 | 27JACKSON | 1 | 230 | 227 | 781 | 1090.7 | 1135.5 | 139.65 | 145.39 | PECO_P4_PEACH245_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220973 | GRANITE6 | 220954 | HOWARD32 | 1 | 230 | 232 | 772 | 1149.6 | 1122.1 | 148.91 | 145.35 | PJM_500_BG_P4_5_CNSTN_J_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204539 | 27HUNTRSTN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 334 | 490.6 | 485.1 | 146.89 | 145.25 | BG_P7_GRNITE_HIRDG_SRT-A | Tower |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220972 | GRANITE1 | 1 | 230 | 232 | 829 | 1235.2 | 1202.5 | 149 | 145.05 | PEPCO_P4_PP40_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 204538 | 27STRABAN | 1 | 115 | 227 | 371 | 525.4 | 537.7 | 141.61 | 144.94 | BG_P7_NEAST_RPHLRD_SRT-A | Tower |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 205912 | AD1-020 TAP | 204544 | 27LINCOLN | 1 | 115 | 227 | 334 | 485.2 | 483.7 | 145.26 | 144.82 | AP_P2-2_WP-138-074_SRT-A | Bus |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200532 | 26ROXBURY | 203981 | AD2-062_POI | 1 | 138 | 226 | 250 | 365.5 | 362 | 146.2 | 144.79 | Base Case | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208031 | MLWD TR2 | 1 | 230 | 229 | 911 | 1226.7 | 1318 | 134.66 | 144.68 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 205912 | AD1-020 TAP | 204544 | 27LINCOLN | 1 | 115 | 227 | 334 | 485.2 | 483 | 145.26 | 144.61 | BG_P7_NWEST_GRNITE_SRT-A | Tower |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204539 | 27HUNTRSTN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 334 | 487.7 | 482.8 | 146.03 | 144.55 | AP_P2-2_WP-138-074_SRT-A | Bus |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220972 | GRANITE1 | 1 | 230 | 232 | 829 | 1230.5 | 1197.6 | 148.44 | 144.47 | PJM_500_BG_P4_5_CNSTN_J_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 235463 | 01TANEY | 1 | 138 | 227/201 | 317 | 462 | 457.9 | 145.75 | 144.46 | BG_P7_GRNITE_HIRDG_SRT-A | Tower |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 235463 | 01TANEY | 1 | 138 | 227/201 | 317 | 464.7 | 457.8 | 146.61 | 144.4 | AP_P2-2_WP-500-DRT16_SRT-W | Bus |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208020 | MANO TR3 | 208019 | MANO | 1 | 230 | 229 | 793 | 1040 | 1144.5 | 131.15 | 144.33 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208020 | MANO TR3 | 208019 | MANO | 1 | 230 | 229 | 793 | 1040 | 1144.5 | 131.14 | 144.33 | PECO_P4_PEACH235_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204539 | 27HUNTRSTN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 334 | 487.7 | 482 | 146.02 | 144.31 | BG_P7_NWEST_GRNITE_SRT-A | Tower |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 204538 | 27STRABAN | 1 | 115 | 227 | 371 | 526.7 | 534.7 | 141.96 | 144.13 | PN_P1-3_PN-115-118_SRT-A | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 204538 | 27STRABAN | 1 | 115 | 227 | 371 | 526.7 | 534.7 | 141.96 | 144.13 | AP_P1-2_WP-138-340BT_SRT-A | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208031 | MLWD TR2 | 1 | 230 | 229 | 911 | 1227.1 | 1312.7 | 134.7 | 144.1 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208031 | MLWD TR2 | 1 | 230 | 229 | 911 | 1227.1 | 1312.7 | 134.69 | 144.09 | PECO_P4_PEACH235_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 204538 | 27STRABAN | 1 | 115 | 227 | 371 | 525.8 | 534.5 | 141.73 | 144.06 | AP_P1-2_WP-138-340AT_SRT-A | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 235463 | 01TANEY | 1 | 138 | 227/201 | 317 | 458.8 | 456.5 | 144.73 | 144.02 | AP_P2-2_WP-138-074_SRT-A | Bus |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 872.5 | 886.8 | 141.41 | 143.73 | BG_P7_GRCTN_CNSTN_SRT-A | Tower |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 884.9 | 886.8 | 143.42 | 143.73 | BG_P7_GRCTN_CNSTN_SRT-A | Tower |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208020 | MANO TR3 | 208019 | MANO | 1 | 230 | 229 | 793 | 1026.2 | 1136.9 | 129.41 | 143.37 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 205912 | AD1-020 TAP | 204544 | 27LINCOLN | 1 | 115 | 227 | 334 | 482.6 | 478.7 | 144.5 | 143.32 | ME_P2-2_ME-115-002T_SRT-A | Bus |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204538 | 27STRABAN | 204529 | 27GERMANTN | 1 | 115 | 227 | 371 | 512.4 | 531 | 138.1 | 143.12 | BG_P7_GRCTN_RAPHEL_SRT-A | Tower |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204539 | 27HUNTRSTN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 334 | 485.1 | 477.6 | 145.24 | 143 | ME_P2-2_ME-115-002T_SRT-A | Bus |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 910.4 | 913.2 | 142.47 | 142.9 | PECO_P1-2_5014_SRT-A | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 205912 | AD1-020 TAP | 204544 | 27LINCOLN | 1 | 115 | 227 | 334 | 481.8 | 477.2 | 144.24 | 142.86 | AP_P2-2_WP-500-DRT17_SRT-W | Bus |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 235463 | 01TANEY | 1 | 138 | 227/201 | 317 | 456.7 | 452.7 | 144.05 | 142.8 | BG_P7_NWEST_GRNITE_SRT-A | Tower |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204539 | 27HUNTRSTN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 334 | 484.3 | 476.2 | 145 | 142.56 | AP_P2-2_WP-500-DRT17_SRT-W | Bus |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204538 | 27STRABAN | 204529 | 27GERMANTN | 1 | 115 | 227 | 371 | 511.1 | 528.8 | 137.76 | 142.53 | BG_P7_CNSTN_NWEST2_SRT-A | Tower |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 878.4 | 879.4 | 142.36 | 142.52 | BG_P1_CNSTN_500-4_SRT-A | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 865.9 | 879.4 | 140.34 | 142.52 | BG_P1_CNSTN_500-4_SRT-A | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 865.6 | 879 | 140.29 | 142.47 | BG_P1_CNSTN_500-2_SRT-A | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 878 | 879 | 142.31 | 142.47 | BG_P1_CNSTN_500-2_SRT-A | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220973 | GRANITE6 | 1 | 230 | 232 | 829 | 1211.3 | 1180.1 | 146.12 | 142.35 | PEPCO_P4_PP40_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220973 | GRANITE6 | 1 | 230 | 232 | 829 | 1206.9 | 1175.5 | 145.59 | 141.8 | PJM_500_BG_P4_5_CNSTN_J_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 235463 | 01TANEY | 1 | 138 | 227/201 | 317 | 454.3 | 449.1 | 143.31 | 141.69 | ME_P2-2_ME-115-002T_SRT-A | Bus |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 235463 | 01TANEY | 1 | 138 | 227/201 | 317 | 454.9 | 449.1 | 143.51 | 141.67 | AP_P2-2_WP-500-DRT17_SRT-W | Bus |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 521 | 724 | 737.6 | 138.97 | 141.58 | Base Case | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 235463 | 01TANEY | 1 | 138 | 227/201 | 317 | 452.4 | 446.9 | 142.72 | 140.99 | AP_P2-2_WP-500-DRT15_SRT-W | Bus |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200512 | 26LEWISTWN | 200519 | 26REED TAP | 1 | 115 | 226 | 271 | 357.9 | 382 | 132.06 | 140.94 | PECO_P1-2_5012_SRT-A | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200025 | W CHAPEL | 1 | 500 | 225 | 1732 | 2479.8 | 2440.4 | 143.18 | 140.9 | PEPCO_P4_PP41_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200512 | 26LEWISTWN | 200519 | 26REED TAP | 1 | 115 | 226 | 271 | 357.3 | 381.7 | 131.83 | 140.87 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200512 | 26LEWISTWN | 200519 | 26REED TAP | 1 | 115 | 226 | 271 | 357.4 | 381.5 | 131.89 | 140.78 | PECO_P4_PEACH235_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200512 | 26LEWISTWN | 200519 | 26REED TAP | 1 | 115 | 226 | 271 | 357.4 | 381.5 | 131.89 | 140.77 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204538 | 27STRABAN | 204529 | 27GERMANTN | 1 | 115 | 227 | 371 | 503.9 | 521.2 | 135.83 | 140.49 | BG_P7_NEAST_RPHLRD_SRT-A | Tower |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 221092 | FIVE.FOR | 221096 | ROCKRGE1 | 1 | 115 | 232 | 293 | 399.2 | 411.3 | 136.24 | 140.39 | BG_P7_NEAST_RPHLRD_SRT-A | Tower |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 893.2 | 896.5 | 139.77 | 140.29 | PECO_P4_PEACH205_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 207922 | BRIS | 207923 | BRISREAC | RX | 230 | 229 | 676 | 886.6 | 947.9 | 131.15 | 140.23 | PECO_P1-2_5012_SRT-A | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 207923 | BRISREAC | 208132 | WHEM TR1 | 1 | 230 | 229 | 676 | 886.6 | 947.9 | 131.15 | 140.23 | PECO_P1-2_5012_SRT-A | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 203981 | AD2-062_POI | 235188 | 01GREENE | 1 | 138 | 226/201 | 317 | 496 | 443.3 | 156.46 | 139.86 | PECO_P1-2_5012_SRT-A | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204538 | 27STRABAN | 204529 | 27GERMANTN | 1 | 115 | 227 | 371 | 505.2 | 518.2 | 136.18 | 139.68 | PN_P1-3_PN-115-118_SRT-A | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204538 | 27STRABAN | 204529 | 27GERMANTN | 1 | 115 | 227 | 371 | 505.2 | 518.2 | 136.18 | 139.67 | AP_P1-2_WP-138-340BT_SRT-A | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204538 | 27STRABAN | 204529 | 27GERMANTN | 1 | 115 | 227 | 371 | 504.4 | 517.9 | 135.95 | 139.6 | AP_P1-2_WP-138-340AT_SRT-A | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 207922 | BRIS | 207923 | BRISREAC | RX | 230 | 229 | 676 | 879.4 | 942.2 | 130.08 | 139.37 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 207923 | BRISREAC | 208132 | WHEM TR1 | 1 | 230 | 229 | 676 | 879.4 | 942.2 | 130.08 | 139.37 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200066 | PCHBTM1N | 200065 | PCHBTM2S | 2 | 500 | 225 | 3022 | 4347.8 | 4210.4 | 143.87 | 139.32 | PECO_P4_PEACH205_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 883.2 | 889.5 | 138.21 | 139.21 | PECO_P1-2_5014_SRT-A | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200532 | 26ROXBURY | 203981 | AD2-062_POI | 1 | 138 | 226 | 317 | 495.4 | 441 | 156.29 | 139.11 | PECO_P1-2_5012_SRT-A | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 204538 | 27STRABAN | 1 | 115 | 227 | 371 | 506.3 | 513 | 136.46 | 138.28 | BG_P7_GRNITE_HIRDG_SRT-A | Tower |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 203981 | AD2-062_POI | 235188 | 01GREENE | 1 | 138 | 226/201 | 317 | 492.6 | 438.3 | 155.4 | 138.27 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 203981 | AD2-062_POI | 235188 | 01GREENE | 1 | 138 | 226/201 | 317 | 492.6 | 438.3 | 155.39 | 138.27 | PECO_P4_PEACH235_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 204538 | 27STRABAN | 1 | 115 | 227 | 371 | 509 | 512.7 | 137.2 | 138.2 | AP_P2-2_WP-500-DRT16_SRT-W | Bus |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 207923 | BRISREAC | 208132 | WHEM TR1 | 1 | 230 | 229 | 676 | 875.6 | 933.1 | 129.52 | 138.04 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 207922 | BRIS | 207923 | BRISREAC | RX | 230 | 229 | 676 | 875.6 | 933.1 | 129.52 | 138.04 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 207922 | BRIS | 207923 | BRISREAC | RX | 230 | 229 | 676 | 875.5 | 933.1 | 129.51 | 138.03 | PECO_P4_PEACH235_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 207923 | BRISREAC | 208132 | WHEM TR1 | 1 | 230 | 229 | 676 | 875.5 | 933.1 | 129.51 | 138.03 | PECO_P4_PEACH235_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 203981 | AD2-062_POI | 235188 | 01GREENE | 1 | 138 | 226/201 | 317 | 492.2 | 437.5 | 155.27 | 138.01 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 204538 | 27STRABAN | 1 | 115 | 227 | 371 | 503.1 | 510.3 | 135.6 | 137.56 | AP_P2-2_WP-138-074_SRT-A | Bus |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200532 | 26ROXBURY | 203981 | AD2-062_POI | 1 | 138 | 226 | 317 | 492.1 | 435.9 | 155.22 | 137.52 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200532 | 26ROXBURY | 203981 | AD2-062_POI | 1 | 138 | 226 | 317 | 492 | 435.9 | 155.22 | 137.52 | PECO_P4_PEACH235_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200532 | 26ROXBURY | 203981 | AD2-062_POI | 1 | 138 | 226 | 317 | 491.7 | 435.1 | 155.1 | 137.26 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208031 | MLWD TR2 | 208020 | MANO TR3 | 1 | 230 | 229 | 903 | 1132.7 | 1237.8 | 125.43 | 137.07 | PECO_P1-2_5012_SRT-A | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 207922 | BRIS | 204515 | 27YORKANA | 1 | 230 | 227/229 | 1031 | 1361.3 | 1412 | 132.04 | 136.95 | PECO_P4_PEACH245_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 865.9 | 872.8 | 135.51 | 136.59 | PECO_P4_PEACH205_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220963 | CONASTON | 220962 | NWEST311 | 1 | 230 | 232 | 1381 | 1828.9 | 1886.1 | 132.43 | 136.58 | PJM_500_BG_P1_5011_SRT-A | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 204538 | 27STRABAN | 1 | 115 | 227 | 371 | 500.9 | 506.6 | 135.02 | 136.54 | BG_P7_NWEST_GRNITE_SRT-A | Tower |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 857.4 | 872.3 | 134.18 | 136.5 | BG_P7_GRCTN_CNSTN_SRT-A | Tower |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204539 | 27HUNTRSTN | 204550 | 27ORRTANNA | 1 | 115 | 227 | 264 | 360.2 | 360.1 | 136.43 | 136.39 | ME_P1-2_ME-115-068_SRT-A | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204539 | 27HUNTRSTN | 204550 | 27ORRTANNA | 1 | 115 | 227 | 264 | 362 | 359.5 | 137.1 | 136.16 | ME_P1-2_ME-115-067_SRT-A | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220963 | CONASTON | 220961 | NWEST326 | 1 | 230 | 232 | 1381 | 1823 | 1880.1 | 132.01 | 136.14 | PJM_500_BG_P1_5011_SRT-A | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200519 | 26REED TAP | 200522 | 26SHADE GP | 1 | 115 | 226 | 271 | 336.9 | 368.1 | 124.32 | 135.83 | PECO_P1-2_5012_SRT-A | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200519 | 26REED TAP | 200522 | 26SHADE GP | 1 | 115 | 226 | 271 | 336.3 | 367.9 | 124.1 | 135.75 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200519 | 26REED TAP | 200522 | 26SHADE GP | 1 | 115 | 226 | 271 | 336.4 | 367.6 | 124.15 | 135.66 | PECO_P4_PEACH235_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200519 | 26REED TAP | 200522 | 26SHADE GP | 1 | 115 | 226 | 271 | 336.4 | 367.6 | 124.15 | 135.66 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 204538 | 27STRABAN | 1 | 115 | 227 | 371 | 498.5 | 503.1 | 134.37 | 135.6 | ME_P2-2_ME-115-002T_SRT-A | Bus |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208031 | MLWD TR2 | 1 | 230 | 229 | 911 | 1172 | 1235.1 | 128.65 | 135.57 | PECO_P4_PEACH245_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 204538 | 27STRABAN | 1 | 115 | 227 | 371 | 499.2 | 502.9 | 134.55 | 135.56 | AP_P2-2_WP-500-DRT17_SRT-W | Bus |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 850.9 | 865.3 | 133.16 | 135.42 | BG_P1_CNSTN_500-4_SRT-A | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 850.6 | 865 | 133.11 | 135.36 | BG_P1_CNSTN_500-2_SRT-A | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223938 | DICKH230 | 223937 | DICK 230 | 1 | 230 | 233 | 793 | 1088 | 1072.9 | 137.2 | 135.3 | AP_P1-2_PE-500-407T_SRT-W | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223938 | DICKH230 | 223937 | DICK 230 | 2 | 230 | 233 | 793 | 1088 | 1072.9 | 137.2 | 135.3 | DVP_P1-2: LN 514_SRT-A | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223938 | DICKH230 | 223937 | DICK 230 | 2 | 230 | 233 | 793 | 1088 | 1072.9 | 137.2 | 135.3 | AP_P1-2_PE-500-407T_SRT-W | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223938 | DICKH230 | 223937 | DICK 230 | 1 | 230 | 233 | 793 | 1088 | 1072.9 | 137.2 | 135.3 | DVP_P1-2: LN 514_SRT-A | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 204538 | 27STRABAN | 1 | 115 | 227 | 371 | 496.7 | 500.7 | 133.88 | 134.97 | AP_P2-2_WP-500-DRT15_SRT-W | Bus |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200512 | 26LEWISTWN | 200519 | 26REED TAP | 1 | 115 | 226 | 271 | 349.8 | 364.9 | 129.07 | 134.66 | PECO_P4_PEACH245_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223938 | DICKH230 | 223937 | DICK 230 | 1 | 230 | 233 | 793 | 1081.6 | 1066.4 | 136.4 | 134.48 | DVP_P4-2: 514T595_SRT-SW | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223938 | DICKH230 | 223937 | DICK 230 | 2 | 230 | 233 | 793 | 1081.6 | 1066.4 | 136.4 | 134.48 | DVP_P4-2: 514T595_SRT-SW | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208020 | MANO TR3 | 208019 | MANO | 1 | 230 | 229 | 793 | 983.7 | 1064.2 | 124.05 | 134.2 | PECO_P4_PEACH245_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204538 | 27STRABAN | 204529 | 27GERMANTN | 1 | 115 | 227 | 371 | 484.8 | 496.5 | 130.68 | 133.84 | BG_P7_GRNITE_HIRDG_SRT-A | Tower |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204538 | 27STRABAN | 204529 | 27GERMANTN | 1 | 115 | 227 | 371 | 487.6 | 496.2 | 131.42 | 133.76 | AP_P2-2_WP-500-DRT16_SRT-W | Bus |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223938 | DICKH230 | 223937 | DICK 230 | 1 | 230 | 233 | 793 | 1074.4 | 1059.3 | 135.49 | 133.58 | DVP_P4-2: 51482_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223938 | DICKH230 | 223937 | DICK 230 | 2 | 230 | 233 | 793 | 1074.4 | 1059.3 | 135.49 | 133.58 | DVP_P4-2: 51482_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204538 | 27STRABAN | 204529 | 27GERMANTN | 1 | 115 | 227 | 371 | 481.6 | 493.8 | 129.82 | 133.11 | AP_P2-2_WP-138-074_SRT-A | Bus |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208031 | MLWD TR2 | 208020 | MANO TR3 | 1 | 230 | 229 | 903 | 1106.8 | 1201.9 | 122.57 | 133.1 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208031 | MLWD TR2 | 208020 | MANO TR3 | 1 | 230 | 229 | 903 | 1106.8 | 1201.9 | 122.57 | 133.1 | PECO_P4_PEACH235_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223938 | DICKH230 | 223937 | DICK 230 | 1 | 230 | 233 | 793 | 1076.2 | 1053.6 | 135.72 | 132.87 | PEPCO_P1_PP2_SRT-A | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223938 | DICKH230 | 223937 | DICK 230 | 2 | 230 | 233 | 793 | 1076.2 | 1053.6 | 135.72 | 132.87 | PEPCO_P1_PP1_SRT-A | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 830.2 | 847.7 | 129.92 | 132.66 | BG_P7_GRCTN_CNSTN_SRT-A | Tower |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208394 | PPL-BGE TIE | 221092 | FIVE.FOR | 1 | 115 | 229/232 | 247 | 320.3 | 327.6 | 129.69 | 132.64 | PL_05_P71_000906_SRT-A | Tower |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204539 | 27HUNTRSTN | 204550 | 27ORRTANNA | 1 | 115 | 227 | 264 | 347.5 | 350.1 | 131.62 | 132.63 | ME_P2-3_ME-115-035A_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220963 | CONASTON | 220962 | NWEST311 | 1 | 230 | 232 | 1381 | 1773.3 | 1825.3 | 128.41 | 132.17 | PEPCO_P4_PP40_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204538 | 27STRABAN | 204529 | 27GERMANTN | 1 | 115 | 227 | 371 | 479.5 | 490.1 | 129.24 | 132.1 | BG_P7_NWEST_GRNITE_SRT-A | Tower |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204693 | 27BOONETOWN | 204512 | 27S.RDG | 1 | 230 | 227 | 607 | 715 | 800.5 | 117.8 | 131.87 | PECO_P1-2_5012_SRT-A | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220963 | CONASTON | 220962 | NWEST311 | 1 | 230 | 232 | 1381 | 1769.2 | 1820.5 | 128.11 | 131.82 | PJM_500_BG_P4_5_CNSTN_J_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220963 | CONASTON | 220961 | NWEST326 | 1 | 230 | 232 | 1381 | 1767.6 | 1819.5 | 128 | 131.75 | PEPCO_P4_PP40_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 823.6 | 841.8 | 128.9 | 131.74 | BG_P1_CNSTN_500-4_SRT-A | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 911 | 1176.6 | 1200.2 | 129.16 | 131.74 | BG_P7_GRCTN_CNSTN_SRT-A | Tower |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 823.3 | 841.5 | 128.85 | 131.69 | BG_P1_CNSTN_500-2_SRT-A | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 809.2 | 811.1 | 131.15 | 131.46 | PJM_500_BG_P2_CNSTN_230-S_SRT-A | Bus |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 796.7 | 811.1 | 129.13 | 131.46 | PJM_500_BG_P2_CNSTN_230-S_SRT-A | Bus |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220963 | CONASTON | 220961 | NWEST326 | 1 | 230 | 232 | 1381 | 1763.7 | 1814.9 | 127.71 | 131.42 | PJM_500_BG_P4_5_CNSTN_J_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 808.9 | 810.8 | 131.1 | 131.41 | PJM_500_BG_P2_CNSTN_230-N_SRT-A | Bus |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 796.4 | 810.8 | 129.08 | 131.41 | PJM_500_BG_P2_CNSTN_230-N_SRT-A | Bus |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 911 | 1185.2 | 1197.1 | 130.1 | 131.4 | PJM_500_BG_P4_5_CNSTN_15_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204529 | 27GERMANTN | 204530 | 27GERMANTN | 1 | 115/138 | 227 | 347 | 442.3 | 455.8 | 127.47 | 131.37 | Base Case | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208395 | FARO FF | 208393 | FARO DC TIE | 2 | 69/115 | 229 | 120 | 162.1 | 157.4 | 135.08 | 131.17 | PL_05_P71_000906_SRT-A | Tower |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208395 | FARO FF | 208393 | FARO DC TIE | 1 | 69/115 | 229 | 120 | 162.1 | 157.4 | 135.07 | 131.17 | PL_05_P71_000906_SRT-A | Tower |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204538 | 27STRABAN | 204529 | 27GERMANTN | 1 | 115 | 227 | 371 | 477.1 | 486.6 | 128.59 | 131.16 | ME_P2-2_ME-115-002T_SRT-A | Bus |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 2 | 500/230 | 225/232 | 2168 | 2726.6 | 2843.2 | 125.77 | 131.14 | PJM_500_BG_P1_5011_SRT-A | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204539 | 27HUNTRSTN | 204550 | 27ORRTANNA | 1 | 115 | 227 | 264 | 347.1 | 346.2 | 131.46 | 131.12 | ME_P2-3_ME-115-013B_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204538 | 27STRABAN | 204529 | 27GERMANTN | 1 | 115 | 227 | 371 | 477.8 | 486.4 | 128.77 | 131.11 | AP_P2-2_WP-500-DRT17_SRT-W | Bus |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204539 | 27HUNTRSTN | 204550 | 27ORRTANNA | 1 | 115 | 227 | 264 | 346.5 | 345.5 | 131.24 | 130.88 | ME_P2-3_ME-115-013A_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 2 | 500/230 | 225/232 | 2168 | 2720.6 | 2836.9 | 125.49 | 130.85 | PEPCO_P4_PP40_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204539 | 27HUNTRSTN | 204550 | 27ORRTANNA | 1 | 115 | 227 | 264 | 343.1 | 345.4 | 129.97 | 130.83 | ME_P2-3_ME-115-035B_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 1 | 500/230 | 225/232 | 2168 | 2719.7 | 2836 | 125.45 | 130.81 | PJM_500_BG_P1_5011_SRT-A | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 2 | 500/230 | 225/232 | 2168 | 2718.7 | 2835.4 | 125.4 | 130.79 | PJM_500_BG_P4_5_CNSTN_J_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200504 | 26CARLISLE | 200520 | 26ROXBURY | 1 | 115 | 226 | 190 | 230.4 | 248.4 | 121.29 | 130.72 | PN_P2-3_PN-115-58B_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200504 | 26CARLISLE | 200520 | 26ROXBURY | 1 | 115 | 226 | 190 | 231.7 | 248.3 | 121.94 | 130.68 | PN_P2-2_PN-115-030_SRT-A | Bus |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200504 | 26CARLISLE | 200520 | 26ROXBURY | 1 | 115 | 226 | 190 | 231.7 | 248.3 | 121.94 | 130.68 | PN_P1-3_PN-115-040_SRT-A | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200504 | 26CARLISLE | 200520 | 26ROXBURY | 1 | 115 | 226 | 190 | 230.1 | 248.2 | 121.1 | 130.64 | PN_P1-2_PN-115-094_SRT-A | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 1 | 500/230 | 225/232 | 2168 | 2714.8 | 2830.9 | 125.22 | 130.58 | PEPCO_P4_PP40_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204538 | 27STRABAN | 204529 | 27GERMANTN | 1 | 115 | 227 | 371 | 475.3 | 484.3 | 128.1 | 130.53 | AP_P2-2_WP-500-DRT15_SRT-W | Bus |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200504 | 26CARLISLE | 200520 | 26ROXBURY | 1 | 115 | 226 | 190 | 228.8 | 248 | 120.42 | 130.52 | PN_P1-2_PN-115-094_A_SRT-A | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208031 | MLWD TR2 | 208020 | MANO TR3 | 1 | 230 | 229 | 903 | 1078.6 | 1178.2 | 119.45 | 130.47 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 1 | 500/230 | 225/232 | 2168 | 2711.8 | 2828.3 | 125.08 | 130.45 | PJM_500_BG_P4_5_CNSTN_J_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204693 | 27BOONETOWN | 204512 | 27S.RDG | 1 | 230 | 227 | 607 | 705.8 | 791.8 | 116.28 | 130.45 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220980 | RAPHAEL | 220965 | NEAST339 | 1 | 230 | 232 | 1340 | 1758.2 | 1746.6 | 131.21 | 130.34 | PJM_500_BG_P1_5011_SRT-A | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 207922 | BRIS | 207923 | BRISREAC | RX | 230 | 229 | 676 | 841.1 | 879.4 | 124.43 | 130.09 | PECO_P4_PEACH245_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 207923 | BRISREAC | 208132 | WHEM TR1 | 1 | 230 | 229 | 676 | 841.1 | 879.4 | 124.43 | 130.09 | PECO_P4_PEACH245_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204693 | 27BOONETOWN | 204512 | 27S.RDG | 1 | 230 | 227 | 607 | 705.1 | 788.8 | 116.17 | 129.96 | PECO_P4_PEACH235_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204693 | 27BOONETOWN | 204512 | 27S.RDG | 1 | 230 | 227 | 607 | 705 | 788.6 | 116.14 | 129.92 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220980 | RAPHAEL | 220965 | NEAST339 | 1 | 230 | 232 | 1340 | 1752.1 | 1740.9 | 130.75 | 129.91 | PEPCO_P4_PP40_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 1164 | 1154.9 | 130.94 | 129.9 | PL_04_P12_000260_SRT-A | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200018 | CHALK PT | 200301 | X4-035 TAP | 1 | 500 | 225 | 1732 | 2255.5 | 2248.8 | 130.23 | 129.84 | PEPCO_P4_PP41_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220980 | RAPHAEL | 220965 | NEAST339 | 1 | 230 | 232 | 1340 | 1751.1 | 1739.5 | 130.68 | 129.82 | PJM_500_BG_P4_5_CNSTN_J_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 801.9 | 800.9 | 129.97 | 129.81 | PL_05_P71_000906_SRT-A | Tower |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 789.5 | 800.9 | 127.96 | 129.81 | PL_05_P71_000906_SRT-A | Tower |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200519 | 26REED TAP | 200522 | 26SHADE GP | 1 | 115 | 226 | 271 | 328.8 | 351.3 | 121.33 | 129.62 | PECO_P4_PEACH245_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223938 | DICKH230 | 223937 | DICK 230 | 1 | 230 | 233 | 793 | 1039.8 | 1019.3 | 131.12 | 128.53 | PEPCO_P4_PP19_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200512 | 26LEWISTWN | 200519 | 26REED TAP | 1 | 115 | 226 | 271 | 339.2 | 348.1 | 125.15 | 128.45 | PJM_500_BG_P1_5011_SRT-A | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200512 | 26LEWISTWN | 200519 | 26REED TAP | 1 | 115 | 226 | 271 | 338.7 | 347.7 | 124.98 | 128.28 | PJM_500_BG_P4_5_CNSTN_J_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200520 | 26ROXBURY | 200532 | 26ROXBURY | 2 | 115/138 | 226 | 435 | 493.3 | 557.1 | 113.41 | 128.07 | PJM_500_BG_P1_5011_SRT-A | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 778.1 | 788.4 | 126.12 | 127.78 | PL_05_P22_000674_SRT-A | Bus |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 790.6 | 788.4 | 128.13 | 127.78 | PL_05_P22_000674_SRT-A | Bus |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 203981 | AD2-062_POI | 235188 | 01GREENE | 1 | 138 | 226/201 | 317 | 416.7 | 403.9 | 131.45 | 127.41 | AP_P1-2_PE-500-004_SRT-W | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 203981 | AD2-062_POI | 235188 | 01GREENE | 1 | 138 | 226/201 | 317 | 416.7 | 403.9 | 131.45 | 127.41 | AP_P1-2_WP-500-006_SRT-A | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 203981 | AD2-062_POI | 235188 | 01GREENE | 1 | 138 | 226/201 | 317 | 413.4 | 403 | 130.41 | 127.13 | AP_P1-2_PE-500-001_SRT-W | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208394 | PPL-BGE TIE | 221092 | FIVE.FOR | 1 | 115 | 229/232 | 247 | 309.1 | 313.5 | 125.15 | 126.93 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208394 | PPL-BGE TIE | 221092 | FIVE.FOR | 1 | 115 | 229/232 | 247 | 309 | 313.3 | 125.09 | 126.84 | PECO_P4_PEACH235_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208394 | PPL-BGE TIE | 221092 | FIVE.FOR | 1 | 115 | 229/232 | 247 | 309 | 313.3 | 125.09 | 126.84 | PECO_P1-2_5012_SRT-A | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208394 | PPL-BGE TIE | 221092 | FIVE.FOR | 1 | 115 | 229/232 | 247 | 309 | 313.3 | 125.09 | 126.84 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200532 | 26ROXBURY | 203981 | AD2-062_POI | 1 | 138 | 226 | 317 | 416.1 | 401.5 | 131.26 | 126.67 | AP_P1-2_PE-500-004_SRT-W | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200532 | 26ROXBURY | 203981 | AD2-062_POI | 1 | 138 | 226 | 317 | 416.1 | 401.5 | 131.26 | 126.67 | AP_P1-2_WP-500-006_SRT-A | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200520 | 26ROXBURY | 200532 | 26ROXBURY | 2 | 115/138 | 226 | 435 | 487 | 550.7 | 111.95 | 126.61 | PJM_500_BG_P4_5_CNSTN_J_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200504 | 26CARLISLE | 200520 | 26ROXBURY | 1 | 115 | 226 | 190 | 211.9 | 240.3 | 111.53 | 126.47 | PN_P2-3_PN-115-0331-B_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200520 | 26ROXBURY | 200532 | 26ROXBURY | 2 | 115/138 | 226 | 435 | 486.4 | 550 | 111.81 | 126.44 | PEPCO_P4_PP40_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200532 | 26ROXBURY | 203981 | AD2-062_POI | 1 | 138 | 226 | 317 | 412.8 | 400.6 | 130.22 | 126.37 | AP_P1-2_PE-500-001_SRT-W | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220980 | RAPHAEL | 220979 | NEAST317 | 1 | 230 | 232 | 1340 | 1703.7 | 1692.5 | 127.14 | 126.31 | PJM_500_BG_P1_5011_SRT-A | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200011 | KEYSTONE | 235118 | 01SOBEND | 1 | 500 | 225/201 | 2078 | 2695.8 | 2624.1 | 129.73 | 126.28 | PN_P2-3_PN-500-004-DRT-002_SRT-W | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200011 | KEYSTONE | 235118 | 01SOBEND | 1 | 500 | 225/201 | 2078 | 2695.8 | 2624.1 | 129.73 | 126.28 | PN_P2-3_PN-500-DRT32_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204539 | 27HUNTRSTN | 204550 | 27ORRTANNA | 1 | 115 | 227 | 264 | 336.9 | 333 | 127.6 | 126.12 | ME_P2-3_ME-115-0102-A_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204539 | 27HUNTRSTN | 204550 | 27ORRTANNA | 1 | 115 | 227 | 264 | 336.9 | 332.9 | 127.6 | 126.12 | ME_P2-2_ME-115-0102-4_SRT-A | Bus |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220964 | GRACETON | 220999 | BAGLEY2 | 13 | 230 | 232 | 1795 | 2243.1 | 2262.4 | 124.96 | 126.04 | BG_P4_5_GRCTN_3T_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208395 | FARO FF | 208393 | FARO DC TIE | 1 | 69/115 | 229 | 120 | 157.4 | 151.2 | 131.2 | 125.99 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208395 | FARO FF | 208393 | FARO DC TIE | 2 | 69/115 | 229 | 120 | 157.4 | 151.2 | 131.21 | 125.99 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204528 | 27GARDNERS | 200504 | 26CARLISLE | 1 | 115 | 226/227 | 150 | 178.7 | 188.9 | 119.15 | 125.94 | Base Case | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208395 | FARO FF | 208393 | FARO DC TIE | 2 | 69/115 | 229 | 120 | 157.4 | 151.1 | 131.15 | 125.92 | PECO_P4_PEACH235_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208395 | FARO FF | 208393 | FARO DC TIE | 1 | 69/115 | 229 | 120 | 157.4 | 151.1 | 131.14 | 125.92 | PECO_P4_PEACH235_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208395 | FARO FF | 208393 | FARO DC TIE | 2 | 69/115 | 229 | 120 | 157.4 | 151.1 | 131.15 | 125.91 | PECO_P1-2_5012_SRT-A | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208395 | FARO FF | 208393 | FARO DC TIE | 1 | 69/115 | 229 | 120 | 157.4 | 151.1 | 131.15 | 125.91 | PECO_P1-2_5012_SRT-A | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208395 | FARO FF | 208393 | FARO DC TIE | 2 | 69/115 | 229 | 120 | 157.4 | 151.1 | 131.15 | 125.91 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208395 | FARO FF | 208393 | FARO DC TIE | 1 | 69/115 | 229 | 120 | 157.4 | 151.1 | 131.15 | 125.91 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220980 | RAPHAEL | 220979 | NEAST317 | 1 | 230 | 232 | 1340 | 1697.9 | 1687.1 | 126.71 | 125.9 | PEPCO_P4_PP40_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220980 | RAPHAEL | 220979 | NEAST317 | 1 | 230 | 232 | 1340 | 1696.9 | 1685.8 | 126.63 | 125.81 | PJM_500_BG_P4_5_CNSTN_J_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200099 | LAUS | 208045 | LAUS | 3 | 500/230 | 225/229 | 1200 | 1489.9 | 1509.6 | 124.16 | 125.8 | PECO_P1-2_5012_SRT-A | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200504 | 26CARLISLE | 200520 | 26ROXBURY | 1 | 115 | 226 | 190 | 224.7 | 239 | 118.25 | 125.79 | PN_P2-3_PN-230-0014-12_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 203981 | AD2-062_POI | 235188 | 01GREENE | 1 | 138 | 226/201 | 317 | 404 | 397.8 | 127.43 | 125.48 | ME_P2-2_ME-115-003_SRT-A | Bus |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 221010 | COLUMB12 | 220941 | H.RDGE16 | 1 | 230 | 232 | 876 | 1134.4 | 1098.7 | 129.49 | 125.42 | PJM_500_BG_P1_5011_SRT-A | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200504 | 26CARLISLE | 200520 | 26ROXBURY | 1 | 115 | 226 | 190 | 224.7 | 238.2 | 118.24 | 125.38 | PN_P2-3_PN-230-0014-11_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200504 | 26CARLISLE | 200520 | 26ROXBURY | 1 | 115 | 226 | 190 | 224.7 | 238.2 | 118.24 | 125.37 | PN_P1-3_PN-230-020A_SRT-A | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200504 | 26CARLISLE | 200520 | 26ROXBURY | 1 | 115 | 226 | 190 | 224.5 | 238.2 | 118.17 | 125.34 | PN_P2-2_PN-115-031_SRT-A | Bus |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208031 | MLWD TR2 | 208020 | MANO TR3 | 1 | 230 | 229 | 903 | 1059.1 | 1130.8 | 117.28 | 125.23 | PECO_P4_PEACH245_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 203981 | AD2-062_POI | 235188 | 01GREENE | 1 | 138 | 226/201 | 317 | 401.2 | 396.2 | 126.56 | 124.98 | AP_P7-1_PE-138-022T_SRT-A | Tower |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 203981 | AD2-062_POI | 235188 | 01GREENE | 1 | 138 | 226/201 | 317 | 401.2 | 396.2 | 126.56 | 124.98 | AP_P2-2_PE-138-073_SRT-A | Bus |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 203981 | AD2-062_POI | 235188 | 01GREENE | 1 | 138 | 226/201 | 317 | 399.4 | 395.5 | 125.99 | 124.75 | AP_P2-2_PE-138-003_SRT-A | Bus |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200532 | 26ROXBURY | 203981 | AD2-062_POI | 1 | 138 | 226 | 317 | 403.4 | 395.5 | 127.26 | 124.75 | ME_P2-2_ME-115-003_SRT-A | Bus |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 781.7 | 797 | 122.33 | 124.72 | PJM_500_BG_P2_CNSTN_230-S_SRT-A | Bus |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 781.4 | 796.7 | 122.29 | 124.67 | PJM_500_BG_P2_CNSTN_230-N_SRT-A | Bus |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208132 | WHEM TR1 | 208131 | WHEM | 1 | 230 | 229 | 691 | 794.5 | 860.2 | 114.98 | 124.49 | PECO_P1-2_5012_SRT-A | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200504 | 26CARLISLE | 200520 | 26ROXBURY | 1 | 115 | 226 | 190 | 216.6 | 236.4 | 114.02 | 124.43 | PJM_500_BG_P1_5011_SRT-A | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200512 | 26LEWISTWN | 200519 | 26REED TAP | 1 | 115 | 226 | 271 | 339.7 | 336.8 | 125.36 | 124.28 | ME_P2-2_ME-115-002T_SRT-A | Bus |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200532 | 26ROXBURY | 203981 | AD2-062_POI | 1 | 138 | 226 | 317 | 400.6 | 393.8 | 126.38 | 124.23 | AP_P2-2_PE-138-073_SRT-A | Bus |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200532 | 26ROXBURY | 203981 | AD2-062_POI | 1 | 138 | 226 | 317 | 400.6 | 393.8 | 126.38 | 124.23 | AP_P7-1_PE-138-022T_SRT-A | Tower |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208394 | PPL-BGE TIE | 221092 | FIVE.FOR | 1 | 115 | 229/232 | 247 | 292.4 | 306.8 | 118.37 | 124.2 | BG_P7_GRCTN_RAPHEL_SRT-A | Tower |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200512 | 26LEWISTWN | 200519 | 26REED TAP | 1 | 115 | 226 | 271 | 339 | 336.1 | 125.09 | 124.04 | ME_P1-2_ME-115-058T_SRT-A | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200532 | 26ROXBURY | 203981 | AD2-062_POI | 1 | 138 | 226 | 317 | 398.8 | 393.1 | 125.81 | 124 | AP_P2-2_PE-138-003_SRT-A | Bus |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200520 | 26ROXBURY | 200532 | 26ROXBURY | 2 | 115/138 | 226 | 435 | 475 | 539 | 109.19 | 123.91 | PECO_P1-2_5012_SRT-A | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208132 | WHEM TR1 | 208131 | WHEM | 1 | 230 | 229 | 691 | 787.8 | 854.9 | 114.01 | 123.72 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200519 | 26REED TAP | 200522 | 26SHADE GP | 1 | 115 | 226 | 271 | 318.2 | 334.7 | 117.41 | 123.5 | PJM_500_BG_P1_5011_SRT-A | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208396 | FARO | 208395 | FARO FF | 1 | 69 | 229 | 270 | 326.3 | 333.2 | 120.85 | 123.42 | PL_05_P71_000906_SRT-A | Tower |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 221092 | FIVE.FOR | 221095 | ROCKRGE2 | 1 | 115 | 232 | 340 | 411.2 | 419.4 | 120.93 | 123.35 | BG_P7_GRCTN_RAPHEL_SRT-A | Tower |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200519 | 26REED TAP | 200522 | 26SHADE GP | 1 | 115 | 226 | 271 | 317.7 | 334.2 | 117.24 | 123.33 | PJM_500_BG_P4_5_CNSTN_J_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220954 | HOWARD32 | 220941 | H.RDGE16 | 1 | 230 | 232 | 990 | 1255.6 | 1220.5 | 126.83 | 123.28 | PJM_500_BG_P1_5011_SRT-A | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204529 | 27GERMANTN | 204530 | 27GERMANTN | 1 | 115/138 | 227 | 453 | 549.4 | 558.3 | 121.29 | 123.24 | PECO_P1-2_5012_SRT-A | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 774.5 | 786.8 | 121.2 | 123.12 | PL_05_P71_000906_SRT-A | Tower |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204693 | 27BOONETOWN | 204512 | 27S.RDG | 1 | 230 | 227 | 607 | 694.3 | 747.2 | 114.39 | 123.1 | PECO_P4_PEACH245_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204693 | 27BOONETOWN | 204512 | 27S.RDG | 1 | 230 | 227 | 607 | 751.5 | 747.1 | 123.81 | 123.09 | PL_04_P42_101307_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220999 | BAGLEY2 | 220980 | RAPHAEL | 13 | 230 | 232 | 1795 | 2163.8 | 2204.2 | 120.54 | 122.8 | BG_P4_5_GRCTN_3T_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200504 | 26CARLISLE | 200520 | 26ROXBURY | 1 | 115 | 226 | 190 | 217.6 | 233.2 | 114.54 | 122.73 | PN_P2-3_PN-115-40A_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208394 | PPL-BGE TIE | 221092 | FIVE.FOR | 1 | 115 | 229/232 | 247 | 298.1 | 302.7 | 120.68 | 122.57 | PECO_P4_PEACH245_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200520 | 26ROXBURY | 200532 | 26ROXBURY | 2 | 115/138 | 226 | 435 | 468.8 | 533.2 | 107.77 | 122.57 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200520 | 26ROXBURY | 200532 | 26ROXBURY | 2 | 115/138 | 226 | 435 | 468.8 | 533.2 | 107.77 | 122.56 | PECO_P4_PEACH235_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208132 | WHEM TR1 | 208131 | WHEM | 1 | 230 | 229 | 691 | 784.1 | 846.4 | 113.48 | 122.49 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208132 | WHEM TR1 | 208131 | WHEM | 1 | 230 | 229 | 691 | 784.1 | 846.4 | 113.47 | 122.48 | PECO_P4_PEACH235_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200520 | 26ROXBURY | 200532 | 26ROXBURY | 2 | 115/138 | 226 | 435 | 468.2 | 532.6 | 107.64 | 122.43 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 758.5 | 755.3 | 122.93 | 122.42 | PL_04_P71_001014_SRT-A | Tower |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 746 | 755.3 | 120.91 | 122.42 | PL_04_P71_001014_SRT-A | Tower |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220965 | NEAST339 | 220977 | RIV2339 | 1 | 230 | 232 | 991 | 1219.7 | 1212.3 | 123.08 | 122.33 | PJM_500_BG_P1_5011_SRT-A | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208395 | FARO FF | 208393 | FARO DC TIE | 1 | 69/115 | 229 | 120 | 149.1 | 146.6 | 124.23 | 122.15 | BG_P7_GRCTN_RAPHEL_SRT-A | Tower |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208395 | FARO FF | 208393 | FARO DC TIE | 2 | 69/115 | 229 | 120 | 149.1 | 146.6 | 124.23 | 122.15 | BG_P7_GRCTN_RAPHEL_SRT-A | Tower |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208395 | FARO FF | 208393 | FARO DC TIE | 1 | 69/115 | 229 | 120 | 151.9 | 146.5 | 126.6 | 122.11 | PECO_P4_PEACH245_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208395 | FARO FF | 208393 | FARO DC TIE | 2 | 69/115 | 229 | 120 | 151.9 | 146.5 | 126.61 | 122.11 | PECO_P4_PEACH245_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220979 | NEAST317 | 220966 | RIV2317 | 1 | 230 | 232 | 940 | 1148.9 | 1145.5 | 122.22 | 121.86 | PJM_500_BG_P1_5011_SRT-A | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200512 | 26LEWISTWN | 200519 | 26REED TAP | 1 | 115 | 226 | 228 | 285.3 | 277.8 | 125.13 | 121.83 | Base Case | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220965 | NEAST339 | 220977 | RIV2339 | 1 | 230 | 232 | 991 | 1213.7 | 1206.5 | 122.48 | 121.74 | PEPCO_P4_PP40_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220965 | NEAST339 | 220977 | RIV2339 | 1 | 230 | 232 | 991 | 1213.4 | 1205.9 | 122.44 | 121.69 | PJM_500_BG_P4_5_CNSTN_J_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204529 | 27GERMANTN | 204530 | 27GERMANTN | 1 | 115/138 | 227 | 453 | 542.1 | 550.5 | 119.67 | 121.52 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204529 | 27GERMANTN | 204530 | 27GERMANTN | 1 | 115/138 | 227 | 453 | 542.1 | 550.5 | 119.67 | 121.51 | PECO_P4_PEACH235_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220979 | NEAST317 | 220966 | RIV2317 | 1 | 230 | 232 | 940 | 1145.2 | 1141.9 | 121.83 | 121.48 | PEPCO_P4_PP40_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220979 | NEAST317 | 220966 | RIV2317 | 1 | 230 | 232 | 940 | 1144.8 | 1141.4 | 121.79 | 121.42 | PJM_500_BG_P4_5_CNSTN_J_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204529 | 27GERMANTN | 204530 | 27GERMANTN | 1 | 115/138 | 227 | 453 | 541.8 | 550 | 119.59 | 121.41 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200512 | 26LEWISTWN | 200519 | 26REED TAP | 1 | 115 | 226 | 271 | 331.3 | 328.9 | 122.23 | 121.38 | PN_P1-2_PN-115-095_SRT-A | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 763.1 | 774.2 | 119.42 | 121.16 | PL_05_P22_000674_SRT-A | Bus |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 1050.2 | 1077.1 | 118.13 | 121.16 | PJM_500_BG_P1_5011_SRT-A | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 754.5 | 773.4 | 118.07 | 121.03 | PJM_500_BG_P2_CNSTN_230-S_SRT-A | Bus |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 754.2 | 773.1 | 118.02 | 120.98 | PJM_500_BG_P2_CNSTN_230-N_SRT-A | Bus |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200512 | 26LEWISTWN | 200519 | 26REED TAP | 1 | 115 | 226 | 271 | 331.4 | 327.6 | 122.27 | 120.9 | PN_P1-2_PN-115-107T_SRT-A | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200099 | LAUS | 208045 | LAUS | 3 | 500/230 | 225/229 | 1200 | 1427.3 | 1447.7 | 118.94 | 120.64 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 733.8 | 743.9 | 118.94 | 120.56 | PL_04_P22_102817_SRT-A | Bus |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 746.3 | 743.9 | 120.95 | 120.56 | PL_04_P22_102817_SRT-A | Bus |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 745.5 | 743.1 | 120.82 | 120.44 | PL_04_P71_000904_SRT-A | Tower |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 733 | 743.1 | 118.81 | 120.44 | PL_04_P71_000904_SRT-A | Tower |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 745.2 | 742.8 | 120.77 | 120.39 | PL_04_P71_001822_SRT-A | Tower |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 732.7 | 742.8 | 118.75 | 120.39 | PL_04_P71_001822_SRT-A | Tower |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 746 | 908.2 | 897.9 | 121.75 | 120.36 | Base Case | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200099 | LAUS | 208045 | LAUS | 3 | 500/230 | 225/229 | 1200 | 1426.2 | 1444 | 118.85 | 120.33 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200099 | LAUS | 208045 | LAUS | 3 | 500/230 | 225/229 | 1200 | 1426.1 | 1443.9 | 118.84 | 120.32 | PECO_P4_PEACH235_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 221092 | FIVE.FOR | 221096 | ROCKRGE1 | 1 | 115 | 232 | 293 | 336.4 | 351.1 | 114.81 | 119.82 | BG_P1_110512_SRT-A | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 203981 | AD2-062_POI | 235188 | 01GREENE | 1 | 138 | 226/201 | 317 | 381.9 | 379.3 | 120.46 | 119.66 | BG_P7_GRCTN_RAPHEL_SRT-A | Tower |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 221010 | COLUMB12 | 220941 | H.RDGE16 | 1 | 230 | 232 | 876 | 1076.6 | 1048.1 | 122.9 | 119.65 | PEPCO_P4_PP40_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200762 | 26GARRETT | 235470 | 01GARRET | 1 | 115 | 226/201 | 190 | 223.6 | 227.2 | 117.7 | 119.56 | PJM_500_BG_P1_5011_SRT-A | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208394 | PPL-BGE TIE | 221092 | FIVE.FOR | 1 | 115 | 229/232 | 247 | 282.2 | 295.2 | 114.23 | 119.51 | BG_P7_NEAST_RPHLRD_SRT-A | Tower |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200762 | 26GARRETT | 235470 | 01GARRET | 1 | 115 | 226/201 | 190 | 223.5 | 227 | 117.63 | 119.49 | PJM_500_BG_P4_5_CNSTN_J_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200519 | 26REED TAP | 200522 | 26SHADE GP | 1 | 115 | 226 | 271 | 318.8 | 323.6 | 117.62 | 119.42 | ME_P2-2_ME-115-002T_SRT-A | Bus |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 747.2 | 763.1 | 116.94 | 119.41 | PL_05_P71_000906_SRT-A | Tower |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200762 | 26GARRETT | 235470 | 01GARRET | 1 | 115 | 226/201 | 190 | 223.2 | 226.7 | 117.47 | 119.32 | PEPCO_P4_PP40_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 203981 | AD2-062_POI | 235188 | 01GREENE | 1 | 138 | 226/201 | 317 | 380.9 | 378 | 120.15 | 119.24 | BG_P7_CNSTN_NWEST2_SRT-A | Tower |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200519 | 26REED TAP | 200522 | 26SHADE GP | 1 | 115 | 226 | 271 | 318 | 323 | 117.35 | 119.18 | ME_P1-2_ME-115-058T_SRT-A | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 221010 | COLUMB12 | 220941 | H.RDGE16 | 1 | 230 | 232 | 876 | 1070.7 | 1042.1 | 122.23 | 118.96 | PJM_500_BG_P4_5_CNSTN_J_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208395 | FARO FF | 208393 | FARO DC TIE | 1 | 69/115 | 229 | 120 | 144.7 | 142.6 | 120.62 | 118.83 | BG_P4_5_GRCTN_2T_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208395 | FARO FF | 208393 | FARO DC TIE | 2 | 69/115 | 229 | 120 | 144.7 | 142.6 | 120.62 | 118.83 | BG_P4_5_GRCTN_2T_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 203981 | AD2-062_POI | 235188 | 01GREENE | 1 | 138 | 226/201 | 317 | 380.6 | 376.4 | 120.06 | 118.74 | AP_P2-2_WP-500-DRT17_SRT-W | Bus |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208394 | PPL-BGE TIE | 221092 | FIVE.FOR | 1 | 115 | 229/232 | 247 | 283.7 | 293.3 | 114.88 | 118.73 | BG_P4_5_GRCTN_2T_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200532 | 26ROXBURY | 203981 | AD2-062_POI | 1 | 138 | 226 | 317 | 380.6 | 376.4 | 120.08 | 118.73 | BG_P7_GRCTN_RAPHEL_SRT-A | Tower |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 720.1 | 732 | 116.71 | 118.63 | AP_P2-2_WP-500-DRT16_SRT-W | Bus |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 732.6 | 732 | 118.73 | 118.63 | AP_P2-2_WP-500-DRT16_SRT-W | Bus |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204528 | 27GARDNERS | 200504 | 26CARLISLE | 1 | 115 | 226/227 | 190 | 213.2 | 225.3 | 112.2 | 118.56 | ME_P2-2_ME-115-003_SRT-A | Bus |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200762 | 26GARRETT | 235470 | 01GARRET | 1 | 115 | 226/201 | 150 | 174.4 | 177.8 | 116.24 | 118.55 | Base Case | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 221090 | GLENARM2 | 221089 | WINDYED1 | 1 | 115 | 232 | 222 | 249.6 | 263 | 112.44 | 118.46 | PJM_500_BG_P1_5011_SRT-A | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208395 | FARO FF | 208393 | FARO DC TIE | 1 | 69/115 | 229 | 120 | 144 | 142 | 119.97 | 118.31 | BG_P7_NEAST_RPHLRD_SRT-A | Tower |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208395 | FARO FF | 208393 | FARO DC TIE | 2 | 69/115 | 229 | 120 | 144 | 142 | 119.97 | 118.31 | BG_P7_NEAST_RPHLRD_SRT-A | Tower |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200532 | 26ROXBURY | 203981 | AD2-062_POI | 1 | 138 | 226 | 317 | 379.7 | 375 | 119.77 | 118.3 | BG_P7_CNSTN_NWEST2_SRT-A | Tower |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208395 | FARO FF | 208393 | FARO DC TIE | 1 | 69/115 | 229 | 96.9 | 113.3 | 114.7 | 116.91 | 118.26 | Base Case | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200519 | 26REED TAP | 200522 | 26SHADE GP | 1 | 115 | 226 | 224 | 264.3 | 264.8 | 118.01 | 118.22 | Base Case | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208396 | FARO | 208395 | FARO FF | 1 | 69 | 229 | 270 | 315.1 | 318.9 | 116.69 | 118.1 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 221090 | GLENARM2 | 221089 | WINDYED1 | 1 | 115 | 232 | 222 | 249.7 | 262.2 | 112.46 | 118.1 | BG_P7_CNSTN_NWEST2_SRT-A | Tower |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 221090 | GLENARM2 | 221089 | WINDYED1 | 1 | 115 | 232 | 222 | 248.7 | 262.1 | 112.03 | 118.07 | PEPCO_P4_PP40_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 221092 | FIVE.FOR | 221096 | ROCKRGE1 | 1 | 115 | 232 | 293 | 331.1 | 345.9 | 112.99 | 118.05 | BG_P4_5_WE512_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208396 | FARO | 208395 | FARO FF | 1 | 69 | 229 | 270 | 314.9 | 318.6 | 116.64 | 118.01 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208396 | FARO | 208395 | FARO FF | 1 | 69 | 229 | 270 | 314.9 | 318.6 | 116.64 | 118.01 | PECO_P1-2_5012_SRT-A | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208396 | FARO | 208395 | FARO FF | 1 | 69 | 229 | 270 | 314.9 | 318.6 | 116.63 | 118.01 | PECO_P4_PEACH235_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200532 | 26ROXBURY | 203981 | AD2-062_POI | 1 | 138 | 226 | 317 | 380 | 374.1 | 119.88 | 118.01 | AP_P2-2_WP-500-DRT17_SRT-W | Bus |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 221051 | CHESTN8A | 221049 | FRED.RD8 | 1 | 115 | 232 | 215 | 245.3 | 253.7 | 114.07 | 118 | BG_P7_GRCTN_RAPHEL_SRT-A | Tower |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 203981 | AD2-062_POI | 235188 | 01GREENE | 1 | 138 | 226/201 | 317 | 376.1 | 374 | 118.66 | 117.99 | BG_P7_NEAST_RPHLRD_SRT-A | Tower |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200065 | PCHBTM2S | 200066 | PCHBTM1N | 2 | 500 | 225 | 3022 | 3618.6 | 3565.5 | 119.74 | 117.98 | PECO_P4_PEACH235_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208394 | PPL-BGE TIE | 221092 | FIVE.FOR | 1 | 115 | 229/232 | 247 | 275.2 | 291.2 | 111.4 | 117.91 | PJM_500_BG_P1_5011_SRT-A | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 221090 | GLENARM2 | 221089 | WINDYED1 | 1 | 115 | 232 | 222 | 248.4 | 261.7 | 111.88 | 117.9 | PJM_500_BG_P4_5_CNSTN_J_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223938 | DICKH230 | 223937 | DICK 230 | 1 | 230 | 233 | 793 | 949 | 932.9 | 119.68 | 117.64 | AP_P2-3_PE-500-019C_SRT-W | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223938 | DICKH230 | 223937 | DICK 230 | 2 | 230 | 233 | 793 | 949 | 932.9 | 119.68 | 117.64 | AP_P2-3_PE-500-019C_SRT-W | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200018 | CHALK PT | 200301 | X4-035 TAP | 1 | 500 | 225 | 1732 | 2047.3 | 2034.3 | 118.21 | 117.45 | AP_P2-3_PE-500-019B_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 735.9 | 750.5 | 115.16 | 117.45 | PL_05_P22_000674_SRT-A | Bus |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208395 | FARO FF | 208393 | FARO DC TIE | 1 | 69/115 | 229 | 120 | 140.5 | 140.9 | 117.05 | 117.41 | PJM_500_BG_P1_5011_SRT-A | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208395 | FARO FF | 208393 | FARO DC TIE | 2 | 69/115 | 229 | 120 | 140.5 | 140.9 | 117.06 | 117.41 | PJM_500_BG_P1_5011_SRT-A | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204528 | 27GARDNERS | 200504 | 26CARLISLE | 1 | 115 | 226/227 | 190 | 211 | 223 | 111.04 | 117.39 | AP_P2-2_PE-138-073_SRT-A | Bus |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204528 | 27GARDNERS | 200504 | 26CARLISLE | 1 | 115 | 226/227 | 190 | 211 | 223 | 111.04 | 117.39 | AP_P7-1_PE-138-022T_SRT-A | Tower |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 221090 | GLENARM2 | 221089 | WINDYED1 | 1 | 115 | 232 | 222 | 244 | 260.6 | 109.91 | 117.37 | BG_P4_5_WE_NORTH_TIE_SRT-A/* WINDY EDGE #1(NORTH) BUS BLACK-RED BUS TIE BREAKER 221089 | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 221090 | GLENARM2 | 221089 | WINDYED1 | 1 | 115 | 232 | 222 | 243.7 | 260.4 | 109.77 | 117.3 | BG_P4_5_WE504_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 221090 | GLENARM2 | 221089 | WINDYED1 | 1 | 115 | 232 | 222 | 243.2 | 260 | 109.55 | 117.1 | BG_P2_WE_115-N-RED_SRT-A | Bus |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200532 | 26ROXBURY | 203981 | AD2-062_POI | 1 | 138 | 226 | 317 | 374.9 | 371.1 | 118.28 | 117.06 | BG_P7_NEAST_RPHLRD_SRT-A | Tower |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204693 | 27BOONETOWN | 204512 | 27S.RDG | 1 | 230 | 227 | 607 | 714.2 | 709.8 | 117.67 | 116.94 | PL_04_P13_101211_SRT-A | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200762 | 26GARRETT | 235470 | 01GARRET | 1 | 115 | 226/201 | 190 | 216.6 | 222 | 113.99 | 116.86 | PECO_P1-2_5012_SRT-A | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220960 | BRANDN.S | 220955 | W.CHAPEL | 42 | 230 | 232 | 991 | 1190.4 | 1157.6 | 120.13 | 116.81 | PJM_500_BG_P1_5011_SRT-A | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200762 | 26GARRETT | 235470 | 01GARRET | 1 | 115 | 226/201 | 190 | 216.4 | 221.9 | 113.88 | 116.81 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200762 | 26GARRETT | 235470 | 01GARRET | 1 | 115 | 226/201 | 190 | 216.4 | 221.9 | 113.91 | 116.79 | PECO_P4_PEACH235_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200762 | 26GARRETT | 235470 | 01GARRET | 1 | 115 | 226/201 | 190 | 216.4 | 221.9 | 113.91 | 116.79 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204528 | 27GARDNERS | 200504 | 26CARLISLE | 1 | 115 | 226/227 | 190 | 208.5 | 221.9 | 109.72 | 116.77 | AP_P2-2_PE-138-003_SRT-A | Bus |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200519 | 26REED TAP | 200522 | 26SHADE GP | 1 | 115 | 226 | 271 | 310.3 | 315.8 | 114.49 | 116.53 | PN_P1-2_PN-115-095_SRT-A | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 203981 | AD2-062_POI | 235188 | 01GREENE | 1 | 138 | 226/201 | 317 | 376.7 | 369.2 | 118.83 | 116.46 | AP_P2-2_WP-500-DRT16_SRT-W | Bus |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200018 | CHALK PT | 200301 | X4-035 TAP | 1 | 500 | 225 | 1732 | 2031.8 | 2016.6 | 117.31 | 116.43 | AP_P1-2_PE-500-406T_SRT-W | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200018 | CHALK PT | 200301 | X4-035 TAP | 1 | 500 | 225 | 1732 | 2031.8 | 2016.6 | 117.31 | 116.43 | PEPCO_P1_5055_SRT-A | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220954 | HOWARD32 | 220941 | H.RDGE16 | 1 | 230 | 232 | 990 | 1180.8 | 1149.8 | 119.27 | 116.14 | PEPCO_P4_PP40_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200519 | 26REED TAP | 200522 | 26SHADE GP | 1 | 115 | 226 | 271 | 310.4 | 314.5 | 114.53 | 116.06 | PN_P1-2_PN-115-107T_SRT-A | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200018 | CHALK PT | 200301 | X4-035 TAP | 1 | 500 | 225 | 1732 | 2024.6 | 2009.5 | 116.89 | 116.02 | AP_P2-3_PE-500-019F_SRT-W | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 731 | 741.1 | 114.4 | 115.99 | PL_04_P71_001014_SRT-A | Tower |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220979 | NEAST317 | 220966 | RIV2317 | 1 | 230 | 232 | 940 | 1080.1 | 1090 | 114.9 | 115.95 | BG_P4_5_NEAST_39_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220979 | NEAST317 | 220966 | RIV2317 | 1 | 230 | 232 | 940 | 1080.1 | 1090 | 114.9 | 115.95 | BG_P4_5_NEAST_37_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208131 | WHEM | 208133 | WHEM TR2 | 1 | 230 | 229 | 691 | 742.4 | 800.6 | 107.44 | 115.87 | PECO_P1-2_5012_SRT-A | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 235105 | 01DOUBS | 1 | 500 | 225/201 | 2598 | 3025.1 | 3003.6 | 116.44 | 115.61 | DVP_P4-2: 560T571_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 235105 | 01DOUBS | 1 | 500 | 225/201 | 2598 | 3024.4 | 3003 | 116.41 | 115.59 | PEPCO_P1_5070_SRT-A | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 235105 | 01DOUBS | 1 | 500 | 225/201 | 2598 | 3024.1 | 3002.7 | 116.4 | 115.58 | DVP_P4-2: H1T560_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 235105 | 01DOUBS | 1 | 500 | 225/201 | 2598 | 3024.1 | 3002.7 | 116.4 | 115.58 | DVP_P4-2: H2T560_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208396 | FARO | 208395 | FARO FF | 1 | 69 | 229 | 270 | 298.3 | 312 | 110.49 | 115.55 | BG_P7_GRCTN_RAPHEL_SRT-A | Tower |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200532 | 26ROXBURY | 203981 | AD2-062_POI | 1 | 138 | 226 | 317 | 375.5 | 366.2 | 118.44 | 115.52 | AP_P2-2_WP-500-DRT16_SRT-W | Bus |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204693 | 27BOONETOWN | 204512 | 27S.RDG | 1 | 230 | 227 | 607 | 705.1 | 701 | 116.16 | 115.48 | PL_04_P22_102291_SRT-A | Bus |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208395 | FARO FF | 208393 | FARO DC TIE | 2 | 69/115 | 229 | 120 | 140.1 | 138.6 | 116.73 | 115.48 | PL_04_P12_000257_SRT-A | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208395 | FARO FF | 208393 | FARO DC TIE | 1 | 69/115 | 229 | 120 | 140.1 | 138.6 | 116.73 | 115.48 | PL_04_P12_000257_SRT-A | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208395 | FARO FF | 208393 | FARO DC TIE | 2 | 69/115 | 229 | 120 | 140.1 | 138.6 | 116.74 | 115.48 | PL_05_P22_000674_SRT-A | Bus |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208395 | FARO FF | 208393 | FARO DC TIE | 1 | 69/115 | 229 | 120 | 140.1 | 138.6 | 116.73 | 115.48 | PL_05_P22_000674_SRT-A | Bus |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204693 | 27BOONETOWN | 204512 | 27S.RDG | 1 | 230 | 227 | 607 | 705.1 | 700.9 | 116.16 | 115.47 | PL_04_P22_102290_SRT-A | Bus |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220954 | HOWARD32 | 220941 | H.RDGE16 | 1 | 230 | 232 | 990 | 1173.7 | 1142.2 | 118.56 | 115.38 | PJM_500_BG_P4_5_CNSTN_J_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208132 | WHEM TR1 | 208131 | WHEM | 1 | 230 | 229 | 691 | 751.1 | 796.3 | 108.7 | 115.24 | PECO_P4_PEACH245_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220963 | CONASTON | 220961 | NWEST326 | 1 | 230 | 232 | 1381 | 1524.6 | 1591.5 | 110.4 | 115.24 | BG_P7_GRCTN_RAPHEL_SRT-A | Tower |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 221092 | FIVE.FOR | 221095 | ROCKRGE2 | 1 | 115 | 232 | 340 | 381.2 | 391.6 | 112.13 | 115.16 | BG_P7_NEAST_RPHLRD_SRT-A | Tower |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208131 | WHEM | 208133 | WHEM TR2 | 1 | 230 | 229 | 691 | 735.8 | 795.5 | 106.48 | 115.12 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220963 | CONASTON | 220962 | NWEST311 | 1 | 230 | 232 | 1381 | 1522.9 | 1589.7 | 110.28 | 115.11 | BG_P7_GRCTN_RAPHEL_SRT-A | Tower |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208394 | PPL-BGE TIE | 221092 | FIVE.FOR | 1 | 115 | 229/232 | 247 | 275.2 | 284.1 | 111.42 | 115.04 | PL_04_P12_000257_SRT-A | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 1033.4 | 1020.1 | 116.25 | 114.75 | PECO_P1-2_220-08_SRT-A | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220980 | RAPHAEL | 220965 | NEAST339 | 1 | 230 | 232 | 1340 | 1540 | 1537.5 | 114.92 | 114.74 | BG_P7_CNSTN_NWEST2_SRT-A | Tower |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208394 | PPL-BGE TIE | 221092 | FIVE.FOR | 1 | 115 | 229/232 | 247 | 274.4 | 283.4 | 111.1 | 114.73 | PL_05_P22_000674_SRT-A | Bus |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 2 | 500/230 | 225/232 | 2168 | 2413.1 | 2485.1 | 111.3 | 114.62 | PJM_500_BG_P4_5_CNSTN_15_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200099 | LAUS | 208045 | LAUS | 3 | 500/230 | 225/229 | 1200 | 1355.9 | 1374.5 | 112.99 | 114.55 | PECO_P4_PEACH245_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 1030.8 | 1017.7 | 115.95 | 114.48 | PECO_P1-2_220-93_SRT-A | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200762 | 26GARRETT | 235470 | 01GARRET | 1 | 115 | 226/201 | 190 | 213 | 217.4 | 112.11 | 114.4 | AP_P1-2_WP-500-006_SRT-A | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200762 | 26GARRETT | 235470 | 01GARRET | 1 | 115 | 226/201 | 190 | 213 | 217.4 | 112.11 | 114.4 | AP_P1-2_PE-500-004_SRT-W | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 718.8 | 729.7 | 112.49 | 114.19 | PL_04_P22_102817_SRT-A | Bus |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 203981 | AD2-062_POI | 235188 | 01GREENE | 1 | 138 | 226/201 | 317 | 366.9 | 362 | 115.73 | 114.19 | AP_P7-1_PE-138-003_SRT-A | Tower |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200066 | PCHBTM1N | 200016 | 3 MILE I | 1 | 500 | 225 | 3250 | 3724.2 | 3708.6 | 114.59 | 114.11 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 718 | 728.9 | 112.36 | 114.07 | PL_04_P71_000904_SRT-A | Tower |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208396 | FARO | 208395 | FARO FF | 1 | 69 | 229 | 270 | 304 | 308 | 112.6 | 114.06 | PECO_P4_PEACH245_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 717.7 | 728.6 | 112.31 | 114.02 | PL_04_P71_001822_SRT-A | Tower |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200066 | PCHBTM1N | 200016 | 3 MILE I | 1 | 500 | 225 | 3250 | 3724.3 | 3705 | 114.59 | 114 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200066 | PCHBTM1N | 200016 | 3 MILE I | 1 | 500 | 225 | 3250 | 3724.3 | 3704.3 | 114.59 | 113.98 | PECO_P1-2_5012_SRT-A | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220979 | NEAST317 | 220966 | RIV2317 | 1 | 230 | 232 | 940 | 1059.1 | 1071.3 | 112.67 | 113.97 | BG_P1_2337_SRT-A | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208131 | WHEM | 208133 | WHEM TR2 | 1 | 230 | 229 | 691 | 732.1 | 787.3 | 105.95 | 113.94 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208131 | WHEM | 208133 | WHEM TR2 | 1 | 230 | 229 | 691 | 732 | 787.3 | 105.94 | 113.93 | PECO_P4_PEACH235_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200066 | PCHBTM1N | 200016 | 3 MILE I | 1 | 500 | 225 | 3250 | 3719.3 | 3700.3 | 114.44 | 113.86 | PECO_P4_PEACH235_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 221054 | CHESTN7A | 221050 | FRED.RD7 | 1 | 115 | 232 | 215 | 236.2 | 244.5 | 109.84 | 113.73 | BG_P7_GRCTN_RAPHEL_SRT-A | Tower |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220960 | BRANDN.S | 220955 | W.CHAPEL | 42 | 230 | 232 | 991 | 1153.4 | 1126.7 | 116.39 | 113.69 | PJM_500_BG_P4_5_CNSTN_J_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220960 | BRANDN.S | 220955 | W.CHAPEL | 42 | 230 | 232 | 991 | 1152.4 | 1125.8 | 116.29 | 113.6 | PEPCO_P4_PP40_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 221090 | GLENARM2 | 221089 | WINDYED1 | 1 | 115 | 232 | 222 | 234.6 | 251.9 | 105.67 | 113.45 | BG_P4_5_WE506_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200532 | 26ROXBURY | 203981 | AD2-062_POI | 1 | 138 | 226 | 317 | 365.6 | 359 | 115.34 | 113.25 | AP_P7-1_PE-138-003_SRT-A | Tower |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220953 | HOWARD12 | 221010 | COLUMB12 | 1 | 230 | 232 | 1049 | 1224.7 | 1187.2 | 116.75 | 113.17 | PJM_500_BG_P1_5011_SRT-A | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220973 | GRANITE6 | 1 | 230 | 232 | 829 | 947 | 936.5 | 114.23 | 112.97 | BG_P7_GRCTN_RAPHEL_SRT-A | Tower |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220965 | NEAST339 | 220977 | RIV2339 | 1 | 230 | 232 | 991 | 1110.2 | 1116.4 | 112.02 | 112.66 | BG_P4_5_NEAST_15_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220965 | NEAST339 | 220977 | RIV2339 | 1 | 230 | 232 | 991 | 1108.6 | 1116.4 | 111.87 | 112.66 | BG_P4_5_NEAST_17_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 1018.3 | 1001.4 | 114.55 | 112.64 | PECO_P2-2_NOTT230B_SRT-A | Bus |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200065 | PCHBTM2S | 200064 | PCHBTM1S | Z2 | 500 | 225 | 2598 | 3029.8 | 2923.8 | 116.62 | 112.54 | Base Case | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 221092 | FIVE.FOR | 221096 | ROCKRGE1 | 1 | 115 | 232 | 293 | 317 | 329.4 | 108.18 | 112.42 | BG_P7_CNSTN_NWEST2_SRT-A | Tower |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 705.1 | 717.7 | 110.34 | 112.32 | AP_P2-2_WP-500-DRT16_SRT-W | Bus |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 703.8 | 717.4 | 110.14 | 112.27 | PL_04_P71_001014_SRT-A | Tower |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220980 | RAPHAEL | 220979 | NEAST317 | 1 | 230 | 232 | 1340 | 1505.9 | 1503.2 | 112.38 | 112.18 | BG_P7_CNSTN_NWEST2_SRT-A | Tower |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 221092 | FIVE.FOR | 221096 | ROCKRGE1 | 1 | 115 | 232 | 293 | 315 | 328.3 | 107.52 | 112.05 | PJM_500_BG_P1_5011_SRT-A | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204528 | 27GARDNERS | 200504 | 26CARLISLE | 1 | 115 | 226/227 | 190 | 198.4 | 212.7 | 104.41 | 111.94 | BG_P7_GRCTN_RAPHEL_SRT-A | Tower |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220972 | GRANITE1 | 1 | 230 | 232 | 829 | 940.2 | 927.8 | 113.41 | 111.92 | BG_P7_GRCTN_RAPHEL_SRT-A | Tower |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208394 | PPL-BGE TIE | 221092 | FIVE.FOR | 1 | 115 | 229/232 | 247 | 261.6 | 276.3 | 105.91 | 111.85 | BG_P7_CNSTN_NWEST2_SRT-A | Tower |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208395 | FARO FF | 208393 | FARO DC TIE | 1 | 69/115 | 229 | 120 | 133.7 | 134.1 | 111.4 | 111.78 | BG_P7_CNSTN_NWEST2_SRT-A | Tower |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208395 | FARO FF | 208393 | FARO DC TIE | 2 | 69/115 | 229 | 120 | 133.7 | 134.1 | 111.41 | 111.78 | BG_P7_CNSTN_NWEST2_SRT-A | Tower |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 221094 | GRACE.-1 | 221092 | FIVE.FOR | 1 | 115 | 232 | 498 | 552.1 | 556.6 | 110.86 | 111.77 | BG_P7_GRCTN_RAPHEL_SRT-A | Tower |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 221092 | FIVE.FOR | 221096 | ROCKRGE1 | 1 | 115 | 232 | 293 | 314.2 | 327.4 | 107.22 | 111.75 | PEPCO_P4_PP40_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 221092 | FIVE.FOR | 221096 | ROCKRGE1 | 1 | 115 | 232 | 293 | 313.8 | 327.1 | 107.1 | 111.62 | PJM_500_BG_P4_5_CNSTN_J_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200018 | CHALK PT | 200301 | X4-035 TAP | 1 | 500 | 225 | 1732 | 1939.3 | 1929.2 | 111.97 | 111.38 | AP_P2-3_PE-500-019C_SRT-W | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208395 | FARO FF | 208393 | FARO DC TIE | 2 | 69/115 | 229 | 102.9 | 113.3 | 114.7 | 110.1 | 111.37 | Base Case | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220980 | RAPHAEL | 220965 | NEAST339 | 1 | 230 | 232 | 1340 | 1497.2 | 1490.7 | 111.73 | 111.24 | BG_P4_5_RPHLRD05_15_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208396 | FARO | 208395 | FARO FF | 1 | 69 | 229 | 270 | 288.1 | 300.2 | 106.7 | 111.19 | BG_P7_NEAST_RPHLRD_SRT-A | Tower |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220965 | NEAST339 | 220977 | RIV2339 | 1 | 230 | 232 | 991 | 1091.3 | 1100.1 | 110.12 | 111.01 | BG_P1_2315_SRT-A | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200009 | JUNI | 208004 | JUNI | 2 | 500/230 | 225/229 | 1040 | 1161 | 1154.4 | 111.63 | 111 | PL_10_P42_000140_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204528 | 27GARDNERS | 200504 | 26CARLISLE | 1 | 115 | 226/227 | 190 | 196.8 | 210.8 | 103.57 | 110.97 | BG_P7_CNSTN_NWEST2_SRT-A | Tower |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 221090 | GLENARM2 | 221089 | WINDYED1 | 1 | 115 | 232 | 222 | 228.1 | 246 | 102.74 | 110.82 | BG_P1_110511_SRT-A | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208133 | WHEM TR2 | 208021 | MANO TR4 | 2 | 230 | 229 | 593 | 607 | 656.6 | 102.36 | 110.73 | PECO_P1-2_5012_SRT-A | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 993.3 | 983.3 | 111.73 | 110.6 | PJM_500_BG_P2_CNSTN_230-S_SRT-A | Bus |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220980 | RAPHAEL | 220979 | NEAST317 | 1 | 230 | 232 | 1340 | 1487.7 | 1481.9 | 111.02 | 110.59 | BG_P4_5_RPHLRD37_13_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 993 | 982.9 | 111.69 | 110.57 | PJM_500_BG_P2_CNSTN_230-N_SRT-A | Bus |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 221092 | FIVE.FOR | 221096 | ROCKRGE1 | 1 | 115 | 232 | 293 | 308.2 | 323.8 | 105.19 | 110.52 | BG_P4_5_WE_EAST_TIE_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 691.6 | 705.9 | 108.23 | 110.47 | PL_04_P22_102817_SRT-A | Bus |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208396 | FARO | 208395 | FARO FF | 1 | 69 | 229 | 270 | 289.7 | 298.3 | 107.29 | 110.46 | BG_P4_5_GRCTN_2T_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208133 | WHEM TR2 | 208021 | MANO TR4 | 2 | 230 | 229 | 593 | 602.9 | 654.6 | 101.67 | 110.39 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 690.8 | 705.1 | 108.1 | 110.35 | PL_04_P71_000904_SRT-A | Tower |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200011 | KEYSTONE | 235104 | 01CABOT | 1 | 500 | 225/201 | 3106 | 3525.3 | 3426.1 | 113.5 | 110.3 | AP_P2-3_WP-500-DRT45_SRT-W | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200011 | KEYSTONE | 235104 | 01CABOT | 1 | 500 | 225/201 | 3106 | 3525.3 | 3426 | 113.5 | 110.3 | AP_P1-2_WP-500-008_SRT-A | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 690.5 | 704.8 | 108.05 | 110.3 | PL_04_P71_001822_SRT-A | Tower |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200762 | 26GARRETT | 235470 | 01GARRET | 1 | 115 | 226/201 | 190 | 209.6 | 209.6 | 110.34 | 110.3 | AP_P1-2_WP-500-008_SRT-A | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220972 | GRANITE1 | 1 | 230 | 232 | 829 | 924.8 | 913.8 | 111.56 | 110.23 | BG_P4_5_NW230-4_2326_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 221092 | FIVE.FOR | 221096 | ROCKRGE1 | 1 | 115 | 232 | 293 | 307 | 322.8 | 104.78 | 110.17 | BG_P2_WE_115-E-BLK_SRT-A | Bus |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 221092 | FIVE.FOR | 221096 | ROCKRGE1 | 1 | 115 | 232 | 293 | 307 | 322.8 | 104.78 | 110.17 | BG_P4_5_WE518_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220964 | GRACETON | 220999 | BAGLEY2 | 13 | 230 | 232 | 1795 | 1954.2 | 1970.6 | 108.87 | 109.78 | BG_P1_2305_SRT-A | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220964 | GRACETON | 221000 | BAGLEY | 5 | 230 | 232 | 1795 | 1954.2 | 1970.6 | 108.87 | 109.78 | BG_P1_2313_SRT-A | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220973 | GRANITE6 | 1 | 230 | 232 | 829 | 922.4 | 909.7 | 111.27 | 109.73 | BG_P4_5_NW230-5_2311_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220963 | CONASTON | 220961 | NWEST326 | 1 | 230 | 232 | 1381 | 1457.1 | 1515.3 | 105.51 | 109.73 | BG_P7_NEAST_RPHLRD_SRT-A | Tower |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208396 | FARO | 208395 | FARO FF | 1 | 69 | 229 | 270 | 281.1 | 296.2 | 104.11 | 109.7 | PJM_500_BG_P1_5011_SRT-A | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220963 | CONASTON | 220962 | NWEST311 | 1 | 230 | 232 | 1381 | 1456 | 1514.2 | 105.43 | 109.64 | BG_P7_NEAST_RPHLRD_SRT-A | Tower |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204528 | 27GARDNERS | 200504 | 26CARLISLE | 1 | 115 | 226/227 | 190 | 194.3 | 208.1 | 102.24 | 109.55 | BG_P7_NEAST_RPHLRD_SRT-A | Tower |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220960 | BRANDN.S | 220955 | W.CHAPEL | 43 | 230 | 232 | 1063 | 1196.7 | 1163.7 | 112.58 | 109.47 | PJM_500_BG_P1_5011_SRT-A | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200512 | 26LEWISTWN | 200519 | 26REED TAP | 1 | 115 | 226 | 271 | 302.6 | 295.9 | 111.67 | 109.21 | AP_P2-2_WP-500-DRT16_SRT-W | Bus |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208133 | WHEM TR2 | 208021 | MANO TR4 | 2 | 230 | 229 | 593 | 599.2 | 647.1 | 101.05 | 109.13 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208133 | WHEM TR2 | 208021 | MANO TR4 | 2 | 230 | 229 | 593 | 599.2 | 647.1 | 101.04 | 109.12 | PECO_P4_PEACH235_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204529 | 27GERMANTN | 204530 | 27GERMANTN | 1 | 115/138 | 227 | 453 | 472.5 | 493.8 | 104.31 | 109 | AP_P1-2_WP-500-DRT17_SRT-W | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204529 | 27GERMANTN | 204530 | 27GERMANTN | 1 | 115/138 | 227 | 453 | 472.5 | 493.8 | 104.31 | 109 | AP_P1-2_PE-500-001_SRT-W | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200018 | CHALK PT | 200301 | X4-035 TAP | 1 | 500 | 225 | 1732 | 1899.1 | 1885.4 | 109.65 | 108.85 | DVP_P4-2: 514T595_SRT-SW | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204529 | 27GERMANTN | 204530 | 27GERMANTN | 1 | 115/138 | 227 | 453 | 469.6 | 492.7 | 103.66 | 108.77 | BG_P7_GRCTN_RAPHEL_SRT-A | Tower |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200018 | CHALK PT | 200301 | X4-035 TAP | 1 | 500 | 225 | 1732 | 1896.6 | 1883.6 | 109.5 | 108.75 | DVP_P1-2: LN 514_SRT-A | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200018 | CHALK PT | 200301 | X4-035 TAP | 1 | 500 | 225 | 1732 | 1896.6 | 1883.6 | 109.5 | 108.75 | AP_P1-2_PE-500-407T_SRT-W | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204529 | 27GERMANTN | 204530 | 27GERMANTN | 1 | 115/138 | 227 | 453 | 472.1 | 492.4 | 104.22 | 108.7 | AP_P1-2_WP-500-006_SRT-A | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220963 | CONASTON | 220962 | NWEST311 | 1 | 230 | 232 | 1381 | 1472.5 | 1500.8 | 106.63 | 108.68 | BG_P1_2322_SRT-A | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220963 | CONASTON | 220961 | NWEST326 | 1 | 230 | 232 | 1381 | 1471.4 | 1499.6 | 106.54 | 108.59 | BG_P1_2310_SRT-A | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 677.8 | 693.8 | 106.08 | 108.57 | AP_P2-2_WP-500-DRT16_SRT-W | Bus |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 2 | 500/230 | 225/232 | 2168 | 2281.7 | 2353.2 | 105.24 | 108.54 | BG_P1_CNSTN_500-2_SRT-A | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208393 | FARO DC TIE | 208394 | PPL-BGE TIE | 1 | 115 | 229 | 302 | 325.4 | 327.7 | 107.76 | 108.51 | PL_05_P71_000906_SRT-A | Tower |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 221051 | CHESTN8A | 221049 | FRED.RD8 | 1 | 115 | 232 | 215 | 225.9 | 233.2 | 105.06 | 108.48 | BG_P7_NEAST_RPHLRD_SRT-A | Tower |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220963 | CONASTON | 220962 | NWEST311 | 1 | 230 | 232 | 1381 | 1469.9 | 1497.5 | 106.44 | 108.43 | BG_P4_5_NW2322_230-4_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 1 | 500/230 | 225/232 | 2168 | 2279.2 | 2350.6 | 105.13 | 108.42 | BG_P1_CNSTN_500-4_SRT-A | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220963 | CONASTON | 220961 | NWEST326 | 1 | 230 | 232 | 1381 | 1468.8 | 1496.8 | 106.36 | 108.38 | BG_P4_5_NW2310_230-5_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220953 | HOWARD12 | 221010 | COLUMB12 | 1 | 230 | 232 | 1049 | 1166.6 | 1136 | 111.21 | 108.3 | PEPCO_P4_PP40_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204529 | 27GERMANTN | 204530 | 27GERMANTN | 1 | 115/138 | 227 | 453 | 468.3 | 490.5 | 103.38 | 108.28 | BG_P7_CNSTN_NWEST2_SRT-A | Tower |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200065 | PCHBTM2S | 200064 | PCHBTM1S | Z2 | 500 | 225 | 3022 | 3393.3 | 3268.4 | 112.29 | 108.15 | PECO_P1-2_5034_SRT-A | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200512 | 26LEWISTWN | 200519 | 26REED TAP | 1 | 115 | 226 | 271 | 296 | 293.1 | 109.22 | 108.15 | BG_P7_CNSTN_NWEST2_SRT-A | Tower |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 911 | 982.5 | 985.2 | 107.85 | 108.15 | PL_04_P12_000260_SRT-A | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200520 | 26ROXBURY | 200532 | 26ROXBURY | 2 | 115/138 | 226 | 364 | 351.3 | 393.6 | 96.52 | 108.13 | Base Case | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200512 | 26LEWISTWN | 200519 | 26REED TAP | 1 | 115 | 226 | 271 | 295.5 | 293 | 109.03 | 108.12 | BG_P7_GRCTN_RAPHEL_SRT-A | Tower |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200520 | 26ROXBURY | 200532 | 26ROXBURY | 2 | 115/138 | 226 | 435 | 416.1 | 469.6 | 95.66 | 107.97 | AP_P1-2_WP-500-006_SRT-A | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200520 | 26ROXBURY | 200532 | 26ROXBURY | 2 | 115/138 | 226 | 435 | 416.1 | 469.6 | 95.66 | 107.97 | AP_P1-2_PE-500-004_SRT-W | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220973 | GRANITE6 | 1 | 230 | 232 | 829 | 903.1 | 894.3 | 108.93 | 107.88 | BG_P7_NEAST_RPHLRD_SRT-A | Tower |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200762 | 26GARRETT | 235470 | 01GARRET | 1 | 115 | 226/201 | 190 | 203.5 | 204.9 | 107.11 | 107.85 | AP_P2-2_WP-500-DRT16_SRT-W | Bus |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220953 | HOWARD12 | 221010 | COLUMB12 | 1 | 230 | 232 | 1049 | 1160.7 | 1129.7 | 110.65 | 107.69 | PJM_500_BG_P4_5_CNSTN_J_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220964 | GRACETON | 221000 | BAGLEY | 5 | 230 | 232 | 1795 | 1870.5 | 1932.3 | 104.21 | 107.65 | PJM_500_BG_P1_5011_SRT-A | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200520 | 26ROXBURY | 200532 | 26ROXBURY | 2 | 115/138 | 226 | 435 | 412.8 | 468.3 | 94.9 | 107.65 | AP_P1-2_WP-500-DRT17_SRT-W | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220964 | GRACETON | 220999 | BAGLEY2 | 13 | 230 | 232 | 1795 | 1868.7 | 1930.5 | 104.1 | 107.55 | PJM_500_BG_P1_5011_SRT-A | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200512 | 26LEWISTWN | 200519 | 26REED TAP | 1 | 115 | 226 | 271 | 300.2 | 291.3 | 110.77 | 107.5 | ME_P2-2_ME-115-018_SRT-A | Bus |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208142 | WIGR-115 | 204520 | 27ALLEN | 1 | 115 | 227/229 | 351.4 | 350.8 | 377.4 | 99.84 | 107.38 | PECO_P1-2_5012_SRT-A | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208142 | WIGR-115 | 204520 | 27ALLEN | 1 | 115 | 227/229 | 351.4 | 350.8 | 377.4 | 99.84 | 107.38 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208142 | WIGR-115 | 204520 | 27ALLEN | 1 | 115 | 227/229 | 351.4 | 350.8 | 377.4 | 99.83 | 107.38 | PECO_P4_PEACH235_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 221100 | GLENARM1 | 221088 | WINDYED2 | 1 | 115 | 232 | 353 | 370.4 | 378.7 | 104.92 | 107.29 | BG_P7_GRCTN_RAPHEL_SRT-A | Tower |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208142 | WIGR-115 | 204520 | 27ALLEN | 1 | 115 | 227/229 | 351.4 | 350.2 | 377 | 99.66 | 107.28 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200512 | 26LEWISTWN | 200519 | 26REED TAP | 1 | 115 | 226 | 271 | 294 | 290.6 | 108.51 | 107.22 | BG_P7_NEAST_RPHLRD_SRT-A | Tower |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220972 | GRANITE1 | 1 | 230 | 232 | 829 | 898.4 | 888.2 | 108.37 | 107.14 | BG_P7_NEAST_RPHLRD_SRT-A | Tower |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220963 | CONASTON | 220962 | NWEST311 | 1 | 230 | 232 | 1381 | 1450.1 | 1478.8 | 105 | 107.08 | BG_P4_5_NW230-2_2322_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208395 | FARO FF | 208393 | FARO DC TIE | 1 | 69/115 | 229 | 120 | 127.2 | 128.4 | 105.98 | 107 | PL_04_P71_001819_SRT-A | Tower |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208395 | FARO FF | 208393 | FARO DC TIE | 2 | 69/115 | 229 | 120 | 127.2 | 128.4 | 105.98 | 107 | PL_04_P71_001819_SRT-A | Tower |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208396 | FARO | 208395 | FARO FF | 1 | 69 | 229 | 270 | 281.2 | 288.9 | 104.13 | 106.99 | PL_04_P12_000257_SRT-A | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220963 | CONASTON | 220961 | NWEST326 | 1 | 230 | 232 | 1381 | 1448.5 | 1477 | 104.89 | 106.95 | BG_P4_5_NW2371_2310_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208131 | WHEM | 208133 | WHEM TR2 | 1 | 230 | 229 | 691 | 699.1 | 739 | 101.18 | 106.95 | PECO_P4_PEACH245_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220963 | CONASTON | 220961 | NWEST326 | 1 | 230 | 232 | 1381 | 1448.5 | 1477 | 104.89 | 106.95 | BG_P4_5_NW230-3_2310_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220972 | GRANITE1 | 220953 | HOWARD12 | 1 | 230 | 232 | 772 | 827.5 | 825.4 | 107.19 | 106.91 | BG_P1_2332_SRT-A | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204693 | 27BOONETOWN | 204512 | 27S.RDG | 1 | 230 | 227 | 607 | 657.2 | 648.8 | 108.27 | 106.88 | PL_24_P12_101212_SRT-A | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208396 | FARO | 208395 | FARO FF | 1 | 69 | 229 | 270 | 280.4 | 288.3 | 103.84 | 106.76 | PL_05_P22_000674_SRT-A | Bus |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204529 | 27GERMANTN | 204530 | 27GERMANTN | 1 | 115/138 | 227 | 453 | 461.1 | 482.9 | 101.8 | 106.6 | BG_P7_NEAST_RPHLRD_SRT-A | Tower |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220960 | BRANDN.S | 220955 | W.CHAPEL | 43 | 230 | 232 | 1063 | 1159.5 | 1132.6 | 109.08 | 106.55 | PJM_500_BG_P4_5_CNSTN_J_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 221000 | BAGLEY | 220980 | RAPHAEL | 5 | 230 | 232 | 1795 | 1874.8 | 1912.3 | 104.45 | 106.54 | BG_P1_2313_SRT-A | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220999 | BAGLEY2 | 220980 | RAPHAEL | 13 | 230 | 232 | 1795 | 1874.9 | 1912.3 | 104.45 | 106.54 | BG_P1_2305_SRT-A | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220960 | BRANDN.S | 220955 | W.CHAPEL | 43 | 230 | 232 | 1063 | 1158.5 | 1131.7 | 108.98 | 106.46 | PEPCO_P4_PP40_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200023 | WESC | 211321 | WESC | 3 | 500/138 | 229/225 | 537 | 551.6 | 571.7 | 102.73 | 106.46 | PL_20_P24_001468_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200026 | HUNTERTN | 200004 | CNASTONE | 1 | 500 | 225 | 3024 | 3092.9 | 3215.4 | 102.28 | 106.33 | PECO_P1-2_5012_SRT-A | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200026 | HUNTERTN | 200004 | CNASTONE | 1 | 500 | 225 | 3024 | 3092.9 | 3215.4 | 102.28 | 106.33 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200026 | HUNTERTN | 200004 | CNASTONE | 1 | 500 | 225 | 3024 | 3092.9 | 3215.4 | 102.28 | 106.33 | PECO_P4_PEACH235_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200065 | PCHBTM2S | 200064 | PCHBTM1S | Z2 | 500 | 225 | 3022 | 3310.1 | 3211.8 | 109.53 | 106.28 | PJM_500_BG_P1_5013_SRT-A | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200065 | PCHBTM2S | 200064 | PCHBTM1S | Z2 | 500 | 225 | 3022 | 3310.1 | 3211.8 | 109.53 | 106.28 | PJM_500_BG_P4_5_CNSTN_M_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200512 | 26LEWISTWN | 200519 | 26REED TAP | 1 | 115 | 226 | 271 | 294.3 | 287.7 | 108.6 | 106.17 | AP_P7-1_PE-138-003_SRT-A | Tower |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208396 | FARO | 208395 | FARO FF | 1 | 69 | 229 | 223 | 226.9 | 236.6 | 101.73 | 106.09 | Base Case | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220999 | BAGLEY2 | 220980 | RAPHAEL | 13 | 230 | 232 | 1795 | 1832.3 | 1904.2 | 102.08 | 106.08 | PJM_500_BG_P1_5011_SRT-A | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 221090 | GLENARM2 | 221089 | WINDYED1 | 1 | 115 | 232 | 176 | 173.2 | 186.6 | 98.39 | 106.04 | Base Case | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 221000 | BAGLEY | 220980 | RAPHAEL | 5 | 230 | 232 | 1795 | 1827.6 | 1899.7 | 101.82 | 105.83 | PJM_500_BG_P1_5011_SRT-A | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220964 | GRACETON | 221094 | GRACE.-1 | 1 | 230/115 | 232 | 510 | 553 | 538.8 | 108.43 | 105.65 | BG_P7_GRCTN_RAPHEL_SRT-A | Tower |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220980 | RAPHAEL | 220965 | NEAST339 | 1 | 230 | 232 | 1340 | 1418.1 | 1415.7 | 105.83 | 105.65 | BG_P1_2317_SRT-A | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208394 | PPL-BGE TIE | 221092 | FIVE.FOR | 1 | 115 | 229/232 | 247 | 248.6 | 260.9 | 100.63 | 105.62 | PL_04_P71_001819_SRT-A | Tower |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200512 | 26LEWISTWN | 200519 | 26REED TAP | 1 | 115 | 226 | 271 | 293.5 | 286.2 | 108.3 | 105.62 | AP_P2-2_WP-500-DRT15_SRT-W | Bus |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200512 | 26LEWISTWN | 200519 | 26REED TAP | 1 | 115 | 226 | 271 | 292.8 | 285.9 | 108.03 | 105.48 | AP_P2-2_PE-138-021B_SRT-A | Bus |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200512 | 26LEWISTWN | 200519 | 26REED TAP | 1 | 115 | 226 | 271 | 292.4 | 285.7 | 107.89 | 105.43 | AP_P7-1_PE-138-017_SRT-A | Tower |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208021 | MANO TR4 | 208019 | MANO | 1 | 230 | 229 | 600 | 572.8 | 632.5 | 95.46 | 105.42 | PECO_P1-2_5012_SRT-A | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220964 | GRACETON | 221000 | BAGLEY | 5 | 230 | 232 | 1795 | 1831.9 | 1890.2 | 102.05 | 105.3 | PEPCO_P4_PP40_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220964 | GRACETON | 221000 | BAGLEY | 5 | 230 | 232 | 1795 | 1830.8 | 1888.6 | 101.99 | 105.21 | PJM_500_BG_P4_5_CNSTN_J_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220964 | GRACETON | 220999 | BAGLEY2 | 13 | 230 | 232 | 1795 | 1830 | 1888.4 | 101.95 | 105.2 | PEPCO_P4_PP40_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200026 | HUNTERTN | 200004 | CNASTONE | 1 | 500 | 225 | 3024 | 3070.4 | 3181.1 | 101.53 | 105.19 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 223960 | BRG 1T 230 | 1 | 500/230 | 225/233 | 1498 | 1569.6 | 1575.6 | 104.78 | 105.18 | PEPCO_P4_PP41_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220964 | GRACETON | 220999 | BAGLEY2 | 13 | 230 | 232 | 1795 | 1828.9 | 1886.7 | 101.89 | 105.11 | PJM_500_BG_P4_5_CNSTN_J_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220972 | GRANITE1 | 1 | 230 | 232 | 829 | 880.1 | 871.2 | 106.17 | 105.08 | BG_P4_5_GRNITE26_32_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200762 | 26GARRETT | 235470 | 01GARRET | 1 | 115 | 226/201 | 190 | 196.2 | 199.5 | 103.25 | 105.02 | AP_P7-1_MP-138-018_SRT-W | Tower |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208021 | MANO TR4 | 208019 | MANO | 1 | 230 | 229 | 600 | 567.8 | 629.7 | 94.64 | 104.95 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 1594 | 1581.6 | 105.7 | 104.88 | DVP_P4-2: GOOSE H1T558_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220977 | RIV2339 | 220960 | BRANDN.S | 44 | 230 | 232 | 1159 | 1218.9 | 1215 | 105.17 | 104.83 | PJM_500_BG_P1_5011_SRT-A | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220972 | GRANITE1 | 220953 | HOWARD12 | 1 | 230 | 232 | 772 | 805.9 | 809.2 | 104.39 | 104.82 | BG_P7_WCHPL_BRNDN_SRT-A | Tower |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204546 | 27MOUNTAIN | 204528 | 27GARDNERS | 1 | 115 | 227 | 190 | 188.2 | 199.2 | 99.04 | 104.82 | PECO_P1-2_5012_SRT-A | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204546 | 27MOUNTAIN | 204528 | 27GARDNERS | 1 | 115 | 227 | 190 | 188.2 | 199.2 | 99.04 | 104.82 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204546 | 27MOUNTAIN | 204528 | 27GARDNERS | 1 | 115 | 227 | 190 | 188.2 | 199.1 | 99.03 | 104.81 | PECO_P4_PEACH235_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220973 | GRANITE6 | 1 | 230 | 232 | 829 | 879.6 | 868.3 | 106.1 | 104.75 | BBG_P1_2311_SRT-A | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220972 | GRANITE1 | 1 | 230 | 232 | 829 | 876.7 | 867.5 | 105.76 | 104.65 | BG_P1_2326_SRT-A | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220973 | GRANITE6 | 1 | 230 | 232 | 829 | 874.2 | 867 | 105.45 | 104.59 | BG_P1_2312_SRT-A | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204546 | 27MOUNTAIN | 204528 | 27GARDNERS | 1 | 115 | 227 | 190 | 187.6 | 198.6 | 98.76 | 104.51 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220980 | RAPHAEL | 220979 | NEAST317 | 1 | 230 | 232 | 1340 | 1402.8 | 1399.6 | 104.68 | 104.45 | BG_P1_2339_SRT-A | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220973 | GRANITE6 | 1 | 230 | 232 | 829 | 874.2 | 865.7 | 105.45 | 104.43 | BG_P4_5_GRNITE11_12_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200519 | 26REED TAP | 200522 | 26SHADE GP | 1 | 115 | 226 | 271 | 281.7 | 282.9 | 103.93 | 104.39 | AP_P2-2_WP-500-DRT16_SRT-W | Bus |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 221054 | CHESTN7A | 221050 | FRED.RD7 | 1 | 115 | 232 | 215 | 216.8 | 224 | 100.83 | 104.18 | BG_P7_NEAST_RPHLRD_SRT-A | Tower |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 2 | 500/230 | 225/232 | 2168 | 2197.5 | 2257.5 | 101.36 | 104.13 | PJM_500_BG_P2_CNSTN_230-N_SRT-A | Bus |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220977 | RIV2339 | 220960 | BRANDN.S | 44 | 230 | 232 | 1159 | 1210.4 | 1206.8 | 104.44 | 104.12 | PEPCO_P4_PP40_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220977 | RIV2339 | 220960 | BRANDN.S | 44 | 230 | 232 | 1159 | 1210.4 | 1206.7 | 104.44 | 104.11 | PJM_500_BG_P4_5_CNSTN_J_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208396 | FARO | 208395 | FARO FF | 1 | 69 | 229 | 270 | 267.5 | 280.9 | 99.09 | 104.06 | BG_P7_CNSTN_NWEST2_SRT-A | Tower |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 1 | 500/230 | 225/232 | 2168 | 2195.1 | 2255 | 101.25 | 104.01 | PJM_500_BG_P2_CNSTN_230-S_SRT-A | Bus |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220979 | NEAST317 | 220966 | RIV2317 | 1 | 230 | 232 | 940 | 973.9 | 977.7 | 103.6 | 104.01 | BG_P1_2339_SRT-A | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200065 | PCHBTM2S | 200064 | PCHBTM1S | Z2 | 500 | 225 | 3022 | 3253.6 | 3142.1 | 107.66 | 103.97 | PECO_P4_NOTTI55_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200065 | PCHBTM2S | 200064 | PCHBTM1S | Z2 | 500 | 225 | 3022 | 3249.4 | 3138.2 | 107.53 | 103.85 | PECO_P2-2_NOTT230B_SRT-A | Bus |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208393 | FARO DC TIE | 208394 | PPL-BGE TIE | 1 | 115 | 229 | 302 | 314.2 | 313.6 | 104.05 | 103.83 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200762 | 26GARRETT | 235470 | 01GARRET | 1 | 115 | 226/201 | 190 | 194.1 | 197.2 | 102.15 | 103.79 | AP_P2-2_MP-138-001_SRT-A | Bus |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208393 | FARO DC TIE | 208394 | PPL-BGE TIE | 1 | 115 | 229 | 302 | 314.1 | 313.4 | 104 | 103.76 | PECO_P4_PEACH235_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208395 | FARO FF | 208393 | FARO DC TIE | 1 | 69/115 | 229 | 120 | 124.1 | 124.5 | 103.43 | 103.76 | PL_04_P12_000260_SRT-A | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208393 | FARO DC TIE | 208394 | PPL-BGE TIE | 1 | 115 | 229 | 302 | 314.1 | 313.4 | 104 | 103.76 | PECO_P1-2_5012_SRT-A | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208393 | FARO DC TIE | 208394 | PPL-BGE TIE | 1 | 115 | 229 | 302 | 314.1 | 313.4 | 104 | 103.76 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208395 | FARO FF | 208393 | FARO DC TIE | 2 | 69/115 | 229 | 120 | 124.1 | 124.5 | 103.43 | 103.75 | PL_04_P12_000260_SRT-A | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220999 | BAGLEY2 | 220980 | RAPHAEL | 13 | 230 | 232 | 1795 | 1793.6 | 1862 | 99.92 | 103.73 | PEPCO_P4_PP40_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200026 | HUNTERTN | 200004 | CNASTONE | 1 | 500 | 225 | 3024 | 3067.9 | 3136.3 | 101.45 | 103.71 | PECO_P4_PEACH245_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200065 | PCHBTM2S | 200064 | PCHBTM1S | Z2 | 500 | 225 | 3022 | 3243.5 | 3133.9 | 107.33 | 103.7 | PECO_P1-2_220-08_SRT-A | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220999 | BAGLEY2 | 220980 | RAPHAEL | 13 | 230 | 232 | 1795 | 1792.6 | 1860.4 | 99.86 | 103.65 | PJM_500_BG_P4_5_CNSTN_J_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 929.7 | 921.1 | 104.57 | 103.61 | ME_P2-2_ME-115-003_SRT-A | Bus |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204528 | 27GARDNERS | 200504 | 26CARLISLE | 1 | 115 | 226/227 | 190 | 185.3 | 196.8 | 97.55 | 103.58 | BG_P7_GRNITE_HIRDG_SRT-A | Tower |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200065 | PCHBTM2S | 200064 | PCHBTM1S | Z2 | 500 | 225 | 3022 | 3235.1 | 3128.6 | 107.05 | 103.53 | PECO_P1-2_220-93_SRT-A | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200762 | 26GARRETT | 235470 | 01GARRET | 1 | 115 | 226/201 | 190 | 193.7 | 196.7 | 101.97 | 103.52 | AP_P2-2_MP-138-101_SRT-A | Bus |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220979 | NEAST317 | 220966 | RIV2317 | 1 | 230 | 232 | 940 | 969.6 | 973 | 103.15 | 103.51 | BG_P4_5_RVRSIDE_39_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 221000 | BAGLEY | 220980 | RAPHAEL | 5 | 230 | 232 | 1795 | 1788.9 | 1857.6 | 99.66 | 103.49 | PEPCO_P4_PP40_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208021 | MANO TR4 | 208019 | MANO | 1 | 230 | 229 | 600 | 564.1 | 620.8 | 94.02 | 103.46 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208021 | MANO TR4 | 208019 | MANO | 1 | 230 | 229 | 600 | 564 | 620.7 | 94.01 | 103.46 | PECO_P4_PEACH235_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200762 | 26GARRETT | 235470 | 01GARRET | 1 | 115 | 226/201 | 190 | 194.9 | 196.6 | 102.58 | 103.45 | AP_P2-2_WP-500-DRT17_SRT-W | Bus |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 221000 | BAGLEY | 220980 | RAPHAEL | 5 | 230 | 232 | 1795 | 1787.8 | 1856 | 99.6 | 103.4 | PJM_500_BG_P4_5_CNSTN_J_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 927.1 | 918.8 | 104.28 | 103.36 | AP_P7-1_PE-138-022T_SRT-A | Tower |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 927.1 | 918.8 | 104.28 | 103.36 | AP_P2-2_PE-138-073_SRT-A | Bus |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200519 | 26REED TAP | 200522 | 26SHADE GP | 1 | 115 | 226 | 271 | 275 | 280 | 101.49 | 103.34 | BG_P7_CNSTN_NWEST2_SRT-A | Tower |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200519 | 26REED TAP | 200522 | 26SHADE GP | 1 | 115 | 226 | 271 | 274.5 | 280 | 101.29 | 103.31 | BG_P7_GRCTN_RAPHEL_SRT-A | Tower |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213553 | 220-05 TAP | 213844 | NOTTNGHM | 1 | 230 | 230 | 598 | 660.7 | 617 | 110.48 | 103.18 | PECO_P1-2_5012_SRT-A | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 221094 | GRACE.-1 | 221092 | FIVE.FOR | 1 | 115 | 232 | 498 | 502.6 | 512.8 | 100.92 | 102.96 | BG_P7_NEAST_RPHLRD_SRT-A | Tower |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 221090 | GLENARM2 | 221089 | WINDYED1 | 1 | 115 | 232 | 222 | 215.9 | 228.4 | 97.25 | 102.87 | BG_P1_2313_SRT-A | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 221090 | GLENARM2 | 221089 | WINDYED1 | 1 | 115 | 232 | 222 | 215.9 | 228.4 | 97.25 | 102.87 | BG_P1_2305_SRT-A | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 221092 | FIVE.FOR | 221095 | ROCKRGE2 | 1 | 115 | 232 | 340 | 334.7 | 349.7 | 98.43 | 102.86 | BG_P1_110511_SRT-A | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208394 | PPL-BGE TIE | 221092 | FIVE.FOR | 1 | 115 | 229/232 | 247 | 243.1 | 254 | 98.42 | 102.85 | PL_04_P12_000260_SRT-A | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204693 | 27BOONETOWN | 204512 | 27S.RDG | 1 | 230 | 227 | 529 | 549 | 544 | 103.78 | 102.83 | Base Case | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200519 | 26REED TAP | 200522 | 26SHADE GP | 1 | 115 | 226 | 271 | 279.2 | 278.3 | 103.03 | 102.71 | ME_P2-2_ME-115-018_SRT-A | Bus |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220973 | GRANITE6 | 1 | 230 | 232 | 829 | 857.1 | 850.3 | 103.38 | 102.57 | BG_P7_HIRDG_SNWDNRVR_SRT-A | Tower |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 235112 | 01PRNTY | 314937 | 8MT STORM2 | 1 | 500 | 201/345 | 4409 | 4548.9 | 4518.1 | 103.17 | 102.48 | DVP_P4-2: 536T550_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200519 | 26REED TAP | 200522 | 26SHADE GP | 1 | 115 | 226 | 271 | 273.1 | 277.5 | 100.77 | 102.42 | BG_P7_NEAST_RPHLRD_SRT-A | Tower |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204514 | 27TMI | 204502 | 27JACKSON | 1 | 230 | 227 | 781 | 807.7 | 799.3 | 103.42 | 102.34 | PL_14_P12_000268_SRT-A | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204514 | 27TMI | 204502 | 27JACKSON | 1 | 230 | 227 | 781 | 807.7 | 799.3 | 103.42 | 102.34 | ME_P1-2_ME-230-218T_SRT-A | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220972 | GRANITE1 | 220953 | HOWARD12 | 1 | 230 | 232 | 772 | 792.8 | 789.4 | 102.7 | 102.26 | BG_P4_5_PMP519_230-1_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 919.6 | 916.7 | 102.52 | 102.2 | PL_04_P12_000257_SRT-A | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 235112 | 01PRNTY | 314937 | 8MT STORM2 | 1 | 500 | 201/345 | 4409 | 4543.5 | 4502.8 | 103.05 | 102.13 | AP_P1-2_WP-500-304T_SRT-A | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 235112 | 01PRNTY | 314937 | 8MT STORM2 | 1 | 500 | 201/345 | 4409 | 4543.5 | 4501.8 | 103.05 | 102.1 | DVP_P4-2: 53672_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208395 | FARO FF | 208393 | FARO DC TIE | 1 | 69/115 | 229 | 120 | 121.4 | 122.5 | 101.21 | 102.05 | BG_P1_2305_SRT-A | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208395 | FARO FF | 208393 | FARO DC TIE | 2 | 69/115 | 229 | 120 | 121.5 | 122.5 | 101.21 | 102.05 | BG_P1_2313_SRT-A | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200762 | 26GARRETT | 235470 | 01GARRET | 1 | 115 | 226/201 | 190 | 190.3 | 193.6 | 100.15 | 101.9 | AP_P7-1_MP-138-056_SRT-A | Tower |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200762 | 26GARRETT | 235470 | 01GARRET | 1 | 115 | 226/201 | 190 | 190.4 | 193.6 | 100.2 | 101.87 | AP_P2-2_WP-138-043_SRT-A | Bus |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208133 | WHEM TR2 | 208021 | MANO TR4 | 2 | 230 | 229 | 593 | 567.5 | 603.9 | 95.7 | 101.84 | PECO_P4_PEACH245_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220973 | GRANITE6 | 220954 | HOWARD32 | 1 | 230 | 232 | 772 | 787.4 | 786 | 102 | 101.82 | BG_P1_2312_SRT-A | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200011 | KEYSTONE | 235118 | 01SOBEND | 1 | 500 | 225/201 | 2598 | 2711.9 | 2645.1 | 104.38 | 101.81 | PN_P2-3_PN-500-DRT28_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 915.8 | 912.7 | 102.1 | 101.75 | PL_05_P22_000674_SRT-A | Bus |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 221051 | CHESTN8A | 221049 | FRED.RD8 | 1 | 115 | 232 | 215 | 212.3 | 218.5 | 98.73 | 101.61 | BG_P7_GRNITE_HIRDG_SRT-A | Tower |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220972 | GRANITE1 | 220953 | HOWARD12 | 1 | 230 | 232 | 772 | 787.8 | 784.3 | 102.05 | 101.59 | BG_P4_5_HR230-5_2332_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200065 | PCHBTM2S | 200064 | PCHBTM1S | Z2 | 500 | 225 | 3022 | 3170.9 | 3069.8 | 104.93 | 101.58 | PL_05_P71_000906_SRT-A | Tower |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208393 | FARO DC TIE | 208394 | PPL-BGE TIE | 1 | 115 | 229 | 302 | 297.5 | 306.8 | 98.51 | 101.58 | BG_P7_GRCTN_RAPHEL_SRT-A | Tower |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 2 | 500/230 | 225/232 | 2168 | 2134.3 | 2200.8 | 98.45 | 101.51 | PJM_500_BG_P4_5_CNSTN_L_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 2 | 500/230 | 225/232 | 2168 | 2139.8 | 2199.9 | 98.7 | 101.47 | PJM_500_BG_P4_5_CNSTN_9_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 221092 | FIVE.FOR | 221095 | ROCKRGE2 | 1 | 115 | 232 | 340 | 329 | 344.7 | 96.77 | 101.4 | BG_P4_5_WE511_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200519 | 26REED TAP | 200522 | 26SHADE GP | 1 | 115 | 226 | 271 | 273.3 | 274.7 | 100.86 | 101.37 | AP_P7-1_PE-138-003_SRT-A | Tower |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 1 | 500/230 | 225/232 | 2168 | 2137.5 | 2197.6 | 98.59 | 101.36 | PJM_500_BG_P4_5_CNSTN_12_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208142 | WIGR-115 | 204520 | 27ALLEN | 1 | 115 | 227/229 | 351.4 | 337.1 | 356 | 95.93 | 101.3 | PECO_P4_PEACH245_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 910.9 | 900.2 | 102.47 | 101.25 | PL_04_P71_100954_SRT-A | Tower |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220965 | NEAST339 | 220977 | RIV2339 | 1 | 230 | 232 | 991 | 1001.3 | 1002.8 | 101.04 | 101.19 | BG_P1_2317_SRT-A | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204529 | 27GERMANTN | 204530 | 27GERMANTN | 1 | 115/138 | 227 | 453 | 442 | 458.1 | 97.57 | 101.12 | BG_P7_GRNITE_HIRDG_SRT-A | Tower |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208394 | PPL-BGE TIE | 221092 | FIVE.FOR | 1 | 115 | 229/232 | 247 | 237.1 | 249.7 | 96 | 101.1 | BG_P1_2313_SRT-A | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204529 | 27GERMANTN | 204530 | 27GERMANTN | 1 | 115/138 | 227 | 453 | 444.9 | 458 | 98.2 | 101.09 | AP_P2-2_WP-500-DRT16_SRT-W | Bus |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200519 | 26REED TAP | 200522 | 26SHADE GP | 1 | 115 | 226 | 271 | 272.5 | 273.2 | 100.56 | 100.82 | AP_P2-2_WP-500-DRT15_SRT-W | Bus |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200519 | 26REED TAP | 200522 | 26SHADE GP | 1 | 115 | 226 | 271 | 271.8 | 272.9 | 100.29 | 100.68 | AP_P2-2_PE-138-021B_SRT-A | Bus |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204529 | 27GERMANTN | 204530 | 27GERMANTN | 1 | 115/138 | 227 | 453 | 439.4 | 456 | 96.99 | 100.67 | AP_P2-2_WP-138-074_SRT-A | Bus |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200519 | 26REED TAP | 200522 | 26SHADE GP | 1 | 115 | 226 | 271 | 271.4 | 272.7 | 100.15 | 100.64 | AP_P7-1_PE-138-017_SRT-A | Tower |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200065 | PCHBTM2S | 200064 | PCHBTM1S | Z2 | 500 | 225 | 3022 | 3150.4 | 3040.2 | 104.25 | 100.6 | PL_04_P71_001014_SRT-A | Tower |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220965 | NEAST339 | 220977 | RIV2339 | 1 | 230 | 232 | 991 | 995.1 | 996.4 | 100.42 | 100.55 | BG_P4_5_RVRSIDE_17_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200011 | KEYSTONE | 235104 | 01CABOT | 1 | 500 | 225/201 | 3106 | 3209 | 3121.6 | 103.32 | 100.5 | AP_P2-3_WP-500-707T_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200011 | KEYSTONE | 235104 | 01CABOT | 1 | 500 | 225/201 | 3106 | 3209 | 3121.4 | 103.32 | 100.49 | AP_P2-3_WP-500-696_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200011 | KEYSTONE | 235104 | 01CABOT | 1 | 500 | 225/201 | 3106 | 3212 | 3120.8 | 103.41 | 100.48 | AP_P2-3_WP-500-706T_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200011 | KEYSTONE | 235104 | 01CABOT | 1 | 500 | 225/201 | 3106 | 3207.9 | 3120.5 | 103.28 | 100.47 | AP_P2-3_WP-500-440T_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 221092 | FIVE.FOR | 221096 | ROCKRGE1 | 1 | 115 | 232 | 293 | 282.3 | 294.2 | 96.34 | 100.4 | BG_P1_2313_SRT-A | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 221092 | FIVE.FOR | 221096 | ROCKRGE1 | 1 | 115 | 232 | 293 | 282.3 | 294.2 | 96.34 | 100.4 | BG_P1_2305_SRT-A | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 902.4 | 892.4 | 101.51 | 100.38 | DVP_P7-1: LN 2114-535_SRT-SW | Tower |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 911 | 869.4 | 914.5 | 95.44 | 100.38 | PJM_500_BG_P1_5011_SRT-A | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 901.6 | 891.7 | 101.42 | 100.3 | DVP_P7-1: LN 2222-535_SRT-A | Tower |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208393 | FARO DC TIE | 208394 | PPL-BGE TIE | 1 | 115 | 229 | 302 | 303.2 | 302.8 | 100.39 | 100.27 | PECO_P4_PEACH245_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200065 | PCHBTM2S | 200064 | PCHBTM1S | Z2 | 500 | 225 | 3022 | 3128.1 | 3023.6 | 103.51 | 100.05 | PL_05_P22_000674_SRT-A | Bus |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214277 | RICHMOND35 | 214012 | WANEETA3 | 1 | 230 | 230 | 803 | 1166.3 | 1145.6 | 145.24 | 142.67 | Base Case | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214277 | RICHMOND35 | 214012 | WANEETA3 | 1 | 230 | 230 | 1201 | 1585.2 | 1550.8 | 131.99 | 129.13 | PECO_P4_PEACH215_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214010 | WANEETA2 | 213817 | N PHILA | 1 | 230 | 230 | 674 | 869.8 | 850.5 | 129.05 | 126.18 | PECO_P4_CHICH045_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214010 | WANEETA2 | 213817 | N PHILA | 1 | 230 | 230 | 674 | 869.6 | 850.5 | 129.02 | 126.18 | PECO_P2-2_CHI230B1_SRT-A | Bus |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214010 | WANEETA2 | 213817 | N PHILA | 1 | 230 | 230 | 674 | 869.6 | 850.4 | 129.03 | 126.18 | PECO_P4_CHICH435_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214010 | WANEETA2 | 213817 | N PHILA | 1 | 230 | 230 | 674 | 870 | 850.4 | 129.07 | 126.18 | PECO_P4_CHICH195_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214277 | RICHMOND35 | 214012 | WANEETA3 | 1 | 230 | 230 | 1201 | 1544.3 | 1512.7 | 128.58 | 125.95 | PECO_P1-2_5014_SRT-A | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214277 | RICHMOND35 | 214012 | WANEETA3 | 1 | 230 | 230 | 1201 | 1543.3 | 1511.8 | 128.5 | 125.88 | PECO_P4_PEACH205_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214277 | RICHMOND35 | 214012 | WANEETA3 | 1 | 230 | 230 | 1201 | 1532.6 | 1503.1 | 127.61 | 125.16 | PECO_P2-2_CHI230B1_SRT-A | Bus |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214277 | RICHMOND35 | 214012 | WANEETA3 | 1 | 230 | 230 | 1201 | 1532.9 | 1503.1 | 127.63 | 125.16 | PECO_P4_CHICH045_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214277 | RICHMOND35 | 214012 | WANEETA3 | 1 | 230 | 230 | 1201 | 1532.9 | 1503.1 | 127.64 | 125.15 | PECO_P4_CHICH195_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214277 | RICHMOND35 | 214012 | WANEETA3 | 1 | 230 | 230 | 1201 | 1532.6 | 1503.1 | 127.61 | 125.15 | PECO_P4_CHICH435_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214277 | RICHMOND35 | 214012 | WANEETA3 | 1 | 230 | 230 | 1201 | 1484.2 | 1454.8 | 123.58 | 121.13 | PJM500_PS_P1-2_5015_SRT-A | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 231004 | RL_230 | 231003 | KEEN_230 | 1 | 230 | 235 | 1171 | 1442.7 | 1413 | 123.21 | 120.67 | PJM500_DPL_P1_2_KEENEY-RED LION_SRT-A | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 231004 | RL_230 | 231003 | KEEN_230 | 1 | 230 | 235 | 1171 | 1367.1 | 1340.2 | 116.74 | 114.45 | PJM500_DPL_P4_2_REDLION-KEENEY AT50_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214277 | RICHMOND35 | 214012 | WANEETA3 | 1 | 230 | 230 | 1201 | 1397.7 | 1373.1 | 116.37 | 114.33 | PECO_P1-2_5025/* $ CHESCO $ PECO_P1-2_5025 $ L_SRT-A | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214277 | RICHMOND35 | 214012 | WANEETA3 | 1 | 230 | 230 | 1201 | 1365 | 1339.5 | 113.66 | 111.53 | PJM500_DPL_P1_2_KEENEY-RED LION_SRT-A | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 231004 | RL_230 | 231003 | KEEN_230 | 1 | 230 | 235 | 1171 | 1323.5 | 1298.3 | 113.02 | 110.87 | PJM500_DPL_P4_2_REDLION-KEENEY AT51_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214277 | RICHMOND35 | 214012 | WANEETA3 | 1 | 230 | 230 | 1201 | 1329.9 | 1305.8 | 110.73 | 108.72 | PECO_P2-2_EMI138B2_SRT-A | Bus |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214277 | RICHMOND35 | 214012 | WANEETA3 | 1 | 230 | 230 | 1201 | 1322.6 | 1298.4 | 110.12 | 108.11 | PECO_P1-2_130-25_SRT-A | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214010 | WANEETA2 | 213817 | N PHILA | 1 | 230 | 230 | 674 | 745.1 | 727.9 | 110.55 | 108 | PJM500_DPL_P4_2_REDLION-HOPE AT51_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214010 | WANEETA2 | 213817 | N PHILA | 1 | 230 | 230 | 674 | 744.6 | 727.4 | 110.48 | 107.92 | PJM500_DPL_P4_2_REDLION-HOPE AT50_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214010 | WANEETA2 | 213817 | N PHILA | 1 | 230 | 230 | 674 | 743.6 | 726.4 | 110.33 | 107.78 | PJM500_PS_P1-2_5015_SRT-A | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213438 | BRADFRD1 | 213553 | 220-05 TAP | 1 | 230 | 230 | 598 | 686.2 | 644.1 | 114.74 | 107.7 | PECO_P1-2_5012_SRT-A | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214277 | RICHMOND35 | 214012 | WANEETA3 | 1 | 230 | 230 | 1201 | 1304.7 | 1280.6 | 108.63 | 106.63 | PECO_P2-2_NES138B9_SRT-A | Bus |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214277 | RICHMOND35 | 214012 | WANEETA3 | 1 | 230 | 230 | 1201 | 1302 | 1278.2 | 108.41 | 106.43 | PECO_P2-2_NES138B8_SRT-A | Bus |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214277 | RICHMOND35 | 214012 | WANEETA3 | 1 | 230 | 230 | 1201 | 1301.3 | 1277.6 | 108.35 | 106.38 | PECO_CBO_NESH785_SRT-A | Bus |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213566 | EDDINGTN | 213664 | HOLMSBTP | 1 | 230 | 230 | 632 | 682 | 670.3 | 107.91 | 106.05 | PS_P1-2_C-220-29_SRT-A | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213566 | EDDINGTN | 213664 | HOLMSBTP | 1 | 230 | 230 | 632 | 682 | 670 | 107.92 | 106.02 | PECO_P1-2_220-29_SRT-A | Single |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214012 | WANEETA3 | 214010 | WANEETA2 | Z | 230 | 230 | 1164 | 1216.6 | 1198.1 | 104.52 | 102.93 | PECO_P2-2_CHI230B1_SRT-A | Bus |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214012 | WANEETA3 | 214010 | WANEETA2 | Z | 230 | 230 | 1164 | 1216.9 | 1198.1 | 104.54 | 102.93 | PECO_P4_CHICH045_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214012 | WANEETA3 | 214010 | WANEETA2 | Z | 230 | 230 | 1164 | 1217 | 1198.1 | 104.55 | 102.93 | PECO_P4_CHICH195_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214012 | WANEETA3 | 214010 | WANEETA2 | Z | 230 | 230 | 1164 | 1216.7 | 1198.1 | 104.52 | 102.93 | PECO_P4_CHICH435_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213566 | EDDINGTN | 213664 | HOLMSBTP | 1 | 230 | 230 | 632 | 660.6 | 648.9 | 104.53 | 102.68 | PS_P2-2_CAMDEN_14_SRT-A | Bus |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213566 | EDDINGTN | 213664 | HOLMSBTP | 1 | 230 | 230 | 632 | 660.6 | 648.9 | 104.53 | 102.68 | PS_P2-3_CAMD_1314_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213566 | EDDINGTN | 213664 | HOLMSBTP | 1 | 230 | 230 | 632 | 660.6 | 648.9 | 104.53 | 102.68 | PS_P2-3_CAMD_2-14_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213566 | EDDINGTN | 213664 | HOLMSBTP | 1 | 230 | 230 | 632 | 660.7 | 648.7 | 104.53 | 102.64 | PECO_P4_RICHM415_SRT-A | Breaker |  | NO | Related to 2022 Window 3, pending window outcome

## Winter IPD
| Note | APS and Dominion zones as a whole are quarantined pending Window 3 outcome and are not included in above results
Related to 2022 Window 3, pending window outcome
2028 RTEP PJM Individual Plant Deliverability Result (Winter)
FG # | Fr Bus | Name | To Bus | Name | CKT | KVs | Areas | Rating | FN DC % | FN AC % | Plant | Cont Label | Conductor/Transformer Rating (MVA) | PJM Accepting Proposals | Reason For Exclusion | Comments
2023W1-IPD-W1 | 243598 | 05BCKSKI | 253030 | 09GRNFLD | 1 | 69 | 205/209 | 72 | 150.13 | 152.92 | AC2-060 | AEP_P4_#14130_05BCKSKI 69.0_A_SRT-A | AEP side:162/176 (WN/WE); Dayton side: 110/122 (WN/WE) | NO | Below 200 kV Exclusion | Dayton-2023-002 increases the rating to Dayton conductor rating
2023W1-IPD-W2 | 204571 | 27ZIONS VW | 205947 | AE1-129_POI | 1 | 115 | 227 | 156 | 103.26 | 113.11 | AE1-129 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | 149/189 (WN/WE) | NO | Substation Equipment Exclusion / Below 200 kV Exclusion
2023W1-IPD-W3 | 204571 | 27ZIONS VW | 205947 | AE1-129_POI | 1 | 115 | 227 | 156 | 103.22 | 113.08 | AE1-129 | PECO_P1-2_5012_SRT-A | 149/189 (WN/WE) | NO | Substation Equipment Exclusion / Below 200 kV Exclusion
2023W1-IPD-W4 | 204571 | 27ZIONS VW | 205947 | AE1-129_POI | 1 | 115 | 227 | 156 | 103.22 | 113.08 | AE1-129 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | 149/189 (WN/WE) | NO | Substation Equipment Exclusion / Below 200 kV Exclusion
2023W1-IPD-W5 | 204571 | 27ZIONS VW | 205947 | AE1-129_POI | 1 | 115 | 227 | 156 | 103.21 | 113.08 | AE1-129 | PECO_P4_PEACH235_SRT-A | 149/189 (WN/WE) | NO | Substation Equipment Exclusion / Below 200 kV Exclusion
2023W1-IPD-W6 | 204571 | 27ZIONS VW | 205947 | AE1-129_POI | 1 | 115 | 227 | 156 | 115.45 | 112.96 | AE1-129 | ME_P2-3_ME-115-033E_SRT-A | 149/189 (WN/WE) | NO | Substation Equipment Exclusion / Below 200 kV Exclusion
2023W1-IPD-W7 | 204571 | 27ZIONS VW | 205947 | AE1-129_POI | 1 | 115 | 227 | 156 | 100.36 | 106.54 | AE1-129 | PECO_P4_PEACH245_SRT-A | 149/189 (WN/WE) | NO | Substation Equipment Exclusion / Below 200 kV Exclusion
N/A | 200504 | 26CARLISLE | 204528 | 27GARDNERS | 1 | 115 | 226/227 | 150 | 93.91 | 100.6 | AC1-158 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.33 | 157.45 | 01CROSSCHOOL | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.33 | 157.45 | 01CROSSCHOOL | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 161.84 | 154.61 | 01CROSSCHOOL | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 155.9 | 150.75 | 01CROSSCHOOL | PN_P1-2_PN-500-010T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.21 | 148.08 | 01CROSSCHOOL | PJM_500_BG_P4_5_CNSTN_L_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.5 | 148.06 | 01CROSSCHOOL | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.3 | 147.87 | 01CROSSCHOOL | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.32 | 147.86 | 01CROSSCHOOL | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.05 | 147.66 | 01CROSSCHOOL | PECO_P4_NOTTI85_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.99 | 147.65 | 01CROSSCHOOL | PECO_P1-2_220-08_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.92 | 147.58 | 01CROSSCHOOL | PECO_P4_COOPR125_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 142.85 | 146.94 | 01CROSSCHOOL | AP_P1-2_PE-500-004_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 142.85 | 146.94 | 01CROSSCHOOL | AP_P2-3_WP-500-DRT19_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 142.85 | 146.94 | 01CROSSCHOOL | AP_P2-3_WP-500-466_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 142.85 | 146.94 | 01CROSSCHOOL | AP_P1-2_WP-500-006_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 142.85 | 146.94 | 01CROSSCHOOL | AP_P2-3_PE-500-014_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 151.05 | 144.34 | 01CROSSCHOOL | PECO_P4_PEACH025_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.93 | 144.25 | 01CROSSCHOOL | PECO_P1-2_PBTIE1_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 137.17 | 139.14 | 01CROSSCHOOL | AP_P2-3_WP-500-706T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 132.52 | 134.53 | 01CROSSCHOOL | AP_P2-3_MP-138-150_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 139.18 | 133.02 | 01CROSSCHOOL | PECO_P1-2_PBTIE2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 225.37 | 236.62 | 01GRNGAP | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 223.37 | 236.62 | 01GRNGAP | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 225.3 | 236.56 | 01GRNGAP | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 223.3 | 236.56 | 01GRNGAP | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 225.3 | 236.56 | 01GRNGAP | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 223.3 | 236.56 | 01GRNGAP | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 213.32 | 226.48 | 01GRNGAP | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 213.26 | 226.42 | 01GRNGAP | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 213.26 | 226.41 | 01GRNGAP | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 209.07 | 223.26 | 01GRNGAP | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 209 | 223.2 | 01GRNGAP | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 209 | 223.2 | 01GRNGAP | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 210.47 | 217.51 | 01GRNGAP | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 208.47 | 217.5 | 01GRNGAP | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 198.94 | 207.95 | 01GRNGAP | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 194.68 | 204.6 | 01GRNGAP | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 172.63 | 167.63 | 01GRNGAP | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 171.66 | 166.19 | 01GRNGAP | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 171.66 | 166.19 | 01GRNGAP | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 171.64 | 166.18 | 01GRNGAP | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 163.48 | 164.7 | 01GRNGAP | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200504 | 26CARLISLE | 204528 | 27GARDNERS | 1 | 115 | 226/227 | 150 | 99.75 | 107.19 | AD1-020 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 161.61 | 161.62 | 01GRNGAP | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 161.61 | 161.62 | 01GRNGAP | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 161.6 | 161.61 | 01GRNGAP | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 163.71 | 158.73 | 01GRNGAP | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 153.39 | 157.8 | 01GRNGAP | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 161.89 | 157 | 01GRNGAP | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 161.89 | 157 | 01GRNGAP | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 151.71 | 156.48 | 01GRNGAP | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 161.32 | 154.1 | 01GRNGAP | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 148.35 | 152.83 | 01GRNGAP | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 903 | 144.16 | 151.94 | 01GRNGAP | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 152.67 | 151.01 | 01GRNGAP | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 155.47 | 150.31 | 01GRNGAP | PN_P1-2_PN-500-010T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 903 | 142.62 | 149.32 | 01GRNGAP | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 903 | 142.62 | 149.32 | 01GRNGAP | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 903 | 142.61 | 149.31 | 01GRNGAP | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.19 | 149.23 | 01GRNGAP | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.12 | 149.15 | 01GRNGAP | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.83 | 147.99 | 01GRNGAP | AP_P2-3_PE-500-016_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.9 | 147.96 | 01GRNGAP | AP_P2-3_PE-500-015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.79 | 147.65 | 01GRNGAP | PJM_500_BG_P4_5_CNSTN_L_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.04 | 147.61 | 01GRNGAP | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.84 | 147.42 | 01GRNGAP | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.87 | 147.4 | 01GRNGAP | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.6 | 147.21 | 01GRNGAP | PECO_P4_NOTTI85_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.54 | 147.19 | 01GRNGAP | PECO_P1-2_220-08_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.47 | 147.13 | 01GRNGAP | PECO_P4_COOPR125_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.01 | 147.12 | 01GRNGAP | AP_P1-2_PE-500-001_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.01 | 147.12 | 01GRNGAP | AP_P1-2_WP-500-DRT17_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 142.96 | 147.05 | 01GRNGAP | AP_P2-3_PE-500-018C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200504 | 26CARLISLE | 204528 | 27GARDNERS | 1 | 115 | 226/227 | 150 | 101.4 | 109.42 | AG2-055 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.54 | 143.83 | 01GRNGAP | PECO_P4_PEACH025_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.39 | 143.72 | 01GRNGAP | PECO_P1-2_PBTIE1_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 911 | 148.87 | 143 | 01GRNGAP | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 911 | 147.93 | 141.68 | 01GRNGAP | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 911 | 147.93 | 141.68 | 01GRNGAP | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 911 | 147.91 | 141.67 | 01GRNGAP | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204502 | 27JACKSON | 204514 | 27TMI | 1 | 230 | 227 | 781 | 132.93 | 141.41 | 01GRNGAP | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204502 | 27JACKSON | 204514 | 27TMI | 1 | 230 | 227 | 781 | 132.93 | 141.41 | 01GRNGAP | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204502 | 27JACKSON | 204514 | 27TMI | 1 | 230 | 227 | 781 | 132.92 | 141.4 | 01GRNGAP | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 903 | 135.55 | 139.47 | 01GRNGAP | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 1031 | 130.74 | 138.99 | 01GRNGAP | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 1031 | 130.24 | 137.92 | 01GRNGAP | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 1031 | 130.24 | 137.92 | 01GRNGAP | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 1031 | 130.23 | 137.91 | 01GRNGAP | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 911 | 140.06 | 134.94 | 01GRNGAP | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 138.81 | 132.87 | 01GRNGAP | PECO_P4_PEACH205_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 138.69 | 132.54 | 01GRNGAP | PECO_P1-2_PBTIE2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208078 | SAKR | 1 | 230 | 229 | 903 | 124.4 | 132.33 | 01GRNGAP | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208078 | SAKR | 1 | 230 | 229 | 903 | 124.4 | 132.33 | 01GRNGAP | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208078 | SAKR | 1 | 230 | 229 | 903 | 124.39 | 132.33 | 01GRNGAP | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 137.77 | 131.68 | 01GRNGAP | PECO_P4_PEACH055_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204502 | 27JACKSON | 204514 | 27TMI | 1 | 230 | 227 | 781 | 125.29 | 130.86 | 01GRNGAP | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 1031 | 124.64 | 129.14 | 01GRNGAP | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 128.96 | 127.24 | 01GRNGAP | DVP_P4-2: 514T595_SRT-SW |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 133.04 | 127.22 | 01GRNGAP | PECO_P4_PEACH015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 131.74 | 125.93 | 01GRNGAP | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220953 | HOWARD12 | 220972 | GRANITE1 | 1 | 230 | 232 | 772 | 129.56 | 125.56 | 01GRNGAP | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 127.22 | 125.52 | 01GRNGAP | DVP_P4-2: 51482_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 127.22 | 125.38 | 01GRNGAP | AP_P1-2_PE-500-407T_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 127.22 | 125.38 | 01GRNGAP | DVP_P1-2: LN 514_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220953 | HOWARD12 | 220972 | GRANITE1 | 1 | 230 | 232 | 772 | 128.64 | 124.59 | 01GRNGAP | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220953 | HOWARD12 | 220972 | GRANITE1 | 1 | 230 | 232 | 772 | 128.64 | 124.59 | 01GRNGAP | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208020 | MANO TR3 | 1 | 230 | 229 | 793 | 111.39 | 124.5 | 01GRNGAP | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208020 | MANO TR3 | 1 | 230 | 229 | 793 | 111.38 | 124.5 | 01GRNGAP | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208020 | MANO TR3 | 1 | 230 | 229 | 793 | 111.39 | 124.5 | 01GRNGAP | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208078 | SAKR | 1 | 230 | 229 | 903 | 117.13 | 122.36 | 01GRNGAP | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200025 | W CHAPEL | 1 | 500 | 225 | 1732 | 123.67 | 121.85 | 01GRNGAP | PEPCO_P4_PP41_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208031 | MLWD TR2 | 1 | 230 | 229 | 911 | 111.7 | 121.08 | 01GRNGAP | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208031 | MLWD TR2 | 1 | 230 | 229 | 911 | 111.69 | 121.08 | 01GRNGAP | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208031 | MLWD TR2 | 1 | 230 | 229 | 911 | 111.7 | 121.08 | 01GRNGAP | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220965 | NEAST339 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 119.73 | 119.06 | 01GRNGAP | BG_P1_2315_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220965 | NEAST339 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 119.46 | 118.86 | 01GRNGAP | BG_P4_5_NEAST_15_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 114.66 | 118.34 | 01GRNGAP | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 114.32 | 118 | 01GRNGAP | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 114.31 | 117.94 | 01GRNGAP | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 114.31 | 117.94 | 01GRNGAP | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 113.97 | 117.61 | 01GRNGAP | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 113.97 | 117.61 | 01GRNGAP | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 122.65 | 117.28 | 01GRNGAP | PECO_P4_PEACH225_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 117.39 | 115.48 | 01GRNGAP | AP_P2-3_PE-500-019C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 2 | 500/230 | 225/232 | 2168 | 109.62 | 114.91 | 01GRNGAP | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 2 | 500/230 | 225/232 | 2168 | 109.44 | 114.7 | 01GRNGAP | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 2 | 500/230 | 225/232 | 2168 | 109.44 | 114.7 | 01GRNGAP | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 1 | 500/230 | 225/232 | 2168 | 109.39 | 114.67 | 01GRNGAP | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 1 | 500/230 | 225/232 | 2168 | 109.21 | 114.46 | 01GRNGAP | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 1 | 500/230 | 225/232 | 2168 | 109.21 | 114.45 | 01GRNGAP | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220964 | GRACETON | 220999 | BAGLEY2 | 13 | 230 | 232 | 1795 | 113.4 | 114.43 | 01GRNGAP | BG_P4_5_GRCTN_3T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208020 | MANO TR3 | 1 | 230 | 229 | 793 | 104.2 | 113.94 | 01GRNGAP | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208020 | MANO TR3 | 208031 | MLWD TR2 | 1 | 230 | 229 | 903 | 102.52 | 113.64 | 01GRNGAP | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208020 | MANO TR3 | 208031 | MLWD TR2 | 1 | 230 | 229 | 903 | 101.81 | 112.44 | 01GRNGAP | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208020 | MANO TR3 | 208031 | MLWD TR2 | 1 | 230 | 229 | 903 | 101.81 | 112.44 | 01GRNGAP | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208020 | MANO TR3 | 208031 | MLWD TR2 | 1 | 230 | 229 | 903 | 101.81 | 112.44 | 01GRNGAP | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208031 | MLWD TR2 | 1 | 230 | 229 | 911 | 104.94 | 111.6 | 01GRNGAP | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 106.45 | 111.2 | 01GRNGAP | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220980 | RAPHAEL | 220999 | BAGLEY2 | 13 | 230 | 232 | 1795 | 108.99 | 111.18 | 01GRNGAP | BG_P4_5_GRCTN_3T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 106.32 | 111.07 | 01GRNGAP | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220965 | NEAST339 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 108.27 | 106.84 | 01GRNGAP | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220965 | NEAST339 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 108.17 | 106.72 | 01GRNGAP | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220965 | NEAST339 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 108.17 | 106.72 | 01GRNGAP | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220979 | NEAST317 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 105.16 | 103.79 | 01GRNGAP | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 99.5 | 103.36 | 01GRNGAP | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 99.5 | 103.36 | 01GRNGAP | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 99.5 | 103.36 | 01GRNGAP | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208020 | MANO TR3 | 208031 | MLWD TR2 | 1 | 230 | 229 | 903 | 95.44 | 103.22 | 01GRNGAP | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 98.57 | 102.03 | 01GRNGAP | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 98.67 | 100.68 | 01GRNGAP | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 223960 | BRG 1T 230 | 1 | 500/230 | 225/233 | 1498 | 100.26 | 100.63 | 01GRNGAP | PEPCO_P4_PP41_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200762 | 26GARRETT | 235470 | 01GARRET | 1 | 115 | 226/201 | 150 | 97.84 | 100.69 | Y1-033 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 153.76 | 158.26 | 05CELAN | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.24 | 157.36 | 05CELAN | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.24 | 157.36 | 05CELAN | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 152.07 | 156.93 | 05CELAN | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 161.72 | 154.5 | 05CELAN | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 148.71 | 153.28 | 05CELAN | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 155.81 | 150.66 | 05CELAN | PN_P1-2_PN-500-010T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.54 | 149.66 | 05CELAN | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.47 | 149.59 | 05CELAN | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.18 | 148.44 | 05CELAN | AP_P2-3_PE-500-016_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.24 | 148.41 | 05CELAN | AP_P2-3_PE-500-015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.12 | 147.99 | 05CELAN | PJM_500_BG_P4_5_CNSTN_L_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.4 | 147.96 | 05CELAN | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.2 | 147.77 | 05CELAN | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.22 | 147.76 | 05CELAN | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.95 | 147.56 | 05CELAN | PECO_P4_NOTTI85_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.35 | 147.56 | 05CELAN | AP_P1-2_PE-500-001_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.35 | 147.56 | 05CELAN | AP_P1-2_WP-500-DRT17_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.89 | 147.55 | 05CELAN | PECO_P1-2_220-08_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.3 | 147.49 | 05CELAN | AP_P2-3_PE-500-018C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.82 | 147.48 | 05CELAN | PECO_P4_COOPR125_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200512 | 26LEWISTWN | 200519 | 26REED TAP | 1 | 115 | 226 | 228 | 120.36 | 116.96 | AC1-158 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.93 | 144.22 | 05CELAN | PECO_P4_PEACH025_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.81 | 144.13 | 05CELAN | PECO_P1-2_PBTIE1_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 139.19 | 133.25 | 05CELAN | PECO_P4_PEACH205_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 139.07 | 132.92 | 05CELAN | PECO_P1-2_PBTIE2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 138.13 | 132.04 | 05CELAN | PECO_P4_PEACH055_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 133.45 | 127.63 | 05CELAN | PECO_P4_PEACH015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 132.12 | 126.3 | 05CELAN | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 123.03 | 117.65 | 05CELAN | PECO_P4_PEACH225_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200512 | 26LEWISTWN | 200519 | 26REED TAP | 1 | 115 | 226 | 228 | 116.01 | 112.5 | AD2-062 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.34 | 157.46 | 05NTRDAM | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.34 | 157.46 | 05NTRDAM | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 161.84 | 154.61 | 05NTRDAM | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.5 | 148.06 | 05NTRDAM | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.29 | 147.87 | 05NTRDAM | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.32 | 147.86 | 05NTRDAM | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.05 | 147.66 | 05NTRDAM | PECO_P4_NOTTI85_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.99 | 147.65 | 05NTRDAM | PECO_P1-2_220-08_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.92 | 147.58 | 05NTRDAM | PECO_P4_COOPR125_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 151.78 | 147.46 | 05NTRDAM | AP_P2-3_PE-500-016_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 151.82 | 147.44 | 05NTRDAM | AP_P2-3_PE-500-015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 151.05 | 144.33 | 05NTRDAM | PECO_P4_PEACH025_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 225.53 | 237.02 | 08HLCRTG | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 223.53 | 237.02 | 08HLCRTG | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 225.46 | 236.96 | 08HLCRTG | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 223.46 | 236.96 | 08HLCRTG | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 225.46 | 236.96 | 08HLCRTG | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 223.46 | 236.96 | 08HLCRTG | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 213.48 | 226.86 | 08HLCRTG | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 213.41 | 226.8 | 08HLCRTG | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 213.41 | 226.8 | 08HLCRTG | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 209.22 | 223.65 | 08HLCRTG | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 209.16 | 223.59 | 08HLCRTG | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 209.15 | 223.59 | 08HLCRTG | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 208.63 | 217.83 | 08HLCRTG | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 210.64 | 217.83 | 08HLCRTG | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 199.1 | 208.27 | 08HLCRTG | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 194.84 | 204.92 | 08HLCRTG | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 172.8 | 167.87 | 08HLCRTG | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 163.65 | 165.01 | 08HLCRTG | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 161.78 | 161.91 | 08HLCRTG | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 161.78 | 161.91 | 08HLCRTG | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200512 | 26LEWISTWN | 200519 | 26REED TAP | 1 | 115 | 226 | 228 | 107.39 | 103.97 | AE1-071 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 161.77 | 161.91 | 08HLCRTG | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 153.59 | 158.06 | 08HLCRTG | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.04 | 157.17 | 08HLCRTG | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.04 | 157.17 | 08HLCRTG | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 151.91 | 156.74 | 08HLCRTG | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 161.45 | 154.23 | 08HLCRTG | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 148.54 | 153.09 | 08HLCRTG | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 155.62 | 150.47 | 08HLCRTG | PN_P1-2_PN-500-010T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.39 | 149.48 | 08HLCRTG | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.32 | 149.4 | 08HLCRTG | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.05 | 148.3 | 08HLCRTG | AP_P2-3_PE-500-016_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.11 | 148.27 | 08HLCRTG | AP_P2-3_PE-500-015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.93 | 147.81 | 08HLCRTG | PJM_500_BG_P4_5_CNSTN_L_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.15 | 147.72 | 08HLCRTG | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.95 | 147.53 | 08HLCRTG | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.97 | 147.52 | 08HLCRTG | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.22 | 147.42 | 08HLCRTG | AP_P1-2_PE-500-001_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.22 | 147.42 | 08HLCRTG | AP_P1-2_WP-500-DRT17_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.17 | 147.35 | 08HLCRTG | AP_P2-3_PE-500-018C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.7 | 147.32 | 08HLCRTG | PECO_P4_NOTTI85_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.64 | 147.31 | 08HLCRTG | PECO_P1-2_220-08_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.58 | 147.24 | 08HLCRTG | PECO_P4_COOPR125_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200512 | 26LEWISTWN | 200519 | 26REED TAP | 1 | 115 | 226 | 228 | 118.11 | 114.64 | AE1-101 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.63 | 143.93 | 08HLCRTG | PECO_P4_PEACH025_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.53 | 143.86 | 08HLCRTG | PECO_P1-2_PBTIE1_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 911 | 149.04 | 143.22 | 08HLCRTG | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 1031 | 130.35 | 138.18 | 08HLCRTG | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 1031 | 130.35 | 138.17 | 08HLCRTG | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 1031 | 130.34 | 138.17 | 08HLCRTG | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 138.94 | 133.01 | 08HLCRTG | PECO_P4_PEACH205_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 138.81 | 132.67 | 08HLCRTG | PECO_P1-2_PBTIE2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208078 | SAKR | 1 | 230 | 229 | 903 | 124.52 | 132.61 | 08HLCRTG | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208078 | SAKR | 1 | 230 | 229 | 903 | 124.52 | 132.61 | 08HLCRTG | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208078 | SAKR | 1 | 230 | 229 | 903 | 124.52 | 132.61 | 08HLCRTG | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 137.89 | 131.8 | 08HLCRTG | PECO_P4_PEACH055_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 133.18 | 127.37 | 08HLCRTG | PECO_P4_PEACH015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 131.87 | 126.06 | 08HLCRTG | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208020 | MANO TR3 | 1 | 230 | 229 | 793 | 111.5 | 124.7 | 08HLCRTG | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208020 | MANO TR3 | 1 | 230 | 229 | 793 | 111.5 | 124.7 | 08HLCRTG | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208020 | MANO TR3 | 1 | 230 | 229 | 793 | 111.5 | 124.7 | 08HLCRTG | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 122.78 | 117.42 | 08HLCRTG | PECO_P4_PEACH225_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 99.68 | 103.64 | 08HLCRTG | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 99.67 | 103.64 | 08HLCRTG | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 99.67 | 103.64 | 08HLCRTG | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200512 | 26LEWISTWN | 200519 | 26REED TAP | 1 | 115 | 226 | 228 | 124.72 | 121.52 | AG2-055 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 154.15 | 158.72 | 09GRNVIL | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.65 | 157.77 | 09GRNVIL | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.65 | 157.77 | 09GRNVIL | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 152.46 | 157.39 | 09GRNVIL | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 162.26 | 155.01 | 09GRNVIL | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 149.09 | 153.74 | 09GRNVIL | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 156.21 | 151.06 | 09GRNVIL | PN_P1-2_PN-500-010T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.91 | 150.1 | 09GRNVIL | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.84 | 150.02 | 09GRNVIL | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.51 | 148.83 | 09GRNVIL | AP_P2-3_PE-500-016_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.58 | 148.8 | 09GRNVIL | AP_P2-3_PE-500-015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.87 | 148.42 | 09GRNVIL | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.52 | 148.38 | 09GRNVIL | PJM_500_BG_P4_5_CNSTN_L_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.67 | 148.23 | 09GRNVIL | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.69 | 148.22 | 09GRNVIL | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.42 | 148.02 | 09GRNVIL | PECO_P4_NOTTI85_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.36 | 148.01 | 09GRNVIL | PECO_P1-2_220-08_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.69 | 147.95 | 09GRNVIL | AP_P1-2_WP-500-DRT17_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.69 | 147.95 | 09GRNVIL | AP_P1-2_PE-500-001_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.29 | 147.94 | 09GRNVIL | PECO_P4_COOPR125_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.64 | 147.88 | 09GRNVIL | AP_P2-3_PE-500-018C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200519 | 26REED TAP | 200522 | 26SHADE GP | 1 | 115 | 226 | 224 | 113.28 | 113.28 | AC1-158 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 151.49 | 144.76 | 09GRNVIL | PECO_P4_PEACH025_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 151.35 | 144.66 | 09GRNVIL | PECO_P1-2_PBTIE1_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 139.67 | 133.71 | 09GRNVIL | PECO_P4_PEACH205_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 139.58 | 133.4 | 09GRNVIL | PECO_P1-2_PBTIE2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 138.6 | 132.5 | 09GRNVIL | PECO_P4_PEACH055_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 133.98 | 128.13 | 09GRNVIL | PECO_P4_PEACH015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 132.61 | 126.76 | 09GRNVIL | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 123.51 | 118.12 | 09GRNVIL | PECO_P4_PEACH225_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 144.37 | 139.21 | 15USSILL | PECO_P4_PEACH025_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 144.3 | 139.16 | 15USSILL | PL_10_P42_100570_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 144.3 | 139.16 | 15USSILL | PL_10_P42_100570_A_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 143.5 | 138.37 | 15USSILL | PL_10_P12_000085_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 143.4 | 138.28 | 15USSILL | PN_P2-3_PN-500-004-DRT-008_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 143.4 | 138.28 | 15USSILL | PN_P2-3_PN-500-DRT31_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 143.02 | 137.91 | 15USSILL | PL_30_P42_000131_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 142.88 | 137.78 | 15USSILL | PL_10_P42_100569_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 142.88 | 137.78 | 15USSILL | PL_10_P42_100569_A_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 142.1 | 137.02 | 15USSILL | PL_10_P12_000086_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200519 | 26REED TAP | 200522 | 26SHADE GP | 1 | 115 | 226 | 224 | 109.12 | 108.77 | AD2-062 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 153.78 | 158.27 | 1DOMTR10 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.27 | 157.39 | 1DOMTR10 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.27 | 157.39 | 1DOMTR10 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 152.09 | 156.95 | 1DOMTR10 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 161.78 | 154.55 | 1DOMTR10 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 148.73 | 153.3 | 1DOMTR10 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 155.84 | 150.69 | 1DOMTR10 | PN_P1-2_PN-500-010T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.56 | 149.68 | 1DOMTR10 | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.49 | 149.6 | 1DOMTR10 | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.18 | 148.43 | 1DOMTR10 | AP_P2-3_PE-500-016_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.24 | 148.4 | 1DOMTR10 | AP_P2-3_PE-500-015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.15 | 148.02 | 1DOMTR10 | PJM_500_BG_P4_5_CNSTN_L_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.45 | 148.01 | 1DOMTR10 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.25 | 147.82 | 1DOMTR10 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.27 | 147.81 | 1DOMTR10 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153 | 147.61 | 1DOMTR10 | PECO_P4_NOTTI85_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.94 | 147.6 | 1DOMTR10 | PECO_P1-2_220-08_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.36 | 147.55 | 1DOMTR10 | AP_P1-2_PE-500-001_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.36 | 147.55 | 1DOMTR10 | AP_P1-2_WP-500-DRT17_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.87 | 147.53 | 1DOMTR10 | PECO_P4_COOPR125_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.31 | 147.48 | 1DOMTR10 | AP_P2-3_PE-500-018C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200519 | 26REED TAP | 200522 | 26SHADE GP | 1 | 115 | 226 | 224 | 100.8 | 100.1 | AE1-071 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 151 | 144.29 | 1DOMTR10 | PECO_P4_PEACH025_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.86 | 144.19 | 1DOMTR10 | PECO_P1-2_PBTIE1_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 139.23 | 133.29 | 1DOMTR10 | PECO_P4_PEACH205_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 139.12 | 132.97 | 1DOMTR10 | PECO_P1-2_PBTIE2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 138.18 | 132.08 | 1DOMTR10 | PECO_P4_PEACH055_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 133.5 | 127.68 | 1DOMTR10 | PECO_P4_PEACH015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 128.94 | 127.21 | 1DOMTR10 | DVP_P4-2: 514T595_SRT-SW |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 132.17 | 126.34 | 1DOMTR10 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 127.2 | 125.49 | 1DOMTR10 | DVP_P4-2: 51482_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 127.2 | 125.4 | 1DOMTR10 | DVP_P1-2: LN 514_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 127.2 | 125.4 | 1DOMTR10 | AP_P1-2_PE-500-407T_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 123.07 | 117.7 | 1DOMTR10 | PECO_P4_PEACH225_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 117.39 | 115.48 | 1DOMTR10 | AP_P2-3_PE-500-019C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200519 | 26REED TAP | 200522 | 26SHADE GP | 1 | 115 | 226 | 224 | 111.12 | 110.94 | AE1-101 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 153.81 | 158.32 | 1DOMTR9 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.3 | 157.43 | 1DOMTR9 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.3 | 157.42 | 1DOMTR9 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 152.12 | 157 | 1DOMTR9 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 161.82 | 154.59 | 1DOMTR9 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 148.76 | 153.34 | 1DOMTR9 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 155.87 | 150.72 | 1DOMTR9 | PN_P1-2_PN-500-010T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.59 | 149.72 | 1DOMTR9 | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.52 | 149.65 | 1DOMTR9 | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.21 | 148.47 | 1DOMTR9 | AP_P2-3_PE-500-016_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.28 | 148.45 | 1DOMTR9 | AP_P2-3_PE-500-015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.18 | 148.05 | 1DOMTR9 | PJM_500_BG_P4_5_CNSTN_L_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.48 | 148.04 | 1DOMTR9 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.28 | 147.86 | 1DOMTR9 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.31 | 147.84 | 1DOMTR9 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.04 | 147.65 | 1DOMTR9 | PECO_P4_NOTTI85_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.98 | 147.63 | 1DOMTR9 | PECO_P1-2_220-08_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.39 | 147.59 | 1DOMTR9 | AP_P1-2_WP-500-DRT17_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.39 | 147.59 | 1DOMTR9 | AP_P1-2_PE-500-001_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.91 | 147.57 | 1DOMTR9 | PECO_P4_COOPR125_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.34 | 147.52 | 1DOMTR9 | AP_P2-3_PE-500-018C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200519 | 26REED TAP | 200522 | 26SHADE GP | 1 | 115 | 226 | 224 | 117.45 | 117.89 | AG2-055 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 151.04 | 144.33 | 1DOMTR9 | PECO_P4_PEACH025_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.91 | 144.23 | 1DOMTR9 | PECO_P1-2_PBTIE1_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 139.27 | 133.33 | 1DOMTR9 | PECO_P4_PEACH205_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 139.16 | 133 | 1DOMTR9 | PECO_P1-2_PBTIE2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 138.21 | 132.12 | 1DOMTR9 | PECO_P4_PEACH055_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 133.54 | 127.72 | 1DOMTR9 | PECO_P4_PEACH015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 132.21 | 126.38 | 1DOMTR9 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 123.11 | 117.73 | 1DOMTR9 | PECO_P4_PEACH225_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200532 | 26ROXBURY | 203981 | AD2-062_POI | 1 | 138 | 226 | 250 | 126.73 | 125.49 | AC1-158 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 153.76 | 158.26 | 1EDGECMA | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.25 | 157.37 | 1EDGECMA | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.25 | 157.37 | 1EDGECMA | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 152.07 | 156.93 | 1EDGECMA | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 161.76 | 154.53 | 1EDGECMA | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 148.71 | 153.28 | 1EDGECMA | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 155.82 | 150.67 | 1EDGECMA | PN_P1-2_PN-500-010T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.55 | 149.66 | 1EDGECMA | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.48 | 149.59 | 1EDGECMA | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.17 | 148.42 | 1EDGECMA | AP_P2-3_PE-500-016_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.23 | 148.39 | 1EDGECMA | AP_P2-3_PE-500-015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.13 | 148 | 1EDGECMA | PJM_500_BG_P4_5_CNSTN_L_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.43 | 147.99 | 1EDGECMA | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.23 | 147.8 | 1EDGECMA | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.25 | 147.79 | 1EDGECMA | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.98 | 147.59 | 1EDGECMA | PECO_P4_NOTTI85_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.92 | 147.58 | 1EDGECMA | PECO_P1-2_220-08_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.34 | 147.54 | 1EDGECMA | AP_P1-2_PE-500-001_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.34 | 147.54 | 1EDGECMA | AP_P1-2_WP-500-DRT17_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.85 | 147.51 | 1EDGECMA | PECO_P4_COOPR125_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.29 | 147.47 | 1EDGECMA | AP_P2-3_PE-500-018C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200532 | 26ROXBURY | 203981 | AD2-062_POI | 1 | 138 | 226 | 250 | 126.75 | 125.5 | AD2-009 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.98 | 144.26 | 1EDGECMA | PECO_P4_PEACH025_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.84 | 144.16 | 1EDGECMA | PECO_P1-2_PBTIE1_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 139.21 | 133.27 | 1EDGECMA | PECO_P4_PEACH205_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 139.1 | 132.95 | 1EDGECMA | PECO_P1-2_PBTIE2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 138.16 | 132.07 | 1EDGECMA | PECO_P4_PEACH055_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 133.48 | 127.66 | 1EDGECMA | PECO_P4_PEACH015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 128.94 | 127.21 | 1EDGECMA | DVP_P4-2: 514T595_SRT-SW |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 132.15 | 126.32 | 1EDGECMA | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 127.2 | 125.49 | 1EDGECMA | DVP_P4-2: 51482_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 127.2 | 125.4 | 1EDGECMA | DVP_P1-2: LN 514_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 127.2 | 125.4 | 1EDGECMA | AP_P1-2_PE-500-407T_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 123.05 | 117.68 | 1EDGECMA | PECO_P4_PEACH225_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 117.39 | 115.48 | 1EDGECMA | AP_P2-3_PE-500-019C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 225.76 | 237.26 | 1HOLLOMANSOL | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 223.75 | 237.26 | 1HOLLOMANSOL | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 225.69 | 237.2 | 1HOLLOMANSOL | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 223.69 | 237.2 | 1HOLLOMANSOL | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 225.69 | 237.2 | 1HOLLOMANSOL | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 223.69 | 237.2 | 1HOLLOMANSOL | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 213.7 | 227.1 | 1HOLLOMANSOL | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 213.63 | 227.04 | 1HOLLOMANSOL | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 213.63 | 227.04 | 1HOLLOMANSOL | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 209.44 | 223.89 | 1HOLLOMANSOL | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 209.37 | 223.83 | 1HOLLOMANSOL | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 209.37 | 223.83 | 1HOLLOMANSOL | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200532 | 26ROXBURY | 203981 | AD2-062_POI | 1 | 138 | 226 | 250 | 118.9 | 117.89 | AD2-062 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 153.64 | 158.11 | 1HOLLOMANSOL | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.13 | 157.26 | 1HOLLOMANSOL | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.13 | 157.25 | 1HOLLOMANSOL | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 151.95 | 156.79 | 1HOLLOMANSOL | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 161.62 | 154.4 | 1HOLLOMANSOL | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 148.59 | 153.14 | 1HOLLOMANSOL | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 155.71 | 150.55 | 1HOLLOMANSOL | PN_P1-2_PN-500-010T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.43 | 149.52 | 1HOLLOMANSOL | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.36 | 149.45 | 1HOLLOMANSOL | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.05 | 148.27 | 1HOLLOMANSOL | AP_P2-3_PE-500-016_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.11 | 148.24 | 1HOLLOMANSOL | AP_P2-3_PE-500-015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.02 | 147.89 | 1HOLLOMANSOL | PJM_500_BG_P4_5_CNSTN_L_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.31 | 147.87 | 1HOLLOMANSOL | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.11 | 147.69 | 1HOLLOMANSOL | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.13 | 147.67 | 1HOLLOMANSOL | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.86 | 147.48 | 1HOLLOMANSOL | PECO_P4_NOTTI85_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.8 | 147.46 | 1HOLLOMANSOL | PECO_P1-2_220-08_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.74 | 147.39 | 1HOLLOMANSOL | PECO_P4_COOPR125_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.23 | 147.39 | 1HOLLOMANSOL | AP_P1-2_PE-500-001_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.23 | 147.39 | 1HOLLOMANSOL | AP_P1-2_WP-500-DRT17_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.18 | 147.32 | 1HOLLOMANSOL | AP_P2-3_PE-500-018C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200532 | 26ROXBURY | 203981 | AD2-062_POI | 1 | 138 | 226 | 250 | 146.03 | 144.59 | AE1-071 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.85 | 144.14 | 1HOLLOMANSOL | PECO_P4_PEACH025_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.7 | 144.03 | 1HOLLOMANSOL | PECO_P1-2_PBTIE1_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 139.08 | 133.15 | 1HOLLOMANSOL | PECO_P4_PEACH205_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 138.97 | 132.82 | 1HOLLOMANSOL | PECO_P1-2_PBTIE2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 138.03 | 131.95 | 1HOLLOMANSOL | PECO_P4_PEACH055_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 133.34 | 127.52 | 1HOLLOMANSOL | PECO_P4_PEACH015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 128.71 | 126.97 | 1HOLLOMANSOL | DVP_P4-2: 514T595_SRT-SW |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 132.02 | 126.2 | 1HOLLOMANSOL | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 126.96 | 125.25 | 1HOLLOMANSOL | DVP_P4-2: 51482_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 126.96 | 125.15 | 1HOLLOMANSOL | DVP_P1-2: LN 514_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 126.96 | 125.15 | 1HOLLOMANSOL | AP_P1-2_PE-500-407T_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200025 | W CHAPEL | 1 | 500 | 225 | 1732 | 123.77 | 121.99 | 1HOLLOMANSOL | PEPCO_P4_PP41_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 122.93 | 117.56 | 1HOLLOMANSOL | PECO_P4_PEACH225_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 117.16 | 115.24 | 1HOLLOMANSOL | AP_P2-3_PE-500-019C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 99.58 | 103.53 | 1HOLLOMANSOL | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 99.57 | 103.53 | 1HOLLOMANSOL | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 99.58 | 103.53 | 1HOLLOMANSOL | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 98.75 | 100.82 | 1HOLLOMANSOL | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200532 | 26ROXBURY | 200520 | 26ROXBURY | 2 | 138/115 | 226 | 364 | 100.29 | 110.98 | AE1-071 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 153.82 | 158.32 | 1STONECA | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.31 | 157.43 | 1STONECA | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.31 | 157.43 | 1STONECA | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 152.13 | 157 | 1STONECA | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 161.83 | 154.6 | 1STONECA | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 148.76 | 153.35 | 1STONECA | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 155.88 | 150.72 | 1STONECA | PN_P1-2_PN-500-010T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.22 | 148.48 | 1STONECA | AP_P2-3_PE-500-016_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.28 | 148.45 | 1STONECA | AP_P2-3_PE-500-015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.19 | 148.06 | 1STONECA | PJM_500_BG_P4_5_CNSTN_L_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.49 | 148.05 | 1STONECA | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.29 | 147.86 | 1STONECA | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.31 | 147.85 | 1STONECA | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.04 | 147.65 | 1STONECA | PECO_P4_NOTTI85_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.98 | 147.64 | 1STONECA | PECO_P1-2_220-08_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.39 | 147.6 | 1STONECA | AP_P1-2_PE-500-001_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.39 | 147.6 | 1STONECA | AP_P1-2_WP-500-DRT17_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.92 | 147.57 | 1STONECA | PECO_P4_COOPR125_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.34 | 147.53 | 1STONECA | AP_P2-3_PE-500-018C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.34 | 147.52 | 1STONECA | AP_P2-3_PE-500-018D_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200520 | 26ROXBURY | 203971 | AE1-071-POI | 1 | 115 | 226 | 395 | 101.56 | 103.83 | AE1-071 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 142.86 | 146.96 | 1STONECA | AP_P2-3_WP-500-DRT19_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 151.05 | 144.33 | 1STONECA | PECO_P4_PEACH025_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.91 | 144.23 | 1STONECA | PECO_P1-2_PBTIE1_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 139.17 | 133.01 | 1STONECA | PECO_P1-2_PBTIE2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 138.22 | 132.13 | 1STONECA | PECO_P4_PEACH055_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 133.55 | 127.72 | 1STONECA | PECO_P4_PEACH015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 132.21 | 126.39 | 1STONECA | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 123.12 | 117.74 | 1STONECA | PECO_P4_PEACH225_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 148.59 | 143.24 | 26ARMNA MT | AP_P2-3_WP-500-696_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 148.59 | 143.24 | 26ARMNA MT | AP_P2-3_WP-500-707T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 148.59 | 143.23 | 26ARMNA MT | AP_P2-3_WP-500-706T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 148.56 | 143.21 | 26ARMNA MT | AP_P2-3_WP-500-440T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 148.44 | 143.16 | 26ARMNA MT | AP_P2-3_WP-500-DRT45_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 148.44 | 143.16 | 26ARMNA MT | AP_P1-2_WP-500-008_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 139.28 | 141.62 | 26ARMNA MT | AP_P1-2_WP-500-005A_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 139.28 | 141.62 | 26ARMNA MT | AP_P2-3_WP-500-DRT20_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 139.28 | 141.62 | 26ARMNA MT | AP_P1-2_WP-500-DRT21_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 139.28 | 141.62 | 26ARMNA MT | AP_P2-2_WP-500-DRT16_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 139.28 | 141.62 | 26ARMNA MT | AP_P2-3_WP-500-465_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 146.65 | 141.4 | 26ARMNA MT | AP_P2-2_WP-500-DRT17_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 146.65 | 141.4 | 26ARMNA MT | AP_P1-2_WP-500-DRT22T_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 146.65 | 141.4 | 26ARMNA MT | AP_P1-2_WP-500-301T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 146.63 | 141.4 | 26ARMNA MT | PN_P2-3_PN-500-004-DRT-006_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 139.06 | 141.27 | 26ARMNA MT | AP_P2-3_WP-500-DRT45_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 139.06 | 141.27 | 26ARMNA MT | AP_P1-2_WP-500-008_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 137.46 | 139.5 | 26ARMNA MT | AP_P2-3_WP-500-696_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 137.46 | 139.5 | 26ARMNA MT | AP_P2-3_WP-500-707T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 137.48 | 139.48 | 26ARMNA MT | AP_P2-3_WP-500-706T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 133.91 | 128.07 | 26ARMNA MT | PECO_P4_PEACH015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 123.45 | 118.06 | 26ARMNA MT | PECO_P4_PEACH225_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200762 | 26GARRETT | 235470 | 01GARRET | 1 | 115 | 226/201 | 190 | 98.76 | 101.01 | 26CSLMN_L13 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200762 | 26GARRETT | 235470 | 01GARRET | 1 | 115 | 226/201 | 190 | 98.76 | 101.01 | 26CSLMN_L13 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200762 | 26GARRETT | 235470 | 01GARRET | 1 | 115 | 226/201 | 190 | 98.6 | 100.84 | 26CSLMN_L13 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200762 | 26GARRETT | 235470 | 01GARRET | 1 | 115 | 226/201 | 190 | 98.76 | 100.95 | 26LOOKOUT | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200762 | 26GARRETT | 235470 | 01GARRET | 1 | 115 | 226/201 | 190 | 98.76 | 100.95 | 26LOOKOUT | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200762 | 26GARRETT | 235470 | 01GARRET | 1 | 115 | 226/201 | 190 | 98.59 | 100.79 | 26LOOKOUT | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200532 | 26ROXBURY | 203981 | AD2-062_POI | 1 | 138 | 226 | 250 | 122.54 | 121.33 | AE1-101 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 162.17 | 154.93 | 28MDLSEXCO | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.79 | 148.34 | 28MDLSEXCO | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.59 | 148.16 | 28MDLSEXCO | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.61 | 148.14 | 28MDLSEXCO | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.34 | 147.95 | 28MDLSEXCO | PECO_P4_NOTTI85_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.28 | 147.93 | 28MDLSEXCO | PECO_P1-2_220-08_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.21 | 147.86 | 28MDLSEXCO | PECO_P4_COOPR125_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.05 | 147.72 | 28MDLSEXCO | AP_P2-3_PE-500-016_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.09 | 147.7 | 28MDLSEXCO | AP_P2-3_PE-500-015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.87 | 147.67 | 28MDLSEXCO | PECO_P1-2_220-93_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 151.57 | 147.24 | 28MDLSEXCO | AP_P1-2_WP-500-DRT17_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 151.41 | 144.68 | 28MDLSEXCO | PECO_P4_PEACH025_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 151.28 | 144.59 | 28MDLSEXCO | PECO_P1-2_PBTIE1_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 139.51 | 133.34 | 28MDLSEXCO | PECO_P1-2_PBTIE2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 133.92 | 128.08 | 28MDLSEXCO | PECO_P4_PEACH015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 123.46 | 118.07 | 28MDLSEXCO | PECO_P4_PEACH225_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.78 | 148.33 | 28SIXFLAGS | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.58 | 148.15 | 28SIXFLAGS | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.6 | 148.13 | 28SIXFLAGS | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.33 | 147.94 | 28SIXFLAGS | PECO_P4_NOTTI85_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.27 | 147.92 | 28SIXFLAGS | PECO_P1-2_220-08_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.2 | 147.85 | 28SIXFLAGS | PECO_P4_COOPR125_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.86 | 147.66 | 28SIXFLAGS | PECO_P1-2_220-93_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 151.08 | 146.11 | 28SIXFLAGS | PL_05_P71_000906_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 150.43 | 145.3 | 28SIXFLAGS | PL_04_P42_000557_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 151.4 | 144.67 | 28SIXFLAGS | PECO_P4_PEACH025_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 151.27 | 144.58 | 28SIXFLAGS | PECO_P1-2_PBTIE1_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 148.59 | 143.24 | 28SIXFLAGS | AP_P2-3_WP-500-696_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 139.5 | 133.33 | 28SIXFLAGS | PECO_P1-2_PBTIE2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 133.91 | 128.07 | 28SIXFLAGS | PECO_P4_PEACH015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 123.45 | 118.05 | 28SIXFLAGS | PECO_P4_PEACH225_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200532 | 26ROXBURY | 203981 | AD2-062_POI | 1 | 138 | 226 | 250 | 134.33 | 133 | AG2-055 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 153.68 | 158.15 | 3MURPHYS | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.17 | 157.29 | 3MURPHYS | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.17 | 157.29 | 3MURPHYS | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 151.99 | 156.83 | 3MURPHYS | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 161.67 | 154.44 | 3MURPHYS | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 148.63 | 153.18 | 3MURPHYS | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 155.74 | 150.59 | 3MURPHYS | PN_P1-2_PN-500-010T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.46 | 149.56 | 3MURPHYS | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.39 | 149.49 | 3MURPHYS | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.08 | 148.31 | 3MURPHYS | AP_P2-3_PE-500-016_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.15 | 148.29 | 3MURPHYS | AP_P2-3_PE-500-015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.06 | 147.92 | 3MURPHYS | PJM_500_BG_P4_5_CNSTN_L_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.35 | 147.91 | 3MURPHYS | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.15 | 147.72 | 3MURPHYS | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.17 | 147.71 | 3MURPHYS | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.9 | 147.51 | 3MURPHYS | PECO_P4_NOTTI85_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.84 | 147.5 | 3MURPHYS | PECO_P1-2_220-08_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.26 | 147.43 | 3MURPHYS | AP_P1-2_WP-500-DRT17_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.26 | 147.43 | 3MURPHYS | AP_P1-2_PE-500-001_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.78 | 147.43 | 3MURPHYS | PECO_P4_COOPR125_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.21 | 147.37 | 3MURPHYS | AP_P2-3_PE-500-018C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200532 | 26ROXBURY | 200520 | 26ROXBURY | 2 | 138/115 | 226 | 364 | 92.26 | 104.94 | AG2-055 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.89 | 144.18 | 3MURPHYS | PECO_P4_PEACH025_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.74 | 144.07 | 3MURPHYS | PECO_P1-2_PBTIE1_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 139.12 | 133.18 | 3MURPHYS | PECO_P4_PEACH205_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 139.01 | 132.86 | 3MURPHYS | PECO_P1-2_PBTIE2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 138.07 | 131.99 | 3MURPHYS | PECO_P4_PEACH055_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 133.39 | 127.57 | 3MURPHYS | PECO_P4_PEACH015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 128.77 | 127.03 | 3MURPHYS | DVP_P4-2: 514T595_SRT-SW |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 132.06 | 126.24 | 3MURPHYS | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 127.02 | 125.31 | 3MURPHYS | DVP_P4-2: 51482_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 127.02 | 125.22 | 3MURPHYS | AP_P1-2_PE-500-407T_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 127.02 | 125.22 | 3MURPHYS | DVP_P1-2: LN 514_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 122.97 | 117.59 | 3MURPHYS | PECO_P4_PEACH225_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 117.22 | 115.3 | 3MURPHYS | AP_P2-3_PE-500-019C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200532 | 26ROXBURY | 203981 | AD2-062_POI | 1 | 138 | 226 | 250 | 126.58 | 125.35 | O66 NFTWR | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.32 | 157.45 | 3UNCAMP | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.32 | 157.45 | 3UNCAMP | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 161.85 | 154.62 | 3UNCAMP | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 155.9 | 150.74 | 3UNCAMP | PN_P1-2_PN-500-010T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.21 | 148.07 | 3UNCAMP | PJM_500_BG_P4_5_CNSTN_L_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.5 | 148.06 | 3UNCAMP | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.3 | 147.88 | 3UNCAMP | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.33 | 147.86 | 3UNCAMP | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.06 | 147.67 | 3UNCAMP | PECO_P4_NOTTI85_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153 | 147.65 | 3UNCAMP | PECO_P1-2_220-08_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.93 | 147.59 | 3UNCAMP | PECO_P4_COOPR125_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 139.24 | 142.1 | 3UNCAMP | DVP_P4-2: 580T592_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 139.16 | 142.05 | 3UNCAMP | DVP_P4-2: 541T580_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 139.25 | 141.97 | 3UNCAMP | DVP_P4-2: 541T592_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 136.83 | 139.45 | 3UNCAMP | DVP_P4-2: 53672_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 136.83 | 139.42 | 3UNCAMP | AP_P1-2_WP-500-304T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.34 | 157.46 | 3WITAKRS | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.33 | 157.46 | 3WITAKRS | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 155.91 | 150.75 | 3WITAKRS | PN_P1-2_PN-500-010T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.51 | 148.07 | 3WITAKRS | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.31 | 147.89 | 3WITAKRS | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.34 | 147.87 | 3WITAKRS | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.07 | 147.68 | 3WITAKRS | PECO_P4_NOTTI85_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.01 | 147.66 | 3WITAKRS | PECO_P1-2_220-08_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.94 | 147.6 | 3WITAKRS | PECO_P4_COOPR125_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 151.83 | 147.44 | 3WITAKRS | AP_P2-3_PE-500-015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200532 | 26ROXBURY | 203981 | AD2-062_POI | 1 | 138 | 226 | 250 | 133.13 | 131.81 | W1-045 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 153.8 | 158.31 | 4E MILL | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.29 | 157.42 | 4E MILL | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.29 | 157.41 | 4E MILL | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 152.12 | 156.99 | 4E MILL | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 161.8 | 154.57 | 4E MILL | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 148.75 | 153.33 | 4E MILL | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 155.86 | 150.71 | 4E MILL | PN_P1-2_PN-500-010T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.59 | 149.71 | 4E MILL | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.52 | 149.64 | 4E MILL | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.21 | 148.47 | 4E MILL | AP_P2-3_PE-500-016_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.27 | 148.44 | 4E MILL | AP_P2-3_PE-500-015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.17 | 148.04 | 4E MILL | PJM_500_BG_P4_5_CNSTN_L_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.47 | 148.03 | 4E MILL | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.26 | 147.84 | 4E MILL | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.29 | 147.83 | 4E MILL | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.02 | 147.63 | 4E MILL | PECO_P4_NOTTI85_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.96 | 147.61 | 4E MILL | PECO_P1-2_220-08_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.39 | 147.59 | 4E MILL | AP_P1-2_PE-500-001_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.39 | 147.59 | 4E MILL | AP_P1-2_WP-500-DRT17_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.89 | 147.55 | 4E MILL | PECO_P4_COOPR125_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.34 | 147.52 | 4E MILL | AP_P2-3_PE-500-018C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200532 | 26ROXBURY | 200520 | 26ROXBURY | 2 | 138/115 | 226 | 364 | 91.43 | 102.09 | W1-045 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 151.02 | 144.3 | 4E MILL | PECO_P4_PEACH025_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.89 | 144.21 | 4E MILL | PECO_P1-2_PBTIE1_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 139.25 | 133.31 | 4E MILL | PECO_P4_PEACH205_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 139.15 | 132.99 | 4E MILL | PECO_P1-2_PBTIE2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 138.2 | 132.11 | 4E MILL | PECO_P4_PEACH055_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 133.53 | 127.7 | 4E MILL | PECO_P4_PEACH015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 132.19 | 126.37 | 4E MILL | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 123.1 | 117.72 | 4E MILL | PECO_P4_PEACH225_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 235463 | 01TANEY | 1 | 138 | 227/201 | 250 | 164.37 | 162.77 | AC1-048 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 153.81 | 158.31 | 6BUCKING | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.29 | 157.42 | 6BUCKING | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.29 | 157.42 | 6BUCKING | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 152.12 | 156.99 | 6BUCKING | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 161.81 | 154.58 | 6BUCKING | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 148.75 | 153.33 | 6BUCKING | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 155.87 | 150.71 | 6BUCKING | PN_P1-2_PN-500-010T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.59 | 149.71 | 6BUCKING | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.52 | 149.64 | 6BUCKING | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.21 | 148.47 | 6BUCKING | AP_P2-3_PE-500-016_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.27 | 148.44 | 6BUCKING | AP_P2-3_PE-500-015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.18 | 148.04 | 6BUCKING | PJM_500_BG_P4_5_CNSTN_L_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.47 | 148.03 | 6BUCKING | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.27 | 147.85 | 6BUCKING | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.3 | 147.83 | 6BUCKING | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.03 | 147.64 | 6BUCKING | PECO_P4_NOTTI85_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.97 | 147.62 | 6BUCKING | PECO_P1-2_220-08_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.38 | 147.59 | 6BUCKING | AP_P1-2_WP-500-DRT17_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.38 | 147.59 | 6BUCKING | AP_P1-2_PE-500-001_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.9 | 147.56 | 6BUCKING | PECO_P4_COOPR125_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.34 | 147.52 | 6BUCKING | AP_P2-3_PE-500-018C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204529 | 27GERMANTN | 204538 | 27STRABAN | 1 | 115 | 227 | 291 | 124.26 | 126.24 | AC1-048 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 151.03 | 144.32 | 6BUCKING | PECO_P4_PEACH025_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.89 | 144.22 | 6BUCKING | PECO_P1-2_PBTIE1_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 139.26 | 133.32 | 6BUCKING | PECO_P4_PEACH205_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 139.15 | 132.99 | 6BUCKING | PECO_P1-2_PBTIE2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 138.2 | 132.11 | 6BUCKING | PECO_P4_PEACH055_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 133.53 | 127.71 | 6BUCKING | PECO_P4_PEACH015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 132.2 | 126.37 | 6BUCKING | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 123.1 | 117.72 | 6BUCKING | PECO_P4_PEACH225_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 204529 | 27GERMANTN | 1 | 138/115 | 227 | 347 | 118.42 | 121.9 | AC1-048 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 153.79 | 158.3 | 6ELIZ CT | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.29 | 157.41 | 6ELIZ CT | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.28 | 157.41 | 6ELIZ CT | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 152.11 | 156.97 | 6ELIZ CT | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 161.8 | 154.57 | 6ELIZ CT | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 148.74 | 153.32 | 6ELIZ CT | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 155.86 | 150.7 | 6ELIZ CT | PN_P1-2_PN-500-010T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.58 | 149.7 | 6ELIZ CT | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.51 | 149.62 | 6ELIZ CT | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.19 | 148.45 | 6ELIZ CT | AP_P2-3_PE-500-016_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.26 | 148.42 | 6ELIZ CT | AP_P2-3_PE-500-015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.17 | 148.04 | 6ELIZ CT | PJM_500_BG_P4_5_CNSTN_L_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.47 | 148.03 | 6ELIZ CT | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.26 | 147.84 | 6ELIZ CT | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.29 | 147.83 | 6ELIZ CT | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.02 | 147.63 | 6ELIZ CT | PECO_P4_NOTTI85_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.96 | 147.61 | 6ELIZ CT | PECO_P1-2_220-08_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.37 | 147.57 | 6ELIZ CT | AP_P1-2_WP-500-DRT17_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.37 | 147.57 | 6ELIZ CT | AP_P1-2_PE-500-001_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.89 | 147.55 | 6ELIZ CT | PECO_P4_COOPR125_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.32 | 147.5 | 6ELIZ CT | AP_P2-3_PE-500-018C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 235463 | 01TANEY | 1 | 138 | 227/201 | 250 | 149.4 | 148.03 | AC1-158 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 151.02 | 144.31 | 6ELIZ CT | PECO_P4_PEACH025_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.89 | 144.21 | 6ELIZ CT | PECO_P1-2_PBTIE1_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 139.25 | 133.31 | 6ELIZ CT | PECO_P4_PEACH205_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 139.14 | 132.99 | 6ELIZ CT | PECO_P1-2_PBTIE2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 138.2 | 132.1 | 6ELIZ CT | PECO_P4_PEACH055_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 133.52 | 127.7 | 6ELIZ CT | PECO_P4_PEACH015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 128.97 | 127.23 | 6ELIZ CT | DVP_P4-2: 514T595_SRT-SW |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 132.19 | 126.37 | 6ELIZ CT | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 127.23 | 125.52 | 6ELIZ CT | DVP_P4-2: 51482_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 127.23 | 125.43 | 6ELIZ CT | DVP_P1-2: LN 514_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 127.23 | 125.43 | 6ELIZ CT | AP_P1-2_PE-500-407T_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 123.09 | 117.72 | 6ELIZ CT | PECO_P4_PEACH225_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 117.42 | 115.51 | 6ELIZ CT | AP_P2-3_PE-500-019C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204529 | 27GERMANTN | 204538 | 27STRABAN | 1 | 115 | 227 | 291 | 135.38 | 138.1 | AC1-158 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 153.72 | 158.2 | 6EVERETS | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.21 | 157.33 | 6EVERETS | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.21 | 157.33 | 6EVERETS | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 152.03 | 156.88 | 6EVERETS | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 161.71 | 154.48 | 6EVERETS | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 148.67 | 153.23 | 6EVERETS | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 155.78 | 150.63 | 6EVERETS | PN_P1-2_PN-500-010T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.5 | 149.61 | 6EVERETS | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.43 | 149.54 | 6EVERETS | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.12 | 148.37 | 6EVERETS | AP_P2-3_PE-500-016_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.19 | 148.34 | 6EVERETS | AP_P2-3_PE-500-015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.09 | 147.96 | 6EVERETS | PJM_500_BG_P4_5_CNSTN_L_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.38 | 147.95 | 6EVERETS | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.18 | 147.76 | 6EVERETS | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.21 | 147.74 | 6EVERETS | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.94 | 147.55 | 6EVERETS | PECO_P4_NOTTI85_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.88 | 147.53 | 6EVERETS | PECO_P1-2_220-08_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.3 | 147.48 | 6EVERETS | AP_P1-2_PE-500-001_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.3 | 147.48 | 6EVERETS | AP_P1-2_WP-500-DRT17_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.81 | 147.47 | 6EVERETS | PECO_P4_COOPR125_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.25 | 147.41 | 6EVERETS | AP_P2-3_PE-500-018C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 204529 | 27GERMANTN | 1 | 138/115 | 227 | 347 | 107.63 | 111.12 | AC1-158 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.93 | 144.22 | 6EVERETS | PECO_P4_PEACH025_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.79 | 144.11 | 6EVERETS | PECO_P1-2_PBTIE1_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 139.16 | 133.22 | 6EVERETS | PECO_P4_PEACH205_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 139.05 | 132.9 | 6EVERETS | PECO_P1-2_PBTIE2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 138.11 | 132.02 | 6EVERETS | PECO_P4_PEACH055_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 133.43 | 127.61 | 6EVERETS | PECO_P4_PEACH015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 128.86 | 127.12 | 6EVERETS | DVP_P4-2: 514T595_SRT-SW |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 132.1 | 126.28 | 6EVERETS | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 127.11 | 125.4 | 6EVERETS | DVP_P4-2: 51482_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 127.11 | 125.31 | 6EVERETS | AP_P1-2_PE-500-407T_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 127.11 | 125.31 | 6EVERETS | DVP_P1-2: LN 514_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 123.01 | 117.63 | 6EVERETS | PECO_P4_PEACH225_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 117.31 | 115.39 | 6EVERETS | AP_P2-3_PE-500-019C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 235463 | 01TANEY | 1 | 138 | 227/201 | 250 | 160.14 | 158.6 | AD1-020 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.32 | 157.45 | 6HICKORY | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.32 | 157.45 | 6HICKORY | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 161.85 | 154.62 | 6HICKORY | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 155.9 | 150.74 | 6HICKORY | PN_P1-2_PN-500-010T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.21 | 148.07 | 6HICKORY | PJM_500_BG_P4_5_CNSTN_L_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.5 | 148.07 | 6HICKORY | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.3 | 147.88 | 6HICKORY | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.33 | 147.86 | 6HICKORY | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.06 | 147.67 | 6HICKORY | PECO_P4_NOTTI85_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153 | 147.65 | 6HICKORY | PECO_P1-2_220-08_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.93 | 147.59 | 6HICKORY | PECO_P4_COOPR125_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 139.24 | 142.1 | 6HICKORY | DVP_P4-2: 580T592_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 139.16 | 142.05 | 6HICKORY | DVP_P4-2: 541T580_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 139.25 | 141.96 | 6HICKORY | DVP_P4-2: 541T592_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 136.83 | 139.45 | 6HICKORY | DVP_P4-2: 53672_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 136.82 | 139.45 | 6HICKORY | DVP_P4-2: 536T550_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 136.83 | 139.42 | 6HICKORY | AP_P1-2_WP-500-304T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204529 | 27GERMANTN | 204538 | 27STRABAN | 1 | 115 | 227 | 291 | 144.62 | 147.91 | AD1-020 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 153.68 | 158.16 | 6HORNRTN | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.17 | 157.29 | 6HORNRTN | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.17 | 157.29 | 6HORNRTN | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 151.99 | 156.83 | 6HORNRTN | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 161.66 | 154.44 | 6HORNRTN | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 148.63 | 153.18 | 6HORNRTN | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 155.74 | 150.59 | 6HORNRTN | PN_P1-2_PN-500-010T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.47 | 149.56 | 6HORNRTN | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.4 | 149.49 | 6HORNRTN | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.09 | 148.32 | 6HORNRTN | AP_P2-3_PE-500-016_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.15 | 148.29 | 6HORNRTN | AP_P2-3_PE-500-015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.06 | 147.92 | 6HORNRTN | PJM_500_BG_P4_5_CNSTN_L_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.35 | 147.91 | 6HORNRTN | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.14 | 147.72 | 6HORNRTN | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.17 | 147.71 | 6HORNRTN | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.9 | 147.51 | 6HORNRTN | PECO_P4_NOTTI85_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.84 | 147.5 | 6HORNRTN | PECO_P1-2_220-08_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.26 | 147.44 | 6HORNRTN | AP_P1-2_PE-500-001_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.26 | 147.44 | 6HORNRTN | AP_P1-2_WP-500-DRT17_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.77 | 147.43 | 6HORNRTN | PECO_P4_COOPR125_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.21 | 147.37 | 6HORNRTN | AP_P2-3_PE-500-018C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 204529 | 27GERMANTN | 1 | 138/115 | 227 | 347 | 115.37 | 119.39 | AD1-020 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.89 | 144.18 | 6HORNRTN | PECO_P4_PEACH025_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.74 | 144.07 | 6HORNRTN | PECO_P1-2_PBTIE1_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 139.12 | 133.18 | 6HORNRTN | PECO_P4_PEACH205_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 139.01 | 132.86 | 6HORNRTN | PECO_P1-2_PBTIE2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 138.07 | 131.99 | 6HORNRTN | PECO_P4_PEACH055_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 133.39 | 127.57 | 6HORNRTN | PECO_P4_PEACH015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 128.78 | 127.05 | 6HORNRTN | DVP_P4-2: 514T595_SRT-SW |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 132.06 | 126.24 | 6HORNRTN | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 127.04 | 125.33 | 6HORNRTN | DVP_P4-2: 51482_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 127.04 | 125.23 | 6HORNRTN | DVP_P1-2: LN 514_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 127.04 | 125.23 | 6HORNRTN | AP_P1-2_PE-500-407T_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 122.97 | 117.59 | 6HORNRTN | PECO_P4_PEACH225_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 117.24 | 115.32 | 6HORNRTN | AP_P2-3_PE-500-019C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.33 | 157.45 | 6LOUISA | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.33 | 157.45 | 6LOUISA | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 155.9 | 150.75 | 6LOUISA | PN_P1-2_PN-500-010T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.23 | 148.5 | 6LOUISA | AP_P2-3_PE-500-016_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.3 | 148.47 | 6LOUISA | AP_P2-3_PE-500-015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.21 | 148.08 | 6LOUISA | PJM_500_BG_P4_5_CNSTN_L_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.51 | 148.07 | 6LOUISA | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.31 | 147.89 | 6LOUISA | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.34 | 147.87 | 6LOUISA | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.07 | 147.68 | 6LOUISA | PECO_P4_NOTTI85_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.01 | 147.66 | 6LOUISA | PECO_P1-2_220-08_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.94 | 147.6 | 6LOUISA | PECO_P4_COOPR125_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 139.24 | 142.11 | 6LOUISA | DVP_P4-2: 580T592_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 139.16 | 142.05 | 6LOUISA | DVP_P4-2: 541T580_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 136.82 | 139.45 | 6LOUISA | DVP_P4-2: 536T550_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204529 | 27GERMANTN | 204538 | 27STRABAN | 1 | 115 | 227 | 291 | 140.14 | 143.04 | AE2-000 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 153.72 | 158.21 | 6OLDCHRC | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.22 | 157.34 | 6OLDCHRC | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.22 | 157.34 | 6OLDCHRC | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 152.04 | 156.89 | 6OLDCHRC | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 161.73 | 154.5 | 6OLDCHRC | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 148.67 | 153.24 | 6OLDCHRC | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 155.79 | 150.64 | 6OLDCHRC | PN_P1-2_PN-500-010T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.51 | 149.62 | 6OLDCHRC | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.44 | 149.54 | 6OLDCHRC | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.13 | 148.36 | 6OLDCHRC | AP_P2-3_PE-500-016_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.19 | 148.34 | 6OLDCHRC | AP_P2-3_PE-500-015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.1 | 147.97 | 6OLDCHRC | PJM_500_BG_P4_5_CNSTN_L_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.4 | 147.96 | 6OLDCHRC | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.2 | 147.78 | 6OLDCHRC | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.23 | 147.76 | 6OLDCHRC | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.95 | 147.57 | 6OLDCHRC | PECO_P4_NOTTI85_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.89 | 147.55 | 6OLDCHRC | PECO_P1-2_220-08_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.31 | 147.49 | 6OLDCHRC | AP_P1-2_WP-500-DRT17_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.31 | 147.49 | 6OLDCHRC | AP_P1-2_PE-500-001_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.83 | 147.49 | 6OLDCHRC | PECO_P4_COOPR125_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.26 | 147.42 | 6OLDCHRC | AP_P2-3_PE-500-018C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 204529 | 27GERMANTN | 1 | 138/115 | 227 | 347 | 111.62 | 115.29 | AE2-000 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.95 | 144.24 | 6OLDCHRC | PECO_P4_PEACH025_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.81 | 144.13 | 6OLDCHRC | PECO_P1-2_PBTIE1_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 139.18 | 133.24 | 6OLDCHRC | PECO_P4_PEACH205_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 139.07 | 132.92 | 6OLDCHRC | PECO_P1-2_PBTIE2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 138.13 | 132.04 | 6OLDCHRC | PECO_P4_PEACH055_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 133.45 | 127.62 | 6OLDCHRC | PECO_P4_PEACH015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 128.83 | 127.09 | 6OLDCHRC | DVP_P4-2: 514T595_SRT-SW |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 132.12 | 126.3 | 6OLDCHRC | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 127.08 | 125.37 | 6OLDCHRC | DVP_P4-2: 51482_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 127.08 | 125.28 | 6OLDCHRC | DVP_P1-2: LN 514_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 127.08 | 125.28 | 6OLDCHRC | AP_P1-2_PE-500-407T_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 123.02 | 117.65 | 6OLDCHRC | PECO_P4_PEACH225_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 117.28 | 115.36 | 6OLDCHRC | AP_P2-3_PE-500-019C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 235463 | 01TANEY | 1 | 138 | 227/201 | 250 | 159.61 | 158.09 | AG2-055 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 153.82 | 158.32 | 6PAPERMILL | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.31 | 157.43 | 6PAPERMILL | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.31 | 157.43 | 6PAPERMILL | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 152.13 | 157 | 6PAPERMILL | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 161.83 | 154.6 | 6PAPERMILL | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 148.77 | 153.35 | 6PAPERMILL | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 155.88 | 150.73 | 6PAPERMILL | PN_P1-2_PN-500-010T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.22 | 148.48 | 6PAPERMILL | AP_P2-3_PE-500-016_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.28 | 148.45 | 6PAPERMILL | AP_P2-3_PE-500-015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.19 | 148.06 | 6PAPERMILL | PJM_500_BG_P4_5_CNSTN_L_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.49 | 148.05 | 6PAPERMILL | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.29 | 147.86 | 6PAPERMILL | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.32 | 147.85 | 6PAPERMILL | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.04 | 147.65 | 6PAPERMILL | PECO_P4_NOTTI85_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.98 | 147.64 | 6PAPERMILL | PECO_P1-2_220-08_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.39 | 147.6 | 6PAPERMILL | AP_P1-2_PE-500-001_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.39 | 147.6 | 6PAPERMILL | AP_P1-2_WP-500-DRT17_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.92 | 147.57 | 6PAPERMILL | PECO_P4_COOPR125_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.35 | 147.53 | 6PAPERMILL | AP_P2-3_PE-500-018C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.34 | 147.52 | 6PAPERMILL | AP_P2-3_PE-500-018D_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204529 | 27GERMANTN | 204538 | 27STRABAN | 1 | 115 | 227 | 291 | 144.18 | 147.58 | AG2-055 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 142.86 | 146.96 | 6PAPERMILL | AP_P2-3_WP-500-466_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 151.05 | 144.34 | 6PAPERMILL | PECO_P4_PEACH025_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.91 | 144.24 | 6PAPERMILL | PECO_P1-2_PBTIE1_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 139.17 | 133.01 | 6PAPERMILL | PECO_P1-2_PBTIE2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 138.22 | 132.13 | 6PAPERMILL | PECO_P4_PEACH055_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 133.55 | 127.73 | 6PAPERMILL | PECO_P4_PEACH015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 132.22 | 126.39 | 6PAPERMILL | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 123.12 | 117.74 | 6PAPERMILL | PECO_P4_PEACH225_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 204529 | 27GERMANTN | 1 | 138/115 | 227 | 347 | 114.99 | 119.11 | AG2-055 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.32 | 157.44 | 6POWHATN | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.32 | 157.44 | 6POWHATN | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 161.84 | 154.61 | 6POWHATN | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 155.89 | 150.74 | 6POWHATN | PN_P1-2_PN-500-010T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.23 | 148.49 | 6POWHATN | AP_P2-3_PE-500-016_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.29 | 148.46 | 6POWHATN | AP_P2-3_PE-500-015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.2 | 148.07 | 6POWHATN | PJM_500_BG_P4_5_CNSTN_L_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.5 | 148.06 | 6POWHATN | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.3 | 147.87 | 6POWHATN | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.32 | 147.86 | 6POWHATN | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.05 | 147.66 | 6POWHATN | PECO_P4_NOTTI85_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.99 | 147.65 | 6POWHATN | PECO_P1-2_220-08_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.41 | 147.61 | 6POWHATN | AP_P1-2_WP-500-DRT17_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.41 | 147.61 | 6POWHATN | AP_P1-2_PE-500-001_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.93 | 147.58 | 6POWHATN | PECO_P4_COOPR125_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.36 | 147.54 | 6POWHATN | AP_P2-3_PE-500-018C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.35 | 147.54 | 6POWHATN | AP_P2-3_PE-500-018D_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 142.87 | 146.98 | 6POWHATN | AP_P2-3_WP-500-DRT19_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 142.87 | 146.98 | 6POWHATN | AP_P1-2_PE-500-004_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.92 | 144.25 | 6POWHATN | PECO_P1-2_PBTIE1_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 139.23 | 142.1 | 6POWHATN | DVP_P4-2: 580T592_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 139.15 | 142.04 | 6POWHATN | DVP_P4-2: 541T580_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 139.18 | 133.02 | 6POWHATN | PECO_P1-2_PBTIE2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 235463 | 01TANEY | 1 | 138 | 227/201 | 250 | 148.77 | 147.45 | O66 NFTWR | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 153.81 | 158.32 | 6WINFALL | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.3 | 157.43 | 6WINFALL | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.3 | 157.42 | 6WINFALL | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 152.12 | 157 | 6WINFALL | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 161.82 | 154.59 | 6WINFALL | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 148.76 | 153.34 | 6WINFALL | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 155.87 | 150.72 | 6WINFALL | PN_P1-2_PN-500-010T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.59 | 149.72 | 6WINFALL | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.52 | 149.64 | 6WINFALL | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.21 | 148.47 | 6WINFALL | AP_P2-3_PE-500-016_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.28 | 148.44 | 6WINFALL | AP_P2-3_PE-500-015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.18 | 148.05 | 6WINFALL | PJM_500_BG_P4_5_CNSTN_L_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.48 | 148.04 | 6WINFALL | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.28 | 147.86 | 6WINFALL | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.31 | 147.84 | 6WINFALL | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.04 | 147.65 | 6WINFALL | PECO_P4_NOTTI85_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.98 | 147.63 | 6WINFALL | PECO_P1-2_220-08_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.39 | 147.59 | 6WINFALL | AP_P1-2_WP-500-DRT17_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.39 | 147.59 | 6WINFALL | AP_P1-2_PE-500-001_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.91 | 147.57 | 6WINFALL | PECO_P4_COOPR125_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.34 | 147.52 | 6WINFALL | AP_P2-3_PE-500-018C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204529 | 27GERMANTN | 204538 | 27STRABAN | 1 | 115 | 227 | 291 | 134.84 | 137.51 | O66 NFTWR | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 151.04 | 144.33 | 6WINFALL | PECO_P4_PEACH025_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.9 | 144.23 | 6WINFALL | PECO_P1-2_PBTIE1_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 139.27 | 133.32 | 6WINFALL | PECO_P4_PEACH205_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 139.16 | 133 | 6WINFALL | PECO_P1-2_PBTIE2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 138.21 | 132.12 | 6WINFALL | PECO_P4_PEACH055_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 133.54 | 127.72 | 6WINFALL | PECO_P4_PEACH015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 132.21 | 126.38 | 6WINFALL | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 123.11 | 117.73 | 6WINFALL | PECO_P4_PEACH225_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 204529 | 27GERMANTN | 1 | 138/115 | 227 | 347 | 107.18 | 110.62 | O66 NFTWR | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 153.76 | 158.26 | 6WINTERP | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.25 | 157.38 | 6WINTERP | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.25 | 157.38 | 6WINTERP | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 152.07 | 156.93 | 6WINTERP | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 161.77 | 154.54 | 6WINTERP | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 148.71 | 153.28 | 6WINTERP | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 155.83 | 150.67 | 6WINTERP | PN_P1-2_PN-500-010T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.54 | 149.66 | 6WINTERP | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.47 | 149.59 | 6WINTERP | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.16 | 148.41 | 6WINTERP | AP_P2-3_PE-500-016_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.23 | 148.38 | 6WINTERP | AP_P2-3_PE-500-015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.14 | 148 | 6WINTERP | PJM_500_BG_P4_5_CNSTN_L_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.43 | 148 | 6WINTERP | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.23 | 147.81 | 6WINTERP | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.26 | 147.79 | 6WINTERP | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.99 | 147.6 | 6WINTERP | PECO_P4_NOTTI85_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.93 | 147.58 | 6WINTERP | PECO_P1-2_220-08_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.34 | 147.53 | 6WINTERP | AP_P1-2_PE-500-001_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.34 | 147.53 | 6WINTERP | AP_P1-2_WP-500-DRT17_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.86 | 147.52 | 6WINTERP | PECO_P4_COOPR125_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.29 | 147.46 | 6WINTERP | AP_P2-3_PE-500-018C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204539 | 27HUNTRSTN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 263 | 144.25 | 141.45 | AC1-048 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.99 | 144.27 | 6WINTERP | PECO_P4_PEACH025_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.85 | 144.17 | 6WINTERP | PECO_P1-2_PBTIE1_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 139.22 | 133.27 | 6WINTERP | PECO_P4_PEACH205_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 139.11 | 132.95 | 6WINTERP | PECO_P1-2_PBTIE2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 138.16 | 132.07 | 6WINTERP | PECO_P4_PEACH055_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 133.49 | 127.66 | 6WINTERP | PECO_P4_PEACH015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 128.9 | 127.16 | 6WINTERP | DVP_P4-2: 514T595_SRT-SW |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 132.16 | 126.33 | 6WINTERP | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 127.15 | 125.44 | 6WINTERP | DVP_P4-2: 51482_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 127.15 | 125.35 | 6WINTERP | DVP_P1-2: LN 514_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 127.15 | 125.35 | 6WINTERP | AP_P1-2_PE-500-407T_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 123.06 | 117.68 | 6WINTERP | PECO_P4_PEACH225_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 117.35 | 115.43 | 6WINTERP | AP_P2-3_PE-500-019C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204539 | 27HUNTRSTN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 263 | 155.96 | 153.05 | AC1-158 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 153.8 | 158.31 | AA1-018 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.27 | 157.4 | AA1-018 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.27 | 157.39 | AA1-018 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 152.11 | 156.98 | AA1-018 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 161.75 | 154.52 | AA1-018 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 148.75 | 153.33 | AA1-018 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 155.84 | 150.69 | AA1-018 | PN_P1-2_PN-500-010T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.58 | 149.71 | AA1-018 | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.51 | 149.63 | AA1-018 | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.22 | 148.5 | AA1-018 | AP_P2-3_PE-500-016_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.28 | 148.47 | AA1-018 | AP_P2-3_PE-500-015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.15 | 148.02 | AA1-018 | PJM_500_BG_P4_5_CNSTN_L_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.42 | 147.98 | AA1-018 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.22 | 147.79 | AA1-018 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.24 | 147.78 | AA1-018 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.4 | 147.62 | AA1-018 | AP_P1-2_PE-500-001_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.4 | 147.62 | AA1-018 | AP_P1-2_WP-500-DRT17_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.97 | 147.58 | AA1-018 | PECO_P4_NOTTI85_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.91 | 147.57 | AA1-018 | PECO_P1-2_220-08_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.35 | 147.55 | AA1-018 | AP_P2-3_PE-500-018C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.85 | 147.5 | AA1-018 | PECO_P4_COOPR125_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204539 | 27HUNTRSTN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 263 | 123.45 | 122.3 | AD1-020 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.95 | 144.24 | AA1-018 | PECO_P4_PEACH025_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.84 | 144.16 | AA1-018 | PECO_P1-2_PBTIE1_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 139.21 | 133.27 | AA1-018 | PECO_P4_PEACH205_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 139.1 | 132.94 | AA1-018 | PECO_P1-2_PBTIE2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 138.15 | 132.06 | AA1-018 | PECO_P4_PEACH055_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 133.48 | 127.66 | AA1-018 | PECO_P4_PEACH015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 132.15 | 126.33 | AA1-018 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 123.05 | 117.68 | AA1-018 | PECO_P4_PEACH225_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204539 | 27HUNTRSTN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 263 | 165.32 | 162.37 | AG2-055 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 153.82 | 158.33 | AA1-038 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.31 | 157.43 | AA1-038 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.31 | 157.43 | AA1-038 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 161.82 | 154.59 | AA1-038 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 155.88 | 150.72 | AA1-038 | PN_P1-2_PN-500-010T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.22 | 148.5 | AA1-038 | AP_P2-3_PE-500-016_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.29 | 148.47 | AA1-038 | AP_P2-3_PE-500-015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.19 | 148.06 | AA1-038 | PJM_500_BG_P4_5_CNSTN_L_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.48 | 148.04 | AA1-038 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.28 | 147.86 | AA1-038 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.31 | 147.84 | AA1-038 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.03 | 147.64 | AA1-038 | PECO_P4_NOTTI85_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.97 | 147.63 | AA1-038 | PECO_P1-2_220-08_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.4 | 147.62 | AA1-038 | AP_P1-2_PE-500-001_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.4 | 147.62 | AA1-038 | AP_P1-2_WP-500-DRT17_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.91 | 147.56 | AA1-038 | PECO_P4_COOPR125_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.35 | 147.55 | AA1-038 | AP_P2-3_PE-500-018C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.35 | 147.54 | AA1-038 | AP_P2-3_PE-500-018D_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204539 | 27HUNTRSTN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 263 | 155.37 | 152.45 | O66 NFTWR | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 142.87 | 146.98 | AA1-038 | AP_P1-2_WP-500-006_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 142.87 | 146.98 | AA1-038 | AP_P1-2_PE-500-004_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 142.87 | 146.98 | AA1-038 | AP_P2-3_WP-500-466_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 151.04 | 144.32 | AA1-038 | PECO_P4_PEACH025_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.9 | 144.23 | AA1-038 | PECO_P1-2_PBTIE1_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 139.27 | 133.33 | AA1-038 | PECO_P4_PEACH205_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 139.16 | 133 | AA1-038 | PECO_P1-2_PBTIE2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 138.21 | 132.12 | AA1-038 | PECO_P4_PEACH055_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 133.54 | 127.72 | AA1-038 | PECO_P4_PEACH015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 132.21 | 126.38 | AA1-038 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 123.11 | 117.73 | AA1-038 | PECO_P4_PEACH225_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 263 | 145.03 | 143.28 | AC1-048 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.59 | 157.71 | AA1-060 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.59 | 157.71 | AA1-060 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 162.19 | 154.94 | AA1-060 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 156.16 | 151.01 | AA1-060 | PN_P1-2_PN-500-010T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.8 | 148.35 | AA1-060 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.6 | 148.17 | AA1-060 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.62 | 148.15 | AA1-060 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.35 | 147.96 | AA1-060 | PECO_P4_NOTTI85_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.29 | 147.94 | AA1-060 | PECO_P1-2_220-08_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.22 | 147.88 | AA1-060 | PECO_P4_COOPR125_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.1 | 147.71 | AA1-060 | AP_P2-3_PE-500-015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 151.43 | 144.7 | AA1-060 | PECO_P4_PEACH025_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 151.3 | 144.6 | AA1-060 | PECO_P1-2_PBTIE1_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 139.53 | 133.35 | AA1-060 | PECO_P1-2_PBTIE2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 138.55 | 132.44 | AA1-060 | PECO_P4_PEACH055_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 133.93 | 128.09 | AA1-060 | PECO_P4_PEACH015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 132.57 | 126.71 | AA1-060 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 123.47 | 118.08 | AA1-060 | PECO_P4_PEACH225_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 263 | 156.54 | 154.9 | AC1-158 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 153.7 | 158.18 | AA1-063 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.19 | 157.31 | AA1-063 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.19 | 157.31 | AA1-063 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 152.01 | 156.86 | AA1-063 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 161.69 | 154.47 | AA1-063 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 148.65 | 153.21 | AA1-063 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 155.76 | 150.61 | AA1-063 | PN_P1-2_PN-500-010T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.49 | 149.59 | AA1-063 | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.42 | 149.52 | AA1-063 | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.11 | 148.34 | AA1-063 | AP_P2-3_PE-500-016_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.17 | 148.31 | AA1-063 | AP_P2-3_PE-500-015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.08 | 147.94 | AA1-063 | PJM_500_BG_P4_5_CNSTN_L_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.37 | 147.93 | AA1-063 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.17 | 147.74 | AA1-063 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.19 | 147.73 | AA1-063 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.92 | 147.53 | AA1-063 | PECO_P4_NOTTI85_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.86 | 147.52 | AA1-063 | PECO_P1-2_220-08_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.28 | 147.46 | AA1-063 | AP_P1-2_WP-500-DRT17_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.28 | 147.46 | AA1-063 | AP_P1-2_PE-500-001_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.8 | 147.45 | AA1-063 | PECO_P4_COOPR125_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.23 | 147.39 | AA1-063 | AP_P2-3_PE-500-018C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 263 | 168.22 | 166.51 | AD1-020 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.91 | 144.2 | AA1-063 | PECO_P4_PEACH025_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.77 | 144.1 | AA1-063 | PECO_P1-2_PBTIE1_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 139.15 | 133.21 | AA1-063 | PECO_P4_PEACH205_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 139.04 | 132.88 | AA1-063 | PECO_P1-2_PBTIE2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 138.1 | 132.01 | AA1-063 | PECO_P4_PEACH055_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 133.41 | 127.59 | AA1-063 | PECO_P4_PEACH015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 128.81 | 127.08 | AA1-063 | DVP_P4-2: 514T595_SRT-SW |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 132.09 | 126.26 | AA1-063 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 127.07 | 125.36 | AA1-063 | DVP_P4-2: 51482_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 127.07 | 125.27 | AA1-063 | DVP_P1-2: LN 514_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 127.07 | 125.27 | AA1-063 | AP_P1-2_PE-500-407T_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 122.99 | 117.62 | AA1-063 | PECO_P4_PEACH225_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 117.27 | 115.35 | AA1-063 | AP_P2-3_PE-500-019C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 229.39 | 242.24 | AA1-102 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 227.32 | 242.24 | AA1-102 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 226.41 | 240.14 | AA1-102 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 228.48 | 240.14 | AA1-102 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 228.41 | 240.08 | AA1-102 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 226.35 | 240.08 | AA1-102 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 228.41 | 240.08 | AA1-102 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 226.35 | 240.08 | AA1-102 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 217.14 | 231.92 | AA1-102 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 216.26 | 229.89 | AA1-102 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 216.2 | 229.83 | AA1-102 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 216.2 | 229.83 | AA1-102 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 212.88 | 228.75 | AA1-102 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 212 | 226.7 | AA1-102 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 211.93 | 226.64 | AA1-102 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 211.93 | 226.64 | AA1-102 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 213.58 | 221.48 | AA1-102 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 211.51 | 221.48 | AA1-102 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 201.88 | 211.81 | AA1-102 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 197.61 | 208.48 | AA1-102 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 174.03 | 169.34 | AA1-102 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 173.09 | 167.93 | AA1-102 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 173.09 | 167.93 | AA1-102 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 173.07 | 167.92 | AA1-102 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 165.03 | 166.87 | AA1-102 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 163.23 | 163.81 | AA1-102 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 163.23 | 163.81 | AA1-102 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 163.22 | 163.8 | AA1-102 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 263 | 165.73 | 164.22 | AG2-055 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 165.15 | 160.22 | AA1-102 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 154.84 | 159.54 | AA1-102 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 163.51 | 158.62 | AA1-102 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 163.51 | 158.62 | AA1-102 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 153.14 | 158.21 | AA1-102 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 163.52 | 156.22 | AA1-102 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 149.77 | 154.56 | AA1-102 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 903 | 145.34 | 153.8 | AA1-102 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 154.29 | 153 | AA1-102 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 157.1 | 151.94 | AA1-102 | PN_P1-2_PN-500-010T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 903 | 143.87 | 151.16 | AA1-102 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 903 | 143.86 | 151.16 | AA1-102 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 903 | 143.85 | 151.16 | AA1-102 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 147.58 | 150.88 | AA1-102 | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 147.51 | 150.81 | AA1-102 | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 145.12 | 149.55 | AA1-102 | AP_P2-3_PE-500-016_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 145.18 | 149.52 | AA1-102 | AP_P2-3_PE-500-015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 154.94 | 149.47 | AA1-102 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 154.73 | 149.28 | AA1-102 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 154.76 | 149.26 | AA1-102 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 154.34 | 149.19 | AA1-102 | PJM_500_BG_P4_5_CNSTN_L_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 154.49 | 149.07 | AA1-102 | PECO_P4_NOTTI85_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 154.43 | 149.05 | AA1-102 | PECO_P1-2_220-08_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 154.36 | 148.99 | AA1-102 | PECO_P4_COOPR125_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.29 | 148.66 | AA1-102 | AP_P1-2_PE-500-001_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.29 | 148.66 | AA1-102 | AP_P1-2_WP-500-DRT17_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.25 | 148.59 | AA1-102 | AP_P2-3_PE-500-018C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 263 | 155.98 | 154.32 | O66 NFTWR | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 153.12 | 146.32 | AA1-102 | PECO_P4_PEACH025_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 152.76 | 146.01 | AA1-102 | PECO_P1-2_PBTIE1_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 911 | 150.24 | 144.57 | AA1-102 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 911 | 149.33 | 143.28 | AA1-102 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 911 | 149.33 | 143.28 | AA1-102 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 911 | 149.31 | 143.27 | AA1-102 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204502 | 27JACKSON | 204514 | 27TMI | 1 | 230 | 227 | 781 | 134.01 | 143.22 | AA1-102 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204502 | 27JACKSON | 204514 | 27TMI | 1 | 230 | 227 | 781 | 134.2 | 143.17 | AA1-102 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204502 | 27JACKSON | 204514 | 27TMI | 1 | 230 | 227 | 781 | 134.2 | 143.16 | AA1-102 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204502 | 27JACKSON | 204514 | 27TMI | 1 | 230 | 227 | 781 | 134.18 | 143.16 | AA1-102 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 903 | 136.79 | 141.22 | AA1-102 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 1031 | 131.74 | 140.59 | AA1-102 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 1031 | 131.26 | 139.5 | AA1-102 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 1031 | 131.26 | 139.5 | AA1-102 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 1031 | 131.25 | 139.49 | AA1-102 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 911 | 141.46 | 136.29 | AA1-102 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 207923 | BRISREAC | 208132 | WHEM TR1 | 1 | 230 | 229 | 676 | 125.87 | 135.72 | AA1-102 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 207922 | BRIS | 207923 | BRISREAC | RX | 230 | 229 | 676 | 125.87 | 135.72 | AA1-102 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208078 | SAKR | 1 | 230 | 229 | 903 | 126.44 | 135.54 | AA1-102 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 140.88 | 134.65 | AA1-102 | PECO_P1-2_PBTIE2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 140.58 | 134.59 | AA1-102 | PECO_P4_PEACH205_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208078 | SAKR | 1 | 230 | 229 | 903 | 125.73 | 134.1 | AA1-102 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208078 | SAKR | 1 | 230 | 229 | 903 | 125.73 | 134.1 | AA1-102 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208078 | SAKR | 1 | 230 | 229 | 903 | 125.73 | 134.09 | AA1-102 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 139.9 | 133.75 | AA1-102 | PECO_P4_PEACH055_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204502 | 27JACKSON | 204514 | 27TMI | 1 | 230 | 227 | 781 | 126.55 | 132.69 | AA1-102 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220972 | GRANITE1 | 1 | 230 | 232 | 829 | 136.16 | 132.15 | AA1-102 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220972 | GRANITE1 | 1 | 230 | 232 | 829 | 135.53 | 131.5 | AA1-102 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220972 | GRANITE1 | 1 | 230 | 232 | 829 | 135.53 | 131.5 | AA1-102 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 1031 | 125.66 | 130.71 | AA1-102 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220973 | GRANITE6 | 1 | 230 | 232 | 829 | 134.06 | 130.24 | AA1-102 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220973 | GRANITE6 | 1 | 230 | 232 | 829 | 133.47 | 129.63 | AA1-102 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220973 | GRANITE6 | 1 | 230 | 232 | 829 | 133.47 | 129.62 | AA1-102 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 135.42 | 129.52 | AA1-102 | PECO_P4_PEACH015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 128.76 | 129.12 | AA1-102 | BG_P7_GRCTN_CNSTN_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 126.69 | 129.12 | AA1-102 | BG_P7_GRCTN_CNSTN_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 129.97 | 128.23 | AA1-102 | DVP_P4-2: 514T595_SRT-SW |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 133.91 | 128 | AA1-102 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208020 | MANO TR3 | 1 | 230 | 229 | 793 | 113.5 | 127.91 | AA1-102 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220953 | HOWARD12 | 220972 | GRANITE1 | 1 | 230 | 232 | 772 | 131.14 | 127.12 | AA1-102 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 128.25 | 126.54 | AA1-102 | DVP_P4-2: 51482_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 128.25 | 126.45 | AA1-102 | DVP_P1-2: LN 514_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 128.25 | 126.45 | AA1-102 | AP_P1-2_PE-500-407T_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220954 | HOWARD32 | 220973 | GRANITE6 | 1 | 230 | 232 | 772 | 129.9 | 126.35 | AA1-102 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208020 | MANO TR3 | 1 | 230 | 229 | 793 | 112.7 | 126.26 | AA1-102 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208020 | MANO TR3 | 1 | 230 | 229 | 793 | 112.71 | 126.26 | AA1-102 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208020 | MANO TR3 | 1 | 230 | 229 | 793 | 112.71 | 126.26 | AA1-102 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220953 | HOWARD12 | 220972 | GRANITE1 | 1 | 230 | 232 | 772 | 130.23 | 126.16 | AA1-102 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220953 | HOWARD12 | 220972 | GRANITE1 | 1 | 230 | 232 | 772 | 130.23 | 126.16 | AA1-102 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 207922 | BRIS | 207923 | BRISREAC | RX | 230 | 229 | 676 | 120.04 | 126.06 | AA1-102 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 207923 | BRISREAC | 208132 | WHEM TR1 | 1 | 230 | 229 | 676 | 120.04 | 126.06 | AA1-102 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220954 | HOWARD32 | 220973 | GRANITE6 | 1 | 230 | 232 | 772 | 129.12 | 125.52 | AA1-102 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220954 | HOWARD32 | 220973 | GRANITE6 | 1 | 230 | 232 | 772 | 129.12 | 125.51 | AA1-102 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 121.67 | 124.55 | AA1-102 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 119.6 | 124.55 | AA1-102 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 119.42 | 124.34 | AA1-102 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 121.49 | 124.34 | AA1-102 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 119.42 | 124.34 | AA1-102 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 121.49 | 124.34 | AA1-102 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208078 | SAKR | 1 | 230 | 229 | 903 | 118.46 | 124.27 | AA1-102 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208031 | MLWD TR2 | 1 | 230 | 229 | 911 | 113.62 | 124.12 | AA1-102 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204512 | 27S.RDG | 204693 | 27BOONETOWN | 1 | 230 | 227 | 607 | 108.21 | 123.76 | AA1-102 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200025 | W CHAPEL | 1 | 500 | 225 | 1732 | 124.8 | 123.06 | AA1-102 | PEPCO_P4_PP41_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208031 | MLWD TR2 | 1 | 230 | 229 | 911 | 112.92 | 122.66 | AA1-102 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208031 | MLWD TR2 | 1 | 230 | 229 | 911 | 112.93 | 122.66 | AA1-102 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208031 | MLWD TR2 | 1 | 230 | 229 | 911 | 112.93 | 122.66 | AA1-102 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 119.98 | 122.4 | AA1-102 | BG_P7_GRCTN_CNSTN_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 120.7 | 121.35 | AA1-102 | PJM_500_BG_P4_5_CNSTN_15_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 118.64 | 121.35 | AA1-102 | PJM_500_BG_P4_5_CNSTN_15_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208131 | WHEM | 208132 | WHEM TR1 | 1 | 230 | 229 | 691 | 110.06 | 120.33 | AA1-102 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220965 | NEAST339 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 120.68 | 120.05 | AA1-102 | BG_P1_2315_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220965 | NEAST339 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 120.24 | 119.83 | AA1-102 | BG_P4_5_NEAST_17_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220965 | NEAST339 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 120.4 | 119.83 | AA1-102 | BG_P4_5_NEAST_15_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 124.84 | 119.39 | AA1-102 | PECO_P4_PEACH225_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 115.56 | 119.36 | AA1-102 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204538 | 27STRABAN | 204544 | 27LINCOLN | 1 | 115 | 227 | 291 | 131.28 | 131.89 | AC1-048 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204538 | 27STRABAN | 204544 | 27LINCOLN | 1 | 115 | 227 | 291 | 142.67 | 143.75 | AC1-158 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220979 | NEAST317 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 119.75 | 119.17 | AA1-102 | BG_P1_2337_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 115.21 | 119.01 | AA1-102 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 115.21 | 118.96 | AA1-102 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 115.21 | 118.96 | AA1-102 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220979 | NEAST317 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 119.41 | 118.89 | AA1-102 | BG_P4_5_NEAST_39_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220979 | NEAST317 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 119.41 | 118.89 | AA1-102 | BG_P4_5_NEAST_37_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 114.87 | 118.62 | AA1-102 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 114.87 | 118.62 | AA1-102 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 115.71 | 118.56 | AA1-102 | BG_P7_GRCTN_CNSTN_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 113.13 | 118 | AA1-102 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 112.96 | 117.79 | AA1-102 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 112.96 | 117.79 | AA1-102 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204538 | 27STRABAN | 204544 | 27LINCOLN | 1 | 115 | 227 | 291 | 152.16 | 153.57 | AD1-020 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 118.44 | 116.52 | AA1-102 | AP_P2-3_PE-500-019C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 2 | 500/230 | 225/232 | 2168 | 110.41 | 115.83 | AA1-102 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208020 | MANO TR3 | 1 | 230 | 229 | 793 | 105.52 | 115.82 | AA1-102 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 2 | 500/230 | 225/232 | 2168 | 110.24 | 115.61 | AA1-102 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 2 | 500/230 | 225/232 | 2168 | 110.24 | 115.61 | AA1-102 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 1 | 500/230 | 225/232 | 2168 | 110.18 | 115.58 | AA1-102 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208020 | MANO TR3 | 208031 | MLWD TR2 | 1 | 230 | 229 | 903 | 103.66 | 115.37 | AA1-102 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 1 | 500/230 | 225/232 | 2168 | 110.01 | 115.37 | AA1-102 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 1 | 500/230 | 225/232 | 2168 | 110 | 115.37 | AA1-102 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220964 | GRACETON | 220999 | BAGLEY2 | 13 | 230 | 232 | 1795 | 114.14 | 115.24 | AA1-102 | BG_P4_5_GRCTN_3T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 112.2 | 114.96 | AA1-102 | PJM_500_BG_P4_5_CNSTN_15_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 108.87 | 114.18 | AA1-102 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 108.69 | 113.97 | AA1-102 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 108.69 | 113.97 | AA1-102 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208020 | MANO TR3 | 208031 | MLWD TR2 | 1 | 230 | 229 | 903 | 102.98 | 113.86 | AA1-102 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208020 | MANO TR3 | 208031 | MLWD TR2 | 1 | 230 | 229 | 903 | 102.98 | 113.86 | AA1-102 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208020 | MANO TR3 | 208031 | MLWD TR2 | 1 | 230 | 229 | 903 | 102.98 | 113.85 | AA1-102 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208031 | MLWD TR2 | 1 | 230 | 229 | 911 | 106.17 | 113.39 | AA1-102 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 2 | 500/230 | 225/232 | 2168 | 109.11 | 112.47 | AA1-102 | PJM_500_BG_P4_5_CNSTN_15_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 107.18 | 112.14 | AA1-102 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 107.06 | 112 | AA1-102 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220980 | RAPHAEL | 220999 | BAGLEY2 | 13 | 230 | 232 | 1795 | 109.71 | 112 | AA1-102 | BG_P4_5_GRCTN_3T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204538 | 27STRABAN | 204544 | 27LINCOLN | 1 | 115 | 227 | 291 | 147.55 | 148.69 | AE2-000 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208131 | WHEM | 208133 | WHEM TR2 | 1 | 230 | 229 | 691 | 102.53 | 111.71 | AA1-102 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208131 | WHEM | 208132 | WHEM TR1 | 1 | 230 | 229 | 691 | 104.58 | 111.45 | AA1-102 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 107.93 | 111.25 | AA1-102 | PJM_500_BG_P4_5_CNSTN_15_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220973 | GRANITE6 | 1 | 230 | 232 | 829 | 109.81 | 108.6 | AA1-102 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220965 | NEAST339 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 109.2 | 107.77 | AA1-102 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220965 | NEAST339 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 109.11 | 107.66 | AA1-102 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220965 | NEAST339 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 109.11 | 107.66 | AA1-102 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220972 | GRANITE1 | 1 | 230 | 232 | 829 | 108.96 | 107.52 | AA1-102 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 102.3 | 106.58 | AA1-102 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208021 | MANO TR4 | 208133 | WHEM TR2 | 2 | 230 | 229 | 593 | 97.16 | 106.5 | AA1-102 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 102.21 | 106.49 | AA1-102 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200099 | LAUS | 208045 | LAUS | 3 | 500/230 | 225/229 | 1200 | 104.12 | 105.92 | AA1-102 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220972 | GRANITE1 | 1 | 230 | 232 | 829 | 106.91 | 105.58 | AA1-102 | BG_P4_5_NW230-4_2326_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 103.4 | 105.47 | AA1-102 | BG_P1_2322_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200099 | LAUS | 208045 | LAUS | 3 | 500/230 | 225/229 | 1200 | 103.82 | 105.42 | AA1-102 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200099 | LAUS | 208045 | LAUS | 3 | 500/230 | 225/229 | 1200 | 103.82 | 105.42 | AA1-102 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200099 | LAUS | 208045 | LAUS | 3 | 500/230 | 225/229 | 1200 | 103.81 | 105.41 | AA1-102 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 103.32 | 105.4 | AA1-102 | BG_P1_2310_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 103.33 | 105.36 | AA1-102 | BG_P4_5_NW2322_230-4_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 103.26 | 105.32 | AA1-102 | BG_P4_5_NW2310_230-5_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220973 | GRANITE6 | 1 | 230 | 232 | 829 | 106.59 | 105.05 | AA1-102 | BG_P4_5_NW230-5_2311_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208020 | MANO TR3 | 208031 | MLWD TR2 | 1 | 230 | 229 | 903 | 96.61 | 104.91 | AA1-102 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220979 | NEAST317 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 106.05 | 104.68 | AA1-102 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220979 | NEAST317 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 105.96 | 104.57 | AA1-102 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220979 | NEAST317 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 105.96 | 104.57 | AA1-102 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 101.97 | 104.08 | AA1-102 | BG_P4_5_NW230-2_2322_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 99.8 | 104.04 | AA1-102 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 99.8 | 104.04 | AA1-102 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 99.8 | 104.04 | AA1-102 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 101.87 | 103.97 | AA1-102 | BG_P4_5_NW2371_2310_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 101.87 | 103.97 | AA1-102 | BG_P4_5_NW230-3_2310_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208131 | WHEM | 208133 | WHEM TR2 | 1 | 230 | 229 | 691 | 97.07 | 103.15 | AA1-102 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 101 | 103.03 | AA1-102 | BG_P4_5_CNSTN_14_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220965 | NEAST339 | 220977 | RIV2339 | 1 | 230 | 232 | 991 | 104.45 | 102.99 | AA1-102 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220966 | RIV2317 | 220979 | NEAST317 | 1 | 230 | 232 | 940 | 104.02 | 102.96 | AA1-102 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220964 | GRACETON | 221000 | BAGLEY | 5 | 230 | 232 | 1795 | 102.14 | 102.94 | AA1-102 | BG_P1_2313_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220964 | GRACETON | 220999 | BAGLEY2 | 13 | 230 | 232 | 1795 | 102.14 | 102.94 | AA1-102 | BG_P1_2305_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220965 | NEAST339 | 220977 | RIV2339 | 1 | 230 | 232 | 991 | 104.4 | 102.94 | AA1-102 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220965 | NEAST339 | 220977 | RIV2339 | 1 | 230 | 232 | 991 | 104.4 | 102.94 | AA1-102 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220966 | RIV2317 | 220979 | NEAST317 | 1 | 230 | 232 | 940 | 103.97 | 102.9 | AA1-102 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220966 | RIV2317 | 220979 | NEAST317 | 1 | 230 | 232 | 940 | 103.97 | 102.9 | AA1-102 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220965 | NEAST339 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 103.5 | 102.9 | AA1-102 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 98.91 | 102.73 | AA1-102 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220972 | GRANITE1 | 1 | 230 | 232 | 829 | 103.92 | 102.69 | AA1-102 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 2 | 500/230 | 225/232 | 2168 | 99.56 | 102.36 | AA1-102 | PJM_500_BG_P2_CNSTN_230-N_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 2 | 500/230 | 225/232 | 2168 | 99.56 | 102.36 | AA1-102 | BG_P1_CNSTN_500-2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 1 | 500/230 | 225/232 | 2168 | 99.46 | 102.25 | AA1-102 | BG_P1_CNSTN_500-4_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 1 | 500/230 | 225/232 | 2168 | 99.46 | 102.25 | AA1-102 | PJM_500_BG_P2_CNSTN_230-S_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 223960 | BRG 1T 230 | 1 | 500/230 | 225/233 | 1498 | 101 | 101.42 | AA1-102 | PEPCO_P4_PP41_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 98.97 | 101.34 | AA1-102 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220979 | NEAST317 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 101.36 | 100.76 | AA1-102 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208021 | MANO TR4 | 1 | 230 | 229 | 600 | 90.23 | 100.68 | AA1-102 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220972 | GRANITE1 | 1 | 230 | 232 | 829 | 101.59 | 100.5 | AA1-102 | BG_P4_5_GRNITE26_32_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220973 | GRANITE6 | 1 | 230 | 232 | 829 | 101.42 | 100.06 | AA1-102 | BBG_P1_2311_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220972 | GRANITE1 | 1 | 230 | 232 | 829 | 101.11 | 100.01 | AA1-102 | BG_P1_2326_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 225.57 | 236.94 | AA1-139 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 223.56 | 236.94 | AA1-139 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 225.5 | 236.87 | AA1-139 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 223.5 | 236.87 | AA1-139 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 225.5 | 236.86 | AA1-139 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 223.5 | 236.86 | AA1-139 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 213.51 | 226.79 | AA1-139 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 213.45 | 226.72 | AA1-139 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 213.45 | 226.71 | AA1-139 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 209.25 | 223.58 | AA1-139 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 209.19 | 223.5 | AA1-139 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 209.19 | 223.5 | AA1-139 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 208.66 | 217.76 | AA1-139 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 210.67 | 217.76 | AA1-139 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 199.12 | 208.2 | AA1-139 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 194.87 | 204.85 | AA1-139 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 172.73 | 167.75 | AA1-139 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 163.6 | 164.87 | AA1-139 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204538 | 27STRABAN | 204544 | 27LINCOLN | 1 | 115 | 227 | 291 | 151.7 | 153.24 | AG2-055 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 161.74 | 161.79 | AA1-139 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 161.74 | 161.79 | AA1-139 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 161.72 | 161.79 | AA1-139 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 153.5 | 157.94 | AA1-139 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162 | 157.13 | AA1-139 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162 | 157.12 | AA1-139 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 151.82 | 156.62 | AA1-139 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 161.48 | 154.26 | AA1-139 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 148.45 | 152.97 | AA1-139 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 903 | 144.23 | 152.08 | AA1-139 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 152.8 | 151.17 | AA1-139 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 155.58 | 150.43 | AA1-139 | PN_P1-2_PN-500-010T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 903 | 142.71 | 149.47 | AA1-139 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 903 | 142.71 | 149.46 | AA1-139 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 903 | 142.69 | 149.46 | AA1-139 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.3 | 149.36 | AA1-139 | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.23 | 149.29 | AA1-139 | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.92 | 148.1 | AA1-139 | AP_P2-3_PE-500-016_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.98 | 148.08 | AA1-139 | AP_P2-3_PE-500-015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.9 | 147.76 | AA1-139 | PJM_500_BG_P4_5_CNSTN_L_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.18 | 147.75 | AA1-139 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.98 | 147.56 | AA1-139 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.01 | 147.55 | AA1-139 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.74 | 147.35 | AA1-139 | PECO_P4_NOTTI85_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.68 | 147.34 | AA1-139 | PECO_P1-2_220-08_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.61 | 147.27 | AA1-139 | PECO_P4_COOPR125_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.09 | 147.23 | AA1-139 | AP_P1-2_WP-500-DRT17_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.09 | 147.23 | AA1-139 | AP_P1-2_PE-500-001_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.04 | 147.16 | AA1-139 | AP_P2-3_PE-500-018C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204538 | 27STRABAN | 204544 | 27LINCOLN | 1 | 115 | 227 | 291 | 142.12 | 143.15 | O66 NFTWR | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.71 | 144 | AA1-139 | PECO_P4_PEACH025_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.55 | 143.88 | AA1-139 | PECO_P1-2_PBTIE1_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 911 | 148.97 | 143.1 | AA1-139 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204502 | 27JACKSON | 204514 | 27TMI | 1 | 230 | 227 | 781 | 133.04 | 141.59 | AA1-139 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204502 | 27JACKSON | 204514 | 27TMI | 1 | 230 | 227 | 781 | 133.03 | 141.59 | AA1-139 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204502 | 27JACKSON | 204514 | 27TMI | 1 | 230 | 227 | 781 | 133.04 | 141.59 | AA1-139 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 903 | 135.63 | 139.6 | AA1-139 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 1031 | 130.31 | 138.07 | AA1-139 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 1031 | 130.32 | 138.07 | AA1-139 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 1031 | 130.32 | 138.07 | AA1-139 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 138.95 | 133.01 | AA1-139 | PECO_P4_PEACH205_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 138.83 | 132.69 | AA1-139 | PECO_P1-2_PBTIE2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208078 | SAKR | 1 | 230 | 229 | 903 | 124.5 | 132.5 | AA1-139 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208078 | SAKR | 1 | 230 | 229 | 903 | 124.5 | 132.5 | AA1-139 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208078 | SAKR | 1 | 230 | 229 | 903 | 124.5 | 132.49 | AA1-139 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 137.9 | 131.82 | AA1-139 | PECO_P4_PEACH055_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 1031 | 124.72 | 129.26 | AA1-139 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 133.19 | 127.38 | AA1-139 | PECO_P4_PEACH015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 128.43 | 126.73 | AA1-139 | DVP_P4-2: 514T595_SRT-SW |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 131.89 | 126.07 | AA1-139 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 126.68 | 124.95 | AA1-139 | DVP_P4-2: 51482_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 2 | 230 | 233 | 793 | 126.59 | 124.86 | AA1-139 | DVP_P4-2: 514T595_SRT-SW |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 793 | 126.59 | 124.86 | AA1-139 | DVP_P4-2: 514T595_SRT-SW |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 126.68 | 124.86 | AA1-139 | AP_P1-2_PE-500-407T_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 126.68 | 124.86 | AA1-139 | DVP_P1-2: LN 514_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208020 | MANO TR3 | 1 | 230 | 229 | 793 | 111.49 | 124.68 | AA1-139 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208020 | MANO TR3 | 1 | 230 | 229 | 793 | 111.49 | 124.67 | AA1-139 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208020 | MANO TR3 | 1 | 230 | 229 | 793 | 111.49 | 124.67 | AA1-139 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 2 | 230 | 233 | 793 | 125.34 | 123.61 | AA1-139 | DVP_P4-2: 51482_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 793 | 125.34 | 123.61 | AA1-139 | DVP_P4-2: 51482_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 793 | 125.34 | 123.53 | AA1-139 | AP_P1-2_PE-500-407T_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 793 | 125.34 | 123.53 | AA1-139 | DVP_P1-2: LN 514_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 2 | 230 | 233 | 793 | 125.34 | 123.53 | AA1-139 | AP_P1-2_PE-500-407T_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 2 | 230 | 233 | 793 | 125.34 | 123.53 | AA1-139 | DVP_P1-2: LN 514_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208078 | SAKR | 1 | 230 | 229 | 903 | 117.23 | 122.51 | AA1-139 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200025 | W CHAPEL | 1 | 500 | 225 | 1732 | 123.64 | 121.85 | AA1-139 | PEPCO_P4_PP41_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208031 | MLWD TR2 | 1 | 230 | 229 | 911 | 111.79 | 121.24 | AA1-139 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208031 | MLWD TR2 | 1 | 230 | 229 | 911 | 111.79 | 121.24 | AA1-139 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208031 | MLWD TR2 | 1 | 230 | 229 | 911 | 111.79 | 121.23 | AA1-139 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 114.71 | 118.41 | AA1-139 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 114.37 | 118.07 | AA1-139 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 122.79 | 117.42 | AA1-139 | PECO_P4_PEACH225_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 2 | 500/230 | 225/232 | 2168 | 109.66 | 114.97 | AA1-139 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 116.88 | 114.95 | AA1-139 | AP_P2-3_PE-500-019C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 2 | 500/230 | 225/232 | 2168 | 109.48 | 114.76 | AA1-139 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 2 | 500/230 | 225/232 | 2168 | 109.48 | 114.76 | AA1-139 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 1 | 500/230 | 225/232 | 2168 | 109.43 | 114.73 | AA1-139 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 1 | 500/230 | 225/232 | 2168 | 109.25 | 114.51 | AA1-139 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 1 | 500/230 | 225/232 | 2168 | 109.25 | 114.51 | AA1-139 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208031 | MLWD TR2 | 1 | 230 | 229 | 911 | 105.04 | 111.74 | AA1-139 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 793 | 112.81 | 110.19 | AA1-139 | PEPCO_P4_PP19_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 793 | 109.56 | 107.66 | AA1-139 | AP_P2-3_PE-500-019C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 2 | 230 | 233 | 793 | 109.56 | 107.66 | AA1-139 | AP_P2-3_PE-500-019C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 99.5 | 103.41 | AA1-139 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 99.5 | 103.41 | AA1-139 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 99.5 | 103.41 | AA1-139 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 98.58 | 102.08 | AA1-139 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 98.67 | 100.71 | AA1-139 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 203981 | AD2-062_POI | 235188 | 01GREENE | 1 | 138 | 226/201 | 250 | 127.67 | 127.12 | AC1-158 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 153.67 | 158.15 | AA2-053 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.17 | 157.29 | AA2-053 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.17 | 157.29 | AA2-053 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 151.99 | 156.83 | AA2-053 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 161.66 | 154.44 | AA2-053 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 148.63 | 153.18 | AA2-053 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 155.74 | 150.59 | AA2-053 | PN_P1-2_PN-500-010T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.46 | 149.56 | AA2-053 | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.39 | 149.49 | AA2-053 | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.08 | 148.31 | AA2-053 | AP_P2-3_PE-500-016_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.15 | 148.29 | AA2-053 | AP_P2-3_PE-500-015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.05 | 147.92 | AA2-053 | PJM_500_BG_P4_5_CNSTN_L_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.34 | 147.91 | AA2-053 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.14 | 147.72 | AA2-053 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.17 | 147.71 | AA2-053 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.9 | 147.51 | AA2-053 | PECO_P4_NOTTI85_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.84 | 147.49 | AA2-053 | PECO_P1-2_220-08_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.26 | 147.44 | AA2-053 | AP_P1-2_WP-500-DRT17_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.26 | 147.44 | AA2-053 | AP_P1-2_PE-500-001_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.77 | 147.43 | AA2-053 | PECO_P4_COOPR125_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.21 | 147.37 | AA2-053 | AP_P2-3_PE-500-018C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 203981 | AD2-062_POI | 235188 | 01GREENE | 1 | 138 | 226/201 | 250 | 127.7 | 127.1 | AD2-009 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.88 | 144.17 | AA2-053 | PECO_P4_PEACH025_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.74 | 144.07 | AA2-053 | PECO_P1-2_PBTIE1_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 139.12 | 133.18 | AA2-053 | PECO_P4_PEACH205_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 139.01 | 132.86 | AA2-053 | PECO_P1-2_PBTIE2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 138.07 | 131.98 | AA2-053 | PECO_P4_PEACH055_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 133.38 | 127.56 | AA2-053 | PECO_P4_PEACH015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 128.78 | 127.04 | AA2-053 | DVP_P4-2: 514T595_SRT-SW |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 132.06 | 126.24 | AA2-053 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 127.03 | 125.32 | AA2-053 | DVP_P4-2: 51482_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 127.03 | 125.23 | AA2-053 | DVP_P1-2: LN 514_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 127.03 | 125.23 | AA2-053 | AP_P1-2_PE-500-407T_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 122.96 | 117.59 | AA2-053 | PECO_P4_PEACH225_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 117.23 | 115.31 | AA2-053 | AP_P2-3_PE-500-019C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 203981 | AD2-062_POI | 235188 | 01GREENE | 1 | 138 | 226/201 | 250 | 150.64 | 150.09 | AD2-062 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 153.71 | 158.2 | AA2-057 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.2 | 157.32 | AA2-057 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.2 | 157.32 | AA2-057 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 152.02 | 156.87 | AA2-057 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 161.7 | 154.47 | AA2-057 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 148.66 | 153.22 | AA2-057 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 155.77 | 150.62 | AA2-057 | PN_P1-2_PN-500-010T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.5 | 149.6 | AA2-057 | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.43 | 149.53 | AA2-057 | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.12 | 148.36 | AA2-057 | AP_P2-3_PE-500-016_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.18 | 148.33 | AA2-057 | AP_P2-3_PE-500-015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.09 | 147.95 | AA2-057 | PJM_500_BG_P4_5_CNSTN_L_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.38 | 147.94 | AA2-057 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.17 | 147.75 | AA2-057 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.2 | 147.74 | AA2-057 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.93 | 147.54 | AA2-057 | PECO_P4_NOTTI85_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.87 | 147.53 | AA2-057 | PECO_P1-2_220-08_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.3 | 147.48 | AA2-057 | AP_P1-2_WP-500-DRT17_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.3 | 147.48 | AA2-057 | AP_P1-2_PE-500-001_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.8 | 147.46 | AA2-057 | PECO_P4_COOPR125_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.25 | 147.41 | AA2-057 | AP_P2-3_PE-500-018C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 203981 | AD2-062_POI | 235188 | 01GREENE | 1 | 138 | 226/201 | 250 | 146.75 | 146.21 | AE1-071 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.92 | 144.21 | AA2-057 | PECO_P4_PEACH025_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.78 | 144.11 | AA2-057 | PECO_P1-2_PBTIE1_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 139.16 | 133.22 | AA2-057 | PECO_P4_PEACH205_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 139.05 | 132.89 | AA2-057 | PECO_P1-2_PBTIE2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 138.1 | 132.02 | AA2-057 | PECO_P4_PEACH055_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 133.42 | 127.6 | AA2-057 | PECO_P4_PEACH015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 128.85 | 127.12 | AA2-057 | DVP_P4-2: 514T595_SRT-SW |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 132.1 | 126.27 | AA2-057 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 127.11 | 125.4 | AA2-057 | DVP_P4-2: 51482_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 127.11 | 125.31 | AA2-057 | DVP_P1-2: LN 514_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 127.11 | 125.31 | AA2-057 | AP_P1-2_PE-500-407T_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 123 | 117.63 | AA2-057 | PECO_P4_PEACH225_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 117.3 | 115.39 | AA2-057 | AP_P2-3_PE-500-019C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.77 | 148.33 | AA2-082 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.57 | 148.14 | AA2-082 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.6 | 148.13 | AA2-082 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.32 | 147.93 | AA2-082 | PECO_P4_NOTTI85_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.26 | 147.91 | AA2-082 | PECO_P1-2_220-08_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.2 | 147.85 | AA2-082 | PECO_P4_COOPR125_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.86 | 147.66 | AA2-082 | PECO_P1-2_220-93_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 151.08 | 146.11 | AA2-082 | PL_05_P71_000906_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 144.59 | 139.44 | AA2-082 | PL_10_P42_100570_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 144.59 | 139.44 | AA2-082 | PL_10_P42_100570_A_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 225.7 | 237.17 | AA2-088 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 223.7 | 237.17 | AA2-088 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 225.64 | 237.11 | AA2-088 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 223.63 | 237.11 | AA2-088 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 225.64 | 237.11 | AA2-088 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 223.63 | 237.11 | AA2-088 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 213.64 | 227.01 | AA2-088 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 213.58 | 226.95 | AA2-088 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 213.58 | 226.95 | AA2-088 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 209.38 | 223.8 | AA2-088 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 209.32 | 223.74 | AA2-088 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 209.32 | 223.74 | AA2-088 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 210.8 | 217.96 | AA2-088 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 199.25 | 208.39 | AA2-088 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 194.99 | 205.04 | AA2-088 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 172.83 | 167.86 | AA2-088 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 163.7 | 165.03 | AA2-088 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 203981 | AD2-062_POI | 235188 | 01GREENE | 1 | 138 | 226/201 | 250 | 123.53 | 122.94 | AE1-101 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 161.84 | 161.93 | AA2-088 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 161.84 | 161.93 | AA2-088 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 161.83 | 161.93 | AA2-088 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 153.6 | 158.06 | AA2-088 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.09 | 157.22 | AA2-088 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.09 | 157.22 | AA2-088 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 151.91 | 156.74 | AA2-088 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 161.58 | 154.36 | AA2-088 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 148.55 | 153.09 | AA2-088 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 155.67 | 150.52 | AA2-088 | PN_P1-2_PN-500-010T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 903 | 142.78 | 149.62 | AA2-088 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.39 | 149.47 | AA2-088 | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.32 | 149.4 | AA2-088 | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.01 | 148.22 | AA2-088 | AP_P2-3_PE-500-016_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.07 | 148.19 | AA2-088 | AP_P2-3_PE-500-015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.98 | 147.85 | AA2-088 | PJM_500_BG_P4_5_CNSTN_L_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.27 | 147.83 | AA2-088 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.07 | 147.65 | AA2-088 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.1 | 147.63 | AA2-088 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.83 | 147.44 | AA2-088 | PECO_P4_NOTTI85_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.77 | 147.42 | AA2-088 | PECO_P1-2_220-08_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.7 | 147.36 | AA2-088 | PECO_P4_COOPR125_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.19 | 147.34 | AA2-088 | AP_P1-2_PE-500-001_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.19 | 147.34 | AA2-088 | AP_P1-2_WP-500-DRT17_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.14 | 147.27 | AA2-088 | AP_P2-3_PE-500-018C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 203981 | AD2-062_POI | 235188 | 01GREENE | 1 | 138 | 226/201 | 250 | 135.19 | 134.61 | AG2-055 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.8 | 144.1 | AA2-088 | PECO_P4_PEACH025_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.65 | 143.98 | AA2-088 | PECO_P1-2_PBTIE1_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 911 | 149.07 | 143.19 | AA2-088 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 1031 | 130.38 | 138.2 | AA2-088 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 139.04 | 133.11 | AA2-088 | PECO_P4_PEACH205_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 138.93 | 132.78 | AA2-088 | PECO_P1-2_PBTIE2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 138 | 131.91 | AA2-088 | PECO_P4_PEACH055_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 133.3 | 127.48 | AA2-088 | PECO_P4_PEACH015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 128.63 | 126.94 | AA2-088 | DVP_P4-2: 514T595_SRT-SW |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 131.98 | 126.17 | AA2-088 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 126.88 | 125.16 | AA2-088 | DVP_P4-2: 51482_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 126.88 | 125.07 | AA2-088 | AP_P1-2_PE-500-407T_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 126.88 | 125.07 | AA2-088 | DVP_P1-2: LN 514_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208020 | MANO TR3 | 1 | 230 | 229 | 793 | 111.57 | 124.76 | AA2-088 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208020 | MANO TR3 | 1 | 230 | 229 | 793 | 111.57 | 124.76 | AA2-088 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208020 | MANO TR3 | 1 | 230 | 229 | 793 | 111.57 | 124.76 | AA2-088 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200025 | W CHAPEL | 1 | 500 | 225 | 1732 | 123.73 | 121.95 | AA2-088 | PEPCO_P4_PP41_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 122.89 | 117.52 | AA2-088 | PECO_P4_PEACH225_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 117.08 | 115.16 | AA2-088 | AP_P2-3_PE-500-019C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 2 | 500/230 | 225/232 | 2168 | 109.71 | 115.03 | AA2-088 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 2 | 500/230 | 225/232 | 2168 | 109.54 | 114.82 | AA2-088 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 2 | 500/230 | 225/232 | 2168 | 109.54 | 114.82 | AA2-088 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 1 | 500/230 | 225/232 | 2168 | 109.48 | 114.79 | AA2-088 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 1 | 500/230 | 225/232 | 2168 | 109.31 | 114.58 | AA2-088 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 1 | 500/230 | 225/232 | 2168 | 109.3 | 114.58 | AA2-088 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 99.56 | 103.5 | AA2-088 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 99.55 | 103.5 | AA2-088 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 99.55 | 103.5 | AA2-088 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 98.63 | 102.17 | AA2-088 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 98.73 | 100.79 | AA2-088 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 203981 | AD2-062_POI | 235188 | 01GREENE | 1 | 138 | 226/201 | 250 | 127.53 | 126.98 | O66 NFTWR | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 153.67 | 158.15 | AA2-178 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.17 | 157.29 | AA2-178 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.17 | 157.29 | AA2-178 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 151.98 | 156.83 | AA2-178 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 161.66 | 154.44 | AA2-178 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 148.62 | 153.18 | AA2-178 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 155.74 | 150.59 | AA2-178 | PN_P1-2_PN-500-010T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.46 | 149.56 | AA2-178 | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.39 | 149.49 | AA2-178 | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.08 | 148.31 | AA2-178 | AP_P2-3_PE-500-016_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.14 | 148.28 | AA2-178 | AP_P2-3_PE-500-015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.05 | 147.92 | AA2-178 | PJM_500_BG_P4_5_CNSTN_L_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.34 | 147.91 | AA2-178 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.14 | 147.72 | AA2-178 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.17 | 147.71 | AA2-178 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.9 | 147.51 | AA2-178 | PECO_P4_NOTTI85_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.84 | 147.49 | AA2-178 | PECO_P1-2_220-08_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.77 | 147.43 | AA2-178 | PECO_P4_COOPR125_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.26 | 147.43 | AA2-178 | AP_P1-2_PE-500-001_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.26 | 147.43 | AA2-178 | AP_P1-2_WP-500-DRT17_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.21 | 147.36 | AA2-178 | AP_P2-3_PE-500-018C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 203981 | AD2-062_POI | 235188 | 01GREENE | 1 | 138 | 226/201 | 250 | 134 | 133.42 | W1-045 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.89 | 144.18 | AA2-178 | PECO_P4_PEACH025_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.74 | 144.07 | AA2-178 | PECO_P1-2_PBTIE1_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 139.12 | 133.18 | AA2-178 | PECO_P4_PEACH205_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 139.01 | 132.86 | AA2-178 | PECO_P1-2_PBTIE2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 138.07 | 131.98 | AA2-178 | PECO_P4_PEACH055_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 133.38 | 127.56 | AA2-178 | PECO_P4_PEACH015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 128.76 | 127.02 | AA2-178 | DVP_P4-2: 514T595_SRT-SW |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 132.06 | 126.24 | AA2-178 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 127.01 | 125.3 | AA2-178 | DVP_P4-2: 51482_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 127.01 | 125.2 | AA2-178 | DVP_P1-2: LN 514_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 127.01 | 125.2 | AA2-178 | AP_P1-2_PE-500-407T_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 122.96 | 117.59 | AA2-178 | PECO_P4_PEACH225_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 117.21 | 115.29 | AA2-178 | AP_P2-3_PE-500-019C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2901 | 144.51 | 146.59 | 01GRNGAP | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 162.17 | 154.93 | AA2-184 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.78 | 148.34 | AA2-184 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.58 | 148.15 | AA2-184 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.61 | 148.14 | AA2-184 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.34 | 147.94 | AA2-184 | PECO_P4_NOTTI85_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.28 | 147.93 | AA2-184 | PECO_P1-2_220-08_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.21 | 147.86 | AA2-184 | PECO_P4_COOPR125_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.05 | 147.71 | AA2-184 | AP_P2-3_PE-500-016_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.08 | 147.7 | AA2-184 | AP_P2-3_PE-500-015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.87 | 147.67 | AA2-184 | PECO_P1-2_220-93_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 151.57 | 147.24 | AA2-184 | AP_P1-2_WP-500-DRT17_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 151.41 | 144.68 | AA2-184 | PECO_P4_PEACH025_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 151.28 | 144.59 | AA2-184 | PECO_P1-2_PBTIE1_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 139.51 | 133.34 | AA2-184 | PECO_P1-2_PBTIE2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 133.92 | 128.08 | AA2-184 | PECO_P4_PEACH015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 123.45 | 118.06 | AA2-184 | PECO_P4_PEACH225_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2901 | 144.87 | 147.01 | 05CELAN | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 153.74 | 158.24 | AB1-006 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.21 | 157.33 | AB1-006 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.21 | 157.33 | AB1-006 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 152.06 | 156.92 | AB1-006 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 161.67 | 154.45 | AB1-006 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 148.69 | 153.27 | AB1-006 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 155.78 | 150.63 | AB1-006 | PN_P1-2_PN-500-010T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.53 | 149.64 | AB1-006 | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.46 | 149.57 | AB1-006 | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.17 | 148.45 | AB1-006 | AP_P2-3_PE-500-016_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.24 | 148.42 | AB1-006 | AP_P2-3_PE-500-015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.09 | 147.97 | AB1-006 | PJM_500_BG_P4_5_CNSTN_L_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.34 | 147.91 | AB1-006 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.14 | 147.72 | AB1-006 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.17 | 147.71 | AB1-006 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.35 | 147.56 | AB1-006 | AP_P1-2_WP-500-DRT17_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.35 | 147.56 | AB1-006 | AP_P1-2_PE-500-001_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.9 | 147.51 | AB1-006 | PECO_P4_NOTTI85_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.84 | 147.5 | AB1-006 | PECO_P1-2_220-08_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.3 | 147.49 | AB1-006 | AP_P2-3_PE-500-018C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.77 | 147.43 | AB1-006 | PECO_P4_COOPR125_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2901 | 144.71 | 146.82 | 08HLCRTG | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.87 | 144.16 | AB1-006 | PECO_P4_PEACH025_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.75 | 144.08 | AB1-006 | PECO_P1-2_PBTIE1_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 139.14 | 133.2 | AB1-006 | PECO_P4_PEACH205_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 139.02 | 132.87 | AB1-006 | PECO_P1-2_PBTIE2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 138.08 | 131.99 | AB1-006 | PECO_P4_PEACH055_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 133.4 | 127.58 | AB1-006 | PECO_P4_PEACH015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 132.07 | 126.25 | AB1-006 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 122.98 | 117.61 | AB1-006 | PECO_P4_PEACH225_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 229.18 | 241.96 | AB1-056 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 227.12 | 241.96 | AB1-056 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 228.27 | 239.84 | AB1-056 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 226.21 | 239.84 | AB1-056 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 228.21 | 239.8 | AB1-056 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 226.14 | 239.8 | AB1-056 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 228.2 | 239.8 | AB1-056 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 226.14 | 239.8 | AB1-056 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 216.95 | 231.65 | AB1-056 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 216.07 | 229.59 | AB1-056 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 216 | 229.55 | AB1-056 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 216 | 229.55 | AB1-056 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 212.69 | 228.48 | AB1-056 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 211.8 | 226.4 | AB1-056 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 211.74 | 226.37 | AB1-056 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 211.74 | 226.36 | AB1-056 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 213.37 | 221.22 | AB1-056 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 211.31 | 221.22 | AB1-056 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 201.68 | 211.55 | AB1-056 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 197.42 | 208.22 | AB1-056 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 173.95 | 169.25 | AB1-056 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 172.99 | 167.84 | AB1-056 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 173.01 | 167.83 | AB1-056 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 173.01 | 167.83 | AB1-056 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 164.94 | 166.74 | AB1-056 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2901 | 145.25 | 147.46 | 09GRNVIL | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 163.12 | 163.68 | AB1-056 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 163.14 | 163.68 | AB1-056 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 163.13 | 163.67 | AB1-056 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 165.06 | 160.14 | AB1-056 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 154.75 | 159.44 | AB1-056 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 163.42 | 158.53 | AB1-056 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 163.41 | 158.53 | AB1-056 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 153.05 | 158.11 | AB1-056 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 163.39 | 156.09 | AB1-056 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 149.69 | 154.46 | AB1-056 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 903 | 145.27 | 153.7 | AB1-056 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 154.2 | 152.88 | AB1-056 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 157.01 | 151.84 | AB1-056 | PN_P1-2_PN-500-010T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 903 | 143.79 | 151.06 | AB1-056 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 903 | 143.79 | 151.05 | AB1-056 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 903 | 143.78 | 151.03 | AB1-056 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 147.5 | 150.78 | AB1-056 | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 147.43 | 150.71 | AB1-056 | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 145.04 | 149.46 | AB1-056 | AP_P2-3_PE-500-016_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 145.11 | 149.43 | AB1-056 | AP_P2-3_PE-500-015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 154.82 | 149.35 | AB1-056 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 154.62 | 149.17 | AB1-056 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 154.65 | 149.15 | AB1-056 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 154.25 | 149.1 | AB1-056 | PJM_500_BG_P4_5_CNSTN_L_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 154.37 | 148.96 | AB1-056 | PECO_P4_NOTTI85_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 154.31 | 148.94 | AB1-056 | PECO_P1-2_220-08_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 154.24 | 148.87 | AB1-056 | PECO_P4_COOPR125_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.22 | 148.58 | AB1-056 | AP_P1-2_WP-500-DRT17_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.22 | 148.58 | AB1-056 | AP_P1-2_PE-500-001_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.17 | 148.51 | AB1-056 | AP_P2-3_PE-500-018C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2901 | 144.89 | 147.03 | 1DOMTR10 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 152.97 | 146.17 | AB1-056 | PECO_P4_PEACH025_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 152.62 | 145.88 | AB1-056 | PECO_P1-2_PBTIE1_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 911 | 150.16 | 144.49 | AB1-056 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 911 | 149.23 | 143.21 | AB1-056 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 911 | 149.25 | 143.2 | AB1-056 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 911 | 149.25 | 143.2 | AB1-056 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204502 | 27JACKSON | 204514 | 27TMI | 1 | 230 | 227 | 781 | 133.93 | 143.1 | AB1-056 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204502 | 27JACKSON | 204514 | 27TMI | 1 | 230 | 227 | 781 | 134.12 | 143.04 | AB1-056 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204502 | 27JACKSON | 204514 | 27TMI | 1 | 230 | 227 | 781 | 134.12 | 143.04 | AB1-056 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204502 | 27JACKSON | 204514 | 27TMI | 1 | 230 | 227 | 781 | 134.11 | 143.02 | AB1-056 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 903 | 136.72 | 141.12 | AB1-056 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 1031 | 131.68 | 140.49 | AB1-056 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 1031 | 131.2 | 139.39 | AB1-056 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 1031 | 131.2 | 139.39 | AB1-056 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 1031 | 131.19 | 139.37 | AB1-056 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 911 | 141.38 | 136.21 | AB1-056 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 207923 | BRISREAC | 208132 | WHEM TR1 | 1 | 230 | 229 | 676 | 125.81 | 135.63 | AB1-056 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 207922 | BRIS | 207923 | BRISREAC | RX | 230 | 229 | 676 | 125.81 | 135.63 | AB1-056 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208078 | SAKR | 1 | 230 | 229 | 903 | 126.37 | 135.42 | AB1-056 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 140.75 | 134.52 | AB1-056 | PECO_P1-2_PBTIE2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 140.48 | 134.49 | AB1-056 | PECO_P4_PEACH205_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208078 | SAKR | 1 | 230 | 229 | 903 | 125.65 | 133.98 | AB1-056 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208078 | SAKR | 1 | 230 | 229 | 903 | 125.65 | 133.97 | AB1-056 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208078 | SAKR | 1 | 230 | 229 | 903 | 125.65 | 133.96 | AB1-056 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 139.78 | 133.62 | AB1-056 | PECO_P4_PEACH055_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204502 | 27JACKSON | 204514 | 27TMI | 1 | 230 | 227 | 781 | 126.48 | 132.58 | AB1-056 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220972 | GRANITE1 | 1 | 230 | 232 | 829 | 136.08 | 132.08 | AB1-056 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220972 | GRANITE1 | 1 | 230 | 232 | 829 | 135.45 | 131.43 | AB1-056 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220972 | GRANITE1 | 1 | 230 | 232 | 829 | 135.45 | 131.43 | AB1-056 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 1031 | 125.6 | 130.62 | AB1-056 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220973 | GRANITE6 | 1 | 230 | 232 | 829 | 133.98 | 130.16 | AB1-056 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220973 | GRANITE6 | 1 | 230 | 232 | 829 | 133.39 | 129.55 | AB1-056 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220973 | GRANITE6 | 1 | 230 | 232 | 829 | 133.39 | 129.55 | AB1-056 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 135.27 | 129.38 | AB1-056 | PECO_P4_PEACH015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 128.64 | 129 | AB1-056 | BG_P7_GRCTN_CNSTN_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 126.58 | 129 | AB1-056 | BG_P7_GRCTN_CNSTN_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 129.9 | 128.16 | AB1-056 | DVP_P4-2: 514T595_SRT-SW |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 133.78 | 127.88 | AB1-056 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208020 | MANO TR3 | 1 | 230 | 229 | 793 | 113.43 | 127.79 | AB1-056 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220953 | HOWARD12 | 220972 | GRANITE1 | 1 | 230 | 232 | 772 | 131.04 | 127.03 | AB1-056 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 128.18 | 126.47 | AB1-056 | DVP_P4-2: 51482_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 128.18 | 126.38 | AB1-056 | AP_P1-2_PE-500-407T_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 128.18 | 126.38 | AB1-056 | DVP_P1-2: LN 514_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220954 | HOWARD32 | 220973 | GRANITE6 | 1 | 230 | 232 | 772 | 129.82 | 126.26 | AB1-056 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208020 | MANO TR3 | 1 | 230 | 229 | 793 | 112.63 | 126.13 | AB1-056 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208020 | MANO TR3 | 1 | 230 | 229 | 793 | 112.63 | 126.13 | AB1-056 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208020 | MANO TR3 | 1 | 230 | 229 | 793 | 112.62 | 126.13 | AB1-056 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220953 | HOWARD12 | 220972 | GRANITE1 | 1 | 230 | 232 | 772 | 130.14 | 126.07 | AB1-056 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220953 | HOWARD12 | 220972 | GRANITE1 | 1 | 230 | 232 | 772 | 130.14 | 126.07 | AB1-056 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220954 | HOWARD32 | 220973 | GRANITE6 | 1 | 230 | 232 | 772 | 129.03 | 125.43 | AB1-056 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220954 | HOWARD32 | 220973 | GRANITE6 | 1 | 230 | 232 | 772 | 129.03 | 125.43 | AB1-056 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 119.48 | 124.42 | AB1-056 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 121.54 | 124.42 | AB1-056 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 121.36 | 124.21 | AB1-056 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 119.3 | 124.21 | AB1-056 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 119.3 | 124.21 | AB1-056 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 121.36 | 124.21 | AB1-056 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208078 | SAKR | 1 | 230 | 229 | 903 | 118.39 | 124.16 | AB1-056 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208031 | MLWD TR2 | 1 | 230 | 229 | 911 | 113.55 | 124.01 | AB1-056 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204512 | 27S.RDG | 204693 | 27BOONETOWN | 1 | 230 | 227 | 607 | 108.17 | 123.65 | AB1-056 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200025 | W CHAPEL | 1 | 500 | 225 | 1732 | 124.74 | 122.99 | AB1-056 | PEPCO_P4_PP41_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208031 | MLWD TR2 | 1 | 230 | 229 | 911 | 112.86 | 122.54 | AB1-056 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208031 | MLWD TR2 | 1 | 230 | 229 | 911 | 112.86 | 122.54 | AB1-056 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208031 | MLWD TR2 | 1 | 230 | 229 | 911 | 112.85 | 122.54 | AB1-056 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 119.87 | 122.28 | AB1-056 | BG_P7_GRCTN_CNSTN_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 120.58 | 121.22 | AB1-056 | PJM_500_BG_P4_5_CNSTN_15_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 118.52 | 121.22 | AB1-056 | PJM_500_BG_P4_5_CNSTN_15_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208131 | WHEM | 208132 | WHEM TR1 | 1 | 230 | 229 | 691 | 110.01 | 120.25 | AB1-056 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220965 | NEAST339 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 120.62 | 119.99 | AB1-056 | BG_P1_2315_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220965 | NEAST339 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 120.19 | 119.77 | AB1-056 | BG_P4_5_NEAST_17_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220965 | NEAST339 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 120.35 | 119.77 | AB1-056 | BG_P4_5_NEAST_15_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 115.5 | 119.3 | AB1-056 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 124.71 | 119.26 | AB1-056 | PECO_P4_PEACH225_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2901 | 144.92 | 147.07 | 1DOMTR9 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2901 | 144.87 | 147.01 | 1EDGECMA | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220979 | NEAST317 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 119.69 | 119.11 | AB1-056 | BG_P1_2337_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 115.16 | 118.96 | AB1-056 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 115.15 | 118.9 | AB1-056 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 115.15 | 118.9 | AB1-056 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220979 | NEAST317 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 119.35 | 118.83 | AB1-056 | BG_P4_5_NEAST_39_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220979 | NEAST317 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 119.35 | 118.83 | AB1-056 | BG_P4_5_NEAST_37_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 114.82 | 118.56 | AB1-056 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 114.82 | 118.56 | AB1-056 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 115.6 | 118.44 | AB1-056 | BG_P7_GRCTN_CNSTN_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 113.01 | 117.87 | AB1-056 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 112.84 | 117.66 | AB1-056 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 112.84 | 117.66 | AB1-056 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 118.36 | 116.44 | AB1-056 | AP_P2-3_PE-500-019C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2901 | 144.75 | 146.88 | 1HOLLOMANSOL | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 2 | 500/230 | 225/232 | 2168 | 110.37 | 115.77 | AB1-056 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208020 | MANO TR3 | 1 | 230 | 229 | 793 | 105.44 | 115.71 | AB1-056 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 2 | 500/230 | 225/232 | 2168 | 110.19 | 115.56 | AB1-056 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 2 | 500/230 | 225/232 | 2168 | 110.19 | 115.56 | AB1-056 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 1 | 500/230 | 225/232 | 2168 | 110.13 | 115.53 | AB1-056 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 1 | 500/230 | 225/232 | 2168 | 109.96 | 115.32 | AB1-056 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 1 | 500/230 | 225/232 | 2168 | 109.96 | 115.32 | AB1-056 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208020 | MANO TR3 | 208031 | MLWD TR2 | 1 | 230 | 229 | 903 | 103.59 | 115.27 | AB1-056 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220964 | GRACETON | 220999 | BAGLEY2 | 13 | 230 | 232 | 1795 | 114.1 | 115.19 | AB1-056 | BG_P4_5_GRCTN_3T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 112.09 | 114.83 | AB1-056 | PJM_500_BG_P4_5_CNSTN_15_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 108.75 | 114.05 | AB1-056 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 108.57 | 113.84 | AB1-056 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 108.57 | 113.84 | AB1-056 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208020 | MANO TR3 | 208031 | MLWD TR2 | 1 | 230 | 229 | 903 | 102.91 | 113.74 | AB1-056 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208020 | MANO TR3 | 208031 | MLWD TR2 | 1 | 230 | 229 | 903 | 102.91 | 113.74 | AB1-056 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208020 | MANO TR3 | 208031 | MLWD TR2 | 1 | 230 | 229 | 903 | 102.91 | 113.74 | AB1-056 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208031 | MLWD TR2 | 1 | 230 | 229 | 911 | 106.1 | 113.28 | AB1-056 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 2 | 500/230 | 225/232 | 2168 | 109.08 | 112.43 | AB1-056 | PJM_500_BG_P4_5_CNSTN_15_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 107.14 | 112.08 | AB1-056 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 107.01 | 111.95 | AB1-056 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220980 | RAPHAEL | 220999 | BAGLEY2 | 13 | 230 | 232 | 1795 | 109.67 | 111.95 | AB1-056 | BG_P4_5_GRCTN_3T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2901 | 144.93 | 147.08 | 1STONECA | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208131 | WHEM | 208133 | WHEM TR2 | 1 | 230 | 229 | 691 | 102.49 | 111.63 | AB1-056 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 107.82 | 111.13 | AB1-056 | PJM_500_BG_P4_5_CNSTN_15_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220965 | NEAST339 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 109.15 | 107.72 | AB1-056 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220965 | NEAST339 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 109.05 | 107.61 | AB1-056 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220965 | NEAST339 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 109.05 | 107.61 | AB1-056 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 102.25 | 106.53 | AB1-056 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 102.17 | 106.44 | AB1-056 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208021 | MANO TR4 | 208133 | WHEM TR2 | 2 | 230 | 229 | 593 | 97.11 | 106.41 | AB1-056 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200099 | LAUS | 208045 | LAUS | 3 | 500/230 | 225/229 | 1200 | 104.07 | 105.86 | AB1-056 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 103.35 | 105.43 | AB1-056 | BG_P1_2322_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200099 | LAUS | 208045 | LAUS | 3 | 500/230 | 225/229 | 1200 | 103.77 | 105.37 | AB1-056 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200099 | LAUS | 208045 | LAUS | 3 | 500/230 | 225/229 | 1200 | 103.77 | 105.37 | AB1-056 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200099 | LAUS | 208045 | LAUS | 3 | 500/230 | 225/229 | 1200 | 103.76 | 105.35 | AB1-056 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 103.28 | 105.35 | AB1-056 | BG_P1_2310_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 103.29 | 105.32 | AB1-056 | BG_P4_5_NW2322_230-4_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 103.22 | 105.28 | AB1-056 | BG_P4_5_NW2310_230-5_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208020 | MANO TR3 | 208031 | MLWD TR2 | 1 | 230 | 229 | 903 | 96.54 | 104.82 | AB1-056 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220979 | NEAST317 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 106 | 104.63 | AB1-056 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220979 | NEAST317 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 105.9 | 104.52 | AB1-056 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220979 | NEAST317 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 105.9 | 104.52 | AB1-056 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 101.93 | 104.04 | AB1-056 | BG_P4_5_NW230-2_2322_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 99.79 | 104 | AB1-056 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 99.79 | 104 | AB1-056 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 99.79 | 104 | AB1-056 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 101.83 | 103.93 | AB1-056 | BG_P4_5_NW2371_2310_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 101.82 | 103.92 | AB1-056 | BG_P4_5_NW230-3_2310_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 100.95 | 102.99 | AB1-056 | BG_P4_5_CNSTN_14_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220965 | NEAST339 | 220977 | RIV2339 | 1 | 230 | 232 | 991 | 104.38 | 102.93 | AB1-056 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220966 | RIV2317 | 220979 | NEAST317 | 1 | 230 | 232 | 940 | 103.95 | 102.9 | AB1-056 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220964 | GRACETON | 220999 | BAGLEY2 | 13 | 230 | 232 | 1795 | 102.1 | 102.9 | AB1-056 | BG_P1_2305_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220964 | GRACETON | 221000 | BAGLEY | 5 | 230 | 232 | 1795 | 102.1 | 102.9 | AB1-056 | BG_P1_2313_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220965 | NEAST339 | 220977 | RIV2339 | 1 | 230 | 232 | 991 | 104.34 | 102.87 | AB1-056 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220965 | NEAST339 | 220977 | RIV2339 | 1 | 230 | 232 | 991 | 104.34 | 102.87 | AB1-056 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220965 | NEAST339 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 103.46 | 102.84 | AB1-056 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220966 | RIV2317 | 220979 | NEAST317 | 1 | 230 | 232 | 940 | 103.91 | 102.84 | AB1-056 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220966 | RIV2317 | 220979 | NEAST317 | 1 | 230 | 232 | 940 | 103.91 | 102.84 | AB1-056 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 98.89 | 102.7 | AB1-056 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 2 | 500/230 | 225/232 | 2168 | 99.53 | 102.33 | AB1-056 | PJM_500_BG_P2_CNSTN_230-N_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 2 | 500/230 | 225/232 | 2168 | 99.53 | 102.33 | AB1-056 | BG_P1_CNSTN_500-2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 1 | 500/230 | 225/232 | 2168 | 99.42 | 102.22 | AB1-056 | PJM_500_BG_P2_CNSTN_230-S_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 1 | 500/230 | 225/232 | 2168 | 99.42 | 102.22 | AB1-056 | BG_P1_CNSTN_500-4_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 223960 | BRG 1T 230 | 1 | 500/230 | 225/233 | 1498 | 100.95 | 101.38 | AB1-056 | PEPCO_P4_PP41_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 98.96 | 101.31 | AB1-056 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220979 | NEAST317 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 101.32 | 100.71 | AB1-056 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2901 | 144.79 | 146.92 | 3MURPHYS | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 153.69 | 158.17 | AB1-081 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.18 | 157.3 | AB1-081 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.18 | 157.3 | AB1-081 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 152 | 156.85 | AB1-081 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 161.67 | 154.45 | AB1-081 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 148.64 | 153.2 | AB1-081 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 155.75 | 150.6 | AB1-081 | PN_P1-2_PN-500-010T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.48 | 149.58 | AB1-081 | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.41 | 149.51 | AB1-081 | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.1 | 148.34 | AB1-081 | AP_P2-3_PE-500-016_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.16 | 148.31 | AB1-081 | AP_P2-3_PE-500-015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.07 | 147.93 | AB1-081 | PJM_500_BG_P4_5_CNSTN_L_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.35 | 147.92 | AB1-081 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.15 | 147.73 | AB1-081 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.18 | 147.71 | AB1-081 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.91 | 147.52 | AB1-081 | PECO_P4_NOTTI85_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.85 | 147.5 | AB1-081 | PECO_P1-2_220-08_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.28 | 147.46 | AB1-081 | AP_P1-2_PE-500-001_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.28 | 147.46 | AB1-081 | AP_P1-2_WP-500-DRT17_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.78 | 147.44 | AB1-081 | PECO_P4_COOPR125_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.23 | 147.39 | AB1-081 | AP_P2-3_PE-500-018C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2901 | 144.91 | 147.06 | 4E MILL | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.89 | 144.18 | AB1-081 | PECO_P4_PEACH025_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.75 | 144.08 | AB1-081 | PECO_P1-2_PBTIE1_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 139.13 | 133.19 | AB1-081 | PECO_P4_PEACH205_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 139.02 | 132.87 | AB1-081 | PECO_P1-2_PBTIE2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 138.08 | 131.99 | AB1-081 | PECO_P4_PEACH055_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 133.39 | 127.57 | AB1-081 | PECO_P4_PEACH015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 128.83 | 127.09 | AB1-081 | DVP_P4-2: 514T595_SRT-SW |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 132.07 | 126.25 | AB1-081 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 127.08 | 125.37 | AB1-081 | DVP_P4-2: 51482_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 127.08 | 125.28 | AB1-081 | AP_P1-2_PE-500-407T_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 127.08 | 125.28 | AB1-081 | DVP_P1-2: LN 514_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 122.97 | 117.6 | AB1-081 | PECO_P4_PEACH225_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 117.28 | 115.36 | AB1-081 | AP_P2-3_PE-500-019C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200504 | 26CARLISLE | 200520 | 26ROXBURY | 1 | 115 | 226 | 190 | 91.72 | 106.85 | AB1-12 | PN_P2-3_PN-115-0331-B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204538 | 27STRABAN | 204544 | 27LINCOLN | 1 | 115 | 227 | 371 | 100.99 | 100.24 | AB1-124 | AP_P1-3_PE-230-006_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204538 | 27STRABAN | 204544 | 27LINCOLN | 1 | 115 | 227 | 371 | 100.99 | 100.24 | AB1-124 | AP_P2-2_PE-230-010_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204538 | 27STRABAN | 204544 | 27LINCOLN | 1 | 115 | 227 | 371 | 100.99 | 100.24 | AB1-124 | AP_P2-3_PE-230-004_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204538 | 27STRABAN | 204544 | 27LINCOLN | 1 | 115 | 227 | 371 | 100.99 | 100.24 | AB1-124 | AP_P1-2_PE-230-003_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204538 | 27STRABAN | 204544 | 27LINCOLN | 1 | 115 | 227 | 371 | 101.01 | 100.23 | AB1-124 | AP_P2-2_PE-230-006_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204538 | 27STRABAN | 204544 | 27LINCOLN | 1 | 115 | 227 | 371 | 101.01 | 100.23 | AB1-124 | AP_P2-3_PE-230-005_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200504 | 26CARLISLE | 200520 | 26ROXBURY | 1 | 115 | 226 | 190 | 91.72 | 106.85 | AB1-127 | PN_P2-3_PN-115-0331-B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 225.6 | 237.03 | AB1-132 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 223.6 | 237.03 | AB1-132 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 225.54 | 236.97 | AB1-132 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 225.54 | 236.97 | AB1-132 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 223.53 | 236.97 | AB1-132 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 223.53 | 236.97 | AB1-132 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 213.55 | 226.87 | AB1-132 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 213.48 | 226.81 | AB1-132 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 213.48 | 226.81 | AB1-132 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 209.29 | 223.66 | AB1-132 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 209.23 | 223.6 | AB1-132 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 209.22 | 223.6 | AB1-132 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 210.7 | 217.82 | AB1-132 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 208.7 | 217.82 | AB1-132 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 199.16 | 208.26 | AB1-132 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 194.9 | 204.91 | AB1-132 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 172.76 | 167.79 | AB1-132 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 163.63 | 164.93 | AB1-132 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2901 | 144.92 | 147.06 | 6BUCKING | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 161.77 | 161.84 | AB1-132 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 161.77 | 161.84 | AB1-132 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 161.76 | 161.83 | AB1-132 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 153.53 | 157.98 | AB1-132 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.03 | 157.15 | AB1-132 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.03 | 157.15 | AB1-132 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 151.85 | 156.66 | AB1-132 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 161.5 | 154.29 | AB1-132 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 148.49 | 153.01 | AB1-132 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 152.83 | 151.21 | AB1-132 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 155.61 | 150.46 | AB1-132 | PN_P1-2_PN-500-010T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 903 | 142.74 | 149.55 | AB1-132 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 903 | 142.74 | 149.55 | AB1-132 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 903 | 142.72 | 149.54 | AB1-132 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.33 | 149.4 | AB1-132 | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.26 | 149.33 | AB1-132 | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.95 | 148.15 | AB1-132 | AP_P2-3_PE-500-016_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.02 | 148.12 | AB1-132 | AP_P2-3_PE-500-015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.92 | 147.79 | AB1-132 | PJM_500_BG_P4_5_CNSTN_L_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.2 | 147.77 | AB1-132 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153 | 147.58 | AB1-132 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.03 | 147.57 | AB1-132 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.76 | 147.37 | AB1-132 | PECO_P4_NOTTI85_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.7 | 147.36 | AB1-132 | PECO_P1-2_220-08_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.63 | 147.29 | AB1-132 | PECO_P4_COOPR125_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.13 | 147.27 | AB1-132 | AP_P1-2_PE-500-001_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.13 | 147.27 | AB1-132 | AP_P1-2_WP-500-DRT17_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.08 | 147.2 | AB1-132 | AP_P2-3_PE-500-018C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2901 | 144.91 | 147.05 | 6ELIZ CT | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.73 | 144.02 | AB1-132 | PECO_P4_PEACH025_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.58 | 143.91 | AB1-132 | PECO_P1-2_PBTIE1_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 911 | 149 | 143.13 | AB1-132 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 903 | 135.66 | 139.64 | AB1-132 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 1031 | 130.35 | 138.14 | AB1-132 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 1031 | 130.34 | 138.14 | AB1-132 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 1031 | 130.34 | 138.14 | AB1-132 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 138.97 | 133.04 | AB1-132 | PECO_P4_PEACH205_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 138.86 | 132.71 | AB1-132 | PECO_P1-2_PBTIE2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208078 | SAKR | 1 | 230 | 229 | 903 | 124.53 | 132.57 | AB1-132 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208078 | SAKR | 1 | 230 | 229 | 903 | 124.52 | 132.57 | AB1-132 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208078 | SAKR | 1 | 230 | 229 | 903 | 124.53 | 132.57 | AB1-132 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 137.93 | 131.85 | AB1-132 | PECO_P4_PEACH055_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 1031 | 124.74 | 129.3 | AB1-132 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 133.22 | 127.41 | AB1-132 | PECO_P4_PEACH015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 128.53 | 126.84 | AB1-132 | DVP_P4-2: 514T595_SRT-SW |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 131.91 | 126.1 | AB1-132 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 126.78 | 125.06 | AB1-132 | DVP_P4-2: 51482_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 126.78 | 124.97 | AB1-132 | DVP_P1-2: LN 514_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 126.78 | 124.97 | AB1-132 | AP_P1-2_PE-500-407T_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208020 | MANO TR3 | 1 | 230 | 229 | 793 | 111.52 | 124.68 | AB1-132 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208020 | MANO TR3 | 1 | 230 | 229 | 793 | 111.51 | 124.68 | AB1-132 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208020 | MANO TR3 | 1 | 230 | 229 | 793 | 111.52 | 124.68 | AB1-132 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208078 | SAKR | 1 | 230 | 229 | 903 | 117.26 | 122.54 | AB1-132 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200025 | W CHAPEL | 1 | 500 | 225 | 1732 | 123.68 | 121.89 | AB1-132 | PEPCO_P4_PP41_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 122.82 | 117.45 | AB1-132 | PECO_P4_PEACH225_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 116.99 | 115.06 | AB1-132 | AP_P2-3_PE-500-019C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 2 | 500/230 | 225/232 | 2168 | 109.68 | 115 | AB1-132 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 2 | 500/230 | 225/232 | 2168 | 109.5 | 114.78 | AB1-132 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 2 | 500/230 | 225/232 | 2168 | 109.5 | 114.78 | AB1-132 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 1 | 500/230 | 225/232 | 2168 | 109.45 | 114.75 | AB1-132 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 1 | 500/230 | 225/232 | 2168 | 109.27 | 114.54 | AB1-132 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 1 | 500/230 | 225/232 | 2168 | 109.27 | 114.54 | AB1-132 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 99.53 | 103.45 | AB1-132 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 99.53 | 103.45 | AB1-132 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 99.53 | 103.45 | AB1-132 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 98.6 | 102.12 | AB1-132 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 98.7 | 100.75 | AB1-132 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2901 | 144.83 | 146.96 | 6EVERETS | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.6 | 157.73 | AB1-141 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.6 | 157.73 | AB1-141 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 162.21 | 154.97 | AB1-141 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 156.18 | 151.02 | AB1-141 | PN_P1-2_PN-500-010T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.82 | 148.37 | AB1-141 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.47 | 148.34 | AB1-141 | PJM_500_BG_P4_5_CNSTN_L_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.62 | 148.19 | AB1-141 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.65 | 148.17 | AB1-141 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.37 | 147.98 | AB1-141 | PECO_P4_NOTTI85_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.31 | 147.96 | AB1-141 | PECO_P1-2_220-08_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.25 | 147.9 | AB1-141 | PECO_P4_COOPR125_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 151.48 | 144.75 | AB1-141 | PECO_P4_PEACH025_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 151.32 | 144.63 | AB1-141 | PECO_P1-2_PBTIE1_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 139.55 | 133.37 | AB1-141 | PECO_P1-2_PBTIE2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 138.58 | 132.48 | AB1-141 | PECO_P4_PEACH055_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 133.96 | 128.12 | AB1-141 | PECO_P4_PEACH015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 132.59 | 126.73 | AB1-141 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204512 | 27S.RDG | 204693 | 27BOONETOWN | 1 | 230 | 227 | 607 | 107.72 | 122.16 | AB1-141 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 123.49 | 118.1 | AB1-141 | PECO_P4_PEACH225_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2901 | 144.79 | 146.92 | 6HORNRTN | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.6 | 157.73 | AB1-142 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.6 | 157.73 | AB1-142 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 162.21 | 154.97 | AB1-142 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 156.18 | 151.02 | AB1-142 | PN_P1-2_PN-500-010T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.82 | 148.37 | AB1-142 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.47 | 148.34 | AB1-142 | PJM_500_BG_P4_5_CNSTN_L_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.62 | 148.19 | AB1-142 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.65 | 148.17 | AB1-142 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.37 | 147.98 | AB1-142 | PECO_P4_NOTTI85_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.31 | 147.96 | AB1-142 | PECO_P1-2_220-08_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.25 | 147.9 | AB1-142 | PECO_P4_COOPR125_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 151.48 | 144.75 | AB1-142 | PECO_P4_PEACH025_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 151.32 | 144.63 | AB1-142 | PECO_P1-2_PBTIE1_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 139.55 | 133.37 | AB1-142 | PECO_P1-2_PBTIE2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 138.58 | 132.48 | AB1-142 | PECO_P4_PEACH055_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 133.96 | 128.12 | AB1-142 | PECO_P4_PEACH015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 132.59 | 126.73 | AB1-142 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204512 | 27S.RDG | 204693 | 27BOONETOWN | 1 | 230 | 227 | 607 | 107.72 | 122.16 | AB1-142 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 123.49 | 118.1 | AB1-142 | PECO_P4_PEACH225_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2901 | 144.84 | 146.97 | 6OLDCHRC | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 153.76 | 158.25 | AB1-173 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.25 | 157.37 | AB1-173 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.25 | 157.37 | AB1-173 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 152.07 | 156.93 | AB1-173 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 161.76 | 154.53 | AB1-173 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 148.71 | 153.28 | AB1-173 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 155.82 | 150.67 | AB1-173 | PN_P1-2_PN-500-010T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.54 | 149.65 | AB1-173 | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.47 | 149.58 | AB1-173 | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.16 | 148.41 | AB1-173 | AP_P2-3_PE-500-016_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.23 | 148.38 | AB1-173 | AP_P2-3_PE-500-015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.13 | 148 | AB1-173 | PJM_500_BG_P4_5_CNSTN_L_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.42 | 147.99 | AB1-173 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.22 | 147.8 | AB1-173 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.25 | 147.79 | AB1-173 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.98 | 147.59 | AB1-173 | PECO_P4_NOTTI85_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.92 | 147.57 | AB1-173 | PECO_P1-2_220-08_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.34 | 147.53 | AB1-173 | AP_P1-2_WP-500-DRT17_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.34 | 147.53 | AB1-173 | AP_P1-2_PE-500-001_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.85 | 147.51 | AB1-173 | PECO_P4_COOPR125_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.29 | 147.46 | AB1-173 | AP_P2-3_PE-500-018C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2901 | 144.93 | 147.08 | 6PAPERMILL | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.98 | 144.26 | AB1-173 | PECO_P4_PEACH025_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.84 | 144.16 | AB1-173 | PECO_P1-2_PBTIE1_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 139.21 | 133.27 | AB1-173 | PECO_P4_PEACH205_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 139.1 | 132.94 | AB1-173 | PECO_P1-2_PBTIE2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 138.15 | 132.06 | AB1-173 | PECO_P4_PEACH055_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 133.48 | 127.65 | AB1-173 | PECO_P4_PEACH015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 128.92 | 127.18 | AB1-173 | DVP_P4-2: 514T595_SRT-SW |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 132.15 | 126.32 | AB1-173 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 127.17 | 125.47 | AB1-173 | DVP_P4-2: 51482_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 127.17 | 125.38 | AB1-173 | AP_P1-2_PE-500-407T_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 127.17 | 125.38 | AB1-173 | DVP_P1-2: LN 514_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 123.05 | 117.67 | AB1-173 | PECO_P4_PEACH225_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 117.37 | 115.46 | AB1-173 | AP_P2-3_PE-500-019C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2901 | 144.92 | 147.07 | 6WINFALL | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.61 | 157.73 | AB2-032 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.6 | 157.73 | AB2-032 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 162.21 | 154.97 | AB2-032 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 156.18 | 151.02 | AB2-032 | PN_P1-2_PN-500-010T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.82 | 148.38 | AB2-032 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.48 | 148.34 | AB2-032 | PJM_500_BG_P4_5_CNSTN_L_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.62 | 148.19 | AB2-032 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.65 | 148.18 | AB2-032 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.38 | 147.98 | AB2-032 | PECO_P4_NOTTI85_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.32 | 147.96 | AB2-032 | PECO_P1-2_220-08_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.25 | 147.9 | AB2-032 | PECO_P4_COOPR125_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 151.48 | 144.75 | AB2-032 | PECO_P4_PEACH025_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 151.32 | 144.63 | AB2-032 | PECO_P1-2_PBTIE1_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 139.55 | 133.38 | AB2-032 | PECO_P1-2_PBTIE2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 138.59 | 132.48 | AB2-032 | PECO_P4_PEACH055_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 133.96 | 128.12 | AB2-032 | PECO_P4_PEACH015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 132.59 | 126.74 | AB2-032 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 123.5 | 118.1 | AB2-032 | PECO_P4_PEACH225_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 228.66 | 241.21 | AB2-036 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 226.61 | 241.21 | AB2-036 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 227.74 | 239.15 | AB2-036 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 225.69 | 239.15 | AB2-036 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 227.68 | 239.09 | AB2-036 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 225.62 | 239.09 | AB2-036 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 227.67 | 239.08 | AB2-036 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 225.62 | 239.08 | AB2-036 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 216.46 | 230.92 | AB2-036 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 215.57 | 228.92 | AB2-036 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 215.5 | 228.86 | AB2-036 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 215.5 | 228.86 | AB2-036 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 212.19 | 227.75 | AB2-036 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 211.3 | 225.73 | AB2-036 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 211.24 | 225.67 | AB2-036 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 211.24 | 225.67 | AB2-036 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 212.84 | 220.55 | AB2-036 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 210.78 | 220.55 | AB2-036 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 201.17 | 210.9 | AB2-036 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 196.91 | 207.57 | AB2-036 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 172.78 | 167.6 | AB2-036 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 172.78 | 167.59 | AB2-036 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 172.76 | 167.59 | AB2-036 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 164.69 | 166.39 | AB2-036 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 162.87 | 163.33 | AB2-036 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 162.87 | 163.33 | AB2-036 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 162.86 | 163.33 | AB2-036 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2901 | 144.87 | 147.01 | 6WINTERP | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 154.52 | 159.16 | AB2-036 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 163.12 | 158.23 | AB2-036 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 163.11 | 158.23 | AB2-036 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 152.82 | 157.83 | AB2-036 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 162.95 | 155.67 | AB2-036 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 149.46 | 154.18 | AB2-036 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 903 | 145.08 | 153.37 | AB2-036 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 153.93 | 152.55 | AB2-036 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 156.7 | 151.54 | AB2-036 | PN_P1-2_PN-500-010T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 903 | 143.59 | 150.74 | AB2-036 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 903 | 143.59 | 150.73 | AB2-036 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 147.27 | 150.52 | AB2-036 | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 147.2 | 150.44 | AB2-036 | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.84 | 149.22 | AB2-036 | AP_P2-3_PE-500-016_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.9 | 149.19 | AB2-036 | AP_P2-3_PE-500-015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 154.46 | 149 | AB2-036 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.96 | 148.82 | AB2-036 | PJM_500_BG_P4_5_CNSTN_L_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 154.26 | 148.81 | AB2-036 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 154.28 | 148.79 | AB2-036 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 154.01 | 148.6 | AB2-036 | PECO_P4_NOTTI85_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.95 | 148.58 | AB2-036 | PECO_P1-2_220-08_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.88 | 148.52 | AB2-036 | PECO_P4_COOPR125_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.02 | 148.34 | AB2-036 | AP_P1-2_PE-500-001_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.02 | 148.34 | AB2-036 | AP_P1-2_WP-500-DRT17_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.97 | 148.27 | AB2-036 | AP_P2-3_PE-500-018C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2901 | 144.91 | 147.06 | AA1-018 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 152.41 | 145.63 | AB2-036 | PECO_P4_PEACH025_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 152.14 | 145.41 | AB2-036 | PECO_P1-2_PBTIE1_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 911 | 149.02 | 142.98 | AB2-036 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 911 | 149.01 | 142.98 | AB2-036 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 911 | 149 | 142.98 | AB2-036 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204502 | 27JACKSON | 204514 | 27TMI | 1 | 230 | 227 | 781 | 133.71 | 142.74 | AB2-036 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 903 | 136.51 | 140.84 | AB2-036 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 1031 | 131.52 | 140.18 | AB2-036 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208078 | SAKR | 1 | 230 | 229 | 903 | 126.14 | 135.05 | AB2-036 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 140.16 | 134.18 | AB2-036 | PECO_P4_PEACH205_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 140.3 | 134.09 | AB2-036 | PECO_P1-2_PBTIE2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 139.33 | 133.19 | AB2-036 | PECO_P4_PEACH055_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204502 | 27JACKSON | 204514 | 27TMI | 1 | 230 | 227 | 781 | 126.25 | 132.26 | AB2-036 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 1031 | 125.43 | 130.36 | AB2-036 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 134.78 | 128.91 | AB2-036 | PECO_P4_PEACH015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 128.39 | 128.73 | AB2-036 | BG_P7_GRCTN_CNSTN_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 126.34 | 128.73 | AB2-036 | BG_P7_GRCTN_CNSTN_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 129.73 | 127.99 | AB2-036 | DVP_P4-2: 514T595_SRT-SW |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 133.33 | 127.45 | AB2-036 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208020 | MANO TR3 | 1 | 230 | 229 | 793 | 113.21 | 127.43 | AB2-036 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 128 | 126.3 | AB2-036 | DVP_P4-2: 51482_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 128 | 126.21 | AB2-036 | AP_P1-2_PE-500-407T_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 128 | 126.21 | AB2-036 | DVP_P1-2: LN 514_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 121.28 | 124.14 | AB2-036 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 119.23 | 124.14 | AB2-036 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 121.1 | 123.93 | AB2-036 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 119.05 | 123.93 | AB2-036 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 119.05 | 123.93 | AB2-036 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 121.1 | 123.93 | AB2-036 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208078 | SAKR | 1 | 230 | 229 | 903 | 118.15 | 123.85 | AB2-036 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208031 | MLWD TR2 | 1 | 230 | 229 | 911 | 113.34 | 123.66 | AB2-036 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200025 | W CHAPEL | 1 | 500 | 225 | 1732 | 124.53 | 122.78 | AB2-036 | PEPCO_P4_PP41_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 119.63 | 122.03 | AB2-036 | BG_P7_GRCTN_CNSTN_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 120.33 | 120.96 | AB2-036 | PJM_500_BG_P4_5_CNSTN_15_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 118.28 | 120.96 | AB2-036 | PJM_500_BG_P4_5_CNSTN_15_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2901 | 144.93 | 147.08 | AA1-038 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2901 | 144.81 | 146.94 | AA1-063 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 124.25 | 118.83 | AB2-036 | PECO_P4_PEACH225_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 115.01 | 118.74 | AB2-036 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 115.01 | 118.74 | AB2-036 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 114.67 | 118.4 | AB2-036 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 114.67 | 118.4 | AB2-036 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 115.37 | 118.18 | AB2-036 | BG_P7_GRCTN_CNSTN_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 112.77 | 117.6 | AB2-036 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 112.59 | 117.39 | AB2-036 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 112.59 | 117.39 | AB2-036 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 118.19 | 116.28 | AB2-036 | AP_P2-3_PE-500-019C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2901 | 145.93 | 148.24 | AA1-102 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 2 | 500/230 | 225/232 | 2168 | 110.22 | 115.61 | AB2-036 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208020 | MANO TR3 | 1 | 230 | 229 | 793 | 105.22 | 115.41 | AB2-036 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 2 | 500/230 | 225/232 | 2168 | 110.05 | 115.4 | AB2-036 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 2 | 500/230 | 225/232 | 2168 | 110.05 | 115.4 | AB2-036 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 1 | 500/230 | 225/232 | 2168 | 109.99 | 115.37 | AB2-036 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 1 | 500/230 | 225/232 | 2168 | 109.82 | 115.16 | AB2-036 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 1 | 500/230 | 225/232 | 2168 | 109.81 | 115.15 | AB2-036 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220964 | GRACETON | 220999 | BAGLEY2 | 13 | 230 | 232 | 1795 | 113.98 | 115.07 | AB2-036 | BG_P4_5_GRCTN_3T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208020 | MANO TR3 | 208031 | MLWD TR2 | 1 | 230 | 229 | 903 | 103.4 | 114.94 | AB2-036 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 111.85 | 114.58 | AB2-036 | PJM_500_BG_P4_5_CNSTN_15_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 108.51 | 113.78 | AB2-036 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 108.33 | 113.57 | AB2-036 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 108.33 | 113.57 | AB2-036 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208031 | MLWD TR2 | 1 | 230 | 229 | 911 | 105.89 | 112.99 | AB2-036 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 2 | 500/230 | 225/232 | 2168 | 108.96 | 112.3 | AB2-036 | PJM_500_BG_P4_5_CNSTN_15_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220980 | RAPHAEL | 220999 | BAGLEY2 | 13 | 230 | 232 | 1795 | 109.56 | 111.82 | AB2-036 | BG_P4_5_GRCTN_3T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2901 | 144.62 | 146.72 | AA1-139 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 107.59 | 110.88 | AB2-036 | PJM_500_BG_P4_5_CNSTN_15_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208020 | MANO TR3 | 208031 | MLWD TR2 | 1 | 230 | 229 | 903 | 96.33 | 104.55 | AB2-036 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 98.87 | 102.6 | AB2-036 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 230.35 | 243.58 | AB2-037 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 228.26 | 243.58 | AB2-037 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 229.45 | 241.49 | AB2-037 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 227.36 | 241.49 | AB2-037 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 229.38 | 241.39 | AB2-037 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 227.3 | 241.39 | AB2-037 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 229.38 | 241.39 | AB2-037 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 227.29 | 241.39 | AB2-037 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 218.05 | 233.22 | AB2-037 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 217.18 | 231.19 | AB2-037 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 217.12 | 231.1 | AB2-037 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 217.12 | 231.1 | AB2-037 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 213.78 | 230.07 | AB2-037 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 212.91 | 228.02 | AB2-037 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 212.85 | 227.93 | AB2-037 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 212.85 | 227.93 | AB2-037 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 214.56 | 222.73 | AB2-037 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 212.47 | 222.73 | AB2-037 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 202.8 | 213.02 | AB2-037 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 198.53 | 209.7 | AB2-037 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204538 | 27STRABAN | 204544 | 27LINCOLN | 1 | 115 | 227 | 371 | 164.96 | 170.06 | AB2-037 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204538 | 27STRABAN | 204544 | 27LINCOLN | 1 | 115 | 227 | 371 | 164.96 | 170.06 | AB2-037 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 174.36 | 169.67 | AB2-037 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 173.44 | 168.25 | AB2-037 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 173.43 | 168.24 | AB2-037 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 173.42 | 168.24 | AB2-037 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 165.41 | 167.41 | AB2-037 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204529 | 27GERMANTN | 204538 | 27STRABAN | 1 | 115 | 227 | 371 | 159.16 | 165.51 | AB2-037 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204529 | 27GERMANTN | 204538 | 27STRABAN | 1 | 115 | 227 | 371 | 159.16 | 165.51 | AB2-037 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2901 | 144.79 | 146.92 | AA2-053 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 163.62 | 164.35 | AB2-037 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 163.64 | 164.35 | AB2-037 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 163.64 | 164.35 | AB2-037 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 165.49 | 160.52 | AB2-037 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 155.2 | 159.97 | AB2-037 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 163.96 | 159.06 | AB2-037 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 163.96 | 159.06 | AB2-037 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 153.5 | 158.64 | AB2-037 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 164.16 | 156.84 | AB2-037 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 150.13 | 154.99 | AB2-037 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 903 | 145.62 | 154.33 | AB2-037 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 154.7 | 153.49 | AB2-037 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 157.56 | 152.39 | AB2-037 | PN_P1-2_PN-500-010T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 903 | 144.15 | 151.68 | AB2-037 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 903 | 144.17 | 151.67 | AB2-037 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 903 | 144.17 | 151.67 | AB2-037 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204539 | 27HUNTRSTN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 334 | 151.98 | 151.56 | AB2-037 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 334 | 152.38 | 151.32 | AB2-037 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 147.93 | 151.3 | AB2-037 | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 147.86 | 151.22 | AB2-037 | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 155.49 | 150.01 | AB2-037 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 145.44 | 149.92 | AB2-037 | AP_P2-3_PE-500-016_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 145.5 | 149.9 | AB2-037 | AP_P2-3_PE-500-015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 155.29 | 149.82 | AB2-037 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 155.32 | 149.81 | AB2-037 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 155.04 | 149.61 | AB2-037 | PECO_P4_NOTTI85_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 154.77 | 149.6 | AB2-037 | PJM_500_BG_P4_5_CNSTN_L_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 154.98 | 149.59 | AB2-037 | PECO_P1-2_220-08_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 154.91 | 149.53 | AB2-037 | PECO_P4_COOPR125_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.61 | 149.04 | AB2-037 | AP_P1-2_PE-500-001_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.61 | 149.04 | AB2-037 | AP_P1-2_WP-500-DRT17_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.57 | 148.97 | AB2-037 | AP_P2-3_PE-500-018C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2901 | 144.82 | 146.96 | AA2-057 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 153.94 | 147.1 | AB2-037 | PECO_P4_PEACH025_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 153.48 | 146.7 | AB2-037 | PECO_P1-2_PBTIE1_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 911 | 150.56 | 144.86 | AB2-037 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204502 | 27JACKSON | 204514 | 27TMI | 1 | 230 | 227 | 781 | 134.35 | 143.79 | AB2-037 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204502 | 27JACKSON | 204514 | 27TMI | 1 | 230 | 227 | 781 | 134.52 | 143.73 | AB2-037 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204502 | 27JACKSON | 204514 | 27TMI | 1 | 230 | 227 | 781 | 134.53 | 143.71 | AB2-037 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204502 | 27JACKSON | 204514 | 27TMI | 1 | 230 | 227 | 781 | 134.53 | 143.71 | AB2-037 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 911 | 149.67 | 143.56 | AB2-037 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 911 | 149.67 | 143.56 | AB2-037 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 911 | 149.65 | 143.54 | AB2-037 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204538 | 27STRABAN | 204544 | 27LINCOLN | 1 | 115 | 227 | 371 | 141.48 | 142.34 | AB2-037 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204538 | 27STRABAN | 204544 | 27LINCOLN | 1 | 115 | 227 | 371 | 141.49 | 142.33 | AB2-037 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204538 | 27STRABAN | 204544 | 27LINCOLN | 1 | 115 | 227 | 371 | 141.49 | 142.33 | AB2-037 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204538 | 27STRABAN | 204544 | 27LINCOLN | 1 | 115 | 227 | 371 | 141.31 | 142.14 | AB2-037 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 903 | 137.09 | 141.71 | AB2-037 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 1031 | 131.98 | 141.08 | AB2-037 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 1031 | 131.5 | 139.98 | AB2-037 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 1031 | 131.51 | 139.96 | AB2-037 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 1031 | 131.51 | 139.96 | AB2-037 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204529 | 27GERMANTN | 204538 | 27STRABAN | 1 | 115 | 227 | 371 | 135.68 | 138.05 | AB2-037 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204529 | 27GERMANTN | 204538 | 27STRABAN | 1 | 115 | 227 | 371 | 135.69 | 138.04 | AB2-037 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204529 | 27GERMANTN | 204538 | 27STRABAN | 1 | 115 | 227 | 371 | 135.69 | 138.04 | AB2-037 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204529 | 27GERMANTN | 204538 | 27STRABAN | 1 | 115 | 227 | 371 | 135.51 | 137.85 | AB2-037 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 911 | 141.8 | 136.54 | AB2-037 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 207923 | BRISREAC | 208132 | WHEM TR1 | 1 | 230 | 229 | 676 | 126.08 | 136.15 | AB2-037 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 207922 | BRIS | 207923 | BRISREAC | RX | 230 | 229 | 676 | 126.08 | 136.15 | AB2-037 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208078 | SAKR | 1 | 230 | 229 | 903 | 126.78 | 136.12 | AB2-037 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 141.53 | 135.28 | AB2-037 | PECO_P1-2_PBTIE2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 141.07 | 135.05 | AB2-037 | PECO_P4_PEACH205_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 207922 | BRIS | 207923 | BRISREAC | RX | 230 | 229 | 676 | 125.35 | 134.65 | AB2-037 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 207923 | BRISREAC | 208132 | WHEM TR1 | 1 | 230 | 229 | 676 | 125.35 | 134.65 | AB2-037 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208078 | SAKR | 1 | 230 | 229 | 903 | 126.07 | 134.64 | AB2-037 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 207922 | BRIS | 207923 | BRISREAC | RX | 230 | 229 | 676 | 125.36 | 134.64 | AB2-037 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 207923 | BRISREAC | 208132 | WHEM TR1 | 1 | 230 | 229 | 676 | 125.36 | 134.64 | AB2-037 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 207922 | BRIS | 207923 | BRISREAC | RX | 230 | 229 | 676 | 125.36 | 134.63 | AB2-037 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 207923 | BRISREAC | 208132 | WHEM TR1 | 1 | 230 | 229 | 676 | 125.36 | 134.63 | AB2-037 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208078 | SAKR | 1 | 230 | 229 | 903 | 126.07 | 134.62 | AB2-037 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208078 | SAKR | 1 | 230 | 229 | 903 | 126.07 | 134.62 | AB2-037 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 140.56 | 134.37 | AB2-037 | PECO_P4_PEACH055_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204502 | 27JACKSON | 204514 | 27TMI | 1 | 230 | 227 | 781 | 126.89 | 133.21 | AB2-037 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220972 | GRANITE1 | 1 | 230 | 232 | 829 | 136.5 | 132.49 | AB2-037 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 204529 | 27GERMANTN | 1 | 138/115 | 227 | 453 | 125.83 | 131.99 | AB2-037 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 204529 | 27GERMANTN | 1 | 138/115 | 227 | 453 | 125.83 | 131.99 | AB2-037 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220972 | GRANITE1 | 1 | 230 | 232 | 829 | 135.88 | 131.83 | AB2-037 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220972 | GRANITE1 | 1 | 230 | 232 | 829 | 135.88 | 131.83 | AB2-037 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 1031 | 125.91 | 131.15 | AB2-037 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220973 | GRANITE6 | 1 | 230 | 232 | 829 | 134.39 | 130.56 | AB2-037 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 136.13 | 130.21 | AB2-037 | PECO_P4_PEACH015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220973 | GRANITE6 | 1 | 230 | 232 | 829 | 133.81 | 129.95 | AB2-037 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220973 | GRANITE6 | 1 | 230 | 232 | 829 | 133.81 | 129.95 | AB2-037 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 129.3 | 129.69 | AB2-037 | BG_P7_GRCTN_CNSTN_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 127.22 | 129.69 | AB2-037 | BG_P7_GRCTN_CNSTN_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 134.56 | 128.63 | AB2-037 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 130.26 | 128.51 | AB2-037 | DVP_P4-2: 514T595_SRT-SW |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208020 | MANO TR3 | 1 | 230 | 229 | 793 | 113.83 | 128.41 | AB2-037 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220953 | HOWARD12 | 220972 | GRANITE1 | 1 | 230 | 232 | 772 | 131.54 | 127.51 | AB2-037 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208020 | MANO TR3 | 1 | 230 | 229 | 793 | 113.04 | 126.97 | AB2-037 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208020 | MANO TR3 | 1 | 230 | 229 | 793 | 113.04 | 126.95 | AB2-037 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208020 | MANO TR3 | 1 | 230 | 229 | 793 | 113.04 | 126.95 | AB2-037 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 128.55 | 126.83 | AB2-037 | DVP_P4-2: 51482_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 128.55 | 126.74 | AB2-037 | DVP_P1-2: LN 514_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 128.55 | 126.74 | AB2-037 | AP_P1-2_PE-500-407T_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220954 | HOWARD32 | 220973 | GRANITE6 | 1 | 230 | 232 | 772 | 130.28 | 126.72 | AB2-037 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220953 | HOWARD12 | 220972 | GRANITE1 | 1 | 230 | 232 | 772 | 130.64 | 126.55 | AB2-037 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220953 | HOWARD12 | 220972 | GRANITE1 | 1 | 230 | 232 | 772 | 130.64 | 126.54 | AB2-037 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 207922 | BRIS | 207923 | BRISREAC | RX | 230 | 229 | 676 | 120.26 | 126.46 | AB2-037 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 207923 | BRISREAC | 208132 | WHEM TR1 | 1 | 230 | 229 | 676 | 120.26 | 126.46 | AB2-037 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220954 | HOWARD32 | 220973 | GRANITE6 | 1 | 230 | 232 | 772 | 129.5 | 125.88 | AB2-037 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220954 | HOWARD32 | 220973 | GRANITE6 | 1 | 230 | 232 | 772 | 129.5 | 125.88 | AB2-037 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 122.25 | 125.16 | AB2-037 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 120.16 | 125.16 | AB2-037 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 119.97 | 124.95 | AB2-037 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 122.06 | 124.95 | AB2-037 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 119.97 | 124.95 | AB2-037 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 122.06 | 124.95 | AB2-037 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208078 | SAKR | 1 | 230 | 229 | 903 | 118.81 | 124.73 | AB2-037 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208031 | MLWD TR2 | 1 | 230 | 229 | 911 | 113.93 | 124.66 | AB2-037 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204512 | 27S.RDG | 204693 | 27BOONETOWN | 1 | 230 | 227 | 607 | 108.38 | 124.32 | AB2-037 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200025 | W CHAPEL | 1 | 500 | 225 | 1732 | 125.11 | 123.38 | AB2-037 | PEPCO_P4_PP41_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208031 | MLWD TR2 | 1 | 230 | 229 | 911 | 113.24 | 123.27 | AB2-037 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208031 | MLWD TR2 | 1 | 230 | 229 | 911 | 113.25 | 123.24 | AB2-037 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208031 | MLWD TR2 | 1 | 230 | 229 | 911 | 113.25 | 123.24 | AB2-037 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 120.48 | 122.95 | AB2-037 | BG_P7_GRCTN_CNSTN_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 121.26 | 121.93 | AB2-037 | PJM_500_BG_P4_5_CNSTN_15_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 119.17 | 121.93 | AB2-037 | PJM_500_BG_P4_5_CNSTN_15_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208131 | WHEM | 208132 | WHEM TR1 | 1 | 230 | 229 | 691 | 110.25 | 120.77 | AB2-037 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220965 | NEAST339 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 120.93 | 120.3 | AB2-037 | BG_P1_2315_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220965 | NEAST339 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 120.49 | 120.08 | AB2-037 | BG_P4_5_NEAST_17_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220965 | NEAST339 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 120.65 | 120.08 | AB2-037 | BG_P4_5_NEAST_15_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 125.5 | 120.02 | AB2-037 | PECO_P4_PEACH225_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2901 | 144.71 | 146.83 | AA2-088 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2901 | 144.79 | 146.91 | AA2-178 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 115.79 | 119.61 | AB2-037 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220979 | NEAST317 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 119.99 | 119.42 | AB2-037 | BG_P1_2337_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208131 | WHEM | 208132 | WHEM TR1 | 1 | 230 | 229 | 691 | 109.57 | 119.33 | AB2-037 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208131 | WHEM | 208132 | WHEM TR1 | 1 | 230 | 229 | 691 | 109.58 | 119.32 | AB2-037 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208131 | WHEM | 208132 | WHEM TR1 | 1 | 230 | 229 | 691 | 109.58 | 119.32 | AB2-037 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 115.44 | 119.27 | AB2-037 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 115.44 | 119.21 | AB2-037 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 115.44 | 119.21 | AB2-037 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220979 | NEAST317 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 119.65 | 119.14 | AB2-037 | BG_P4_5_NEAST_39_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220979 | NEAST317 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 119.65 | 119.14 | AB2-037 | BG_P4_5_NEAST_37_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 116.21 | 119.11 | AB2-037 | BG_P7_GRCTN_CNSTN_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 115.1 | 118.88 | AB2-037 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 115.1 | 118.88 | AB2-037 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 113.67 | 118.59 | AB2-037 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 113.49 | 118.38 | AB2-037 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 113.49 | 118.38 | AB2-037 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200532 | 26ROXBURY | 200520 | 26ROXBURY | 2 | 138/115 | 226 | 435 | 102.16 | 117.84 | AB2-037 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200532 | 26ROXBURY | 200520 | 26ROXBURY | 2 | 138/115 | 226 | 435 | 102.16 | 117.82 | AB2-037 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200532 | 26ROXBURY | 200520 | 26ROXBURY | 2 | 138/115 | 226 | 435 | 102.16 | 117.82 | AB2-037 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200532 | 26ROXBURY | 200520 | 26ROXBURY | 2 | 138/115 | 226 | 435 | 102 | 117.68 | AB2-037 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2901 | 144.85 | 146.99 | AB1-006 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 118.73 | 116.8 | AB2-037 | AP_P2-3_PE-500-019C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204512 | 27S.RDG | 204693 | 27BOONETOWN | 1 | 230 | 227 | 607 | 106.45 | 116.58 | AB2-037 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208020 | MANO TR3 | 1 | 230 | 229 | 793 | 105.86 | 116.43 | AB2-037 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 2 | 500/230 | 225/232 | 2168 | 110.62 | 116.06 | AB2-037 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208020 | MANO TR3 | 208031 | MLWD TR2 | 1 | 230 | 229 | 903 | 103.95 | 115.87 | AB2-037 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 2 | 500/230 | 225/232 | 2168 | 110.45 | 115.85 | AB2-037 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 2 | 500/230 | 225/232 | 2168 | 110.45 | 115.85 | AB2-037 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 1 | 500/230 | 225/232 | 2168 | 110.39 | 115.82 | AB2-037 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 1 | 500/230 | 225/232 | 2168 | 110.22 | 115.61 | AB2-037 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 1 | 500/230 | 225/232 | 2168 | 110.22 | 115.61 | AB2-037 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 112.71 | 115.52 | AB2-037 | PJM_500_BG_P4_5_CNSTN_15_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220964 | GRACETON | 220999 | BAGLEY2 | 13 | 230 | 232 | 1795 | 114.34 | 115.45 | AB2-037 | BG_P4_5_GRCTN_3T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 109.4 | 114.77 | AB2-037 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 109.22 | 114.56 | AB2-037 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 109.22 | 114.56 | AB2-037 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208020 | MANO TR3 | 208031 | MLWD TR2 | 1 | 230 | 229 | 903 | 103.27 | 114.55 | AB2-037 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208020 | MANO TR3 | 208031 | MLWD TR2 | 1 | 230 | 229 | 903 | 103.28 | 114.53 | AB2-037 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208020 | MANO TR3 | 208031 | MLWD TR2 | 1 | 230 | 229 | 903 | 103.28 | 114.53 | AB2-037 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208031 | MLWD TR2 | 1 | 230 | 229 | 911 | 106.49 | 113.9 | AB2-037 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 2 | 500/230 | 225/232 | 2168 | 109.28 | 112.65 | AB2-037 | PJM_500_BG_P4_5_CNSTN_15_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2901 | 145.84 | 148.15 | AB1-056 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 107.37 | 112.37 | AB2-037 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 107.25 | 112.24 | AB2-037 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220980 | RAPHAEL | 220999 | BAGLEY2 | 13 | 230 | 232 | 1795 | 109.9 | 112.2 | AB2-037 | BG_P4_5_GRCTN_3T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208131 | WHEM | 208133 | WHEM TR2 | 1 | 230 | 229 | 691 | 102.73 | 112.13 | AB2-037 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208131 | WHEM | 208132 | WHEM TR1 | 1 | 230 | 229 | 691 | 104.79 | 111.82 | AB2-037 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 108.44 | 111.82 | AB2-037 | PJM_500_BG_P4_5_CNSTN_15_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 793 | 114.16 | 111.52 | AB2-037 | PEPCO_P4_PP19_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208131 | WHEM | 208133 | WHEM TR2 | 1 | 230 | 229 | 691 | 102.04 | 110.72 | AB2-037 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208131 | WHEM | 208133 | WHEM TR2 | 1 | 230 | 229 | 691 | 102.06 | 110.71 | AB2-037 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208131 | WHEM | 208133 | WHEM TR2 | 1 | 230 | 229 | 691 | 102.06 | 110.71 | AB2-037 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 204529 | 27GERMANTN | 1 | 138/115 | 227 | 453 | 106.6 | 109.18 | AB2-037 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 204529 | 27GERMANTN | 1 | 138/115 | 227 | 453 | 106.6 | 109.17 | AB2-037 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 204529 | 27GERMANTN | 1 | 138/115 | 227 | 453 | 106.61 | 109.17 | AB2-037 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 204529 | 27GERMANTN | 1 | 138/115 | 227 | 453 | 106.46 | 109.02 | AB2-037 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220973 | GRANITE6 | 1 | 230 | 232 | 829 | 110.07 | 108.88 | AB2-037 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220965 | NEAST339 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 109.44 | 108.01 | AB2-037 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220965 | NEAST339 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 109.35 | 107.9 | AB2-037 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220965 | NEAST339 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 109.35 | 107.9 | AB2-037 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220972 | GRANITE1 | 1 | 230 | 232 | 829 | 109.22 | 107.8 | AB2-037 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208021 | MANO TR4 | 208133 | WHEM TR2 | 2 | 230 | 229 | 593 | 97.38 | 107.02 | AB2-037 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 102.48 | 106.81 | AB2-037 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 102.4 | 106.72 | AB2-037 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200099 | LAUS | 208045 | LAUS | 3 | 500/230 | 225/229 | 1200 | 104.37 | 106.2 | AB2-037 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220972 | GRANITE1 | 1 | 230 | 232 | 829 | 107.18 | 105.85 | AB2-037 | BG_P4_5_NW230-4_2326_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200099 | LAUS | 208045 | LAUS | 3 | 500/230 | 225/229 | 1200 | 104.08 | 105.69 | AB2-037 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200099 | LAUS | 208045 | LAUS | 3 | 500/230 | 225/229 | 1200 | 104.08 | 105.69 | AB2-037 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200099 | LAUS | 208045 | LAUS | 3 | 500/230 | 225/229 | 1200 | 104.06 | 105.68 | AB2-037 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 103.58 | 105.67 | AB2-037 | BG_P1_2322_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 103.5 | 105.59 | AB2-037 | BG_P1_2310_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 103.51 | 105.56 | AB2-037 | BG_P4_5_NW2322_230-4_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 103.44 | 105.52 | AB2-037 | BG_P4_5_NW2310_230-5_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208020 | MANO TR3 | 208031 | MLWD TR2 | 1 | 230 | 229 | 903 | 96.91 | 105.51 | AB2-037 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208021 | MANO TR4 | 208133 | WHEM TR2 | 2 | 230 | 229 | 593 | 96.6 | 105.41 | AB2-037 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208021 | MANO TR4 | 208133 | WHEM TR2 | 2 | 230 | 229 | 593 | 96.62 | 105.4 | AB2-037 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208021 | MANO TR4 | 208133 | WHEM TR2 | 2 | 230 | 229 | 593 | 96.62 | 105.4 | AB2-037 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220973 | GRANITE6 | 1 | 230 | 232 | 829 | 106.86 | 105.32 | AB2-037 | BG_P4_5_NW230-5_2311_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220979 | NEAST317 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 106.28 | 104.91 | AB2-037 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220979 | NEAST317 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 106.19 | 104.8 | AB2-037 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220979 | NEAST317 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 106.19 | 104.8 | AB2-037 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 102.15 | 104.28 | AB2-037 | BG_P4_5_NW230-2_2322_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 99.83 | 104.21 | AB2-037 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 99.83 | 104.2 | AB2-037 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 99.83 | 104.2 | AB2-037 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 102.04 | 104.16 | AB2-037 | BG_P4_5_NW2371_2310_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 102.04 | 104.16 | AB2-037 | BG_P4_5_NW230-3_2310_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220973 | GRANITE6 | 1 | 230 | 232 | 829 | 104.77 | 103.73 | AB2-037 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208131 | WHEM | 208133 | WHEM TR2 | 1 | 230 | 229 | 691 | 97.28 | 103.5 | AB2-037 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220965 | NEAST339 | 220977 | RIV2339 | 1 | 230 | 232 | 991 | 104.73 | 103.27 | AB2-037 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220966 | RIV2317 | 220979 | NEAST317 | 1 | 230 | 232 | 940 | 104.29 | 103.23 | AB2-037 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 101.18 | 103.23 | AB2-037 | BG_P4_5_CNSTN_14_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220965 | NEAST339 | 220977 | RIV2339 | 1 | 230 | 232 | 991 | 104.69 | 103.21 | AB2-037 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220965 | NEAST339 | 220977 | RIV2339 | 1 | 230 | 232 | 991 | 104.68 | 103.21 | AB2-037 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220966 | RIV2317 | 220979 | NEAST317 | 1 | 230 | 232 | 940 | 104.25 | 103.17 | AB2-037 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220966 | RIV2317 | 220979 | NEAST317 | 1 | 230 | 232 | 940 | 104.25 | 103.17 | AB2-037 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220964 | GRACETON | 220999 | BAGLEY2 | 13 | 230 | 232 | 1795 | 102.32 | 103.13 | AB2-037 | BG_P1_2305_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220964 | GRACETON | 221000 | BAGLEY | 5 | 230 | 232 | 1795 | 102.32 | 103.13 | AB2-037 | BG_P1_2313_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220965 | NEAST339 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 103.71 | 103.12 | AB2-037 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220972 | GRANITE1 | 1 | 230 | 232 | 829 | 104.18 | 102.96 | AB2-037 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 98.95 | 102.9 | AB2-037 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 2 | 500/230 | 225/232 | 2168 | 99.72 | 102.53 | AB2-037 | PJM_500_BG_P2_CNSTN_230-N_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 2 | 500/230 | 225/232 | 2168 | 99.72 | 102.53 | AB2-037 | BG_P1_CNSTN_500-2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 1 | 500/230 | 225/232 | 2168 | 99.61 | 102.42 | AB2-037 | PJM_500_BG_P2_CNSTN_230-S_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 1 | 500/230 | 225/232 | 2168 | 99.61 | 102.42 | AB2-037 | BG_P1_CNSTN_500-4_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 223960 | BRG 1T 230 | 1 | 500/230 | 225/233 | 1498 | 101.17 | 101.61 | AB2-037 | PEPCO_P4_PP41_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 99 | 101.47 | AB2-037 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208021 | MANO TR4 | 1 | 230 | 229 | 600 | 90.44 | 101.13 | AB2-037 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220979 | NEAST317 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 101.56 | 100.98 | AB2-037 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220972 | GRANITE1 | 1 | 230 | 232 | 829 | 101.85 | 100.77 | AB2-037 | BG_P4_5_GRNITE26_32_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220973 | GRANITE6 | 1 | 230 | 232 | 829 | 101.68 | 100.32 | AB2-037 | BBG_P1_2311_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220972 | GRANITE1 | 1 | 230 | 232 | 829 | 101.37 | 100.27 | AB2-037 | BG_P1_2326_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220973 | GRANITE6 | 1 | 230 | 232 | 829 | 101.09 | 100.24 | AB2-037 | BG_P1_2312_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220973 | GRANITE6 | 1 | 230 | 232 | 829 | 101.24 | 100.22 | AB2-037 | BG_P4_5_GRNITE11_12_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2901 | 144.8 | 146.93 | AB1-081 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 153.68 | 158.16 | AB2-040 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.17 | 157.29 | AB2-040 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.17 | 157.29 | AB2-040 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 151.99 | 156.83 | AB2-040 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 161.67 | 154.44 | AB2-040 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 148.63 | 153.18 | AB2-040 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 155.74 | 150.59 | AB2-040 | PN_P1-2_PN-500-010T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.47 | 149.56 | AB2-040 | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.4 | 149.49 | AB2-040 | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.09 | 148.32 | AB2-040 | AP_P2-3_PE-500-016_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.15 | 148.29 | AB2-040 | AP_P2-3_PE-500-015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.06 | 147.92 | AB2-040 | PJM_500_BG_P4_5_CNSTN_L_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.35 | 147.91 | AB2-040 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.14 | 147.72 | AB2-040 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.17 | 147.71 | AB2-040 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.9 | 147.51 | AB2-040 | PECO_P4_NOTTI85_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.84 | 147.5 | AB2-040 | PECO_P1-2_220-08_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.26 | 147.44 | AB2-040 | AP_P1-2_WP-500-DRT17_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.26 | 147.44 | AB2-040 | AP_P1-2_PE-500-001_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.77 | 147.43 | AB2-040 | PECO_P4_COOPR125_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.21 | 147.37 | AB2-040 | AP_P2-3_PE-500-018C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2901 | 144.65 | 146.76 | AB1-132 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.89 | 144.18 | AB2-040 | PECO_P4_PEACH025_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.74 | 144.07 | AB2-040 | PECO_P1-2_PBTIE1_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 139.12 | 133.18 | AB2-040 | PECO_P4_PEACH205_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 139.01 | 132.86 | AB2-040 | PECO_P1-2_PBTIE2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 138.07 | 131.99 | AB2-040 | PECO_P4_PEACH055_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 133.39 | 127.57 | AB2-040 | PECO_P4_PEACH015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 128.78 | 127.04 | AB2-040 | DVP_P4-2: 514T595_SRT-SW |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 132.06 | 126.24 | AB2-040 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 127.04 | 125.33 | AB2-040 | DVP_P4-2: 51482_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 127.04 | 125.23 | AB2-040 | DVP_P1-2: LN 514_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 127.04 | 125.23 | AB2-040 | AP_P1-2_PE-500-407T_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 122.97 | 117.59 | AB2-040 | PECO_P4_PEACH225_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 117.23 | 115.32 | AB2-040 | AP_P2-3_PE-500-019C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2901 | 144.87 | 147.01 | AB1-173 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 153.8 | 158.3 | AB2-043 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.29 | 157.41 | AB2-043 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.29 | 157.41 | AB2-043 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 152.11 | 156.98 | AB2-043 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 161.8 | 154.57 | AB2-043 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 148.75 | 153.33 | AB2-043 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 155.86 | 150.71 | AB2-043 | PN_P1-2_PN-500-010T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.58 | 149.7 | AB2-043 | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.51 | 149.63 | AB2-043 | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.2 | 148.46 | AB2-043 | AP_P2-3_PE-500-016_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.26 | 148.43 | AB2-043 | AP_P2-3_PE-500-015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.17 | 148.04 | AB2-043 | PJM_500_BG_P4_5_CNSTN_L_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.46 | 148.02 | AB2-043 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.26 | 147.84 | AB2-043 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.29 | 147.82 | AB2-043 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.02 | 147.63 | AB2-043 | PECO_P4_NOTTI85_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.96 | 147.61 | AB2-043 | PECO_P1-2_220-08_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.38 | 147.58 | AB2-043 | AP_P1-2_PE-500-001_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.38 | 147.58 | AB2-043 | AP_P1-2_WP-500-DRT17_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.89 | 147.55 | AB2-043 | PECO_P4_COOPR125_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.33 | 147.51 | AB2-043 | AP_P2-3_PE-500-018C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2901 | 145.61 | 147.88 | AB2-036 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 151.02 | 144.3 | AB2-043 | PECO_P4_PEACH025_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.88 | 144.21 | AB2-043 | PECO_P1-2_PBTIE1_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 139.25 | 133.31 | AB2-043 | PECO_P4_PEACH205_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 139.14 | 132.98 | AB2-043 | PECO_P1-2_PBTIE2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 138.19 | 132.1 | AB2-043 | PECO_P4_PEACH055_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 133.52 | 127.7 | AB2-043 | PECO_P4_PEACH015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 132.19 | 126.36 | AB2-043 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 123.09 | 117.72 | AB2-043 | PECO_P4_PEACH225_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 225.7 | 237.25 | AB2-047 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 223.69 | 237.25 | AB2-047 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 225.64 | 237.19 | AB2-047 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 223.63 | 237.19 | AB2-047 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 225.63 | 237.19 | AB2-047 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 223.63 | 237.19 | AB2-047 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 213.64 | 227.09 | AB2-047 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 213.58 | 227.03 | AB2-047 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 213.58 | 227.03 | AB2-047 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 209.38 | 223.88 | AB2-047 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 209.32 | 223.82 | AB2-047 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 209.32 | 223.82 | AB2-047 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2901 | 146.29 | 148.66 | AB2-037 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 153.68 | 158.16 | AB2-047 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.14 | 157.26 | AB2-047 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.13 | 157.26 | AB2-047 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 151.99 | 156.84 | AB2-047 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 161.58 | 154.36 | AB2-047 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 148.63 | 153.19 | AB2-047 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 155.71 | 150.56 | AB2-047 | PN_P1-2_PN-500-010T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.46 | 149.57 | AB2-047 | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.39 | 149.5 | AB2-047 | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.11 | 148.38 | AB2-047 | AP_P2-3_PE-500-016_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.18 | 148.35 | AB2-047 | AP_P2-3_PE-500-015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.02 | 147.9 | AB2-047 | PJM_500_BG_P4_5_CNSTN_L_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.26 | 147.83 | AB2-047 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.06 | 147.64 | AB2-047 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.09 | 147.63 | AB2-047 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.29 | 147.49 | AB2-047 | AP_P1-2_PE-500-001_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.29 | 147.49 | AB2-047 | AP_P1-2_WP-500-DRT17_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.82 | 147.43 | AB2-047 | PECO_P4_NOTTI85_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.24 | 147.42 | AB2-047 | AP_P2-3_PE-500-018C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.76 | 147.42 | AB2-047 | PECO_P1-2_220-08_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.69 | 147.35 | AB2-047 | PECO_P4_COOPR125_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2901 | 144.79 | 146.92 | AB2-040 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.77 | 144.06 | AB2-047 | PECO_P4_PEACH025_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.66 | 143.99 | AB2-047 | PECO_P1-2_PBTIE1_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 139.06 | 133.12 | AB2-047 | PECO_P4_PEACH205_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 138.93 | 132.78 | AB2-047 | PECO_P1-2_PBTIE2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 138 | 131.91 | AB2-047 | PECO_P4_PEACH055_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 133.31 | 127.49 | AB2-047 | PECO_P4_PEACH015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 131.99 | 126.17 | AB2-047 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 122.9 | 117.53 | AB2-047 | PECO_P4_PEACH225_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 225.73 | 237.23 | AB2-059 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 223.73 | 237.23 | AB2-059 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 225.67 | 237.17 | AB2-059 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 223.66 | 237.17 | AB2-059 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 225.67 | 237.17 | AB2-059 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 223.66 | 237.16 | AB2-059 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 213.67 | 227.07 | AB2-059 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 213.61 | 227.01 | AB2-059 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 213.61 | 227 | AB2-059 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 209.41 | 223.86 | AB2-059 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 209.35 | 223.8 | AB2-059 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 209.35 | 223.8 | AB2-059 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 172.86 | 167.9 | AB2-059 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2901 | 144.91 | 147.06 | AB2-043 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 153.63 | 158.1 | AB2-059 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.12 | 157.24 | AB2-059 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.12 | 157.24 | AB2-059 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 151.94 | 156.77 | AB2-059 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 161.6 | 154.38 | AB2-059 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 148.58 | 153.12 | AB2-059 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 155.69 | 150.54 | AB2-059 | PN_P1-2_PN-500-010T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.42 | 149.51 | AB2-059 | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.35 | 149.44 | AB2-059 | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.04 | 148.26 | AB2-059 | AP_P2-3_PE-500-016_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.1 | 148.24 | AB2-059 | AP_P2-3_PE-500-015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.01 | 147.88 | AB2-059 | PJM_500_BG_P4_5_CNSTN_L_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.29 | 147.85 | AB2-059 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.09 | 147.67 | AB2-059 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.12 | 147.65 | AB2-059 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.85 | 147.46 | AB2-059 | PECO_P4_NOTTI85_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.78 | 147.44 | AB2-059 | PECO_P1-2_220-08_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.22 | 147.38 | AB2-059 | AP_P1-2_WP-500-DRT17_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.22 | 147.38 | AB2-059 | AP_P1-2_PE-500-001_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.72 | 147.38 | AB2-059 | PECO_P4_COOPR125_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.17 | 147.32 | AB2-059 | AP_P2-3_PE-500-018C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2901 | 144.79 | 146.92 | AB2-047 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.82 | 144.11 | AB2-059 | PECO_P4_PEACH025_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.68 | 144.01 | AB2-059 | PECO_P1-2_PBTIE1_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 911 | 149.1 | 143.23 | AB2-059 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 139.07 | 133.13 | AB2-059 | PECO_P4_PEACH205_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 138.95 | 132.8 | AB2-059 | PECO_P1-2_PBTIE2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 138.02 | 131.93 | AB2-059 | PECO_P4_PEACH055_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 133.32 | 127.51 | AB2-059 | PECO_P4_PEACH015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 128.72 | 126.98 | AB2-059 | DVP_P4-2: 514T595_SRT-SW |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 132.01 | 126.18 | AB2-059 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 126.97 | 125.26 | AB2-059 | DVP_P4-2: 51482_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 126.97 | 125.17 | AB2-059 | DVP_P1-2: LN 514_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 126.97 | 125.17 | AB2-059 | AP_P1-2_PE-500-407T_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200025 | W CHAPEL | 1 | 500 | 225 | 1732 | 123.77 | 121.98 | AB2-059 | PEPCO_P4_PP41_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 122.91 | 117.54 | AB2-059 | PECO_P4_PEACH225_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 117.17 | 115.25 | AB2-059 | AP_P2-3_PE-500-019C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 99.58 | 103.53 | AB2-059 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 99.58 | 103.53 | AB2-059 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 99.58 | 103.53 | AB2-059 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 98.65 | 102.2 | AB2-059 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2901 | 144.74 | 146.86 | AB2-059 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 153.69 | 158.17 | AB2-060 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.18 | 157.3 | AB2-060 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.18 | 157.3 | AB2-060 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 152 | 156.85 | AB2-060 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 161.68 | 154.45 | AB2-060 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 148.64 | 153.19 | AB2-060 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 155.75 | 150.6 | AB2-060 | PN_P1-2_PN-500-010T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.48 | 149.58 | AB2-060 | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.41 | 149.5 | AB2-060 | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.1 | 148.33 | AB2-060 | AP_P2-3_PE-500-016_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.16 | 148.3 | AB2-060 | AP_P2-3_PE-500-015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.07 | 147.93 | AB2-060 | PJM_500_BG_P4_5_CNSTN_L_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.35 | 147.92 | AB2-060 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.15 | 147.73 | AB2-060 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.18 | 147.72 | AB2-060 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.91 | 147.52 | AB2-060 | PECO_P4_NOTTI85_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.85 | 147.51 | AB2-060 | PECO_P1-2_220-08_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.27 | 147.45 | AB2-060 | AP_P1-2_PE-500-001_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.27 | 147.45 | AB2-060 | AP_P1-2_WP-500-DRT17_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.78 | 147.44 | AB2-060 | PECO_P4_COOPR125_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.23 | 147.38 | AB2-060 | AP_P2-3_PE-500-018C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2901 | 144.8 | 146.93 | AB2-060 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.9 | 144.19 | AB2-060 | PECO_P4_PEACH025_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.75 | 144.08 | AB2-060 | PECO_P1-2_PBTIE1_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 139.13 | 133.19 | AB2-060 | PECO_P4_PEACH205_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 139.02 | 132.87 | AB2-060 | PECO_P1-2_PBTIE2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 138.08 | 131.99 | AB2-060 | PECO_P4_PEACH055_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 133.4 | 127.58 | AB2-060 | PECO_P4_PEACH015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 128.82 | 127.08 | AB2-060 | DVP_P4-2: 514T595_SRT-SW |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 132.07 | 126.25 | AB2-060 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 127.07 | 125.36 | AB2-060 | DVP_P4-2: 51482_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 127.07 | 125.27 | AB2-060 | DVP_P1-2: LN 514_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 127.07 | 125.27 | AB2-060 | AP_P1-2_PE-500-407T_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 122.98 | 117.6 | AB2-060 | PECO_P4_PEACH225_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 117.27 | 115.35 | AB2-060 | AP_P2-3_PE-500-019C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2901 | 144.85 | 146.98 | AB2-070 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 153.74 | 158.23 | AB2-070 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.2 | 157.33 | AB2-070 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.2 | 157.33 | AB2-070 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 152.05 | 156.91 | AB2-070 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 161.66 | 154.44 | AB2-070 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 148.69 | 153.26 | AB2-070 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 155.78 | 150.63 | AB2-070 | PN_P1-2_PN-500-010T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.52 | 149.63 | AB2-070 | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.45 | 149.56 | AB2-070 | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.16 | 148.43 | AB2-070 | AP_P2-3_PE-500-016_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.23 | 148.41 | AB2-070 | AP_P2-3_PE-500-015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.09 | 147.96 | AB2-070 | PJM_500_BG_P4_5_CNSTN_L_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.34 | 147.9 | AB2-070 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.14 | 147.72 | AB2-070 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.16 | 147.7 | AB2-070 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.34 | 147.55 | AB2-070 | AP_P1-2_WP-500-DRT17_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.34 | 147.55 | AB2-070 | AP_P1-2_PE-500-001_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.89 | 147.51 | AB2-070 | PECO_P4_NOTTI85_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.83 | 147.49 | AB2-070 | PECO_P1-2_220-08_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.29 | 147.48 | AB2-070 | AP_P2-3_PE-500-018C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.77 | 147.43 | AB2-070 | PECO_P4_COOPR125_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2901 | 144.93 | 147.08 | AB2-085 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.86 | 144.15 | AB2-070 | PECO_P4_PEACH025_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.75 | 144.07 | AB2-070 | PECO_P1-2_PBTIE1_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 139.13 | 133.2 | AB2-070 | PECO_P4_PEACH205_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 139.02 | 132.86 | AB2-070 | PECO_P1-2_PBTIE2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 138.08 | 131.99 | AB2-070 | PECO_P4_PEACH055_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 133.39 | 127.58 | AB2-070 | PECO_P4_PEACH015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 132.07 | 126.25 | AB2-070 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204512 | 27S.RDG | 204693 | 27BOONETOWN | 1 | 230 | 227 | 607 | 107.65 | 123.39 | AB2-070 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 122.97 | 117.6 | AB2-070 | PECO_P4_PEACH225_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2901 | 144.72 | 146.84 | AB2-100 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 153.82 | 158.33 | AB2-085 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.29 | 157.41 | AB2-085 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.28 | 157.41 | AB2-085 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 152.13 | 157 | AB2-085 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 161.77 | 154.54 | AB2-085 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 148.77 | 153.35 | AB2-085 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 155.86 | 150.71 | AB2-085 | PN_P1-2_PN-500-010T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.17 | 148.04 | AB2-085 | PJM_500_BG_P4_5_CNSTN_L_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.44 | 148 | AB2-085 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.23 | 147.81 | AB2-085 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.26 | 147.8 | AB2-085 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.99 | 147.6 | AB2-085 | PECO_P4_NOTTI85_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.93 | 147.59 | AB2-085 | PECO_P1-2_220-08_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.86 | 147.52 | AB2-085 | PECO_P4_COOPR125_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2901 | 145.42 | 147.65 | AB2-133 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 142.88 | 147 | AB2-085 | AP_P2-3_PE-500-014_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 142.88 | 146.99 | AB2-085 | AP_P2-3_WP-500-466_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 142.88 | 146.99 | AB2-085 | AP_P1-2_PE-500-004_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 142.88 | 146.99 | AB2-085 | AP_P2-3_WP-500-DRT19_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 142.88 | 146.99 | AB2-085 | AP_P1-2_WP-500-006_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.97 | 144.26 | AB2-085 | PECO_P4_PEACH025_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.86 | 144.18 | AB2-085 | PECO_P1-2_PBTIE1_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 141.2 | 143.95 | AB2-085 | BG_P7_GRNITE_HIRDG_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 138.97 | 141.26 | AB2-085 | AP_P2-3_WP-500-465_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 139.23 | 133.29 | AB2-085 | PECO_P4_PEACH205_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 139.12 | 132.96 | AB2-085 | PECO_P1-2_PBTIE2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 138.17 | 132.08 | AB2-085 | PECO_P4_PEACH055_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 133.5 | 127.68 | AB2-085 | PECO_P4_PEACH015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 132.17 | 126.35 | AB2-085 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 123.07 | 117.7 | AB2-085 | PECO_P4_PEACH225_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 223.7 | 237.19 | AB2-100 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 225.71 | 237.19 | AB2-100 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 223.64 | 237.13 | AB2-100 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 225.64 | 237.12 | AB2-100 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 223.64 | 237.12 | AB2-100 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 225.64 | 237.12 | AB2-100 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 213.65 | 227.02 | AB2-100 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 213.59 | 226.96 | AB2-100 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 213.58 | 226.96 | AB2-100 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 209.39 | 223.82 | AB2-100 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 209.33 | 223.75 | AB2-100 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 209.32 | 223.75 | AB2-100 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 172.84 | 167.87 | AB2-100 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2901 | 144.53 | 146.62 | AB2-134 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 161.85 | 161.95 | AB2-100 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 161.85 | 161.94 | AB2-100 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 161.84 | 161.94 | AB2-100 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 153.6 | 158.07 | AB2-100 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.1 | 157.22 | AB2-100 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.1 | 157.22 | AB2-100 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 151.92 | 156.75 | AB2-100 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 161.58 | 154.36 | AB2-100 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 148.56 | 153.09 | AB2-100 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 155.67 | 150.52 | AB2-100 | PN_P1-2_PN-500-010T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.4 | 149.48 | AB2-100 | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.33 | 149.41 | AB2-100 | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.02 | 148.23 | AB2-100 | AP_P2-3_PE-500-016_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.08 | 148.2 | AB2-100 | AP_P2-3_PE-500-015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.99 | 147.86 | AB2-100 | PJM_500_BG_P4_5_CNSTN_L_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.27 | 147.84 | AB2-100 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.07 | 147.65 | AB2-100 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.1 | 147.64 | AB2-100 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.83 | 147.44 | AB2-100 | PECO_P4_NOTTI85_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.77 | 147.43 | AB2-100 | PECO_P1-2_220-08_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.7 | 147.36 | AB2-100 | PECO_P4_COOPR125_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.19 | 147.35 | AB2-100 | AP_P1-2_PE-500-001_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.19 | 147.35 | AB2-100 | AP_P1-2_WP-500-DRT17_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.15 | 147.28 | AB2-100 | AP_P2-3_PE-500-018C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2901 | 145.46 | 147.69 | AB2-135 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.81 | 144.1 | AB2-100 | PECO_P4_PEACH025_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.66 | 143.99 | AB2-100 | PECO_P1-2_PBTIE1_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 911 | 149.07 | 143.2 | AB2-100 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 1031 | 130.39 | 138.21 | AB2-100 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 139.05 | 133.11 | AB2-100 | PECO_P4_PEACH205_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 138.94 | 132.79 | AB2-100 | PECO_P1-2_PBTIE2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 138 | 131.92 | AB2-100 | PECO_P4_PEACH055_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 133.3 | 127.49 | AB2-100 | PECO_P4_PEACH015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 128.65 | 126.96 | AB2-100 | DVP_P4-2: 514T595_SRT-SW |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 131.99 | 126.17 | AB2-100 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 126.9 | 125.18 | AB2-100 | DVP_P4-2: 51482_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 126.9 | 125.09 | AB2-100 | DVP_P1-2: LN 514_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 126.9 | 125.09 | AB2-100 | AP_P1-2_PE-500-407T_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208020 | MANO TR3 | 1 | 230 | 229 | 793 | 111.58 | 124.77 | AB2-100 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208020 | MANO TR3 | 1 | 230 | 229 | 793 | 111.57 | 124.77 | AB2-100 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208020 | MANO TR3 | 1 | 230 | 229 | 793 | 111.58 | 124.77 | AB2-100 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200025 | W CHAPEL | 1 | 500 | 225 | 1732 | 123.74 | 121.95 | AB2-100 | PEPCO_P4_PP41_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 122.89 | 117.52 | AB2-100 | PECO_P4_PEACH225_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 117.1 | 115.18 | AB2-100 | AP_P2-3_PE-500-019C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 2 | 500/230 | 225/232 | 2168 | 109.72 | 115.04 | AB2-100 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 1 | 500/230 | 225/232 | 2168 | 109.48 | 114.8 | AB2-100 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 99.56 | 103.51 | AB2-100 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 99.56 | 103.5 | AB2-100 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 99.56 | 103.5 | AB2-100 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 98.63 | 102.18 | AB2-100 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 98.73 | 100.8 | AB2-100 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 228.17 | 240.51 | AB2-133 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 226.13 | 240.51 | AB2-133 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 215.99 | 230.24 | AB2-133 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 211.73 | 227.06 | AB2-133 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 212.34 | 219.95 | AB2-133 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 210.29 | 219.95 | AB2-133 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 200.7 | 210.31 | AB2-133 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 196.44 | 206.98 | AB2-133 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 172.59 | 167.42 | AB2-133 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 172.59 | 167.41 | AB2-133 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 172.57 | 167.4 | AB2-133 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2901 | 145.4 | 147.63 | AB2-136 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 154.32 | 158.92 | AB2-133 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.87 | 157.99 | AB2-133 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.87 | 157.99 | AB2-133 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 152.63 | 157.6 | AB2-133 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 162.6 | 155.34 | AB2-133 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 149.26 | 153.95 | AB2-133 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 156.45 | 151.29 | AB2-133 | PN_P1-2_PN-500-010T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 147.08 | 150.29 | AB2-133 | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 147.01 | 150.22 | AB2-133 | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.67 | 149.02 | AB2-133 | AP_P2-3_PE-500-016_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.73 | 148.99 | AB2-133 | AP_P2-3_PE-500-015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 154.16 | 148.7 | AB2-133 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.73 | 148.59 | AB2-133 | PJM_500_BG_P4_5_CNSTN_L_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.96 | 148.52 | AB2-133 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.98 | 148.5 | AB2-133 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.71 | 148.31 | AB2-133 | PECO_P4_NOTTI85_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.65 | 148.29 | AB2-133 | PECO_P1-2_220-08_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.58 | 148.23 | AB2-133 | PECO_P4_COOPR125_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.85 | 148.14 | AB2-133 | AP_P1-2_PE-500-001_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.85 | 148.14 | AB2-133 | AP_P1-2_WP-500-DRT17_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.8 | 148.07 | AB2-133 | AP_P2-3_PE-500-018C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2901 | 144.67 | 146.78 | AB2-158 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 151.97 | 145.21 | AB2-133 | PECO_P4_PEACH025_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 151.75 | 145.04 | AB2-133 | PECO_P1-2_PBTIE1_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 911 | 148.83 | 142.83 | AB2-133 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 911 | 148.83 | 142.82 | AB2-133 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 911 | 148.81 | 142.81 | AB2-133 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 139.89 | 133.93 | AB2-133 | PECO_P4_PEACH205_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 139.94 | 133.75 | AB2-133 | PECO_P1-2_PBTIE2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 138.97 | 132.85 | AB2-133 | PECO_P4_PEACH055_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 134.39 | 128.53 | AB2-133 | PECO_P4_PEACH015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 132.98 | 127.11 | AB2-133 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200025 | W CHAPEL | 1 | 500 | 225 | 1732 | 124.36 | 122.6 | AB2-133 | PEPCO_P4_PP41_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 123.89 | 118.48 | AB2-133 | PECO_P4_PEACH225_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 118.42 | 116.8 | AB2-133 | PECO_P4_PEACH205_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 116.38 | 116.8 | AB2-133 | PECO_P4_PEACH205_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 117.98 | 116.4 | AB2-133 | PECO_P1-2_5014_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 115.94 | 116.4 | AB2-133 | PECO_P1-2_5014_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 115.54 | 115.74 | AB2-133 | PECO_P4_PEACH215_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 117.58 | 115.74 | AB2-133 | PECO_P4_PEACH215_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 110.02 | 110.57 | AB2-133 | PECO_P4_PEACH205_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 109.6 | 110.18 | AB2-133 | PECO_P1-2_5014_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 109.21 | 109.54 | AB2-133 | PECO_P4_PEACH215_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 105.75 | 106.86 | AB2-133 | PECO_P4_PEACH205_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 105.33 | 106.47 | AB2-133 | PECO_P1-2_5014_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 106.68 | 106.01 | AB2-133 | PECO_P1-2_5025/* $ CHESCO $ PECO_P1-2_5025 $ L_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 104.64 | 106.01 | AB2-133 | PECO_P1-2_5025/* $ CHESCO $ PECO_P1-2_5025 $ L_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 104.94 | 105.84 | AB2-133 | PECO_P4_PEACH215_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 106.22 | 105.54 | AB2-133 | PJM500_DPL_P4_2_KEENEY-ROCK AT51_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 106.22 | 105.54 | AB2-133 | PJM500_DPL_P4_2_KEENEY-ROCK AT50_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 104.18 | 105.54 | AB2-133 | PJM500_DPL_P4_2_KEENEY-ROCK AT50_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 104.18 | 105.54 | AB2-133 | PJM500_DPL_P4_2_KEENEY-ROCK AT51_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 98.69 | 100.13 | AB2-133 | PECO_P1-2_5025/* $ CHESCO $ PECO_P1-2_5025 $ L_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 225.43 | 236.74 | AB2-134 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 223.43 | 236.74 | AB2-134 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 225.37 | 236.68 | AB2-134 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 223.37 | 236.68 | AB2-134 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 225.37 | 236.68 | AB2-134 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 223.37 | 236.68 | AB2-134 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 213.39 | 226.59 | AB2-134 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 213.33 | 226.53 | AB2-134 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 213.32 | 226.53 | AB2-134 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 209.13 | 223.38 | AB2-134 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 209.07 | 223.32 | AB2-134 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 209.07 | 223.32 | AB2-134 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 210.54 | 217.58 | AB2-134 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 208.53 | 217.58 | AB2-134 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 199 | 208.02 | AB2-134 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 194.74 | 204.67 | AB2-134 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 172.63 | 167.65 | AB2-134 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 171.67 | 166.21 | AB2-134 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 171.67 | 166.21 | AB2-134 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 171.65 | 166.2 | AB2-134 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 163.5 | 164.75 | AB2-134 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2901 | 144.77 | 146.9 | AB2-160 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 161.64 | 161.67 | AB2-134 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 161.64 | 161.67 | AB2-134 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 161.62 | 161.66 | AB2-134 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 163.72 | 158.75 | AB2-134 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 153.41 | 157.84 | AB2-134 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 161.92 | 157.04 | AB2-134 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 161.92 | 157.04 | AB2-134 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 151.73 | 156.52 | AB2-134 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 161.38 | 154.17 | AB2-134 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 148.37 | 152.87 | AB2-134 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 903 | 144.15 | 151.97 | AB2-134 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 152.7 | 151.05 | AB2-134 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 155.5 | 150.35 | AB2-134 | PN_P1-2_PN-500-010T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 903 | 142.63 | 149.36 | AB2-134 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 903 | 142.62 | 149.35 | AB2-134 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 903 | 142.61 | 149.35 | AB2-134 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.21 | 149.27 | AB2-134 | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.14 | 149.2 | AB2-134 | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.83 | 148.01 | AB2-134 | AP_P2-3_PE-500-016_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.89 | 147.98 | AB2-134 | AP_P2-3_PE-500-015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.81 | 147.68 | AB2-134 | PJM_500_BG_P4_5_CNSTN_L_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.1 | 147.67 | AB2-134 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.9 | 147.48 | AB2-134 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.92 | 147.47 | AB2-134 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.65 | 147.27 | AB2-134 | PECO_P4_NOTTI85_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.59 | 147.25 | AB2-134 | PECO_P1-2_220-08_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.53 | 147.19 | AB2-134 | PECO_P4_COOPR125_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.01 | 147.13 | AB2-134 | AP_P1-2_PE-500-001_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.01 | 147.13 | AB2-134 | AP_P1-2_WP-500-DRT17_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 142.96 | 147.07 | AB2-134 | AP_P2-3_PE-500-018C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2901 | 144.89 | 147.04 | AB2-161 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.61 | 143.91 | AB2-134 | PECO_P4_PEACH025_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.44 | 143.79 | AB2-134 | PECO_P1-2_PBTIE1_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 911 | 148.88 | 143.01 | AB2-134 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204502 | 27JACKSON | 204514 | 27TMI | 1 | 230 | 227 | 781 | 132.98 | 141.48 | AB2-134 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204502 | 27JACKSON | 204514 | 27TMI | 1 | 230 | 227 | 781 | 132.98 | 141.48 | AB2-134 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204502 | 27JACKSON | 204514 | 27TMI | 1 | 230 | 227 | 781 | 132.96 | 141.47 | AB2-134 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 903 | 135.55 | 139.49 | AB2-134 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 1031 | 130.26 | 137.97 | AB2-134 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 1031 | 130.26 | 137.97 | AB2-134 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 1031 | 130.25 | 137.97 | AB2-134 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 911 | 140.06 | 134.96 | AB2-134 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 138.85 | 132.93 | AB2-134 | PECO_P4_PEACH205_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 138.74 | 132.6 | AB2-134 | PECO_P1-2_PBTIE2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208078 | SAKR | 1 | 230 | 229 | 903 | 124.42 | 132.38 | AB2-134 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208078 | SAKR | 1 | 230 | 229 | 903 | 124.42 | 132.38 | AB2-134 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208078 | SAKR | 1 | 230 | 229 | 903 | 124.42 | 132.38 | AB2-134 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 137.81 | 131.74 | AB2-134 | PECO_P4_PEACH055_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204502 | 27JACKSON | 204514 | 27TMI | 1 | 230 | 227 | 781 | 125.33 | 130.91 | AB2-134 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 1031 | 124.66 | 129.16 | AB2-134 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 133.09 | 127.28 | AB2-134 | PECO_P4_PEACH015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 128.27 | 126.55 | AB2-134 | DVP_P4-2: 514T595_SRT-SW |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 131.79 | 125.98 | AB2-134 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220953 | HOWARD12 | 220972 | GRANITE1 | 1 | 230 | 232 | 772 | 129.55 | 125.57 | AB2-134 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 126.51 | 124.77 | AB2-134 | DVP_P4-2: 51482_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 793 | 126.47 | 124.72 | AB2-134 | DVP_P4-2: 514T595_SRT-SW |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 2 | 230 | 233 | 793 | 126.47 | 124.72 | AB2-134 | DVP_P4-2: 514T595_SRT-SW |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 126.51 | 124.68 | AB2-134 | DVP_P1-2: LN 514_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 126.51 | 124.68 | AB2-134 | AP_P1-2_PE-500-407T_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208020 | MANO TR3 | 1 | 230 | 229 | 793 | 111.41 | 124.56 | AB2-134 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208020 | MANO TR3 | 1 | 230 | 229 | 793 | 111.41 | 124.56 | AB2-134 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208020 | MANO TR3 | 1 | 230 | 229 | 793 | 111.41 | 124.56 | AB2-134 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 793 | 125.21 | 123.46 | AB2-134 | DVP_P4-2: 51482_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 2 | 230 | 233 | 793 | 125.21 | 123.46 | AB2-134 | DVP_P4-2: 51482_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 793 | 125.21 | 123.38 | AB2-134 | AP_P1-2_PE-500-407T_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 2 | 230 | 233 | 793 | 125.21 | 123.38 | AB2-134 | DVP_P1-2: LN 514_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 793 | 125.21 | 123.38 | AB2-134 | DVP_P1-2: LN 514_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 2 | 230 | 233 | 793 | 125.21 | 123.38 | AB2-134 | AP_P1-2_PE-500-407T_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208078 | SAKR | 1 | 230 | 229 | 903 | 117.16 | 122.4 | AB2-134 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200025 | W CHAPEL | 1 | 500 | 225 | 1732 | 123.56 | 121.77 | AB2-134 | PEPCO_P4_PP41_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208031 | MLWD TR2 | 1 | 230 | 229 | 911 | 111.72 | 121.13 | AB2-134 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208031 | MLWD TR2 | 1 | 230 | 229 | 911 | 111.72 | 121.13 | AB2-134 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208031 | MLWD TR2 | 1 | 230 | 229 | 911 | 111.72 | 121.13 | AB2-134 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220965 | NEAST339 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 119.71 | 119.06 | AB2-134 | BG_P1_2315_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220965 | NEAST339 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 119.29 | 118.85 | AB2-134 | BG_P4_5_NEAST_17_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220965 | NEAST339 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 119.44 | 118.85 | AB2-134 | BG_P4_5_NEAST_15_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 114.66 | 118.35 | AB2-134 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220979 | NEAST317 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 118.79 | 118.19 | AB2-134 | BG_P1_2337_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 114.32 | 118.01 | AB2-134 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 114.3 | 117.95 | AB2-134 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 114.3 | 117.95 | AB2-134 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220979 | NEAST317 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 118.46 | 117.92 | AB2-134 | BG_P4_5_NEAST_39_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220979 | NEAST317 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 118.46 | 117.92 | AB2-134 | BG_P4_5_NEAST_37_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 113.97 | 117.61 | AB2-134 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 113.97 | 117.61 | AB2-134 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 122.7 | 117.34 | AB2-134 | PECO_P4_PEACH225_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 793 | 118.55 | 115.77 | AB2-134 | PEPCO_P1_PP2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 2 | 230 | 233 | 793 | 118.55 | 115.77 | AB2-134 | PEPCO_P1_PP1_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 2 | 500/230 | 225/232 | 2168 | 109.61 | 114.92 | AB2-134 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 116.72 | 114.77 | AB2-134 | AP_P2-3_PE-500-019C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 2 | 500/230 | 225/232 | 2168 | 109.44 | 114.7 | AB2-134 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 2 | 500/230 | 225/232 | 2168 | 109.43 | 114.7 | AB2-134 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 1 | 500/230 | 225/232 | 2168 | 109.38 | 114.67 | AB2-134 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 1 | 500/230 | 225/232 | 2168 | 109.2 | 114.46 | AB2-134 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 1 | 500/230 | 225/232 | 2168 | 109.2 | 114.46 | AB2-134 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220964 | GRACETON | 220999 | BAGLEY2 | 13 | 230 | 232 | 1795 | 113.39 | 114.42 | AB2-134 | BG_P4_5_GRCTN_3T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208020 | MANO TR3 | 1 | 230 | 229 | 793 | 104.23 | 113.98 | AB2-134 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208020 | MANO TR3 | 208031 | MLWD TR2 | 1 | 230 | 229 | 903 | 102.54 | 113.68 | AB2-134 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208020 | MANO TR3 | 208031 | MLWD TR2 | 1 | 230 | 229 | 903 | 101.83 | 112.49 | AB2-134 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208020 | MANO TR3 | 208031 | MLWD TR2 | 1 | 230 | 229 | 903 | 101.83 | 112.49 | AB2-134 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208020 | MANO TR3 | 208031 | MLWD TR2 | 1 | 230 | 229 | 903 | 101.83 | 112.49 | AB2-134 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 2 | 500/230 | 225/232 | 2168 | 108.48 | 111.77 | AB2-134 | PJM_500_BG_P4_5_CNSTN_15_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208031 | MLWD TR2 | 1 | 230 | 229 | 911 | 104.96 | 111.63 | AB2-134 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 106.44 | 111.2 | AB2-134 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220980 | RAPHAEL | 220999 | BAGLEY2 | 13 | 230 | 232 | 1795 | 108.97 | 111.18 | AB2-134 | BG_P4_5_GRCTN_3T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 106.31 | 111.07 | AB2-134 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 793 | 112.69 | 110.02 | AB2-134 | PEPCO_P4_PP19_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 793 | 109.44 | 107.52 | AB2-134 | AP_P2-3_PE-500-019C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 2 | 230 | 233 | 793 | 109.44 | 107.52 | AB2-134 | AP_P2-3_PE-500-019C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220965 | NEAST339 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 108.26 | 106.84 | AB2-134 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220965 | NEAST339 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 108.17 | 106.73 | AB2-134 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220965 | NEAST339 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 108.17 | 106.73 | AB2-134 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220979 | NEAST317 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 105.16 | 103.79 | AB2-134 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 99.46 | 103.34 | AB2-134 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 99.46 | 103.34 | AB2-134 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 99.46 | 103.34 | AB2-134 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208020 | MANO TR3 | 208031 | MLWD TR2 | 1 | 230 | 229 | 903 | 95.46 | 103.25 | AB2-134 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220964 | GRACETON | 221000 | BAGLEY | 5 | 230 | 232 | 1795 | 101.45 | 102.2 | AB2-134 | BG_P1_2313_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220964 | GRACETON | 220999 | BAGLEY2 | 13 | 230 | 232 | 1795 | 101.45 | 102.2 | AB2-134 | BG_P1_2305_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 98.53 | 102.01 | AB2-134 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 98.63 | 100.65 | AB2-134 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 228.26 | 240.66 | AB2-135 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 226.22 | 240.65 | AB2-135 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 216.07 | 230.39 | AB2-135 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 211.81 | 227.2 | AB2-135 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 212.42 | 220.04 | AB2-135 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 210.38 | 220.04 | AB2-135 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 200.79 | 210.41 | AB2-135 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 196.52 | 207.08 | AB2-135 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 172.63 | 167.46 | AB2-135 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 172.63 | 167.46 | AB2-135 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 172.61 | 167.45 | AB2-135 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2901 | 144.82 | 146.95 | AB2-169 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 154.36 | 158.97 | AB2-135 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.92 | 158.04 | AB2-135 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.92 | 158.04 | AB2-135 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 152.66 | 157.64 | AB2-135 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 162.66 | 155.4 | AB2-135 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 149.3 | 153.99 | AB2-135 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 156.5 | 151.34 | AB2-135 | PN_P1-2_PN-500-010T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 147.12 | 150.34 | AB2-135 | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 147.05 | 150.26 | AB2-135 | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.7 | 149.06 | AB2-135 | AP_P2-3_PE-500-016_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.77 | 149.03 | AB2-135 | AP_P2-3_PE-500-015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 154.21 | 148.76 | AB2-135 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.77 | 148.63 | AB2-135 | PJM_500_BG_P4_5_CNSTN_L_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 154.01 | 148.57 | AB2-135 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 154.04 | 148.56 | AB2-135 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.77 | 148.36 | AB2-135 | PECO_P4_NOTTI85_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.71 | 148.35 | AB2-135 | PECO_P1-2_220-08_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.64 | 148.28 | AB2-135 | PECO_P4_COOPR125_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.88 | 148.17 | AB2-135 | AP_P1-2_PE-500-001_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.88 | 148.17 | AB2-135 | AP_P1-2_WP-500-DRT17_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.83 | 148.1 | AB2-135 | AP_P2-3_PE-500-018C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2901 | 145.39 | 147.62 | AB2-172 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 152.05 | 145.29 | AB2-135 | PECO_P4_PEACH025_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 151.82 | 145.11 | AB2-135 | PECO_P1-2_PBTIE1_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 911 | 148.87 | 142.86 | AB2-135 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 911 | 148.86 | 142.86 | AB2-135 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 911 | 148.85 | 142.86 | AB2-135 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208078 | SAKR | 1 | 230 | 229 | 903 | 125.99 | 134.81 | AB2-135 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 139.94 | 133.98 | AB2-135 | PECO_P4_PEACH205_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 140.01 | 133.82 | AB2-135 | PECO_P1-2_PBTIE2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 139.04 | 132.92 | AB2-135 | PECO_P4_PEACH055_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 134.46 | 128.6 | AB2-135 | PECO_P4_PEACH015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 133.04 | 127.17 | AB2-135 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200025 | W CHAPEL | 1 | 500 | 225 | 1732 | 124.4 | 122.63 | AB2-135 | PEPCO_P4_PP41_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 123.96 | 118.55 | AB2-135 | PECO_P4_PEACH225_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 118.49 | 116.88 | AB2-135 | PECO_P4_PEACH205_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 116.45 | 116.88 | AB2-135 | PECO_P4_PEACH205_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 118.06 | 116.47 | AB2-135 | PECO_P1-2_5014_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 116.02 | 116.47 | AB2-135 | PECO_P1-2_5014_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 117.66 | 115.81 | AB2-135 | PECO_P4_PEACH215_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 115.61 | 115.81 | AB2-135 | PECO_P4_PEACH215_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 2 | 500/230 | 225/232 | 2168 | 109.95 | 115.29 | AB2-135 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 2 | 500/230 | 225/232 | 2168 | 109.95 | 115.29 | AB2-135 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 1 | 500/230 | 225/232 | 2168 | 109.72 | 115.05 | AB2-135 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 1 | 500/230 | 225/232 | 2168 | 109.72 | 115.05 | AB2-135 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 110.09 | 110.64 | AB2-135 | PECO_P4_PEACH205_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 109.67 | 110.25 | AB2-135 | PECO_P1-2_5014_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 109.28 | 109.61 | AB2-135 | PECO_P4_PEACH215_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 105.83 | 106.93 | AB2-135 | PECO_P4_PEACH205_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 105.41 | 106.54 | AB2-135 | PECO_P1-2_5014_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 106.76 | 106.08 | AB2-135 | PECO_P1-2_5025/* $ CHESCO $ PECO_P1-2_5025 $ L_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 104.72 | 106.08 | AB2-135 | PECO_P1-2_5025/* $ CHESCO $ PECO_P1-2_5025 $ L_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 105.02 | 105.91 | AB2-135 | PECO_P4_PEACH215_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 106.3 | 105.61 | AB2-135 | PJM500_DPL_P4_2_KEENEY-ROCK AT50_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 106.3 | 105.61 | AB2-135 | PJM500_DPL_P4_2_KEENEY-ROCK AT51_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 104.26 | 105.61 | AB2-135 | PJM500_DPL_P4_2_KEENEY-ROCK AT50_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 104.26 | 105.61 | AB2-135 | PJM500_DPL_P4_2_KEENEY-ROCK AT51_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 98.76 | 100.21 | AB2-135 | PECO_P1-2_5025/* $ CHESCO $ PECO_P1-2_5025 $ L_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 228.03 | 240.35 | AB2-136 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 226 | 240.34 | AB2-136 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 215.86 | 230.08 | AB2-136 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 211.6 | 226.9 | AB2-136 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 212.2 | 219.79 | AB2-136 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 210.16 | 219.79 | AB2-136 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 200.57 | 210.17 | AB2-136 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 196.31 | 206.83 | AB2-136 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2901 | 144.79 | 146.92 | AB2-174 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 154.3 | 158.9 | AB2-136 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.85 | 157.97 | AB2-136 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.85 | 157.97 | AB2-136 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 152.61 | 157.58 | AB2-136 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 162.57 | 155.31 | AB2-136 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 149.24 | 153.93 | AB2-136 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 156.43 | 151.27 | AB2-136 | PN_P1-2_PN-500-010T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 147.06 | 150.27 | AB2-136 | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.99 | 150.2 | AB2-136 | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.65 | 149 | AB2-136 | AP_P2-3_PE-500-016_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.72 | 148.97 | AB2-136 | AP_P2-3_PE-500-015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 154.13 | 148.67 | AB2-136 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.71 | 148.57 | AB2-136 | PJM_500_BG_P4_5_CNSTN_L_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.93 | 148.49 | AB2-136 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.95 | 148.47 | AB2-136 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.68 | 148.28 | AB2-136 | PECO_P4_NOTTI85_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.62 | 148.26 | AB2-136 | PECO_P1-2_220-08_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.55 | 148.2 | AB2-136 | PECO_P4_COOPR125_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.83 | 148.12 | AB2-136 | AP_P1-2_PE-500-001_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.83 | 148.12 | AB2-136 | AP_P1-2_WP-500-DRT17_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.78 | 148.05 | AB2-136 | AP_P2-3_PE-500-018C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2901 | 145.37 | 147.59 | AB2-179 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 151.93 | 145.18 | AB2-136 | PECO_P4_PEACH025_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 151.72 | 145.01 | AB2-136 | PECO_P1-2_PBTIE1_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 911 | 148.82 | 142.81 | AB2-136 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 911 | 148.82 | 142.81 | AB2-136 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 911 | 148.81 | 142.8 | AB2-136 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 139.87 | 133.9 | AB2-136 | PECO_P4_PEACH205_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 139.91 | 133.72 | AB2-136 | PECO_P1-2_PBTIE2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 138.95 | 132.83 | AB2-136 | PECO_P4_PEACH055_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 134.36 | 128.5 | AB2-136 | PECO_P4_PEACH015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 132.95 | 127.08 | AB2-136 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 123.86 | 118.45 | AB2-136 | PECO_P4_PEACH225_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2901 | 144.47 | 146.55 | AB2-190 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.61 | 157.73 | AB2-153 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.6 | 157.73 | AB2-153 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 162.21 | 154.97 | AB2-153 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 156.18 | 151.02 | AB2-153 | PN_P1-2_PN-500-010T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.82 | 148.38 | AB2-153 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.48 | 148.34 | AB2-153 | PJM_500_BG_P4_5_CNSTN_L_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.62 | 148.19 | AB2-153 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.65 | 148.18 | AB2-153 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.38 | 147.98 | AB2-153 | PECO_P4_NOTTI85_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.32 | 147.97 | AB2-153 | PECO_P1-2_220-08_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.25 | 147.9 | AB2-153 | PECO_P4_COOPR125_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 151.48 | 144.75 | AB2-153 | PECO_P4_PEACH025_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 151.33 | 144.63 | AB2-153 | PECO_P1-2_PBTIE1_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 139.55 | 133.38 | AB2-153 | PECO_P1-2_PBTIE2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 138.59 | 132.48 | AB2-153 | PECO_P4_PEACH055_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 133.96 | 128.12 | AB2-153 | PECO_P4_PEACH015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 132.59 | 126.74 | AB2-153 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 123.5 | 118.1 | AB2-153 | PECO_P4_PEACH225_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 223.66 | 237.1 | AB2-158 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 225.66 | 237.1 | AB2-158 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 223.59 | 237.04 | AB2-158 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 225.6 | 237.04 | AB2-158 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 223.59 | 237.03 | AB2-158 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 225.59 | 237.03 | AB2-158 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 213.6 | 226.94 | AB2-158 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 213.54 | 226.88 | AB2-158 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 213.54 | 226.87 | AB2-158 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 209.34 | 223.73 | AB2-158 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 209.28 | 223.67 | AB2-158 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 209.28 | 223.66 | AB2-158 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 210.76 | 217.89 | AB2-158 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 208.75 | 217.89 | AB2-158 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 199.21 | 208.32 | AB2-158 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 194.95 | 204.97 | AB2-158 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 172.79 | 167.81 | AB2-158 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 163.66 | 164.97 | AB2-158 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2901 | 144.83 | 146.96 | AC1-034 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 161.8 | 161.87 | AB2-158 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 161.8 | 161.87 | AB2-158 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 161.79 | 161.86 | AB2-158 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 153.55 | 158.01 | AB2-158 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.06 | 157.18 | AB2-158 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.06 | 157.18 | AB2-158 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 151.87 | 156.68 | AB2-158 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 161.55 | 154.33 | AB2-158 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 148.51 | 153.03 | AB2-158 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 152.86 | 151.24 | AB2-158 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 155.63 | 150.48 | AB2-158 | PN_P1-2_PN-500-010T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 903 | 142.76 | 149.57 | AB2-158 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 903 | 142.76 | 149.57 | AB2-158 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 903 | 142.74 | 149.56 | AB2-158 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.35 | 149.42 | AB2-158 | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.28 | 149.35 | AB2-158 | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.96 | 148.16 | AB2-158 | AP_P2-3_PE-500-016_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.03 | 148.13 | AB2-158 | AP_P2-3_PE-500-015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.95 | 147.82 | AB2-158 | PJM_500_BG_P4_5_CNSTN_L_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.24 | 147.81 | AB2-158 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.04 | 147.62 | AB2-158 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.07 | 147.61 | AB2-158 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.8 | 147.41 | AB2-158 | PECO_P4_NOTTI85_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.74 | 147.4 | AB2-158 | PECO_P1-2_220-08_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.67 | 147.33 | AB2-158 | PECO_P4_COOPR125_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.14 | 147.28 | AB2-158 | AP_P1-2_WP-500-DRT17_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.14 | 147.28 | AB2-158 | AP_P1-2_PE-500-001_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.09 | 147.22 | AB2-158 | AP_P2-3_PE-500-018C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2901 | 144.65 | 146.76 | AC1-043 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.78 | 144.07 | AB2-158 | PECO_P4_PEACH025_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.62 | 143.95 | AB2-158 | PECO_P1-2_PBTIE1_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 911 | 149.03 | 143.14 | AB2-158 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 903 | 135.68 | 139.67 | AB2-158 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 1031 | 130.37 | 138.16 | AB2-158 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 1031 | 130.37 | 138.16 | AB2-158 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 1031 | 130.36 | 138.16 | AB2-158 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 139.01 | 133.07 | AB2-158 | PECO_P4_PEACH205_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 138.9 | 132.75 | AB2-158 | PECO_P1-2_PBTIE2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208078 | SAKR | 1 | 230 | 229 | 903 | 124.55 | 132.6 | AB2-158 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208078 | SAKR | 1 | 230 | 229 | 903 | 124.55 | 132.6 | AB2-158 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208078 | SAKR | 1 | 230 | 229 | 903 | 124.55 | 132.6 | AB2-158 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 137.97 | 131.88 | AB2-158 | PECO_P4_PEACH055_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 133.26 | 127.45 | AB2-158 | PECO_P4_PEACH015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 128.42 | 126.67 | AB2-158 | DVP_P4-2: 514T595_SRT-SW |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 131.95 | 126.14 | AB2-158 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 126.67 | 124.95 | AB2-158 | DVP_P4-2: 51482_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 126.67 | 124.85 | AB2-158 | DVP_P1-2: LN 514_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 126.67 | 124.85 | AB2-158 | AP_P1-2_PE-500-407T_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 2 | 230 | 233 | 793 | 126.58 | 124.81 | AB2-158 | DVP_P4-2: 514T595_SRT-SW |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 793 | 126.58 | 124.81 | AB2-158 | DVP_P4-2: 514T595_SRT-SW |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208020 | MANO TR3 | 1 | 230 | 229 | 793 | 111.54 | 124.71 | AB2-158 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208020 | MANO TR3 | 1 | 230 | 229 | 793 | 111.54 | 124.71 | AB2-158 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208020 | MANO TR3 | 1 | 230 | 229 | 793 | 111.54 | 124.71 | AB2-158 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 793 | 125.33 | 123.6 | AB2-158 | DVP_P4-2: 51482_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 2 | 230 | 233 | 793 | 125.33 | 123.6 | AB2-158 | DVP_P4-2: 51482_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 793 | 125.33 | 123.52 | AB2-158 | AP_P1-2_PE-500-407T_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 2 | 230 | 233 | 793 | 125.33 | 123.52 | AB2-158 | DVP_P1-2: LN 514_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 2 | 230 | 233 | 793 | 125.33 | 123.52 | AB2-158 | AP_P1-2_PE-500-407T_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 793 | 125.33 | 123.52 | AB2-158 | DVP_P1-2: LN 514_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200025 | W CHAPEL | 1 | 500 | 225 | 1732 | 123.69 | 121.91 | AB2-158 | PEPCO_P4_PP41_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 122.85 | 117.48 | AB2-158 | PECO_P4_PEACH225_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 2 | 500/230 | 225/232 | 2168 | 109.69 | 115 | AB2-158 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 116.88 | 114.94 | AB2-158 | AP_P2-3_PE-500-019C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 2 | 500/230 | 225/232 | 2168 | 109.51 | 114.79 | AB2-158 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 2 | 500/230 | 225/232 | 2168 | 109.51 | 114.79 | AB2-158 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 1 | 500/230 | 225/232 | 2168 | 109.46 | 114.76 | AB2-158 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 1 | 500/230 | 225/232 | 2168 | 109.28 | 114.55 | AB2-158 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 1 | 500/230 | 225/232 | 2168 | 109.28 | 114.55 | AB2-158 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 793 | 112.81 | 110.19 | AB2-158 | PEPCO_P4_PP19_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 2 | 230 | 233 | 793 | 109.55 | 107.65 | AB2-158 | AP_P2-3_PE-500-019C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 793 | 109.55 | 107.65 | AB2-158 | AP_P2-3_PE-500-019C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 99.52 | 103.45 | AB2-158 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 99.52 | 103.45 | AB2-158 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 99.52 | 103.44 | AB2-158 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 98.59 | 102.12 | AB2-158 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 98.69 | 100.74 | AB2-158 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2901 | 144.85 | 146.98 | AC1-053 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 153.66 | 158.13 | AB2-160 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.16 | 157.28 | AB2-160 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.15 | 157.28 | AB2-160 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 151.97 | 156.81 | AB2-160 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 161.65 | 154.43 | AB2-160 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 148.61 | 153.16 | AB2-160 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 155.73 | 150.58 | AB2-160 | PN_P1-2_PN-500-010T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.45 | 149.54 | AB2-160 | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.38 | 149.47 | AB2-160 | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.06 | 148.29 | AB2-160 | AP_P2-3_PE-500-016_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.13 | 148.26 | AB2-160 | AP_P2-3_PE-500-015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.04 | 147.91 | AB2-160 | PJM_500_BG_P4_5_CNSTN_L_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.33 | 147.9 | AB2-160 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.13 | 147.71 | AB2-160 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.16 | 147.7 | AB2-160 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.89 | 147.5 | AB2-160 | PECO_P4_NOTTI85_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.83 | 147.49 | AB2-160 | PECO_P1-2_220-08_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.76 | 147.42 | AB2-160 | PECO_P4_COOPR125_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.24 | 147.41 | AB2-160 | AP_P1-2_PE-500-001_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.24 | 147.41 | AB2-160 | AP_P1-2_WP-500-DRT17_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.19 | 147.34 | AB2-160 | AP_P2-3_PE-500-018C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2901 | 144.86 | 146.99 | AC1-054 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.88 | 144.17 | AB2-160 | PECO_P4_PEACH025_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.73 | 144.06 | AB2-160 | PECO_P1-2_PBTIE1_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 139.11 | 133.17 | AB2-160 | PECO_P4_PEACH205_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 139 | 132.85 | AB2-160 | PECO_P1-2_PBTIE2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 138.06 | 131.97 | AB2-160 | PECO_P4_PEACH055_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 133.37 | 127.55 | AB2-160 | PECO_P4_PEACH015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 128.72 | 127.03 | AB2-160 | DVP_P4-2: 514T595_SRT-SW |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 132.05 | 126.23 | AB2-160 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 126.97 | 125.25 | AB2-160 | DVP_P4-2: 51482_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 126.97 | 125.16 | AB2-160 | DVP_P1-2: LN 514_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 126.97 | 125.16 | AB2-160 | AP_P1-2_PE-500-407T_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200025 | W CHAPEL | 1 | 500 | 225 | 1732 | 123.78 | 122 | AB2-160 | PEPCO_P4_PP41_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 122.95 | 117.58 | AB2-160 | PECO_P4_PEACH225_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 117.17 | 115.25 | AB2-160 | AP_P2-3_PE-500-019C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 99.58 | 103.54 | AB2-160 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 99.58 | 103.54 | AB2-160 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 99.58 | 103.54 | AB2-160 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 98.75 | 100.83 | AB2-160 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2901 | 144.49 | 146.57 | AC1-065 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 153.78 | 158.28 | AB2-161 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.27 | 157.4 | AB2-161 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.27 | 157.4 | AB2-161 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 152.09 | 156.96 | AB2-161 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 161.79 | 154.56 | AB2-161 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 148.73 | 153.31 | AB2-161 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 155.85 | 150.69 | AB2-161 | PN_P1-2_PN-500-010T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.57 | 149.68 | AB2-161 | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.5 | 149.61 | AB2-161 | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.18 | 148.44 | AB2-161 | AP_P2-3_PE-500-016_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.25 | 148.41 | AB2-161 | AP_P2-3_PE-500-015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.16 | 148.02 | AB2-161 | PJM_500_BG_P4_5_CNSTN_L_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.45 | 148.01 | AB2-161 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.25 | 147.83 | AB2-161 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.28 | 147.81 | AB2-161 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.01 | 147.62 | AB2-161 | PECO_P4_NOTTI85_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.95 | 147.6 | AB2-161 | PECO_P1-2_220-08_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.36 | 147.56 | AB2-161 | AP_P1-2_WP-500-DRT17_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.36 | 147.56 | AB2-161 | AP_P1-2_PE-500-001_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.88 | 147.54 | AB2-161 | PECO_P4_COOPR125_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.31 | 147.49 | AB2-161 | AP_P2-3_PE-500-018C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2901 | 144.9 | 147.05 | AC1-074 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 151.01 | 144.29 | AB2-161 | PECO_P4_PEACH025_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.87 | 144.19 | AB2-161 | PECO_P1-2_PBTIE1_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 139.24 | 133.29 | AB2-161 | PECO_P4_PEACH205_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 139.13 | 132.97 | AB2-161 | PECO_P1-2_PBTIE2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 138.18 | 132.09 | AB2-161 | PECO_P4_PEACH055_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 133.51 | 127.68 | AB2-161 | PECO_P4_PEACH015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 128.95 | 127.21 | AB2-161 | DVP_P4-2: 514T595_SRT-SW |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 132.18 | 126.35 | AB2-161 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 127.2 | 125.5 | AB2-161 | DVP_P4-2: 51482_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 127.2 | 125.4 | AB2-161 | DVP_P1-2: LN 514_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 127.2 | 125.4 | AB2-161 | AP_P1-2_PE-500-407T_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 123.08 | 117.7 | AB2-161 | PECO_P4_PEACH225_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 117.4 | 115.49 | AB2-161 | AP_P2-3_PE-500-019C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2901 | 144.83 | 146.97 | AC1-075 and AC1-080 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 153.71 | 158.19 | AB2-169 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.2 | 157.32 | AB2-169 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.2 | 157.32 | AB2-169 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 152.02 | 156.87 | AB2-169 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 161.7 | 154.47 | AB2-169 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 148.66 | 153.22 | AB2-169 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 155.77 | 150.62 | AB2-169 | PN_P1-2_PN-500-010T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.49 | 149.6 | AB2-169 | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.42 | 149.52 | AB2-169 | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.11 | 148.35 | AB2-169 | AP_P2-3_PE-500-016_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.18 | 148.32 | AB2-169 | AP_P2-3_PE-500-015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.08 | 147.95 | AB2-169 | PJM_500_BG_P4_5_CNSTN_L_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.37 | 147.94 | AB2-169 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.17 | 147.75 | AB2-169 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.2 | 147.74 | AB2-169 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.93 | 147.54 | AB2-169 | PECO_P4_NOTTI85_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.87 | 147.52 | AB2-169 | PECO_P1-2_220-08_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.29 | 147.47 | AB2-169 | AP_P1-2_WP-500-DRT17_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.29 | 147.47 | AB2-169 | AP_P1-2_PE-500-001_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.8 | 147.46 | AB2-169 | PECO_P4_COOPR125_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.24 | 147.4 | AB2-169 | AP_P2-3_PE-500-018C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2901 | 144.81 | 146.95 | AC1-076 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.92 | 144.21 | AB2-169 | PECO_P4_PEACH025_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.78 | 144.1 | AB2-169 | PECO_P1-2_PBTIE1_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 139.15 | 133.21 | AB2-169 | PECO_P4_PEACH205_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 139.04 | 132.89 | AB2-169 | PECO_P1-2_PBTIE2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 138.1 | 132.01 | AB2-169 | PECO_P4_PEACH055_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 133.42 | 127.6 | AB2-169 | PECO_P4_PEACH015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 128.83 | 127.09 | AB2-169 | DVP_P4-2: 514T595_SRT-SW |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 132.09 | 126.27 | AB2-169 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 127.09 | 125.38 | AB2-169 | DVP_P4-2: 51482_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 127.09 | 125.28 | AB2-169 | DVP_P1-2: LN 514_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 127.09 | 125.28 | AB2-169 | AP_P1-2_PE-500-407T_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 123 | 117.62 | AB2-169 | PECO_P4_PEACH225_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 117.28 | 115.37 | AB2-169 | AP_P2-3_PE-500-019C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 228.02 | 240.32 | AB2-172 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 225.98 | 240.32 | AB2-172 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 215.85 | 230.06 | AB2-172 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 211.58 | 226.87 | AB2-172 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 212.18 | 219.77 | AB2-172 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 210.14 | 219.77 | AB2-172 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 200.55 | 210.14 | AB2-172 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 196.29 | 206.81 | AB2-172 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2901 | 144.74 | 146.86 | AC1-078 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 154.29 | 158.89 | AB2-172 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.84 | 157.96 | AB2-172 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.84 | 157.96 | AB2-172 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 152.6 | 157.57 | AB2-172 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 162.55 | 155.3 | AB2-172 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 149.24 | 153.91 | AB2-172 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 156.42 | 151.26 | AB2-172 | PN_P1-2_PN-500-010T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 147.05 | 150.26 | AB2-172 | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.98 | 150.19 | AB2-172 | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.64 | 148.99 | AB2-172 | AP_P2-3_PE-500-016_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.71 | 148.96 | AB2-172 | AP_P2-3_PE-500-015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 154.11 | 148.66 | AB2-172 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.7 | 148.56 | AB2-172 | PJM_500_BG_P4_5_CNSTN_L_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.91 | 148.48 | AB2-172 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.94 | 148.46 | AB2-172 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.67 | 148.26 | AB2-172 | PECO_P4_NOTTI85_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.61 | 148.25 | AB2-172 | PECO_P1-2_220-08_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.54 | 148.18 | AB2-172 | PECO_P4_COOPR125_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.82 | 148.11 | AB2-172 | AP_P1-2_WP-500-DRT17_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.82 | 148.11 | AB2-172 | AP_P1-2_PE-500-001_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.77 | 148.04 | AB2-172 | AP_P2-3_PE-500-018C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2901 | 144.74 | 146.86 | AC1-083 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 151.91 | 145.16 | AB2-172 | PECO_P4_PEACH025_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 151.7 | 144.99 | AB2-172 | PECO_P1-2_PBTIE1_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 911 | 148.82 | 142.8 | AB2-172 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 911 | 148.81 | 142.8 | AB2-172 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 911 | 148.8 | 142.79 | AB2-172 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 139.86 | 133.89 | AB2-172 | PECO_P4_PEACH205_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 139.9 | 133.71 | AB2-172 | PECO_P1-2_PBTIE2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 138.93 | 132.81 | AB2-172 | PECO_P4_PEACH055_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 134.34 | 128.48 | AB2-172 | PECO_P4_PEACH015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 132.93 | 127.07 | AB2-172 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 123.85 | 118.44 | AB2-172 | PECO_P4_PEACH225_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2901 | 144.33 | 146.39 | AC1-085 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 153.68 | 158.16 | AB2-174 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.17 | 157.3 | AB2-174 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.17 | 157.3 | AB2-174 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 151.99 | 156.84 | AB2-174 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 161.67 | 154.45 | AB2-174 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 148.63 | 153.19 | AB2-174 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 155.75 | 150.59 | AB2-174 | PN_P1-2_PN-500-010T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.47 | 149.57 | AB2-174 | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.4 | 149.5 | AB2-174 | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.09 | 148.32 | AB2-174 | AP_P2-3_PE-500-016_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.15 | 148.29 | AB2-174 | AP_P2-3_PE-500-015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.06 | 147.93 | AB2-174 | PJM_500_BG_P4_5_CNSTN_L_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.35 | 147.91 | AB2-174 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.15 | 147.73 | AB2-174 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.18 | 147.71 | AB2-174 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.9 | 147.52 | AB2-174 | PECO_P4_NOTTI85_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.84 | 147.5 | AB2-174 | PECO_P1-2_220-08_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.27 | 147.44 | AB2-174 | AP_P1-2_WP-500-DRT17_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.27 | 147.44 | AB2-174 | AP_P1-2_PE-500-001_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.78 | 147.44 | AB2-174 | PECO_P4_COOPR125_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.22 | 147.37 | AB2-174 | AP_P2-3_PE-500-018C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2901 | 144.44 | 146.51 | AC1-086 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.89 | 144.18 | AB2-174 | PECO_P4_PEACH025_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.75 | 144.08 | AB2-174 | PECO_P1-2_PBTIE1_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 139.13 | 133.19 | AB2-174 | PECO_P4_PEACH205_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 139.02 | 132.86 | AB2-174 | PECO_P1-2_PBTIE2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 138.08 | 131.99 | AB2-174 | PECO_P4_PEACH055_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 133.39 | 127.57 | AB2-174 | PECO_P4_PEACH015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 128.79 | 127.05 | AB2-174 | DVP_P4-2: 514T595_SRT-SW |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 132.07 | 126.25 | AB2-174 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 127.04 | 125.33 | AB2-174 | DVP_P4-2: 51482_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 127.04 | 125.24 | AB2-174 | DVP_P1-2: LN 514_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 127.04 | 125.24 | AB2-174 | AP_P1-2_PE-500-407T_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 122.97 | 117.6 | AB2-174 | PECO_P4_PEACH225_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 117.24 | 115.32 | AB2-174 | AP_P2-3_PE-500-019C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 226.06 | 240.48 | AB2-179 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 228.1 | 240.47 | AB2-179 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 215.93 | 230.2 | AB2-179 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 211.66 | 227.01 | AB2-179 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 212.26 | 219.86 | AB2-179 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 210.22 | 219.86 | AB2-179 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 200.63 | 210.23 | AB2-179 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 196.37 | 206.89 | AB2-179 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2901 | 144.8 | 146.93 | AC1-089 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 154.27 | 158.86 | AB2-179 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.8 | 157.92 | AB2-179 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.8 | 157.92 | AB2-179 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 152.58 | 157.54 | AB2-179 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 162.5 | 155.24 | AB2-179 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 149.21 | 153.89 | AB2-179 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 156.38 | 151.22 | AB2-179 | PN_P1-2_PN-500-010T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 147.03 | 150.23 | AB2-179 | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.96 | 150.16 | AB2-179 | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.62 | 148.96 | AB2-179 | AP_P2-3_PE-500-016_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.69 | 148.94 | AB2-179 | AP_P2-3_PE-500-015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 154.08 | 148.63 | AB2-179 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.66 | 148.53 | AB2-179 | PJM_500_BG_P4_5_CNSTN_L_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.88 | 148.44 | AB2-179 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.91 | 148.43 | AB2-179 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.63 | 148.23 | AB2-179 | PECO_P4_NOTTI85_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.57 | 148.21 | AB2-179 | PECO_P1-2_220-08_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.51 | 148.15 | AB2-179 | PECO_P4_COOPR125_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.8 | 148.08 | AB2-179 | AP_P1-2_PE-500-001_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.8 | 148.08 | AB2-179 | AP_P1-2_WP-500-DRT17_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.75 | 148.01 | AB2-179 | AP_P2-3_PE-500-018C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2901 | 144.87 | 147.01 | AC1-098 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 151.84 | 145.09 | AB2-179 | PECO_P4_PEACH025_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 151.64 | 144.93 | AB2-179 | PECO_P1-2_PBTIE1_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 139.82 | 133.86 | AB2-179 | PECO_P4_PEACH205_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 139.84 | 133.66 | AB2-179 | PECO_P1-2_PBTIE2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 138.87 | 132.76 | AB2-179 | PECO_P4_PEACH055_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 134.28 | 128.43 | AB2-179 | PECO_P4_PEACH015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 132.88 | 127.01 | AB2-179 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 123.79 | 118.38 | AB2-179 | PECO_P4_PEACH225_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 106.62 | 105.95 | AB2-179 | PECO_P1-2_5025/* $ CHESCO $ PECO_P1-2_5025 $ L_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 104.58 | 105.95 | AB2-179 | PECO_P1-2_5025/* $ CHESCO $ PECO_P1-2_5025 $ L_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 106.16 | 105.48 | AB2-179 | PJM500_DPL_P4_2_KEENEY-ROCK AT51_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 106.16 | 105.48 | AB2-179 | PJM500_DPL_P4_2_KEENEY-ROCK AT50_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 104.12 | 105.48 | AB2-179 | PJM500_DPL_P4_2_KEENEY-ROCK AT51_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 104.12 | 105.48 | AB2-179 | PJM500_DPL_P4_2_KEENEY-ROCK AT50_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 98.63 | 100.08 | AB2-179 | PECO_P1-2_5025/* $ CHESCO $ PECO_P1-2_5025 $ L_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 225.34 | 236.57 | AB2-190 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 223.34 | 236.57 | AB2-190 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 225.27 | 236.51 | AB2-190 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 223.27 | 236.51 | AB2-190 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 225.27 | 236.51 | AB2-190 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 223.27 | 236.51 | AB2-190 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 213.3 | 226.43 | AB2-190 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 213.23 | 226.37 | AB2-190 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 213.23 | 226.37 | AB2-190 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 209.04 | 223.21 | AB2-190 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 208.98 | 223.15 | AB2-190 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 208.97 | 223.15 | AB2-190 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 210.44 | 217.46 | AB2-190 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 208.44 | 217.45 | AB2-190 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 198.91 | 207.9 | AB2-190 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 194.65 | 204.55 | AB2-190 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 172.57 | 167.58 | AB2-190 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 171.6 | 166.14 | AB2-190 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 171.6 | 166.14 | AB2-190 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 171.58 | 166.13 | AB2-190 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 163.43 | 164.65 | AB2-190 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2901 | 144.91 | 147.06 | AC1-105 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 161.56 | 161.57 | AB2-190 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 161.56 | 161.57 | AB2-190 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 161.55 | 161.56 | AB2-190 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 163.65 | 158.69 | AB2-190 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 153.35 | 157.77 | AB2-190 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 161.86 | 156.98 | AB2-190 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 161.85 | 156.98 | AB2-190 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 151.66 | 156.45 | AB2-190 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 161.31 | 154.1 | AB2-190 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 148.3 | 152.79 | AB2-190 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 903 | 144.09 | 151.88 | AB2-190 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 152.62 | 150.97 | AB2-190 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 155.44 | 150.29 | AB2-190 | PN_P1-2_PN-500-010T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 903 | 142.57 | 149.26 | AB2-190 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 903 | 142.56 | 149.26 | AB2-190 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 903 | 142.55 | 149.25 | AB2-190 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.15 | 149.2 | AB2-190 | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.08 | 149.12 | AB2-190 | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.77 | 147.93 | AB2-190 | AP_P2-3_PE-500-016_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.83 | 147.9 | AB2-190 | AP_P2-3_PE-500-015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.75 | 147.62 | AB2-190 | PJM_500_BG_P4_5_CNSTN_L_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.03 | 147.6 | AB2-190 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.83 | 147.42 | AB2-190 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.86 | 147.4 | AB2-190 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.59 | 147.21 | AB2-190 | PECO_P4_NOTTI85_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.53 | 147.19 | AB2-190 | PECO_P1-2_220-08_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.46 | 147.13 | AB2-190 | PECO_P4_COOPR125_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 142.95 | 147.06 | AB2-190 | AP_P1-2_PE-500-001_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 142.95 | 147.06 | AB2-190 | AP_P1-2_WP-500-DRT17_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 142.9 | 146.99 | AB2-190 | AP_P2-3_PE-500-018C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2901 | 144.83 | 146.96 | AC1-120 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.54 | 143.84 | AB2-190 | PECO_P4_PEACH025_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.37 | 143.71 | AB2-190 | PECO_P1-2_PBTIE1_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 911 | 148.81 | 142.95 | AB2-190 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 911 | 147.87 | 141.63 | AB2-190 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 911 | 147.87 | 141.63 | AB2-190 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 911 | 147.85 | 141.62 | AB2-190 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204502 | 27JACKSON | 204514 | 27TMI | 1 | 230 | 227 | 781 | 132.93 | 141.39 | AB2-190 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204502 | 27JACKSON | 204514 | 27TMI | 1 | 230 | 227 | 781 | 132.93 | 141.39 | AB2-190 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204502 | 27JACKSON | 204514 | 27TMI | 1 | 230 | 227 | 781 | 132.91 | 141.38 | AB2-190 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 140.93 | 140.54 | AB2-190 | PJM_500_BG_P4_5_CNSTN_15_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 903 | 135.49 | 139.4 | AB2-190 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 1031 | 130.71 | 138.96 | AB2-190 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 1031 | 130.21 | 137.88 | AB2-190 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 1031 | 130.21 | 137.88 | AB2-190 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 1031 | 130.2 | 137.88 | AB2-190 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 911 | 140 | 134.91 | AB2-190 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 138.78 | 132.86 | AB2-190 | PECO_P4_PEACH205_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 207923 | BRISREAC | 208132 | WHEM TR1 | 1 | 230 | 229 | 676 | 124.19 | 132.72 | AB2-190 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 207922 | BRIS | 207923 | BRISREAC | RX | 230 | 229 | 676 | 124.19 | 132.72 | AB2-190 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 207923 | BRISREAC | 208132 | WHEM TR1 | 1 | 230 | 229 | 676 | 124.19 | 132.72 | AB2-190 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 207922 | BRIS | 207923 | BRISREAC | RX | 230 | 229 | 676 | 124.19 | 132.71 | AB2-190 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 207923 | BRISREAC | 208132 | WHEM TR1 | 1 | 230 | 229 | 676 | 124.18 | 132.71 | AB2-190 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 207922 | BRIS | 207923 | BRISREAC | RX | 230 | 229 | 676 | 124.18 | 132.71 | AB2-190 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 138.67 | 132.53 | AB2-190 | PECO_P1-2_PBTIE2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208078 | SAKR | 1 | 230 | 229 | 903 | 124.37 | 132.29 | AB2-190 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208078 | SAKR | 1 | 230 | 229 | 903 | 124.37 | 132.29 | AB2-190 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208078 | SAKR | 1 | 230 | 229 | 903 | 124.36 | 132.29 | AB2-190 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 137.75 | 131.68 | AB2-190 | PECO_P4_PEACH055_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204502 | 27JACKSON | 204514 | 27TMI | 1 | 230 | 227 | 781 | 125.28 | 130.84 | AB2-190 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220972 | GRANITE1 | 1 | 230 | 232 | 829 | 134.74 | 130.78 | AB2-190 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220972 | GRANITE1 | 1 | 230 | 232 | 829 | 134.11 | 130.13 | AB2-190 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220972 | GRANITE1 | 1 | 230 | 232 | 829 | 134.11 | 130.13 | AB2-190 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 1031 | 124.62 | 129.09 | AB2-190 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220973 | GRANITE6 | 1 | 230 | 232 | 829 | 132.67 | 128.89 | AB2-190 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 133.02 | 127.21 | AB2-190 | PECO_P4_PEACH015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 128.16 | 126.44 | AB2-190 | DVP_P4-2: 514T595_SRT-SW |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208020 | MANO TR3 | 1 | 230 | 229 | 793 | 112.18 | 126.01 | AB2-190 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 131.73 | 125.92 | AB2-190 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220953 | HOWARD12 | 220972 | GRANITE1 | 1 | 230 | 232 | 772 | 129.48 | 125.5 | AB2-190 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220954 | HOWARD32 | 220973 | GRANITE6 | 1 | 230 | 232 | 772 | 128.34 | 124.81 | AB2-190 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 126.4 | 124.65 | AB2-190 | DVP_P4-2: 51482_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 793 | 126.39 | 124.63 | AB2-190 | DVP_P4-2: 514T595_SRT-SW |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 2 | 230 | 233 | 793 | 126.39 | 124.63 | AB2-190 | DVP_P4-2: 514T595_SRT-SW |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 126.4 | 124.56 | AB2-190 | DVP_P1-2: LN 514_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 126.4 | 124.56 | AB2-190 | AP_P1-2_PE-500-407T_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220953 | HOWARD12 | 220972 | GRANITE1 | 1 | 230 | 232 | 772 | 128.57 | 124.53 | AB2-190 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220953 | HOWARD12 | 220972 | GRANITE1 | 1 | 230 | 232 | 772 | 128.56 | 124.53 | AB2-190 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208020 | MANO TR3 | 1 | 230 | 229 | 793 | 111.36 | 124.47 | AB2-190 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208020 | MANO TR3 | 1 | 230 | 229 | 793 | 111.35 | 124.46 | AB2-190 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208020 | MANO TR3 | 1 | 230 | 229 | 793 | 111.36 | 124.46 | AB2-190 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220954 | HOWARD32 | 220973 | GRANITE6 | 1 | 230 | 232 | 772 | 127.55 | 123.97 | AB2-190 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220954 | HOWARD32 | 220973 | GRANITE6 | 1 | 230 | 232 | 772 | 127.54 | 123.97 | AB2-190 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 793 | 125.13 | 123.37 | AB2-190 | DVP_P4-2: 51482_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 2 | 230 | 233 | 793 | 125.13 | 123.37 | AB2-190 | DVP_P4-2: 51482_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 2 | 230 | 233 | 793 | 125.13 | 123.3 | AB2-190 | DVP_P1-2: LN 514_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 793 | 125.13 | 123.3 | AB2-190 | DVP_P1-2: LN 514_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 793 | 125.13 | 123.3 | AB2-190 | AP_P1-2_PE-500-407T_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 2 | 230 | 233 | 793 | 125.13 | 123.3 | AB2-190 | AP_P1-2_PE-500-407T_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208031 | MLWD TR2 | 1 | 230 | 229 | 911 | 112.38 | 122.36 | AB2-190 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208078 | SAKR | 1 | 230 | 229 | 903 | 117.1 | 122.31 | AB2-190 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200025 | W CHAPEL | 1 | 500 | 225 | 1732 | 123.5 | 121.71 | AB2-190 | PEPCO_P4_PP41_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208031 | MLWD TR2 | 1 | 230 | 229 | 911 | 111.67 | 121.04 | AB2-190 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208031 | MLWD TR2 | 1 | 230 | 229 | 911 | 111.66 | 121.04 | AB2-190 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208031 | MLWD TR2 | 1 | 230 | 229 | 911 | 111.67 | 121.04 | AB2-190 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220965 | NEAST339 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 119.66 | 119.01 | AB2-190 | BG_P1_2315_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 911 | 117.94 | 118.93 | AB2-190 | PJM_500_BG_P4_5_CNSTN_15_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220965 | NEAST339 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 119.24 | 118.8 | AB2-190 | BG_P4_5_NEAST_17_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220965 | NEAST339 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 119.4 | 118.8 | AB2-190 | BG_P4_5_NEAST_15_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 114.61 | 118.3 | AB2-190 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220979 | NEAST317 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 118.75 | 118.14 | AB2-190 | BG_P1_2337_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 114.28 | 117.96 | AB2-190 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 114.26 | 117.9 | AB2-190 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 114.26 | 117.9 | AB2-190 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220979 | NEAST317 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 118.42 | 117.88 | AB2-190 | BG_P4_5_NEAST_39_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220979 | NEAST317 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 118.42 | 117.88 | AB2-190 | BG_P4_5_NEAST_37_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 113.93 | 117.56 | AB2-190 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 113.93 | 117.56 | AB2-190 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 122.63 | 117.27 | AB2-190 | PECO_P4_PEACH225_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 793 | 118.48 | 115.7 | AB2-190 | PEPCO_P1_PP2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 2 | 230 | 233 | 793 | 118.48 | 115.7 | AB2-190 | PEPCO_P1_PP1_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 2 | 500/230 | 225/232 | 2168 | 109.58 | 114.88 | AB2-190 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 2 | 500/230 | 225/232 | 2168 | 109.4 | 114.66 | AB2-190 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 2 | 500/230 | 225/232 | 2168 | 109.4 | 114.66 | AB2-190 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 116.61 | 114.66 | AB2-190 | AP_P2-3_PE-500-019C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 1 | 500/230 | 225/232 | 2168 | 109.35 | 114.63 | AB2-190 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 1 | 500/230 | 225/232 | 2168 | 109.17 | 114.42 | AB2-190 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 1 | 500/230 | 225/232 | 2168 | 109.17 | 114.42 | AB2-190 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220964 | GRACETON | 220999 | BAGLEY2 | 13 | 230 | 232 | 1795 | 113.35 | 114.38 | AB2-190 | BG_P4_5_GRCTN_3T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208020 | MANO TR3 | 1 | 230 | 229 | 793 | 104.17 | 113.95 | AB2-190 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208020 | MANO TR3 | 208031 | MLWD TR2 | 1 | 230 | 229 | 903 | 102.49 | 113.6 | AB2-190 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208020 | MANO TR3 | 208031 | MLWD TR2 | 1 | 230 | 229 | 903 | 101.78 | 112.41 | AB2-190 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208020 | MANO TR3 | 208031 | MLWD TR2 | 1 | 230 | 229 | 903 | 101.78 | 112.41 | AB2-190 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208020 | MANO TR3 | 208031 | MLWD TR2 | 1 | 230 | 229 | 903 | 101.78 | 112.41 | AB2-190 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 2 | 500/230 | 225/232 | 2168 | 108.45 | 111.74 | AB2-190 | PJM_500_BG_P4_5_CNSTN_15_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208031 | MLWD TR2 | 1 | 230 | 229 | 911 | 104.91 | 111.55 | AB2-190 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 106.4 | 111.16 | AB2-190 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220980 | RAPHAEL | 220999 | BAGLEY2 | 13 | 230 | 232 | 1795 | 108.94 | 111.14 | AB2-190 | BG_P4_5_GRCTN_3T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 106.28 | 111.02 | AB2-190 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 793 | 112.61 | 109.94 | AB2-190 | PEPCO_P4_PP19_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 793 | 109.36 | 107.43 | AB2-190 | AP_P2-3_PE-500-019C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 2 | 230 | 233 | 793 | 109.36 | 107.43 | AB2-190 | AP_P2-3_PE-500-019C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220965 | NEAST339 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 108.22 | 106.8 | AB2-190 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220965 | NEAST339 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 108.12 | 106.68 | AB2-190 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220965 | NEAST339 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 108.12 | 106.68 | AB2-190 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 101.52 | 105.68 | AB2-190 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 101.44 | 105.59 | AB2-190 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220979 | NEAST317 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 105.12 | 103.75 | AB2-190 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220979 | NEAST317 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 105.02 | 103.64 | AB2-190 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220979 | NEAST317 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 105.02 | 103.64 | AB2-190 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 99.43 | 103.29 | AB2-190 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 99.43 | 103.29 | AB2-190 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 99.43 | 103.29 | AB2-190 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208020 | MANO TR3 | 208031 | MLWD TR2 | 1 | 230 | 229 | 903 | 95.41 | 103.18 | AB2-190 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220964 | GRACETON | 220999 | BAGLEY2 | 13 | 230 | 232 | 1795 | 101.42 | 102.16 | AB2-190 | BG_P1_2305_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220964 | GRACETON | 221000 | BAGLEY | 5 | 230 | 232 | 1795 | 101.41 | 102.16 | AB2-190 | BG_P1_2313_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220965 | NEAST339 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 102.66 | 101.97 | AB2-190 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 98.5 | 101.96 | AB2-190 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220965 | NEAST339 | 220977 | RIV2339 | 1 | 230 | 232 | 991 | 103.29 | 101.85 | AB2-190 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 2 | 500/230 | 225/232 | 2168 | 98.96 | 101.71 | AB2-190 | BG_P1_CNSTN_500-2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 2 | 500/230 | 225/232 | 2168 | 98.96 | 101.71 | AB2-190 | PJM_500_BG_P2_CNSTN_230-N_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 1 | 500/230 | 225/232 | 2168 | 98.86 | 101.6 | AB2-190 | BG_P1_CNSTN_500-4_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 1 | 500/230 | 225/232 | 2168 | 98.86 | 101.6 | AB2-190 | PJM_500_BG_P2_CNSTN_230-S_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 98.6 | 100.61 | AB2-190 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 144.32 | 139.17 | AC1-001 | PL_10_P42_100570_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 144.32 | 139.17 | AC1-001 | PL_10_P42_100570_A_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 143.51 | 138.38 | AC1-001 | PL_10_P12_000085_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 143.41 | 138.29 | AC1-001 | PN_P2-3_PN-500-004-DRT-008_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 143.41 | 138.29 | AC1-001 | PN_P2-3_PN-500-DRT31_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 143.03 | 137.92 | AC1-001 | PL_30_P42_000131_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 142.1 | 137.03 | AC1-001 | PL_10_P12_000086_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 142.1 | 137.02 | AC1-001 | PN_P2-3_PN-500-001C-DRT_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2901 | 144.87 | 147.01 | AC1-122 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.33 | 157.46 | AC1-033 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.33 | 157.46 | AC1-033 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 161.83 | 154.6 | AC1-033 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 155.9 | 150.75 | AC1-033 | PN_P1-2_PN-500-010T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.21 | 148.08 | AC1-033 | PJM_500_BG_P4_5_CNSTN_L_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.49 | 148.05 | AC1-033 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.29 | 147.87 | AC1-033 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.32 | 147.85 | AC1-033 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.04 | 147.66 | AC1-033 | PECO_P4_NOTTI85_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.98 | 147.64 | AC1-033 | PECO_P1-2_220-08_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.92 | 147.58 | AC1-033 | PECO_P4_COOPR125_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 151.04 | 144.32 | AC1-033 | PECO_P4_PEACH025_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.92 | 144.24 | AC1-033 | PECO_P1-2_PBTIE1_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 139.18 | 133.02 | AC1-033 | PECO_P1-2_PBTIE2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2901 | 144.83 | 146.96 | AC1-143 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 153.71 | 158.2 | AC1-034 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.2 | 157.33 | AC1-034 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.2 | 157.33 | AC1-034 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 152.03 | 156.88 | AC1-034 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 161.7 | 154.48 | AC1-034 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 148.66 | 153.23 | AC1-034 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 155.78 | 150.63 | AC1-034 | PN_P1-2_PN-500-010T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.5 | 149.61 | AC1-034 | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.43 | 149.53 | AC1-034 | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.12 | 148.37 | AC1-034 | AP_P2-3_PE-500-016_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.19 | 148.34 | AC1-034 | AP_P2-3_PE-500-015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.09 | 147.96 | AC1-034 | PJM_500_BG_P4_5_CNSTN_L_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.38 | 147.94 | AC1-034 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.18 | 147.75 | AC1-034 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.2 | 147.74 | AC1-034 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.93 | 147.54 | AC1-034 | PECO_P4_NOTTI85_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.87 | 147.53 | AC1-034 | PECO_P1-2_220-08_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.3 | 147.48 | AC1-034 | AP_P1-2_PE-500-001_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.3 | 147.48 | AC1-034 | AP_P1-2_WP-500-DRT17_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.81 | 147.46 | AC1-034 | PECO_P4_COOPR125_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.25 | 147.41 | AC1-034 | AP_P2-3_PE-500-018C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2901 | 142.17 | 143.89 | AC1-158 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.92 | 144.21 | AC1-034 | PECO_P4_PEACH025_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.78 | 144.11 | AC1-034 | PECO_P1-2_PBTIE1_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 139.16 | 133.22 | AC1-034 | PECO_P4_PEACH205_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 139.05 | 132.89 | AC1-034 | PECO_P1-2_PBTIE2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 138.11 | 132.02 | AC1-034 | PECO_P4_PEACH055_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 133.42 | 127.6 | AC1-034 | PECO_P4_PEACH015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 128.86 | 127.13 | AC1-034 | DVP_P4-2: 514T595_SRT-SW |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 132.1 | 126.28 | AC1-034 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 127.12 | 125.41 | AC1-034 | DVP_P4-2: 51482_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 127.12 | 125.32 | AC1-034 | DVP_P1-2: LN 514_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 127.12 | 125.32 | AC1-034 | AP_P1-2_PE-500-407T_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 123 | 117.63 | AC1-034 | PECO_P4_PEACH225_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 117.32 | 115.4 | AC1-034 | AP_P2-3_PE-500-019C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.34 | 157.46 | AC1-042 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.34 | 157.46 | AC1-042 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.51 | 148.07 | AC1-042 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.31 | 147.89 | AC1-042 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.34 | 147.87 | AC1-042 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.06 | 147.67 | AC1-042 | PECO_P4_NOTTI85_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153 | 147.66 | AC1-042 | PECO_P1-2_220-08_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.94 | 147.59 | AC1-042 | PECO_P4_COOPR125_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 151.79 | 147.46 | AC1-042 | AP_P2-3_PE-500-016_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 151.83 | 147.45 | AC1-042 | AP_P2-3_PE-500-015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 223.64 | 237.07 | AC1-043 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 225.64 | 237.07 | AC1-043 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 223.57 | 237.01 | AC1-043 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 225.58 | 237.01 | AC1-043 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 223.57 | 237 | AC1-043 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 225.57 | 237 | AC1-043 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 213.58 | 226.91 | AC1-043 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 213.52 | 226.85 | AC1-043 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 213.52 | 226.85 | AC1-043 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 209.32 | 223.7 | AC1-043 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 209.26 | 223.64 | AC1-043 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 209.26 | 223.64 | AC1-043 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 210.74 | 217.86 | AC1-043 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 208.73 | 217.86 | AC1-043 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 199.19 | 208.29 | AC1-043 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 194.93 | 204.94 | AC1-043 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 172.77 | 167.79 | AC1-043 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 163.65 | 164.94 | AC1-043 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2901 | 144.16 | 146.18 | AC1-161 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 161.79 | 161.85 | AC1-043 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 161.79 | 161.85 | AC1-043 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 161.77 | 161.84 | AC1-043 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 153.54 | 157.99 | AC1-043 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.04 | 157.17 | AC1-043 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.04 | 157.16 | AC1-043 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 151.85 | 156.66 | AC1-043 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 161.53 | 154.31 | AC1-043 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 148.49 | 153.01 | AC1-043 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 152.84 | 151.22 | AC1-043 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 155.62 | 150.47 | AC1-043 | PN_P1-2_PN-500-010T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 903 | 142.75 | 149.55 | AC1-043 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 903 | 142.75 | 149.55 | AC1-043 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 903 | 142.73 | 149.54 | AC1-043 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.33 | 149.4 | AC1-043 | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.26 | 149.33 | AC1-043 | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.94 | 148.14 | AC1-043 | AP_P2-3_PE-500-016_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.01 | 148.11 | AC1-043 | AP_P2-3_PE-500-015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.93 | 147.8 | AC1-043 | PJM_500_BG_P4_5_CNSTN_L_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.23 | 147.79 | AC1-043 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.03 | 147.61 | AC1-043 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.06 | 147.59 | AC1-043 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.79 | 147.4 | AC1-043 | PECO_P4_NOTTI85_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.73 | 147.38 | AC1-043 | PECO_P1-2_220-08_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.66 | 147.32 | AC1-043 | PECO_P4_COOPR125_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.12 | 147.26 | AC1-043 | AP_P1-2_PE-500-001_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.12 | 147.26 | AC1-043 | AP_P1-2_WP-500-DRT17_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.07 | 147.2 | AC1-043 | AP_P2-3_PE-500-018C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2901 | 144.35 | 146.41 | AC1-164 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.77 | 144.06 | AC1-043 | PECO_P4_PEACH025_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.6 | 143.94 | AC1-043 | PECO_P1-2_PBTIE1_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 911 | 149.01 | 143.13 | AC1-043 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 903 | 135.67 | 139.65 | AC1-043 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 1031 | 130.36 | 138.15 | AC1-043 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 1031 | 130.36 | 138.15 | AC1-043 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 1031 | 130.35 | 138.14 | AC1-043 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 138.99 | 133.06 | AC1-043 | PECO_P4_PEACH205_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 138.88 | 132.74 | AC1-043 | PECO_P1-2_PBTIE2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208078 | SAKR | 1 | 230 | 229 | 903 | 124.54 | 132.59 | AC1-043 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208078 | SAKR | 1 | 230 | 229 | 903 | 124.54 | 132.58 | AC1-043 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208078 | SAKR | 1 | 230 | 229 | 903 | 124.54 | 132.58 | AC1-043 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 137.95 | 131.87 | AC1-043 | PECO_P4_PEACH055_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 1031 | 124.76 | 129.31 | AC1-043 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 133.25 | 127.43 | AC1-043 | PECO_P4_PEACH015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 128.33 | 126.58 | AC1-043 | DVP_P4-2: 514T595_SRT-SW |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 131.94 | 126.12 | AC1-043 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 126.57 | 124.85 | AC1-043 | DVP_P4-2: 51482_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 126.57 | 124.75 | AC1-043 | AP_P1-2_PE-500-407T_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 126.57 | 124.75 | AC1-043 | DVP_P1-2: LN 514_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 2 | 230 | 233 | 793 | 126.51 | 124.74 | AC1-043 | DVP_P4-2: 514T595_SRT-SW |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 793 | 126.51 | 124.74 | AC1-043 | DVP_P4-2: 514T595_SRT-SW |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208020 | MANO TR3 | 1 | 230 | 229 | 793 | 111.53 | 124.69 | AC1-043 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208020 | MANO TR3 | 1 | 230 | 229 | 793 | 111.53 | 124.69 | AC1-043 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208020 | MANO TR3 | 1 | 230 | 229 | 793 | 111.53 | 124.69 | AC1-043 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 2 | 230 | 233 | 793 | 125.26 | 123.53 | AC1-043 | DVP_P4-2: 51482_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 793 | 125.26 | 123.53 | AC1-043 | DVP_P4-2: 51482_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 2 | 230 | 233 | 793 | 125.26 | 123.45 | AC1-043 | DVP_P1-2: LN 514_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 2 | 230 | 233 | 793 | 125.26 | 123.45 | AC1-043 | AP_P1-2_PE-500-407T_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 793 | 125.26 | 123.45 | AC1-043 | AP_P1-2_PE-500-407T_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 793 | 125.26 | 123.45 | AC1-043 | DVP_P1-2: LN 514_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200025 | W CHAPEL | 1 | 500 | 225 | 1732 | 123.69 | 121.9 | AC1-043 | PEPCO_P4_PP41_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 122.84 | 117.47 | AC1-043 | PECO_P4_PEACH225_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 2 | 500/230 | 225/232 | 2168 | 109.68 | 114.99 | AC1-043 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 116.78 | 114.85 | AC1-043 | AP_P2-3_PE-500-019C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 2 | 500/230 | 225/232 | 2168 | 109.5 | 114.78 | AC1-043 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 2 | 500/230 | 225/232 | 2168 | 109.5 | 114.78 | AC1-043 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 1 | 500/230 | 225/232 | 2168 | 109.45 | 114.75 | AC1-043 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 1 | 500/230 | 225/232 | 2168 | 109.27 | 114.54 | AC1-043 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 1 | 500/230 | 225/232 | 2168 | 109.27 | 114.54 | AC1-043 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 793 | 112.75 | 110.12 | AC1-043 | PEPCO_P4_PP19_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 2 | 230 | 233 | 793 | 109.48 | 107.59 | AC1-043 | AP_P2-3_PE-500-019C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 793 | 109.48 | 107.59 | AC1-043 | AP_P2-3_PE-500-019C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 99.51 | 103.43 | AC1-043 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 99.51 | 103.43 | AC1-043 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 99.51 | 103.43 | AC1-043 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 98.58 | 102.1 | AC1-043 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 98.68 | 100.73 | AC1-043 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 235463 | 01TANEY | 1 | 138 | 227/201 | 317 | 187.44 | 182.19 | AC1-048 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 235463 | 01TANEY | 1 | 138 | 227/201 | 317 | 187.44 | 182.19 | AC1-048 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 235463 | 01TANEY | 1 | 138 | 227/201 | 317 | 187.28 | 182.05 | AC1-048 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 334 | 162.91 | 165.42 | AC1-048 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 334 | 162.91 | 165.42 | AC1-048 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 334 | 162.78 | 165.27 | AC1-048 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204539 | 27HUNTRSTN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 334 | 162.3 | 163.75 | AC1-048 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204539 | 27HUNTRSTN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 334 | 162.3 | 163.75 | AC1-048 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204539 | 27HUNTRSTN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 334 | 162.17 | 163.6 | AC1-048 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2901 | 144.9 | 147.04 | AC1-174 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204538 | 27STRABAN | 204544 | 27LINCOLN | 1 | 115 | 227 | 371 | 152.37 | 156.66 | AC1-048 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204538 | 27STRABAN | 204544 | 27LINCOLN | 1 | 115 | 227 | 371 | 152.37 | 156.65 | AC1-048 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204538 | 27STRABAN | 204544 | 27LINCOLN | 1 | 115 | 227 | 371 | 152.24 | 156.51 | AC1-048 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 903 | 145.51 | 153.27 | AC1-048 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204529 | 27GERMANTN | 204538 | 27STRABAN | 1 | 115 | 227 | 371 | 146.86 | 152.12 | AC1-048 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204529 | 27GERMANTN | 204538 | 27STRABAN | 1 | 115 | 227 | 371 | 146.86 | 152.12 | AC1-048 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204529 | 27GERMANTN | 204538 | 27STRABAN | 1 | 115 | 227 | 371 | 146.73 | 151.97 | AC1-048 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 155.86 | 150.69 | AC1-048 | PN_P1-2_PN-500-010T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 204550 | 27ORRTANNA | 1 | 115 | 227 | 189 | 148.54 | 147.87 | AC1-048 | ME_P1-2_ME-115-068_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 204550 | 27ORRTANNA | 1 | 115 | 227 | 189 | 147.03 | 147.77 | AC1-048 | ME_P2-3_ME-115-035A_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 204550 | 27ORRTANNA | 1 | 115 | 227 | 189 | 147.85 | 146.31 | AC1-048 | ME_P1-2_ME-115-067_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 204550 | 27ORRTANNA | 1 | 115 | 227 | 189 | 146.24 | 145.47 | AC1-048 | ME_P2-3_ME-115-013B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 204550 | 27ORRTANNA | 1 | 115 | 227 | 189 | 144.73 | 145.35 | AC1-048 | ME_P2-3_ME-115-035B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 235463 | 01TANEY | 1 | 138 | 227/201 | 317 | 146.69 | 145.29 | AC1-048 | AP_P2-3_PE-500-016_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 235463 | 01TANEY | 1 | 138 | 227/201 | 317 | 146.8 | 145.22 | AC1-048 | AP_P2-3_PE-500-015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 204550 | 27ORRTANNA | 1 | 115 | 227 | 189 | 145.94 | 145.15 | AC1-048 | ME_P2-3_ME-115-013A_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 235463 | 01TANEY | 1 | 138 | 227/201 | 317 | 145.38 | 144.38 | AC1-048 | AP_P2-3_PE-500-018D_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 235463 | 01TANEY | 1 | 138 | 227/201 | 317 | 145.37 | 144.37 | AC1-048 | AP_P2-3_PE-500-018C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 235463 | 01TANEY | 1 | 138 | 227/201 | 317 | 145.23 | 144.11 | AC1-048 | AP_P1-2_WP-500-DRT17_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 235463 | 01TANEY | 1 | 138 | 227/201 | 317 | 145.23 | 144.11 | AC1-048 | AP_P1-2_PE-500-001_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 235463 | 01TANEY | 1 | 138 | 227/201 | 317 | 145.07 | 143.71 | AC1-048 | AP_P2-3_WP-500-466_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2901 | 144.9 | 147.04 | AC1-175 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 147.03 | 141.85 | AC1-048 | ME_P2-3_ME-230-018A_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 147.01 | 141.79 | AC1-048 | PL_10_P42_100562_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 146.92 | 141.74 | AC1-048 | ME_P2-3_ME-230-DTR030_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 146.92 | 141.74 | AC1-048 | ME_P2-3_ME-230-007C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 146.92 | 141.74 | AC1-048 | ME_P1-2_ME-230-008_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 142.08 | 141.72 | AC1-048 | PJM_500_BG_P4_5_CNSTN_15_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 146.89 | 141.71 | AC1-048 | ME_P2-3_ME-230-007D_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 146.89 | 141.68 | AC1-048 | PL_10_P42_100561_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2901 | 144.79 | 146.92 | AC1-189 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 146.13 | 140.97 | AC1-048 | ME_P2-3_ME-115-013C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 146.12 | 140.96 | AC1-048 | ME_P2-3_ME-115-013D_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 903 | 136.92 | 140.81 | AC1-048 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204502 | 27JACKSON | 204514 | 27TMI | 1 | 230 | 227 | 781 | 131.67 | 140.35 | AC1-048 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204502 | 27JACKSON | 204514 | 27TMI | 1 | 230 | 227 | 781 | 131.87 | 140.33 | AC1-048 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204502 | 27JACKSON | 204514 | 27TMI | 1 | 230 | 227 | 781 | 131.87 | 140.33 | AC1-048 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204502 | 27JACKSON | 204514 | 27TMI | 1 | 230 | 227 | 781 | 131.86 | 140.32 | AC1-048 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 204550 | 27ORRTANNA | 1 | 115 | 227 | 189 | 141.57 | 139.58 | AC1-048 | ME_P2-3_ME-115-0102-A_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 204550 | 27ORRTANNA | 1 | 115 | 227 | 189 | 141.57 | 139.58 | AC1-048 | ME_P2-2_ME-115-0102-4_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 136.87 | 139.06 | AC1-048 | ME_P2-4_ME-115-0102-B134_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 1031 | 130.68 | 138.94 | AC1-048 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 136.21 | 138.53 | AC1-048 | AP_P1-2_WP-138-341T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 136 | 138.38 | AC1-048 | AP_P2-2_PE-138-073_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 136 | 138.38 | AC1-048 | AP_P7-1_PE-138-022T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 136 | 138.37 | AC1-048 | ME_P1-2_ME-115-240T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 135.85 | 138.36 | AC1-048 | AP_P2-3_PE-138-071_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 135.82 | 138.35 | AC1-048 | AP_P2-2_PE-138-003_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 135.82 | 138.35 | AC1-048 | AP_P1-2_PE-138-028_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 135.82 | 138.35 | AC1-048 | AP_P2-3_PE-138-027_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 135.99 | 138.25 | AC1-048 | ME_P2-3_ME-115-013D_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 1031 | 130.19 | 137.88 | AC1-048 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 1031 | 130.19 | 137.88 | AC1-048 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 1031 | 130.18 | 137.87 | AC1-048 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204539 | 27HUNTRSTN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 334 | 139.21 | 137.77 | AC1-048 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204539 | 27HUNTRSTN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 334 | 139.21 | 137.77 | AC1-048 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204539 | 27HUNTRSTN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 334 | 139.2 | 137.77 | AC1-048 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204539 | 27HUNTRSTN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 334 | 139.03 | 137.58 | AC1-048 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 334 | 139.82 | 137.56 | AC1-048 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 334 | 139.82 | 137.56 | AC1-048 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 334 | 139.81 | 137.56 | AC1-048 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 204529 | 27GERMANTN | 1 | 138/115 | 227 | 453 | 131.17 | 137.44 | AC1-048 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 204529 | 27GERMANTN | 1 | 138/115 | 227 | 453 | 131.17 | 137.44 | AC1-048 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 334 | 139.63 | 137.34 | AC1-048 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 204529 | 27GERMANTN | 1 | 138/115 | 227 | 453 | 131.06 | 137.32 | AC1-048 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2901 | 144.75 | 146.87 | AC1-191 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 334 | 131.5 | 130.33 | AC1-048 | ME_P2-3_ME-115-019A-A_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 334 | 131.5 | 130.33 | AC1-048 | ME_P1-2_ME-115-061_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204502 | 27JACKSON | 204514 | 27TMI | 1 | 230 | 227 | 781 | 124.22 | 129.77 | AC1-048 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 334 | 132.77 | 129.3 | AC1-048 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 1031 | 124.59 | 129.08 | AC1-048 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204539 | 27HUNTRSTN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 334 | 130.89 | 128.89 | AC1-048 | ME_P2-3_ME-115-019A-A_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204539 | 27HUNTRSTN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 334 | 130.89 | 128.89 | AC1-048 | ME_P1-2_ME-115-061_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204539 | 27HUNTRSTN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 334 | 132.14 | 128.67 | AC1-048 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204538 | 27STRABAN | 204544 | 27LINCOLN | 1 | 115 | 227 | 371 | 128.95 | 128.26 | AC1-048 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204538 | 27STRABAN | 204544 | 27LINCOLN | 1 | 115 | 227 | 371 | 128.95 | 128.26 | AC1-048 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204538 | 27STRABAN | 204544 | 27LINCOLN | 1 | 115 | 227 | 371 | 128.94 | 128.25 | AC1-048 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 129.87 | 128.15 | AC1-048 | DVP_P4-2: 514T595_SRT-SW |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204538 | 27STRABAN | 204544 | 27LINCOLN | 1 | 115 | 227 | 371 | 128.76 | 128.04 | AC1-048 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 128.15 | 126.46 | AC1-048 | DVP_P4-2: 51482_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 128.15 | 126.37 | AC1-048 | DVP_P1-2: LN 514_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 128.15 | 126.37 | AC1-048 | AP_P1-2_PE-500-407T_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2901 | 144.86 | 147 | AC1-194 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204529 | 27GERMANTN | 204538 | 27STRABAN | 1 | 115 | 227 | 371 | 123.44 | 123.98 | AC1-048 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204529 | 27GERMANTN | 204538 | 27STRABAN | 1 | 115 | 227 | 371 | 123.44 | 123.98 | AC1-048 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204529 | 27GERMANTN | 204538 | 27STRABAN | 1 | 115 | 227 | 371 | 123.43 | 123.98 | AC1-048 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204529 | 27GERMANTN | 204538 | 27STRABAN | 1 | 115 | 227 | 371 | 123.26 | 123.77 | AC1-048 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2901 | 144.8 | 146.93 | AC1-208 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 911 | 119.06 | 120.08 | AC1-048 | PJM_500_BG_P4_5_CNSTN_15_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204538 | 27STRABAN | 204544 | 27LINCOLN | 1 | 115 | 227 | 371 | 121.8 | 119.95 | AC1-048 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204538 | 27STRABAN | 204544 | 27LINCOLN | 1 | 115 | 227 | 371 | 117.55 | 119.88 | AC1-048 | AP_P2-3_PE-500-016_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204538 | 27STRABAN | 204544 | 27LINCOLN | 1 | 115 | 227 | 371 | 117.65 | 119.81 | AC1-048 | AP_P2-3_PE-500-015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 119.11 | 117.8 | AC1-048 | PL_04_P42_000564_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 119.11 | 117.8 | AC1-048 | PL_04_P12_000260_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 793 | 120.06 | 117.34 | AC1-048 | PEPCO_P1_PP2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 2 | 230 | 233 | 793 | 120.06 | 117.34 | AC1-048 | PEPCO_P1_PP1_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 118.38 | 116.48 | AC1-048 | AP_P2-3_PE-500-019C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204529 | 27GERMANTN | 204538 | 27STRABAN | 1 | 115 | 227 | 371 | 116.29 | 115.61 | AC1-048 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204539 | 27HUNTRSTN | 204550 | 27ORRTANNA | 1 | 115 | 227 | 264 | 116.01 | 115.52 | AC1-048 | ME_P1-2_ME-115-068_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204539 | 27HUNTRSTN | 204550 | 27ORRTANNA | 1 | 115 | 227 | 264 | 114.93 | 115.45 | AC1-048 | ME_P2-3_ME-115-035A_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204529 | 27GERMANTN | 204538 | 27STRABAN | 1 | 115 | 227 | 371 | 112.04 | 115.43 | AC1-048 | AP_P2-3_PE-500-016_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204529 | 27GERMANTN | 204538 | 27STRABAN | 1 | 115 | 227 | 371 | 112.14 | 115.35 | AC1-048 | AP_P2-3_PE-500-015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204539 | 27HUNTRSTN | 204550 | 27ORRTANNA | 1 | 115 | 227 | 264 | 115.52 | 114.31 | AC1-048 | ME_P1-2_ME-115-067_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 204529 | 27GERMANTN | 1 | 138/115 | 227 | 453 | 111.99 | 114.02 | AC1-048 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 204529 | 27GERMANTN | 1 | 138/115 | 227 | 453 | 111.99 | 114.02 | AC1-048 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 204529 | 27GERMANTN | 1 | 138/115 | 227 | 453 | 111.98 | 114.01 | AC1-048 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 204529 | 27GERMANTN | 1 | 138/115 | 227 | 453 | 111.83 | 113.84 | AC1-048 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204539 | 27HUNTRSTN | 204550 | 27ORRTANNA | 1 | 115 | 227 | 264 | 114.36 | 113.78 | AC1-048 | ME_P2-3_ME-115-013B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204539 | 27HUNTRSTN | 204550 | 27ORRTANNA | 1 | 115 | 227 | 264 | 113.28 | 113.7 | AC1-048 | ME_P2-3_ME-115-035B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204539 | 27HUNTRSTN | 204550 | 27ORRTANNA | 1 | 115 | 227 | 264 | 114.14 | 113.54 | AC1-048 | ME_P2-3_ME-115-013A_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 114.55 | 113.4 | AC1-048 | BG_P4_5_CNSTN_14_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 793 | 114.28 | 111.66 | AC1-048 | PEPCO_P4_PP19_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204539 | 27HUNTRSTN | 204550 | 27ORRTANNA | 1 | 115 | 227 | 264 | 111.02 | 109.47 | AC1-048 | ME_P2-2_ME-115-0102-4_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204539 | 27HUNTRSTN | 204550 | 27ORRTANNA | 1 | 115 | 227 | 264 | 111.02 | 109.47 | AC1-048 | ME_P2-3_ME-115-0102-A_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 793 | 110.85 | 108.98 | AC1-048 | AP_P2-3_PE-500-019C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 2 | 230 | 233 | 793 | 110.85 | 108.98 | AC1-048 | AP_P2-3_PE-500-019C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200009 | JUNI | 208004 | JUNI | 2 | 500/230 | 225/229 | 1040 | 107.93 | 107.36 | AC1-048 | PL_10_P42_000140_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 204529 | 27GERMANTN | 1 | 138/115 | 227 | 453 | 106.13 | 107.11 | AC1-048 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 204529 | 27GERMANTN | 1 | 138/115 | 227 | 453 | 102.65 | 106.98 | AC1-048 | AP_P2-3_PE-500-016_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 204529 | 27GERMANTN | 1 | 138/115 | 227 | 453 | 102.73 | 106.92 | AC1-048 | AP_P2-3_PE-500-015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200504 | 26CARLISLE | 204528 | 27GARDNERS | 1 | 115 | 226/227 | 190 | 96.26 | 102.52 | AC1-048 | AP_P1-2_WP-138-341T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200504 | 26CARLISLE | 204528 | 27GARDNERS | 1 | 115 | 226/227 | 190 | 95.79 | 102.22 | AC1-048 | AP_P7-1_PE-138-022T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200504 | 26CARLISLE | 204528 | 27GARDNERS | 1 | 115 | 226/227 | 190 | 95.79 | 102.22 | AC1-048 | AP_P2-2_PE-138-073_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200504 | 26CARLISLE | 204528 | 27GARDNERS | 1 | 115 | 226/227 | 190 | 95.79 | 102.17 | AC1-048 | ME_P1-2_ME-115-240T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204520 | 27ALLEN | 208142 | WIGR-115 | 1 | 115 | 227/229 | 351.4 | 94.38 | 101.95 | AC1-048 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204520 | 27ALLEN | 208142 | WIGR-115 | 1 | 115 | 227/229 | 351.4 | 94.38 | 101.95 | AC1-048 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204520 | 27ALLEN | 208142 | WIGR-115 | 1 | 115 | 227/229 | 351.4 | 94.38 | 101.95 | AC1-048 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204520 | 27ALLEN | 208142 | WIGR-115 | 1 | 115 | 227/229 | 351.4 | 94.14 | 101.78 | AC1-048 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200504 | 26CARLISLE | 204528 | 27GARDNERS | 1 | 115 | 226/227 | 190 | 94.36 | 101.5 | AC1-048 | AP_P2-2_PE-138-003_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200504 | 26CARLISLE | 204528 | 27GARDNERS | 1 | 115 | 226/227 | 190 | 94.36 | 101.5 | AC1-048 | AP_P2-3_PE-138-027_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200504 | 26CARLISLE | 204528 | 27GARDNERS | 1 | 115 | 226/227 | 190 | 94.36 | 101.5 | AC1-048 | AP_P1-2_PE-138-028_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200504 | 26CARLISLE | 204528 | 27GARDNERS | 1 | 115 | 226/227 | 190 | 93.94 | 101.16 | AC1-048 | AP_P2-3_PE-138-071_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200504 | 26CARLISLE | 204528 | 27GARDNERS | 1 | 115 | 226/227 | 190 | 93.64 | 100.85 | AC1-048 | AP_P2-3_PE-138-052A_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2901 | 144.7 | 146.82 | AC1-216 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 153.74 | 158.23 | AC1-053 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.2 | 157.33 | AC1-053 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.2 | 157.33 | AC1-053 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 152.05 | 156.91 | AC1-053 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 161.66 | 154.44 | AC1-053 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 148.69 | 153.26 | AC1-053 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 155.78 | 150.63 | AC1-053 | PN_P1-2_PN-500-010T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.52 | 149.64 | AC1-053 | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.45 | 149.56 | AC1-053 | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.16 | 148.44 | AC1-053 | AP_P2-3_PE-500-016_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.23 | 148.41 | AC1-053 | AP_P2-3_PE-500-015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.09 | 147.96 | AC1-053 | PJM_500_BG_P4_5_CNSTN_L_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.34 | 147.9 | AC1-053 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.14 | 147.72 | AC1-053 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.16 | 147.7 | AC1-053 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.34 | 147.55 | AC1-053 | AP_P1-2_WP-500-DRT17_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.34 | 147.55 | AC1-053 | AP_P1-2_PE-500-001_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.89 | 147.51 | AC1-053 | PECO_P4_NOTTI85_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.83 | 147.49 | AC1-053 | PECO_P1-2_220-08_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.29 | 147.48 | AC1-053 | AP_P2-3_PE-500-018C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.77 | 147.43 | AC1-053 | PECO_P4_COOPR125_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2901 | 144.88 | 147.02 | AC1-221 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.86 | 144.15 | AC1-053 | PECO_P4_PEACH025_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.75 | 144.07 | AC1-053 | PECO_P1-2_PBTIE1_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 139.13 | 133.2 | AC1-053 | PECO_P4_PEACH205_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 139.02 | 132.86 | AC1-053 | PECO_P1-2_PBTIE2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 138.08 | 131.99 | AC1-053 | PECO_P4_PEACH055_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 133.39 | 127.58 | AC1-053 | PECO_P4_PEACH015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 132.07 | 126.25 | AC1-053 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204512 | 27S.RDG | 204693 | 27BOONETOWN | 1 | 230 | 227 | 607 | 107.65 | 123.39 | AC1-053 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 122.97 | 117.6 | AC1-053 | PECO_P4_PEACH225_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2901 | 144.87 | 147.01 | AC1-222 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 153.74 | 158.24 | AC1-054 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.23 | 157.36 | AC1-054 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.23 | 157.36 | AC1-054 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 152.06 | 156.91 | AC1-054 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 161.74 | 154.51 | AC1-054 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 148.69 | 153.26 | AC1-054 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 155.81 | 150.65 | AC1-054 | PN_P1-2_PN-500-010T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.53 | 149.64 | AC1-054 | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.46 | 149.57 | AC1-054 | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.15 | 148.4 | AC1-054 | AP_P2-3_PE-500-016_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.21 | 148.37 | AC1-054 | AP_P2-3_PE-500-015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.12 | 147.99 | AC1-054 | PJM_500_BG_P4_5_CNSTN_L_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.41 | 147.97 | AC1-054 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.21 | 147.79 | AC1-054 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.23 | 147.77 | AC1-054 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.96 | 147.58 | AC1-054 | PECO_P4_NOTTI85_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.9 | 147.56 | AC1-054 | PECO_P1-2_220-08_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.33 | 147.52 | AC1-054 | AP_P1-2_WP-500-DRT17_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.33 | 147.52 | AC1-054 | AP_P1-2_PE-500-001_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.84 | 147.49 | AC1-054 | PECO_P4_COOPR125_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.28 | 147.45 | AC1-054 | AP_P2-3_PE-500-018C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2901 | 144.5 | 146.59 | AC2-012 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.96 | 144.25 | AC1-054 | PECO_P4_PEACH025_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.82 | 144.14 | AC1-054 | PECO_P1-2_PBTIE1_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 139.19 | 133.25 | AC1-054 | PECO_P4_PEACH205_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 139.08 | 132.93 | AC1-054 | PECO_P1-2_PBTIE2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 138.14 | 132.05 | AC1-054 | PECO_P4_PEACH055_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 133.46 | 127.64 | AC1-054 | PECO_P4_PEACH015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 128.91 | 127.17 | AC1-054 | DVP_P4-2: 514T595_SRT-SW |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 132.13 | 126.31 | AC1-054 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 127.16 | 125.46 | AC1-054 | DVP_P4-2: 51482_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 127.16 | 125.36 | AC1-054 | AP_P1-2_PE-500-407T_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 127.16 | 125.36 | AC1-054 | DVP_P1-2: LN 514_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 123.03 | 117.66 | AC1-054 | PECO_P4_PEACH225_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 117.36 | 115.45 | AC1-054 | AP_P2-3_PE-500-019C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 225.38 | 236.63 | AC1-065 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 223.38 | 236.63 | AC1-065 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 225.31 | 236.57 | AC1-065 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 223.31 | 236.57 | AC1-065 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 225.31 | 236.57 | AC1-065 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 223.31 | 236.57 | AC1-065 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 213.33 | 226.49 | AC1-065 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 213.27 | 226.43 | AC1-065 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 213.27 | 226.43 | AC1-065 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 209.08 | 223.27 | AC1-065 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 209.01 | 223.21 | AC1-065 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 209.01 | 223.21 | AC1-065 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 210.48 | 217.52 | AC1-065 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 208.48 | 217.5 | AC1-065 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 198.95 | 207.95 | AC1-065 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 194.69 | 204.6 | AC1-065 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 172.59 | 167.61 | AC1-065 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 171.62 | 166.17 | AC1-065 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 171.62 | 166.17 | AC1-065 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 171.61 | 166.16 | AC1-065 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 163.46 | 164.68 | AC1-065 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2901 | 145.36 | 147.58 | AC2-023 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 161.59 | 161.6 | AC1-065 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 161.59 | 161.6 | AC1-065 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 161.58 | 161.6 | AC1-065 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 163.68 | 158.7 | AC1-065 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 153.37 | 157.79 | AC1-065 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 161.88 | 157 | AC1-065 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 161.88 | 157 | AC1-065 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 151.69 | 156.47 | AC1-065 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 161.34 | 154.12 | AC1-065 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 148.33 | 152.82 | AC1-065 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 903 | 144.11 | 151.9 | AC1-065 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 152.65 | 150.99 | AC1-065 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 155.46 | 150.31 | AC1-065 | PN_P1-2_PN-500-010T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 903 | 142.59 | 149.29 | AC1-065 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 903 | 142.59 | 149.29 | AC1-065 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 903 | 142.57 | 149.28 | AC1-065 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.17 | 149.22 | AC1-065 | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.1 | 149.15 | AC1-065 | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.79 | 147.95 | AC1-065 | AP_P2-3_PE-500-016_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.85 | 147.93 | AC1-065 | AP_P2-3_PE-500-015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.78 | 147.65 | AC1-065 | PJM_500_BG_P4_5_CNSTN_L_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.06 | 147.63 | AC1-065 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.86 | 147.44 | AC1-065 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.88 | 147.43 | AC1-065 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.61 | 147.23 | AC1-065 | PECO_P4_NOTTI85_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.55 | 147.22 | AC1-065 | PECO_P1-2_220-08_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.49 | 147.15 | AC1-065 | PECO_P4_COOPR125_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 142.97 | 147.08 | AC1-065 | AP_P1-2_WP-500-DRT17_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 142.97 | 147.08 | AC1-065 | AP_P1-2_PE-500-001_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 142.92 | 147.01 | AC1-065 | AP_P2-3_PE-500-018C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2901 | 144.82 | 146.95 | AC2-059 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.57 | 143.87 | AC1-065 | PECO_P4_PEACH025_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.4 | 143.74 | AC1-065 | PECO_P1-2_PBTIE1_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 911 | 148.84 | 142.97 | AC1-065 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 911 | 147.89 | 141.65 | AC1-065 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 911 | 147.89 | 141.65 | AC1-065 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 911 | 147.88 | 141.64 | AC1-065 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204502 | 27JACKSON | 204514 | 27TMI | 1 | 230 | 227 | 781 | 132.95 | 141.42 | AC1-065 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204502 | 27JACKSON | 204514 | 27TMI | 1 | 230 | 227 | 781 | 132.95 | 141.42 | AC1-065 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204502 | 27JACKSON | 204514 | 27TMI | 1 | 230 | 227 | 781 | 132.93 | 141.41 | AC1-065 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 903 | 135.51 | 139.44 | AC1-065 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 1031 | 130.73 | 138.98 | AC1-065 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 1031 | 130.23 | 137.91 | AC1-065 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 1031 | 130.23 | 137.91 | AC1-065 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 1031 | 130.22 | 137.91 | AC1-065 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 911 | 140.02 | 134.91 | AC1-065 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 138.81 | 132.89 | AC1-065 | PECO_P4_PEACH205_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 207923 | BRISREAC | 208132 | WHEM TR1 | 1 | 230 | 229 | 676 | 124.19 | 132.74 | AC1-065 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 207922 | BRIS | 207923 | BRISREAC | RX | 230 | 229 | 676 | 124.19 | 132.74 | AC1-065 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 138.7 | 132.56 | AC1-065 | PECO_P1-2_PBTIE2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208078 | SAKR | 1 | 230 | 229 | 903 | 124.39 | 132.32 | AC1-065 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208078 | SAKR | 1 | 230 | 229 | 903 | 124.39 | 132.32 | AC1-065 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208078 | SAKR | 1 | 230 | 229 | 903 | 124.38 | 132.32 | AC1-065 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 137.78 | 131.7 | AC1-065 | PECO_P4_PEACH055_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204502 | 27JACKSON | 204514 | 27TMI | 1 | 230 | 227 | 781 | 125.3 | 130.87 | AC1-065 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 1031 | 124.63 | 129.13 | AC1-065 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 133.05 | 127.24 | AC1-065 | PECO_P4_PEACH015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 128.17 | 126.45 | AC1-065 | DVP_P4-2: 514T595_SRT-SW |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 131.75 | 125.95 | AC1-065 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220953 | HOWARD12 | 220972 | GRANITE1 | 1 | 230 | 232 | 772 | 129.5 | 125.52 | AC1-065 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220954 | HOWARD32 | 220973 | GRANITE6 | 1 | 230 | 232 | 772 | 128.36 | 124.84 | AC1-065 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 126.41 | 124.67 | AC1-065 | DVP_P4-2: 51482_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 793 | 126.39 | 124.64 | AC1-065 | DVP_P4-2: 514T595_SRT-SW |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 2 | 230 | 233 | 793 | 126.39 | 124.64 | AC1-065 | DVP_P4-2: 514T595_SRT-SW |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 126.41 | 124.58 | AC1-065 | AP_P1-2_PE-500-407T_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 126.41 | 124.58 | AC1-065 | DVP_P1-2: LN 514_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220953 | HOWARD12 | 220972 | GRANITE1 | 1 | 230 | 232 | 772 | 128.59 | 124.55 | AC1-065 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220953 | HOWARD12 | 220972 | GRANITE1 | 1 | 230 | 232 | 772 | 128.59 | 124.55 | AC1-065 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208020 | MANO TR3 | 1 | 230 | 229 | 793 | 111.38 | 124.5 | AC1-065 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208020 | MANO TR3 | 1 | 230 | 229 | 793 | 111.37 | 124.5 | AC1-065 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208020 | MANO TR3 | 1 | 230 | 229 | 793 | 111.38 | 124.5 | AC1-065 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220954 | HOWARD32 | 220973 | GRANITE6 | 1 | 230 | 232 | 772 | 127.57 | 123.99 | AC1-065 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220954 | HOWARD32 | 220973 | GRANITE6 | 1 | 230 | 232 | 772 | 127.57 | 123.99 | AC1-065 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 793 | 125.14 | 123.38 | AC1-065 | DVP_P4-2: 51482_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 2 | 230 | 233 | 793 | 125.14 | 123.38 | AC1-065 | DVP_P4-2: 51482_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 793 | 125.14 | 123.3 | AC1-065 | AP_P1-2_PE-500-407T_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 793 | 125.14 | 123.3 | AC1-065 | DVP_P1-2: LN 514_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 2 | 230 | 233 | 793 | 125.14 | 123.3 | AC1-065 | DVP_P1-2: LN 514_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 2 | 230 | 233 | 793 | 125.14 | 123.3 | AC1-065 | AP_P1-2_PE-500-407T_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208078 | SAKR | 1 | 230 | 229 | 903 | 117.12 | 122.35 | AC1-065 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200025 | W CHAPEL | 1 | 500 | 225 | 1732 | 123.51 | 121.73 | AC1-065 | PEPCO_P4_PP41_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208031 | MLWD TR2 | 1 | 230 | 229 | 911 | 111.69 | 121.07 | AC1-065 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208031 | MLWD TR2 | 1 | 230 | 229 | 911 | 111.68 | 121.07 | AC1-065 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208031 | MLWD TR2 | 1 | 230 | 229 | 911 | 111.69 | 121.07 | AC1-065 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220965 | NEAST339 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 119.68 | 119.02 | AC1-065 | BG_P1_2315_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220965 | NEAST339 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 119.26 | 118.82 | AC1-065 | BG_P4_5_NEAST_17_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220965 | NEAST339 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 119.41 | 118.82 | AC1-065 | BG_P4_5_NEAST_15_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 114.63 | 118.31 | AC1-065 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220979 | NEAST317 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 118.76 | 118.16 | AC1-065 | BG_P1_2337_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 114.29 | 117.97 | AC1-065 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 114.28 | 117.91 | AC1-065 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 114.28 | 117.91 | AC1-065 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220979 | NEAST317 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 118.43 | 117.89 | AC1-065 | BG_P4_5_NEAST_39_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220979 | NEAST317 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 118.43 | 117.89 | AC1-065 | BG_P4_5_NEAST_37_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 113.94 | 117.58 | AC1-065 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 113.94 | 117.58 | AC1-065 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 122.66 | 117.3 | AC1-065 | PECO_P4_PEACH225_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 793 | 118.48 | 115.7 | AC1-065 | PEPCO_P1_PP2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 2 | 230 | 233 | 793 | 118.48 | 115.7 | AC1-065 | PEPCO_P1_PP1_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 2 | 500/230 | 225/232 | 2168 | 109.59 | 114.89 | AC1-065 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 2 | 500/230 | 225/232 | 2168 | 109.41 | 114.67 | AC1-065 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 2 | 500/230 | 225/232 | 2168 | 109.41 | 114.67 | AC1-065 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 116.63 | 114.67 | AC1-065 | AP_P2-3_PE-500-019C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 1 | 500/230 | 225/232 | 2168 | 109.36 | 114.65 | AC1-065 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 1 | 500/230 | 225/232 | 2168 | 109.18 | 114.43 | AC1-065 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 1 | 500/230 | 225/232 | 2168 | 109.18 | 114.43 | AC1-065 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220964 | GRACETON | 220999 | BAGLEY2 | 13 | 230 | 232 | 1795 | 113.36 | 114.4 | AC1-065 | BG_P4_5_GRCTN_3T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208020 | MANO TR3 | 1 | 230 | 229 | 793 | 104.19 | 113.93 | AC1-065 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208020 | MANO TR3 | 208031 | MLWD TR2 | 1 | 230 | 229 | 903 | 102.51 | 113.63 | AC1-065 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208020 | MANO TR3 | 208031 | MLWD TR2 | 1 | 230 | 229 | 903 | 101.8 | 112.44 | AC1-065 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208020 | MANO TR3 | 208031 | MLWD TR2 | 1 | 230 | 229 | 903 | 101.8 | 112.44 | AC1-065 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208020 | MANO TR3 | 208031 | MLWD TR2 | 1 | 230 | 229 | 903 | 101.8 | 112.44 | AC1-065 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 2 | 500/230 | 225/232 | 2168 | 108.46 | 111.75 | AC1-065 | PJM_500_BG_P4_5_CNSTN_15_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208031 | MLWD TR2 | 1 | 230 | 229 | 911 | 104.93 | 111.59 | AC1-065 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 106.41 | 111.17 | AC1-065 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220980 | RAPHAEL | 220999 | BAGLEY2 | 13 | 230 | 232 | 1795 | 108.95 | 111.15 | AC1-065 | BG_P4_5_GRCTN_3T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 106.29 | 111.04 | AC1-065 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 793 | 112.61 | 109.95 | AC1-065 | PEPCO_P4_PP19_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 793 | 109.37 | 107.44 | AC1-065 | AP_P2-3_PE-500-019C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 2 | 230 | 233 | 793 | 109.37 | 107.44 | AC1-065 | AP_P2-3_PE-500-019C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220965 | NEAST339 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 108.24 | 106.81 | AC1-065 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220965 | NEAST339 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 108.14 | 106.7 | AC1-065 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220965 | NEAST339 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 108.14 | 106.7 | AC1-065 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 101.53 | 105.69 | AC1-065 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 101.45 | 105.6 | AC1-065 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220979 | NEAST317 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 105.13 | 103.76 | AC1-065 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220979 | NEAST317 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 105.03 | 103.65 | AC1-065 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220979 | NEAST317 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 105.03 | 103.65 | AC1-065 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 99.44 | 103.3 | AC1-065 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 99.43 | 103.3 | AC1-065 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 99.44 | 103.3 | AC1-065 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208020 | MANO TR3 | 208031 | MLWD TR2 | 1 | 230 | 229 | 903 | 95.43 | 103.21 | AC1-065 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220964 | GRACETON | 220999 | BAGLEY2 | 13 | 230 | 232 | 1795 | 101.43 | 102.17 | AC1-065 | BG_P1_2305_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220964 | GRACETON | 221000 | BAGLEY | 5 | 230 | 232 | 1795 | 101.42 | 102.17 | AC1-065 | BG_P1_2313_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220965 | NEAST339 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 102.67 | 101.99 | AC1-065 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 98.51 | 101.97 | AC1-065 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 98.61 | 100.62 | AC1-065 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 144.32 | 139.17 | AC1-068 | PL_10_P42_100570_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 144.32 | 139.17 | AC1-068 | PL_10_P42_100570_A_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 143.51 | 138.38 | AC1-068 | PL_10_P12_000085_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 143.41 | 138.29 | AC1-068 | PN_P2-3_PN-500-004-DRT-008_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 143.41 | 138.29 | AC1-068 | PN_P2-3_PN-500-DRT31_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 143.04 | 137.92 | AC1-068 | PL_30_P42_000131_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 144.32 | 139.17 | AC1-069 | PL_10_P42_100570_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 144.32 | 139.17 | AC1-069 | PL_10_P42_100570_A_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 143.51 | 138.38 | AC1-069 | PL_10_P12_000085_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 143.41 | 138.29 | AC1-069 | PN_P2-3_PN-500-004-DRT-008_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 143.41 | 138.29 | AC1-069 | PN_P2-3_PN-500-DRT31_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 143.04 | 137.92 | AC1-069 | PL_30_P42_000131_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2901 | 144.85 | 146.99 | AC2-060 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 153.79 | 158.3 | AC1-074 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.26 | 157.39 | AC1-074 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.26 | 157.39 | AC1-074 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 152.1 | 156.98 | AC1-074 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 161.74 | 154.52 | AC1-074 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 148.74 | 153.32 | AC1-074 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 155.83 | 150.68 | AC1-074 | PN_P1-2_PN-500-010T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.58 | 149.7 | AC1-074 | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.51 | 149.63 | AC1-074 | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.21 | 148.49 | AC1-074 | AP_P2-3_PE-500-016_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.28 | 148.46 | AC1-074 | AP_P2-3_PE-500-015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.15 | 148.02 | AC1-074 | PJM_500_BG_P4_5_CNSTN_L_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.41 | 147.97 | AC1-074 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.21 | 147.79 | AC1-074 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.23 | 147.77 | AC1-074 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.39 | 147.61 | AC1-074 | AP_P1-2_WP-500-DRT17_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.39 | 147.61 | AC1-074 | AP_P1-2_PE-500-001_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.96 | 147.58 | AC1-074 | PECO_P4_NOTTI85_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.9 | 147.56 | AC1-074 | PECO_P1-2_220-08_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.34 | 147.54 | AC1-074 | AP_P2-3_PE-500-018C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.84 | 147.5 | AC1-074 | PECO_P4_COOPR125_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2901 | 144.86 | 147 | AC2-061 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.94 | 144.23 | AC1-074 | PECO_P4_PEACH025_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.83 | 144.15 | AC1-074 | PECO_P1-2_PBTIE1_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 139.21 | 133.27 | AC1-074 | PECO_P4_PEACH205_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 139.09 | 132.93 | AC1-074 | PECO_P1-2_PBTIE2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 138.15 | 132.06 | AC1-074 | PECO_P4_PEACH055_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 133.47 | 127.65 | AC1-074 | PECO_P4_PEACH015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 132.14 | 126.32 | AC1-074 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 123.04 | 117.67 | AC1-074 | PECO_P4_PEACH225_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2901 | 144.76 | 146.88 | AC2-079 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 153.72 | 158.21 | AC1-075 and AC1-080 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.21 | 157.33 | AC1-075 and AC1-080 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.21 | 157.33 | AC1-075 and AC1-080 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 152.03 | 156.89 | AC1-075 and AC1-080 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 161.7 | 154.48 | AC1-075 and AC1-080 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 148.67 | 153.24 | AC1-075 and AC1-080 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 155.78 | 150.63 | AC1-075 and AC1-080 | PN_P1-2_PN-500-010T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.51 | 149.62 | AC1-075 and AC1-080 | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.44 | 149.54 | AC1-075 and AC1-080 | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.13 | 148.38 | AC1-075 and AC1-080 | AP_P2-3_PE-500-016_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.2 | 148.35 | AC1-075 and AC1-080 | AP_P2-3_PE-500-015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.09 | 147.96 | AC1-075 and AC1-080 | PJM_500_BG_P4_5_CNSTN_L_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.38 | 147.94 | AC1-075 and AC1-080 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.18 | 147.75 | AC1-075 and AC1-080 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.2 | 147.74 | AC1-075 and AC1-080 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.93 | 147.54 | AC1-075 and AC1-080 | PECO_P4_NOTTI85_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.87 | 147.53 | AC1-075 and AC1-080 | PECO_P1-2_220-08_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.31 | 147.5 | AC1-075 and AC1-080 | AP_P1-2_WP-500-DRT17_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.31 | 147.5 | AC1-075 and AC1-080 | AP_P1-2_PE-500-001_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.81 | 147.46 | AC1-075 and AC1-080 | PECO_P4_COOPR125_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.26 | 147.43 | AC1-075 and AC1-080 | AP_P2-3_PE-500-018C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2901 | 144.87 | 147.01 | AC2-084 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.92 | 144.21 | AC1-075 and AC1-080 | PECO_P4_PEACH025_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.78 | 144.11 | AC1-075 and AC1-080 | PECO_P1-2_PBTIE1_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 139.16 | 133.22 | AC1-075 and AC1-080 | PECO_P4_PEACH205_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 139.05 | 132.89 | AC1-075 and AC1-080 | PECO_P1-2_PBTIE2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 138.11 | 132.02 | AC1-075 and AC1-080 | PECO_P4_PEACH055_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 133.43 | 127.6 | AC1-075 and AC1-080 | PECO_P4_PEACH015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 128.92 | 127.19 | AC1-075 and AC1-080 | DVP_P4-2: 514T595_SRT-SW |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 132.1 | 126.28 | AC1-075 and AC1-080 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 127.18 | 125.48 | AC1-075 and AC1-080 | DVP_P4-2: 51482_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 127.18 | 125.39 | AC1-075 and AC1-080 | DVP_P1-2: LN 514_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 127.18 | 125.39 | AC1-075 and AC1-080 | AP_P1-2_PE-500-407T_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 123 | 117.63 | AC1-075 and AC1-080 | PECO_P4_PEACH225_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 117.37 | 115.47 | AC1-075 and AC1-080 | AP_P2-3_PE-500-019C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2901 | 144.93 | 147.08 | AC2-088 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 153.7 | 158.18 | AC1-076 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.2 | 157.32 | AC1-076 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.2 | 157.32 | AC1-076 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 152.01 | 156.86 | AC1-076 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 161.71 | 154.48 | AC1-076 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 148.65 | 153.21 | AC1-076 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 155.77 | 150.62 | AC1-076 | PN_P1-2_PN-500-010T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.49 | 149.59 | AC1-076 | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.42 | 149.52 | AC1-076 | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.1 | 148.34 | AC1-076 | AP_P2-3_PE-500-016_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.17 | 148.31 | AC1-076 | AP_P2-3_PE-500-015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.09 | 147.95 | AC1-076 | PJM_500_BG_P4_5_CNSTN_L_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.38 | 147.95 | AC1-076 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.18 | 147.76 | AC1-076 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.21 | 147.75 | AC1-076 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.94 | 147.55 | AC1-076 | PECO_P4_NOTTI85_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.88 | 147.53 | AC1-076 | PECO_P1-2_220-08_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.81 | 147.47 | AC1-076 | PECO_P4_COOPR125_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.28 | 147.46 | AC1-076 | AP_P1-2_PE-500-001_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.28 | 147.46 | AC1-076 | AP_P1-2_WP-500-DRT17_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.23 | 147.39 | AC1-076 | AP_P2-3_PE-500-018C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2901 | 144.89 | 147.03 | AC2-100 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.94 | 144.22 | AC1-076 | PECO_P4_PEACH025_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.79 | 144.11 | AC1-076 | PECO_P1-2_PBTIE1_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 139.16 | 133.22 | AC1-076 | PECO_P4_PEACH205_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 139.05 | 132.9 | AC1-076 | PECO_P1-2_PBTIE2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 138.11 | 132.02 | AC1-076 | PECO_P4_PEACH055_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 133.43 | 127.61 | AC1-076 | PECO_P4_PEACH015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 128.71 | 126.97 | AC1-076 | DVP_P4-2: 514T595_SRT-SW |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 132.1 | 126.28 | AC1-076 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 126.96 | 125.25 | AC1-076 | DVP_P4-2: 51482_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 126.96 | 125.16 | AC1-076 | DVP_P1-2: LN 514_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 126.96 | 125.16 | AC1-076 | AP_P1-2_PE-500-407T_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 123 | 117.63 | AC1-076 | PECO_P4_PEACH225_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 117.17 | 115.24 | AC1-076 | AP_P2-3_PE-500-019C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 225.57 | 237.07 | AC1-078 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 223.56 | 237.07 | AC1-078 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 225.5 | 237.01 | AC1-078 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 223.5 | 237.01 | AC1-078 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 225.5 | 237.01 | AC1-078 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 223.5 | 237.01 | AC1-078 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 213.51 | 226.91 | AC1-078 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 213.45 | 226.85 | AC1-078 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 213.45 | 226.85 | AC1-078 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 209.25 | 223.7 | AC1-078 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 209.19 | 223.64 | AC1-078 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 209.19 | 223.64 | AC1-078 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 208.67 | 217.89 | AC1-078 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 210.67 | 217.88 | AC1-078 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 199.13 | 208.32 | AC1-078 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 194.87 | 204.97 | AC1-078 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 172.83 | 167.9 | AC1-078 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 161.81 | 161.96 | AC1-078 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 161.81 | 161.95 | AC1-078 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 161.8 | 161.95 | AC1-078 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2901 | 144.85 | 146.99 | AC2-103 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 153.62 | 158.1 | AC1-078 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.07 | 157.2 | AC1-078 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.07 | 157.2 | AC1-078 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 151.94 | 156.78 | AC1-078 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 161.48 | 154.26 | AC1-078 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 148.57 | 153.13 | AC1-078 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 155.65 | 150.5 | AC1-078 | PN_P1-2_PN-500-010T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.41 | 149.51 | AC1-078 | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.34 | 149.44 | AC1-078 | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.07 | 148.34 | AC1-078 | AP_P2-3_PE-500-016_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.14 | 148.31 | AC1-078 | AP_P2-3_PE-500-015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.96 | 147.84 | AC1-078 | PJM_500_BG_P4_5_CNSTN_L_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.17 | 147.74 | AC1-078 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.97 | 147.56 | AC1-078 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153 | 147.54 | AC1-078 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.25 | 147.46 | AC1-078 | AP_P1-2_PE-500-001_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.25 | 147.46 | AC1-078 | AP_P1-2_WP-500-DRT17_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.2 | 147.39 | AC1-078 | AP_P2-3_PE-500-018C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.73 | 147.35 | AC1-078 | PECO_P4_NOTTI85_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.67 | 147.33 | AC1-078 | PECO_P1-2_220-08_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.6 | 147.27 | AC1-078 | PECO_P4_COOPR125_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2901 | 144.93 | 147.08 | AC2-111 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.66 | 143.95 | AC1-078 | PECO_P4_PEACH025_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.56 | 143.89 | AC1-078 | PECO_P1-2_PBTIE1_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 911 | 149.07 | 143.24 | AC1-078 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 1031 | 130.37 | 138.2 | AC1-078 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 1031 | 130.37 | 138.2 | AC1-078 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 1031 | 130.36 | 138.2 | AC1-078 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 138.97 | 133.04 | AC1-078 | PECO_P4_PEACH205_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 138.84 | 132.69 | AC1-078 | PECO_P1-2_PBTIE2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208078 | SAKR | 1 | 230 | 229 | 903 | 124.54 | 132.64 | AC1-078 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 137.91 | 131.83 | AC1-078 | PECO_P4_PEACH055_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 133.21 | 127.4 | AC1-078 | PECO_P4_PEACH015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 131.9 | 126.09 | AC1-078 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208020 | MANO TR3 | 1 | 230 | 229 | 793 | 111.53 | 124.74 | AC1-078 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208020 | MANO TR3 | 1 | 230 | 229 | 793 | 111.52 | 124.74 | AC1-078 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208020 | MANO TR3 | 1 | 230 | 229 | 793 | 111.53 | 124.74 | AC1-078 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 122.81 | 117.44 | AC1-078 | PECO_P4_PEACH225_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.51 | 148.07 | AC1-082 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.31 | 147.89 | AC1-082 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.34 | 147.87 | AC1-082 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.07 | 147.68 | AC1-082 | PECO_P4_NOTTI85_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153 | 147.66 | AC1-082 | PECO_P1-2_220-08_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.94 | 147.6 | AC1-082 | PECO_P4_COOPR125_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.6 | 147.4 | AC1-082 | PECO_P1-2_220-93_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 150.82 | 145.86 | AC1-082 | PL_05_P71_000906_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 150.94 | 145.62 | AC1-082 | DVP_P4-3: H1TH3_SRT-SW |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 148.47 | 143.25 | AC1-082 | AP_P2-2_WP-500-DRT16_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 225.7 | 237.21 | AC1-083 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 223.7 | 237.21 | AC1-083 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 225.64 | 237.14 | AC1-083 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 223.63 | 237.14 | AC1-083 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 225.64 | 237.14 | AC1-083 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 223.63 | 237.14 | AC1-083 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 213.64 | 227.04 | AC1-083 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 213.58 | 226.98 | AC1-083 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 213.58 | 226.98 | AC1-083 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 209.38 | 223.84 | AC1-083 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 209.32 | 223.78 | AC1-083 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 209.32 | 223.77 | AC1-083 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 172.86 | 167.9 | AC1-083 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2901 | 144.57 | 146.67 | AC2-112 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 153.63 | 158.1 | AC1-083 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.11 | 157.24 | AC1-083 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.11 | 157.23 | AC1-083 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 151.94 | 156.78 | AC1-083 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 161.58 | 154.36 | AC1-083 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 148.58 | 153.13 | AC1-083 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 155.69 | 150.54 | AC1-083 | PN_P1-2_PN-500-010T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.42 | 149.51 | AC1-083 | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.35 | 149.44 | AC1-083 | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.05 | 148.29 | AC1-083 | AP_P2-3_PE-500-016_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.12 | 148.26 | AC1-083 | AP_P2-3_PE-500-015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153 | 147.87 | AC1-083 | PJM_500_BG_P4_5_CNSTN_L_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.27 | 147.83 | AC1-083 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.07 | 147.65 | AC1-083 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.09 | 147.63 | AC1-083 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.82 | 147.44 | AC1-083 | PECO_P4_NOTTI85_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.76 | 147.42 | AC1-083 | PECO_P1-2_220-08_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.23 | 147.41 | AC1-083 | AP_P1-2_WP-500-DRT17_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.23 | 147.41 | AC1-083 | AP_P1-2_PE-500-001_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.7 | 147.36 | AC1-083 | PECO_P4_COOPR125_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.18 | 147.34 | AC1-083 | AP_P2-3_PE-500-018C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2901 | 144.9 | 147.05 | AC2-123 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.79 | 144.08 | AC1-083 | PECO_P4_PEACH025_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.66 | 143.99 | AC1-083 | PECO_P1-2_PBTIE1_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 911 | 149.1 | 143.23 | AC1-083 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 1031 | 130.39 | 138.22 | AC1-083 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 139.05 | 133.11 | AC1-083 | PECO_P4_PEACH205_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 138.93 | 132.78 | AC1-083 | PECO_P1-2_PBTIE2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 138 | 131.91 | AC1-083 | PECO_P4_PEACH055_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 133.3 | 127.49 | AC1-083 | PECO_P4_PEACH015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 128.85 | 127.13 | AC1-083 | DVP_P4-2: 514T595_SRT-SW |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 131.99 | 126.17 | AC1-083 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 127.11 | 125.41 | AC1-083 | DVP_P4-2: 51482_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 127.11 | 125.32 | AC1-083 | AP_P1-2_PE-500-407T_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 127.11 | 125.32 | AC1-083 | DVP_P1-2: LN 514_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200025 | W CHAPEL | 1 | 500 | 225 | 1732 | 123.79 | 122 | AC1-083 | PEPCO_P4_PP41_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 122.89 | 117.52 | AC1-083 | PECO_P4_PEACH225_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 117.3 | 115.4 | AC1-083 | AP_P2-3_PE-500-019C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 99.61 | 103.57 | AC1-083 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 99.6 | 103.57 | AC1-083 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 99.61 | 103.57 | AC1-083 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 98.78 | 100.86 | AC1-083 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 225.76 | 237.99 | AC1-085 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 223.77 | 237.99 | AC1-085 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 224.79 | 235.83 | AC1-085 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 222.8 | 235.82 | AC1-085 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 224.72 | 235.8 | AC1-085 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 222.74 | 235.8 | AC1-085 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 224.73 | 235.77 | AC1-085 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 222.74 | 235.76 | AC1-085 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 213.71 | 227.81 | AC1-085 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 212.78 | 225.71 | AC1-085 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 212.71 | 225.68 | AC1-085 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 212.71 | 225.65 | AC1-085 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 209.45 | 224.6 | AC1-085 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 208.52 | 222.49 | AC1-085 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 208.46 | 222.46 | AC1-085 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 208.46 | 222.43 | AC1-085 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 209.92 | 216.88 | AC1-085 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 207.93 | 216.88 | AC1-085 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 198.42 | 207.34 | AC1-085 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 194.16 | 203.99 | AC1-085 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 172.36 | 167.44 | AC1-085 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 171.38 | 166.08 | AC1-085 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 171.38 | 166.07 | AC1-085 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 171.36 | 166.07 | AC1-085 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 163.18 | 164.4 | AC1-085 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2901 | 144.7 | 146.82 | AC2-165 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 161.29 | 161.33 | AC1-085 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 161.29 | 161.32 | AC1-085 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 161.28 | 161.31 | AC1-085 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 163.45 | 158.64 | AC1-085 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 153.21 | 157.61 | AC1-085 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 161.62 | 156.76 | AC1-085 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 161.62 | 156.76 | AC1-085 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 151.53 | 156.3 | AC1-085 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 160.89 | 153.7 | AC1-085 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 148.17 | 152.64 | AC1-085 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 903 | 143.97 | 151.71 | AC1-085 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 152.37 | 150.79 | AC1-085 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 155.21 | 150.07 | AC1-085 | PN_P1-2_PN-500-010T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.02 | 149.05 | AC1-085 | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 903 | 142.41 | 149.02 | AC1-085 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 903 | 142.41 | 149 | AC1-085 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 903 | 142.4 | 148.99 | AC1-085 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 145.95 | 148.98 | AC1-085 | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.73 | 147.94 | AC1-085 | AP_P2-3_PE-500-016_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.79 | 147.91 | AC1-085 | AP_P2-3_PE-500-015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.53 | 147.41 | AC1-085 | PJM_500_BG_P4_5_CNSTN_L_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.66 | 147.24 | AC1-085 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 142.9 | 147.06 | AC1-085 | AP_P1-2_PE-500-001_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 142.9 | 147.06 | AC1-085 | AP_P1-2_WP-500-DRT17_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.46 | 147.05 | AC1-085 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.48 | 147.04 | AC1-085 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 142.85 | 146.99 | AC1-085 | AP_P2-3_PE-500-018C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.21 | 146.84 | AC1-085 | PECO_P4_NOTTI85_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.15 | 146.82 | AC1-085 | PECO_P1-2_220-08_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.09 | 146.76 | AC1-085 | PECO_P4_COOPR125_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2901 | 145.31 | 147.52 | AC2-185 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.04 | 143.36 | AC1-085 | PECO_P4_PEACH025_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 149.96 | 143.32 | AC1-085 | PECO_P1-2_PBTIE1_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 911 | 148.63 | 142.85 | AC1-085 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 911 | 147.68 | 141.62 | AC1-085 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 911 | 147.68 | 141.62 | AC1-085 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 911 | 147.66 | 141.61 | AC1-085 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204502 | 27JACKSON | 204514 | 27TMI | 1 | 230 | 227 | 781 | 132.45 | 141.08 | AC1-085 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204502 | 27JACKSON | 204514 | 27TMI | 1 | 230 | 227 | 781 | 132.65 | 141.01 | AC1-085 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204502 | 27JACKSON | 204514 | 27TMI | 1 | 230 | 227 | 781 | 132.65 | 140.99 | AC1-085 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204502 | 27JACKSON | 204514 | 27TMI | 1 | 230 | 227 | 781 | 132.64 | 140.98 | AC1-085 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 140.9 | 140.51 | AC1-085 | PJM_500_BG_P4_5_CNSTN_15_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 903 | 135.35 | 139.22 | AC1-085 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 1031 | 130.53 | 138.71 | AC1-085 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 1031 | 130.03 | 137.6 | AC1-085 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 1031 | 130.03 | 137.57 | AC1-085 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 1031 | 130.02 | 137.57 | AC1-085 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 911 | 139.82 | 134.91 | AC1-085 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208078 | SAKR | 1 | 230 | 229 | 903 | 124.88 | 133.46 | AC1-085 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 138.45 | 132.54 | AC1-085 | PECO_P4_PEACH205_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 207923 | BRISREAC | 208132 | WHEM TR1 | 1 | 230 | 229 | 676 | 124.07 | 132.48 | AC1-085 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 207922 | BRIS | 207923 | BRISREAC | RX | 230 | 229 | 676 | 124.07 | 132.48 | AC1-085 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 207922 | BRIS | 207923 | BRISREAC | RX | 230 | 229 | 676 | 124.07 | 132.46 | AC1-085 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 207923 | BRISREAC | 208132 | WHEM TR1 | 1 | 230 | 229 | 676 | 124.07 | 132.46 | AC1-085 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 207922 | BRIS | 207923 | BRISREAC | RX | 230 | 229 | 676 | 124.05 | 132.45 | AC1-085 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 207923 | BRISREAC | 208132 | WHEM TR1 | 1 | 230 | 229 | 676 | 124.05 | 132.45 | AC1-085 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 138.29 | 132.16 | AC1-085 | PECO_P1-2_PBTIE2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208078 | SAKR | 1 | 230 | 229 | 903 | 124.13 | 132.05 | AC1-085 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208078 | SAKR | 1 | 230 | 229 | 903 | 124.13 | 132.03 | AC1-085 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208078 | SAKR | 1 | 230 | 229 | 903 | 124.12 | 132.03 | AC1-085 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 137.39 | 131.33 | AC1-085 | PECO_P4_PEACH055_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220972 | GRANITE1 | 1 | 230 | 232 | 829 | 134.63 | 130.73 | AC1-085 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204502 | 27JACKSON | 204514 | 27TMI | 1 | 230 | 227 | 781 | 125.02 | 130.53 | AC1-085 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220972 | GRANITE1 | 1 | 230 | 232 | 829 | 134 | 130.07 | AC1-085 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220972 | GRANITE1 | 1 | 230 | 232 | 829 | 134 | 130.07 | AC1-085 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 1031 | 124.44 | 128.87 | AC1-085 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220973 | GRANITE6 | 1 | 230 | 232 | 829 | 132.57 | 128.84 | AC1-085 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220973 | GRANITE6 | 1 | 230 | 232 | 829 | 131.97 | 128.22 | AC1-085 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220973 | GRANITE6 | 1 | 230 | 232 | 829 | 131.97 | 128.22 | AC1-085 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 128.77 | 127.09 | AC1-085 | DVP_P4-2: 514T595_SRT-SW |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 132.64 | 126.85 | AC1-085 | PECO_P4_PEACH015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208020 | MANO TR3 | 1 | 230 | 229 | 793 | 111.94 | 125.71 | AC1-085 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 131.37 | 125.58 | AC1-085 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220953 | HOWARD12 | 220972 | GRANITE1 | 1 | 230 | 232 | 772 | 129.35 | 125.43 | AC1-085 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 127.02 | 125.37 | AC1-085 | DVP_P4-2: 51482_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 127.02 | 125.23 | AC1-085 | DVP_P1-2: LN 514_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 127.02 | 125.23 | AC1-085 | AP_P1-2_PE-500-407T_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220954 | HOWARD32 | 220973 | GRANITE6 | 1 | 230 | 232 | 772 | 128.22 | 124.75 | AC1-085 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220953 | HOWARD12 | 220972 | GRANITE1 | 1 | 230 | 232 | 772 | 128.43 | 124.45 | AC1-085 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220953 | HOWARD12 | 220972 | GRANITE1 | 1 | 230 | 232 | 772 | 128.43 | 124.45 | AC1-085 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 207922 | BRIS | 207923 | BRISREAC | RX | 230 | 229 | 676 | 118.97 | 124.39 | AC1-085 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 207923 | BRISREAC | 208132 | WHEM TR1 | 1 | 230 | 229 | 676 | 118.97 | 124.39 | AC1-085 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208020 | MANO TR3 | 1 | 230 | 229 | 793 | 111.1 | 124.03 | AC1-085 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208020 | MANO TR3 | 1 | 230 | 229 | 793 | 111.1 | 124.01 | AC1-085 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208020 | MANO TR3 | 1 | 230 | 229 | 793 | 111.1 | 124.01 | AC1-085 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220954 | HOWARD32 | 220973 | GRANITE6 | 1 | 230 | 232 | 772 | 127.42 | 123.9 | AC1-085 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220954 | HOWARD32 | 220973 | GRANITE6 | 1 | 230 | 232 | 772 | 127.42 | 123.9 | AC1-085 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 119.61 | 122.39 | AC1-085 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 117.62 | 122.39 | AC1-085 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208078 | SAKR | 1 | 230 | 229 | 903 | 116.87 | 122.16 | AC1-085 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208031 | MLWD TR2 | 1 | 230 | 229 | 911 | 112.17 | 122.09 | AC1-085 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200025 | W CHAPEL | 1 | 500 | 225 | 1732 | 123.55 | 121.73 | AC1-085 | PEPCO_P4_PP41_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204512 | 27S.RDG | 204693 | 27BOONETOWN | 1 | 230 | 227 | 607 | 107.09 | 121.01 | AC1-085 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204512 | 27S.RDG | 204693 | 27BOONETOWN | 1 | 230 | 227 | 607 | 107.07 | 121 | AC1-085 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204512 | 27S.RDG | 204693 | 27BOONETOWN | 1 | 230 | 227 | 607 | 107.07 | 120.98 | AC1-085 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208031 | MLWD TR2 | 1 | 230 | 229 | 911 | 111.44 | 120.73 | AC1-085 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208031 | MLWD TR2 | 1 | 230 | 229 | 911 | 111.44 | 120.7 | AC1-085 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208031 | MLWD TR2 | 1 | 230 | 229 | 911 | 111.43 | 120.7 | AC1-085 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220965 | NEAST339 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 119.6 | 118.95 | AC1-085 | BG_P1_2315_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 911 | 117.93 | 118.92 | AC1-085 | PJM_500_BG_P4_5_CNSTN_15_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220965 | NEAST339 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 119.18 | 118.74 | AC1-085 | BG_P4_5_NEAST_17_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220965 | NEAST339 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 119.34 | 118.74 | AC1-085 | BG_P4_5_NEAST_15_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 114.55 | 118.26 | AC1-085 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220979 | NEAST317 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 118.69 | 118.08 | AC1-085 | BG_P1_2337_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 114.21 | 117.92 | AC1-085 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 114.19 | 117.86 | AC1-085 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 114.19 | 117.85 | AC1-085 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220979 | NEAST317 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 118.36 | 117.82 | AC1-085 | BG_P4_5_NEAST_39_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220979 | NEAST317 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 118.36 | 117.82 | AC1-085 | BG_P4_5_NEAST_37_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 113.86 | 117.52 | AC1-085 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 113.86 | 117.52 | AC1-085 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208131 | WHEM | 208132 | WHEM TR1 | 1 | 230 | 229 | 691 | 108.37 | 117.35 | AC1-085 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208131 | WHEM | 208132 | WHEM TR1 | 1 | 230 | 229 | 691 | 108.37 | 117.33 | AC1-085 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208131 | WHEM | 208132 | WHEM TR1 | 1 | 230 | 229 | 691 | 108.35 | 117.33 | AC1-085 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 122.28 | 116.94 | AC1-085 | PECO_P4_PEACH225_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 111.22 | 115.91 | AC1-085 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 117.19 | 115.34 | AC1-085 | AP_P2-3_PE-500-019C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 116.66 | 115.06 | AC1-085 | PECO_P4_PEACH205_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 114.67 | 115.06 | AC1-085 | PECO_P4_PEACH205_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 2 | 500/230 | 225/232 | 2168 | 109.53 | 114.85 | AC1-085 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 116.24 | 114.66 | AC1-085 | PECO_P1-2_5014_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 114.25 | 114.66 | AC1-085 | PECO_P1-2_5014_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 2 | 500/230 | 225/232 | 2168 | 109.35 | 114.63 | AC1-085 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 2 | 500/230 | 225/232 | 2168 | 109.35 | 114.63 | AC1-085 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 1 | 500/230 | 225/232 | 2168 | 109.3 | 114.61 | AC1-085 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 1 | 500/230 | 225/232 | 2168 | 109.12 | 114.39 | AC1-085 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 1 | 500/230 | 225/232 | 2168 | 109.12 | 114.39 | AC1-085 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220964 | GRACETON | 220999 | BAGLEY2 | 13 | 230 | 232 | 1795 | 113.3 | 114.33 | AC1-085 | BG_P4_5_GRCTN_3T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 115.83 | 114.01 | AC1-085 | PECO_P4_PEACH215_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 113.84 | 114.01 | AC1-085 | PECO_P4_PEACH215_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208020 | MANO TR3 | 1 | 230 | 229 | 793 | 103.93 | 113.62 | AC1-085 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204512 | 27S.RDG | 204693 | 27BOONETOWN | 1 | 230 | 227 | 607 | 105.31 | 113.55 | AC1-085 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208020 | MANO TR3 | 208031 | MLWD TR2 | 1 | 230 | 229 | 903 | 102.28 | 113.34 | AC1-085 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 106.96 | 112.09 | AC1-085 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208020 | MANO TR3 | 208031 | MLWD TR2 | 1 | 230 | 229 | 903 | 101.56 | 111.97 | AC1-085 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208020 | MANO TR3 | 208031 | MLWD TR2 | 1 | 230 | 229 | 903 | 101.56 | 111.95 | AC1-085 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208020 | MANO TR3 | 208031 | MLWD TR2 | 1 | 230 | 229 | 903 | 101.56 | 111.95 | AC1-085 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 2 | 500/230 | 225/232 | 2168 | 108.44 | 111.73 | AC1-085 | PJM_500_BG_P4_5_CNSTN_15_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208031 | MLWD TR2 | 1 | 230 | 229 | 911 | 104.7 | 111.32 | AC1-085 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 106.36 | 111.1 | AC1-085 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220980 | RAPHAEL | 220999 | BAGLEY2 | 13 | 230 | 232 | 1795 | 108.89 | 111.09 | AC1-085 | BG_P4_5_GRCTN_3T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 106.23 | 110.97 | AC1-085 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208131 | WHEM | 208132 | WHEM TR1 | 1 | 230 | 229 | 691 | 103.59 | 109.87 | AC1-085 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 108.37 | 108.88 | AC1-085 | PECO_P4_PEACH205_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208131 | WHEM | 208133 | WHEM TR2 | 1 | 230 | 229 | 691 | 100.85 | 108.82 | AC1-085 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208131 | WHEM | 208133 | WHEM TR2 | 1 | 230 | 229 | 691 | 100.85 | 108.8 | AC1-085 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208131 | WHEM | 208133 | WHEM TR2 | 1 | 230 | 229 | 691 | 100.83 | 108.79 | AC1-085 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 107.96 | 108.5 | AC1-085 | PECO_P1-2_5014_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 107.57 | 107.87 | AC1-085 | PECO_P4_PEACH215_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220965 | NEAST339 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 108.15 | 106.76 | AC1-085 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220965 | NEAST339 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 108.05 | 106.64 | AC1-085 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220965 | NEAST339 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 108.05 | 106.64 | AC1-085 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 101.48 | 105.63 | AC1-085 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 101.39 | 105.54 | AC1-085 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 104.12 | 105.17 | AC1-085 | PECO_P4_PEACH205_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 103.7 | 104.79 | AC1-085 | PECO_P1-2_5014_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 102.59 | 104.6 | AC1-085 | BG_P1_2322_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 102.52 | 104.52 | AC1-085 | BG_P1_2310_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 102.53 | 104.49 | AC1-085 | BG_P4_5_NW2322_230-4_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 102.46 | 104.45 | AC1-085 | BG_P4_5_NW2310_230-5_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200099 | LAUS | 208045 | LAUS | 3 | 500/230 | 225/229 | 1200 | 102.8 | 104.34 | AC1-085 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200099 | LAUS | 208045 | LAUS | 3 | 500/230 | 225/229 | 1200 | 102.8 | 104.34 | AC1-085 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200099 | LAUS | 208045 | LAUS | 3 | 500/230 | 225/229 | 1200 | 102.79 | 104.33 | AC1-085 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 104.96 | 104.28 | AC1-085 | PECO_P1-2_5025/* $ CHESCO $ PECO_P1-2_5025 $ L_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 102.97 | 104.28 | AC1-085 | PECO_P1-2_5025/* $ CHESCO $ PECO_P1-2_5025 $ L_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 103.32 | 104.17 | AC1-085 | PECO_P4_PEACH215_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220979 | NEAST317 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 105.05 | 103.71 | AC1-085 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220979 | NEAST317 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 104.95 | 103.6 | AC1-085 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220979 | NEAST317 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 104.95 | 103.6 | AC1-085 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 99.62 | 103.45 | AC1-085 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 99.62 | 103.44 | AC1-085 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 99.62 | 103.44 | AC1-085 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208021 | MANO TR4 | 208133 | WHEM TR2 | 2 | 230 | 229 | 593 | 95.26 | 103.44 | AC1-085 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208021 | MANO TR4 | 208133 | WHEM TR2 | 2 | 230 | 229 | 593 | 95.26 | 103.42 | AC1-085 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208021 | MANO TR4 | 208133 | WHEM TR2 | 2 | 230 | 229 | 593 | 95.25 | 103.41 | AC1-085 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 101.19 | 103.23 | AC1-085 | BG_P4_5_NW230-2_2322_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 101.09 | 103.12 | AC1-085 | BG_P4_5_NW2371_2310_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 101.09 | 103.12 | AC1-085 | BG_P4_5_NW230-3_2310_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208020 | MANO TR3 | 208031 | MLWD TR2 | 1 | 230 | 229 | 903 | 95.2 | 102.84 | AC1-085 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 100.21 | 102.18 | AC1-085 | BG_P4_5_CNSTN_14_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 98.68 | 102.13 | AC1-085 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220964 | GRACETON | 220999 | BAGLEY2 | 13 | 230 | 232 | 1795 | 101.37 | 102.12 | AC1-085 | BG_P1_2305_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220964 | GRACETON | 221000 | BAGLEY | 5 | 230 | 232 | 1795 | 101.37 | 102.12 | AC1-085 | BG_P1_2313_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220965 | NEAST339 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 102.61 | 101.92 | AC1-085 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220965 | NEAST339 | 220977 | RIV2339 | 1 | 230 | 232 | 991 | 103.21 | 101.81 | AC1-085 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220966 | RIV2317 | 220979 | NEAST317 | 1 | 230 | 232 | 940 | 102.81 | 101.79 | AC1-085 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220965 | NEAST339 | 220977 | RIV2339 | 1 | 230 | 232 | 991 | 103.16 | 101.75 | AC1-085 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220965 | NEAST339 | 220977 | RIV2339 | 1 | 230 | 232 | 991 | 103.16 | 101.75 | AC1-085 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220966 | RIV2317 | 220979 | NEAST317 | 1 | 230 | 232 | 940 | 102.76 | 101.73 | AC1-085 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220966 | RIV2317 | 220979 | NEAST317 | 1 | 230 | 232 | 940 | 102.76 | 101.73 | AC1-085 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 2 | 500/230 | 225/232 | 2168 | 98.95 | 101.7 | AC1-085 | BG_P1_CNSTN_500-2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 2 | 500/230 | 225/232 | 2168 | 98.95 | 101.7 | AC1-085 | PJM_500_BG_P2_CNSTN_230-N_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208131 | WHEM | 208133 | WHEM TR2 | 1 | 230 | 229 | 691 | 96.07 | 101.63 | AC1-085 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 1 | 500/230 | 225/232 | 2168 | 98.84 | 101.59 | AC1-085 | PJM_500_BG_P2_CNSTN_230-S_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 1 | 500/230 | 225/232 | 2168 | 98.84 | 101.59 | AC1-085 | BG_P1_CNSTN_500-4_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 98.79 | 100.8 | AC1-085 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 223960 | BRG 1T 230 | 1 | 500/230 | 225/233 | 1498 | 100.15 | 100.53 | AC1-085 | PEPCO_P4_PP41_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 225.27 | 236.49 | AC1-086 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 223.27 | 236.49 | AC1-086 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 223.21 | 236.4 | AC1-086 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 225.21 | 236.4 | AC1-086 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 223.21 | 236.4 | AC1-086 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 225.2 | 236.4 | AC1-086 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 213.23 | 226.34 | AC1-086 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 213.17 | 226.26 | AC1-086 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 213.17 | 226.26 | AC1-086 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 208.97 | 223.13 | AC1-086 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 208.91 | 223.05 | AC1-086 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 208.91 | 223.05 | AC1-086 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 210.38 | 217.37 | AC1-086 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 208.38 | 217.36 | AC1-086 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 198.85 | 207.81 | AC1-086 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 194.59 | 204.46 | AC1-086 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 172.53 | 167.55 | AC1-086 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 171.56 | 166.11 | AC1-086 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 171.56 | 166.11 | AC1-086 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 171.54 | 166.1 | AC1-086 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 163.39 | 164.6 | AC1-086 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2901 | 144.92 | 147.07 | AC2-195 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 161.52 | 161.52 | AC1-086 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 161.52 | 161.51 | AC1-086 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 161.51 | 161.51 | AC1-086 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 163.61 | 158.67 | AC1-086 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 153.32 | 157.73 | AC1-086 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 161.82 | 156.94 | AC1-086 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 161.82 | 156.94 | AC1-086 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 151.63 | 156.41 | AC1-086 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 161.26 | 154.05 | AC1-086 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 148.27 | 152.75 | AC1-086 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 903 | 144.06 | 151.83 | AC1-086 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 152.58 | 150.93 | AC1-086 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 155.4 | 150.25 | AC1-086 | PN_P1-2_PN-500-010T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 903 | 142.52 | 149.21 | AC1-086 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 903 | 142.53 | 149.2 | AC1-086 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 903 | 142.53 | 149.2 | AC1-086 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.12 | 149.16 | AC1-086 | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.05 | 149.09 | AC1-086 | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.74 | 147.9 | AC1-086 | AP_P2-3_PE-500-016_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.81 | 147.88 | AC1-086 | AP_P2-3_PE-500-015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.72 | 147.59 | AC1-086 | PJM_500_BG_P4_5_CNSTN_L_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.99 | 147.56 | AC1-086 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.79 | 147.37 | AC1-086 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.81 | 147.36 | AC1-086 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.54 | 147.16 | AC1-086 | PECO_P4_NOTTI85_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.48 | 147.15 | AC1-086 | PECO_P1-2_220-08_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.42 | 147.08 | AC1-086 | PECO_P4_COOPR125_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 142.92 | 147.03 | AC1-086 | AP_P1-2_PE-500-001_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 142.92 | 147.03 | AC1-086 | AP_P1-2_WP-500-DRT17_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 142.87 | 146.96 | AC1-086 | AP_P2-3_PE-500-018C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2901 | 145.46 | 147.7 | AD1-020 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.48 | 143.79 | AC1-086 | PECO_P4_PEACH025_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.32 | 143.66 | AC1-086 | PECO_P1-2_PBTIE1_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 911 | 148.78 | 142.92 | AC1-086 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 911 | 147.83 | 141.61 | AC1-086 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 911 | 147.83 | 141.61 | AC1-086 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 911 | 147.82 | 141.6 | AC1-086 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204502 | 27JACKSON | 204514 | 27TMI | 1 | 230 | 227 | 781 | 132.88 | 141.33 | AC1-086 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204502 | 27JACKSON | 204514 | 27TMI | 1 | 230 | 227 | 781 | 132.89 | 141.32 | AC1-086 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204502 | 27JACKSON | 204514 | 27TMI | 1 | 230 | 227 | 781 | 132.89 | 141.32 | AC1-086 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 140.9 | 140.52 | AC1-086 | PJM_500_BG_P4_5_CNSTN_15_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 903 | 135.46 | 139.36 | AC1-086 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 1031 | 130.68 | 138.91 | AC1-086 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 1031 | 130.18 | 137.84 | AC1-086 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 1031 | 130.19 | 137.83 | AC1-086 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 1031 | 130.19 | 137.83 | AC1-086 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 911 | 139.96 | 134.89 | AC1-086 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208078 | SAKR | 1 | 230 | 229 | 903 | 125.07 | 133.69 | AC1-086 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 138.74 | 132.82 | AC1-086 | PECO_P4_PEACH205_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 207923 | BRISREAC | 208132 | WHEM TR1 | 1 | 230 | 229 | 676 | 124.15 | 132.67 | AC1-086 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 207922 | BRIS | 207923 | BRISREAC | RX | 230 | 229 | 676 | 124.15 | 132.67 | AC1-086 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 207923 | BRISREAC | 208132 | WHEM TR1 | 1 | 230 | 229 | 676 | 124.17 | 132.67 | AC1-086 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 207922 | BRIS | 207923 | BRISREAC | RX | 230 | 229 | 676 | 124.17 | 132.67 | AC1-086 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 207923 | BRISREAC | 208132 | WHEM TR1 | 1 | 230 | 229 | 676 | 124.17 | 132.67 | AC1-086 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 207922 | BRIS | 207923 | BRISREAC | RX | 230 | 229 | 676 | 124.17 | 132.67 | AC1-086 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 138.62 | 132.49 | AC1-086 | PECO_P1-2_PBTIE2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208078 | SAKR | 1 | 230 | 229 | 903 | 124.33 | 132.24 | AC1-086 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208078 | SAKR | 1 | 230 | 229 | 903 | 124.33 | 132.23 | AC1-086 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208078 | SAKR | 1 | 230 | 229 | 903 | 124.33 | 132.23 | AC1-086 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 137.7 | 131.63 | AC1-086 | PECO_P4_PEACH055_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204502 | 27JACKSON | 204514 | 27TMI | 1 | 230 | 227 | 781 | 125.25 | 130.79 | AC1-086 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220972 | GRANITE1 | 1 | 230 | 232 | 829 | 134.71 | 130.76 | AC1-086 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220972 | GRANITE1 | 1 | 230 | 232 | 829 | 134.08 | 130.1 | AC1-086 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220972 | GRANITE1 | 1 | 230 | 232 | 829 | 134.08 | 130.1 | AC1-086 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 1031 | 124.59 | 129.06 | AC1-086 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220973 | GRANITE6 | 1 | 230 | 232 | 829 | 132.64 | 128.87 | AC1-086 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220973 | GRANITE6 | 1 | 230 | 232 | 829 | 132.05 | 128.25 | AC1-086 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220973 | GRANITE6 | 1 | 230 | 232 | 829 | 132.05 | 128.25 | AC1-086 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 132.97 | 127.16 | AC1-086 | PECO_P4_PEACH015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 128.16 | 126.45 | AC1-086 | DVP_P4-2: 514T595_SRT-SW |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208020 | MANO TR3 | 1 | 230 | 229 | 793 | 112.15 | 125.96 | AC1-086 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 131.68 | 125.87 | AC1-086 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220953 | HOWARD12 | 220972 | GRANITE1 | 1 | 230 | 232 | 772 | 129.44 | 125.47 | AC1-086 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220954 | HOWARD32 | 220973 | GRANITE6 | 1 | 230 | 232 | 772 | 128.3 | 124.78 | AC1-086 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 126.4 | 124.66 | AC1-086 | DVP_P4-2: 51482_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 2 | 230 | 233 | 793 | 126.4 | 124.66 | AC1-086 | DVP_P4-2: 514T595_SRT-SW |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 793 | 126.4 | 124.66 | AC1-086 | DVP_P4-2: 514T595_SRT-SW |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 126.4 | 124.57 | AC1-086 | AP_P1-2_PE-500-407T_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 126.4 | 124.57 | AC1-086 | DVP_P1-2: LN 514_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220953 | HOWARD12 | 220972 | GRANITE1 | 1 | 230 | 232 | 772 | 128.53 | 124.5 | AC1-086 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220953 | HOWARD12 | 220972 | GRANITE1 | 1 | 230 | 232 | 772 | 128.53 | 124.5 | AC1-086 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208020 | MANO TR3 | 1 | 230 | 229 | 793 | 111.32 | 124.42 | AC1-086 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208020 | MANO TR3 | 1 | 230 | 229 | 793 | 111.32 | 124.41 | AC1-086 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208020 | MANO TR3 | 1 | 230 | 229 | 793 | 111.32 | 124.41 | AC1-086 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220954 | HOWARD32 | 220973 | GRANITE6 | 1 | 230 | 232 | 772 | 127.51 | 123.94 | AC1-086 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220954 | HOWARD32 | 220973 | GRANITE6 | 1 | 230 | 232 | 772 | 127.51 | 123.94 | AC1-086 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 2 | 230 | 233 | 793 | 125.15 | 123.39 | AC1-086 | DVP_P4-2: 51482_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 793 | 125.15 | 123.39 | AC1-086 | DVP_P4-2: 51482_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 2 | 230 | 233 | 793 | 125.15 | 123.32 | AC1-086 | DVP_P1-2: LN 514_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 2 | 230 | 233 | 793 | 125.15 | 123.32 | AC1-086 | AP_P1-2_PE-500-407T_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 793 | 125.15 | 123.32 | AC1-086 | AP_P1-2_PE-500-407T_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 793 | 125.15 | 123.32 | AC1-086 | DVP_P1-2: LN 514_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208031 | MLWD TR2 | 1 | 230 | 229 | 911 | 112.35 | 122.32 | AC1-086 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208078 | SAKR | 1 | 230 | 229 | 903 | 117.07 | 122.27 | AC1-086 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204512 | 27S.RDG | 204693 | 27BOONETOWN | 1 | 230 | 227 | 607 | 107.33 | 122.12 | AC1-086 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204512 | 27S.RDG | 204693 | 27BOONETOWN | 1 | 230 | 227 | 607 | 107.31 | 122.06 | AC1-086 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204512 | 27S.RDG | 204693 | 27BOONETOWN | 1 | 230 | 227 | 607 | 107.31 | 122.06 | AC1-086 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200025 | W CHAPEL | 1 | 500 | 225 | 1732 | 123.49 | 121.69 | AC1-086 | PEPCO_P4_PP41_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208031 | MLWD TR2 | 1 | 230 | 229 | 911 | 111.63 | 121 | AC1-086 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208031 | MLWD TR2 | 1 | 230 | 229 | 911 | 111.64 | 120.99 | AC1-086 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208031 | MLWD TR2 | 1 | 230 | 229 | 911 | 111.63 | 120.99 | AC1-086 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220965 | NEAST339 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 119.64 | 118.99 | AC1-086 | BG_P1_2315_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 911 | 117.92 | 118.91 | AC1-086 | PJM_500_BG_P4_5_CNSTN_15_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220965 | NEAST339 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 119.22 | 118.78 | AC1-086 | BG_P4_5_NEAST_17_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220965 | NEAST339 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 119.38 | 118.78 | AC1-086 | BG_P4_5_NEAST_15_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 114.59 | 118.28 | AC1-086 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220979 | NEAST317 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 118.73 | 118.12 | AC1-086 | BG_P1_2337_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 114.26 | 117.94 | AC1-086 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 114.24 | 117.88 | AC1-086 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 114.24 | 117.88 | AC1-086 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220979 | NEAST317 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 118.4 | 117.86 | AC1-086 | BG_P4_5_NEAST_39_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220979 | NEAST317 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 118.4 | 117.86 | AC1-086 | BG_P4_5_NEAST_37_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 113.91 | 117.54 | AC1-086 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 113.91 | 117.54 | AC1-086 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208131 | WHEM | 208132 | WHEM TR1 | 1 | 230 | 229 | 691 | 108.45 | 117.52 | AC1-086 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208131 | WHEM | 208132 | WHEM TR1 | 1 | 230 | 229 | 691 | 108.46 | 117.52 | AC1-086 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208131 | WHEM | 208132 | WHEM TR1 | 1 | 230 | 229 | 691 | 108.46 | 117.52 | AC1-086 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 122.58 | 117.23 | AC1-086 | PECO_P4_PEACH225_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 2 | 230 | 233 | 793 | 118.49 | 115.71 | AC1-086 | PEPCO_P1_PP1_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 793 | 118.49 | 115.71 | AC1-086 | PEPCO_P1_PP2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 2 | 500/230 | 225/232 | 2168 | 109.56 | 114.86 | AC1-086 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 116.61 | 114.66 | AC1-086 | AP_P2-3_PE-500-019C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 2 | 500/230 | 225/232 | 2168 | 109.39 | 114.64 | AC1-086 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 2 | 500/230 | 225/232 | 2168 | 109.38 | 114.64 | AC1-086 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 1 | 500/230 | 225/232 | 2168 | 109.33 | 114.62 | AC1-086 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 1 | 500/230 | 225/232 | 2168 | 109.15 | 114.4 | AC1-086 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 1 | 500/230 | 225/232 | 2168 | 109.15 | 114.4 | AC1-086 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220964 | GRACETON | 220999 | BAGLEY2 | 13 | 230 | 232 | 1795 | 113.34 | 114.37 | AC1-086 | BG_P4_5_GRCTN_3T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208020 | MANO TR3 | 1 | 230 | 229 | 793 | 104.14 | 113.91 | AC1-086 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208020 | MANO TR3 | 208031 | MLWD TR2 | 1 | 230 | 229 | 903 | 102.46 | 113.56 | AC1-086 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208020 | MANO TR3 | 208031 | MLWD TR2 | 1 | 230 | 229 | 903 | 101.75 | 112.37 | AC1-086 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208020 | MANO TR3 | 208031 | MLWD TR2 | 1 | 230 | 229 | 903 | 101.75 | 112.36 | AC1-086 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208020 | MANO TR3 | 208031 | MLWD TR2 | 1 | 230 | 229 | 903 | 101.75 | 112.35 | AC1-086 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 2 | 500/230 | 225/232 | 2168 | 108.44 | 111.73 | AC1-086 | PJM_500_BG_P4_5_CNSTN_15_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208031 | MLWD TR2 | 1 | 230 | 229 | 911 | 104.88 | 111.51 | AC1-086 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 106.39 | 111.14 | AC1-086 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220980 | RAPHAEL | 220999 | BAGLEY2 | 13 | 230 | 232 | 1795 | 108.92 | 111.12 | AC1-086 | BG_P4_5_GRCTN_3T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 106.26 | 111 | AC1-086 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 793 | 112.61 | 109.95 | AC1-086 | PEPCO_P4_PP19_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 2 | 230 | 233 | 793 | 109.38 | 107.45 | AC1-086 | AP_P2-3_PE-500-019C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 793 | 109.38 | 107.45 | AC1-086 | AP_P2-3_PE-500-019C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220965 | NEAST339 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 108.2 | 106.78 | AC1-086 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220965 | NEAST339 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 108.1 | 106.66 | AC1-086 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220965 | NEAST339 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 108.1 | 106.66 | AC1-086 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 101.5 | 105.66 | AC1-086 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 101.42 | 105.57 | AC1-086 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220979 | NEAST317 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 105.1 | 103.73 | AC1-086 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220979 | NEAST317 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 105 | 103.62 | AC1-086 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220979 | NEAST317 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 105 | 103.62 | AC1-086 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 99.43 | 103.28 | AC1-086 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 99.43 | 103.28 | AC1-086 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 99.43 | 103.27 | AC1-086 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208020 | MANO TR3 | 208031 | MLWD TR2 | 1 | 230 | 229 | 903 | 95.38 | 103.14 | AC1-086 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220964 | GRACETON | 220999 | BAGLEY2 | 13 | 230 | 232 | 1795 | 101.4 | 102.15 | AC1-086 | BG_P1_2305_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220964 | GRACETON | 221000 | BAGLEY | 5 | 230 | 232 | 1795 | 101.4 | 102.15 | AC1-086 | BG_P1_2313_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220965 | NEAST339 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 102.64 | 101.95 | AC1-086 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 98.5 | 101.95 | AC1-086 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220965 | NEAST339 | 220977 | RIV2339 | 1 | 230 | 232 | 991 | 103.27 | 101.83 | AC1-086 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220965 | NEAST339 | 220977 | RIV2339 | 1 | 230 | 232 | 991 | 103.22 | 101.77 | AC1-086 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220965 | NEAST339 | 220977 | RIV2339 | 1 | 230 | 232 | 991 | 103.22 | 101.77 | AC1-086 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 2 | 500/230 | 225/232 | 2168 | 98.95 | 101.7 | AC1-086 | BG_P1_CNSTN_500-2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 2 | 500/230 | 225/232 | 2168 | 98.95 | 101.7 | AC1-086 | PJM_500_BG_P2_CNSTN_230-N_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 1 | 500/230 | 225/232 | 2168 | 98.85 | 101.59 | AC1-086 | PJM_500_BG_P2_CNSTN_230-S_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 1 | 500/230 | 225/232 | 2168 | 98.85 | 101.59 | AC1-086 | BG_P1_CNSTN_500-4_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 223960 | BRG 1T 230 | 1 | 500/230 | 225/233 | 1498 | 100.26 | 100.63 | AC1-086 | PEPCO_P4_PP41_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 98.6 | 100.6 | AC1-086 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 225.71 | 237.27 | AC1-089 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 223.71 | 237.27 | AC1-089 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 225.65 | 237.21 | AC1-089 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 223.64 | 237.21 | AC1-089 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 225.65 | 237.21 | AC1-089 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 223.64 | 237.21 | AC1-089 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 213.65 | 227.11 | AC1-089 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 213.59 | 227.05 | AC1-089 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 213.59 | 227.05 | AC1-089 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 209.39 | 223.9 | AC1-089 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 209.33 | 223.84 | AC1-089 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 209.33 | 223.84 | AC1-089 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2901 | 144.78 | 146.91 | AD1-022 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 153.69 | 158.18 | AC1-089 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.15 | 157.27 | AC1-089 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.14 | 157.27 | AC1-089 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 152 | 156.85 | AC1-089 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 161.59 | 154.37 | AC1-089 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 148.64 | 153.2 | AC1-089 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 155.72 | 150.57 | AC1-089 | PN_P1-2_PN-500-010T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.48 | 149.58 | AC1-089 | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.41 | 149.51 | AC1-089 | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.13 | 148.39 | AC1-089 | AP_P2-3_PE-500-016_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.19 | 148.36 | AC1-089 | AP_P2-3_PE-500-015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.03 | 147.91 | AC1-089 | PJM_500_BG_P4_5_CNSTN_L_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.27 | 147.84 | AC1-089 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.07 | 147.65 | AC1-089 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.1 | 147.64 | AC1-089 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.3 | 147.51 | AC1-089 | AP_P1-2_PE-500-001_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.3 | 147.51 | AC1-089 | AP_P1-2_WP-500-DRT17_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.83 | 147.44 | AC1-089 | PECO_P4_NOTTI85_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.25 | 147.44 | AC1-089 | AP_P2-3_PE-500-018C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.77 | 147.43 | AC1-089 | PECO_P1-2_220-08_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.7 | 147.36 | AC1-089 | PECO_P4_COOPR125_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2901 | 144.49 | 146.57 | AD1-025 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.78 | 144.07 | AC1-089 | PECO_P4_PEACH025_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.67 | 144 | AC1-089 | PECO_P1-2_PBTIE1_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 139.07 | 133.13 | AC1-089 | PECO_P4_PEACH205_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 138.94 | 132.79 | AC1-089 | PECO_P1-2_PBTIE2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 138.01 | 131.92 | AC1-089 | PECO_P4_PEACH055_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 133.32 | 127.5 | AC1-089 | PECO_P4_PEACH015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 132 | 126.18 | AC1-089 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 122.91 | 117.54 | AC1-089 | PECO_P4_PEACH225_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2901 | 144.81 | 146.95 | AD1-033 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.6 | 157.72 | AC1-091 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.6 | 157.72 | AC1-091 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 162.2 | 154.96 | AC1-091 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 156.17 | 151.02 | AC1-091 | PN_P1-2_PN-500-010T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.81 | 148.37 | AC1-091 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.47 | 148.34 | AC1-091 | PJM_500_BG_P4_5_CNSTN_L_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.61 | 148.18 | AC1-091 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.64 | 148.17 | AC1-091 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.37 | 147.97 | AC1-091 | PECO_P4_NOTTI85_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.31 | 147.96 | AC1-091 | PECO_P1-2_220-08_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.24 | 147.89 | AC1-091 | PECO_P4_COOPR125_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 151.48 | 144.74 | AC1-091 | PECO_P4_PEACH025_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 151.32 | 144.62 | AC1-091 | PECO_P1-2_PBTIE1_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 139.54 | 133.37 | AC1-091 | PECO_P1-2_PBTIE2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 138.58 | 132.47 | AC1-091 | PECO_P4_PEACH055_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 133.95 | 128.11 | AC1-091 | PECO_P4_PEACH015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 132.58 | 126.73 | AC1-091 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204512 | 27S.RDG | 204693 | 27BOONETOWN | 1 | 230 | 227 | 607 | 107.72 | 122.15 | AC1-091 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 123.49 | 118.1 | AC1-091 | PECO_P4_PEACH225_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2901 | 144.88 | 147.03 | AD1-041 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.6 | 157.72 | AC1-092 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.6 | 157.72 | AC1-092 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 162.2 | 154.96 | AC1-092 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 156.17 | 151.02 | AC1-092 | PN_P1-2_PN-500-010T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.81 | 148.37 | AC1-092 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.47 | 148.34 | AC1-092 | PJM_500_BG_P4_5_CNSTN_L_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.61 | 148.18 | AC1-092 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.64 | 148.17 | AC1-092 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.37 | 147.97 | AC1-092 | PECO_P4_NOTTI85_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.31 | 147.96 | AC1-092 | PECO_P1-2_220-08_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.24 | 147.89 | AC1-092 | PECO_P4_COOPR125_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 151.48 | 144.74 | AC1-092 | PECO_P4_PEACH025_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 151.32 | 144.62 | AC1-092 | PECO_P1-2_PBTIE1_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 139.54 | 133.37 | AC1-092 | PECO_P1-2_PBTIE2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 138.58 | 132.47 | AC1-092 | PECO_P4_PEACH055_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 133.95 | 128.11 | AC1-092 | PECO_P4_PEACH015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 132.58 | 126.73 | AC1-092 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204512 | 27S.RDG | 204693 | 27BOONETOWN | 1 | 230 | 227 | 607 | 107.72 | 122.15 | AC1-092 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 123.49 | 118.1 | AC1-092 | PECO_P4_PEACH225_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2901 | 144.76 | 146.89 | AD1-070 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.59 | 157.72 | AC1-093 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.59 | 157.72 | AC1-093 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 162.19 | 154.95 | AC1-093 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 156.17 | 151.01 | AC1-093 | PN_P1-2_PN-500-010T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.8 | 148.36 | AC1-093 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.6 | 148.17 | AC1-093 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.63 | 148.16 | AC1-093 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.36 | 147.96 | AC1-093 | PECO_P4_NOTTI85_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.3 | 147.95 | AC1-093 | PECO_P1-2_220-08_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.23 | 147.88 | AC1-093 | PECO_P4_COOPR125_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.89 | 147.69 | AC1-093 | PECO_P1-2_220-93_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 151.46 | 144.73 | AC1-093 | PECO_P4_PEACH025_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 151.31 | 144.61 | AC1-093 | PECO_P1-2_PBTIE1_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 139.53 | 133.36 | AC1-093 | PECO_P1-2_PBTIE2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 138.57 | 132.46 | AC1-093 | PECO_P4_PEACH055_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 133.94 | 128.1 | AC1-093 | PECO_P4_PEACH015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 132.57 | 126.72 | AC1-093 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204512 | 27S.RDG | 204693 | 27BOONETOWN | 1 | 230 | 227 | 607 | 107.72 | 122.14 | AC1-093 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 123.48 | 118.09 | AC1-093 | PECO_P4_PEACH225_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 162.17 | 154.92 | AC1-094 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.78 | 148.34 | AC1-094 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.58 | 148.15 | AC1-094 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.6 | 148.13 | AC1-094 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.33 | 147.94 | AC1-094 | PECO_P4_NOTTI85_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.27 | 147.92 | AC1-094 | PECO_P1-2_220-08_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.21 | 147.86 | AC1-094 | PECO_P4_COOPR125_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.87 | 147.67 | AC1-094 | PECO_P1-2_220-93_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 151.43 | 144.69 | AC1-094 | PECO_P4_PEACH025_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 151.27 | 144.58 | AC1-094 | PECO_P1-2_PBTIE1_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 145.17 | 139.98 | AC1-094 | DPL_P1_2_CKT 22074XX_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 144.64 | 139.48 | AC1-094 | PECO_P4_PEACH025_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 144.94 | 139.47 | AC1-094 | DPL_P1_2_CKT 23033_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 139.5 | 133.33 | AC1-094 | PECO_P1-2_PBTIE2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 138.54 | 132.44 | AC1-094 | PECO_P4_PEACH055_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 133.91 | 128.07 | AC1-094 | PECO_P4_PEACH015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204512 | 27S.RDG | 204693 | 27BOONETOWN | 1 | 230 | 227 | 607 | 107.71 | 122.13 | AC1-094 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 123.45 | 118.06 | AC1-094 | PECO_P4_PEACH225_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2901 | 144.83 | 146.96 | AD1-082 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 153.76 | 158.26 | AC1-098 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.25 | 157.37 | AC1-098 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.25 | 157.37 | AC1-098 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 152.07 | 156.93 | AC1-098 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 161.76 | 154.53 | AC1-098 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 148.71 | 153.28 | AC1-098 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 155.82 | 150.67 | AC1-098 | PN_P1-2_PN-500-010T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.54 | 149.66 | AC1-098 | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.47 | 149.59 | AC1-098 | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.16 | 148.42 | AC1-098 | AP_P2-3_PE-500-016_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.23 | 148.39 | AC1-098 | AP_P2-3_PE-500-015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.13 | 148 | AC1-098 | PJM_500_BG_P4_5_CNSTN_L_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.43 | 147.99 | AC1-098 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.23 | 147.8 | AC1-098 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.25 | 147.79 | AC1-098 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.98 | 147.59 | AC1-098 | PECO_P4_NOTTI85_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.92 | 147.58 | AC1-098 | PECO_P1-2_220-08_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.34 | 147.53 | AC1-098 | AP_P1-2_WP-500-DRT17_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.34 | 147.53 | AC1-098 | AP_P1-2_PE-500-001_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.85 | 147.51 | AC1-098 | PECO_P4_COOPR125_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.29 | 147.46 | AC1-098 | AP_P2-3_PE-500-018C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2901 | 144.7 | 146.81 | AD1-083 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.98 | 144.26 | AC1-098 | PECO_P4_PEACH025_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.84 | 144.16 | AC1-098 | PECO_P1-2_PBTIE1_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 139.21 | 133.27 | AC1-098 | PECO_P4_PEACH205_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 139.1 | 132.95 | AC1-098 | PECO_P1-2_PBTIE2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 138.16 | 132.07 | AC1-098 | PECO_P4_PEACH055_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 133.48 | 127.66 | AC1-098 | PECO_P4_PEACH015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 128.93 | 127.19 | AC1-098 | DVP_P4-2: 514T595_SRT-SW |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 132.15 | 126.32 | AC1-098 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 127.19 | 125.48 | AC1-098 | DVP_P4-2: 51482_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 127.19 | 125.39 | AC1-098 | AP_P1-2_PE-500-407T_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 127.19 | 125.39 | AC1-098 | DVP_P1-2: LN 514_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 123.05 | 117.68 | AC1-098 | PECO_P4_PEACH225_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 117.38 | 115.47 | AC1-098 | AP_P2-3_PE-500-019C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.51 | 148.07 | AC1-101 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.31 | 147.89 | AC1-101 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.34 | 147.87 | AC1-101 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.07 | 147.68 | AC1-101 | PECO_P4_NOTTI85_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.01 | 147.66 | AC1-101 | PECO_P1-2_220-08_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.94 | 147.6 | AC1-101 | PECO_P4_COOPR125_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.6 | 147.41 | AC1-101 | PECO_P1-2_220-93_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 150.83 | 145.86 | AC1-101 | PL_05_P71_000906_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 148.33 | 142.99 | AC1-101 | AP_P2-3_WP-500-696_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 148.33 | 142.98 | AC1-101 | AP_P2-3_WP-500-707T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.51 | 148.07 | AC1-102 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.31 | 147.89 | AC1-102 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.34 | 147.87 | AC1-102 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.07 | 147.68 | AC1-102 | PECO_P4_NOTTI85_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.01 | 147.66 | AC1-102 | PECO_P1-2_220-08_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.94 | 147.6 | AC1-102 | PECO_P4_COOPR125_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.6 | 147.41 | AC1-102 | PECO_P1-2_220-93_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 150.83 | 145.86 | AC1-102 | PL_05_P71_000906_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 148.33 | 142.99 | AC1-102 | AP_P2-3_WP-500-696_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 148.33 | 142.98 | AC1-102 | AP_P2-3_WP-500-707T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2901 | 144.86 | 147 | AD1-087 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 153.8 | 158.3 | AC1-105 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.29 | 157.41 | AC1-105 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.29 | 157.41 | AC1-105 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 152.11 | 156.98 | AC1-105 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 161.8 | 154.57 | AC1-105 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 148.75 | 153.33 | AC1-105 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 155.86 | 150.71 | AC1-105 | PN_P1-2_PN-500-010T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.58 | 149.7 | AC1-105 | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.51 | 149.63 | AC1-105 | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.2 | 148.46 | AC1-105 | AP_P2-3_PE-500-016_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.27 | 148.44 | AC1-105 | AP_P2-3_PE-500-015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.17 | 148.04 | AC1-105 | PJM_500_BG_P4_5_CNSTN_L_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.46 | 148.02 | AC1-105 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.26 | 147.84 | AC1-105 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.29 | 147.82 | AC1-105 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.02 | 147.63 | AC1-105 | PECO_P4_NOTTI85_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.96 | 147.61 | AC1-105 | PECO_P1-2_220-08_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.38 | 147.58 | AC1-105 | AP_P1-2_WP-500-DRT17_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.38 | 147.58 | AC1-105 | AP_P1-2_PE-500-001_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.89 | 147.55 | AC1-105 | PECO_P4_COOPR125_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.33 | 147.51 | AC1-105 | AP_P2-3_PE-500-018C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2901 | 144.68 | 146.79 | AD1-088 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 151.02 | 144.3 | AC1-105 | PECO_P4_PEACH025_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.88 | 144.21 | AC1-105 | PECO_P1-2_PBTIE1_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 139.25 | 133.31 | AC1-105 | PECO_P4_PEACH205_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 139.14 | 132.98 | AC1-105 | PECO_P1-2_PBTIE2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 138.19 | 132.1 | AC1-105 | PECO_P4_PEACH055_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 133.52 | 127.7 | AC1-105 | PECO_P4_PEACH015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 132.19 | 126.36 | AC1-105 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 123.09 | 117.72 | AC1-105 | PECO_P4_PEACH225_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2901 | 144.77 | 146.9 | AD1-105 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 153.71 | 158.2 | AC1-120 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.21 | 157.34 | AC1-120 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.21 | 157.33 | AC1-120 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 152.03 | 156.88 | AC1-120 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 161.72 | 154.5 | AC1-120 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 148.66 | 153.23 | AC1-120 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 155.79 | 150.63 | AC1-120 | PN_P1-2_PN-500-010T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.5 | 149.61 | AC1-120 | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.43 | 149.53 | AC1-120 | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.11 | 148.35 | AC1-120 | AP_P2-3_PE-500-016_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.18 | 148.32 | AC1-120 | AP_P2-3_PE-500-015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.1 | 147.96 | AC1-120 | PJM_500_BG_P4_5_CNSTN_L_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.4 | 147.96 | AC1-120 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.2 | 147.77 | AC1-120 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.22 | 147.76 | AC1-120 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.95 | 147.56 | AC1-120 | PECO_P4_NOTTI85_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.89 | 147.55 | AC1-120 | PECO_P1-2_220-08_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.83 | 147.48 | AC1-120 | PECO_P4_COOPR125_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.29 | 147.47 | AC1-120 | AP_P1-2_WP-500-DRT17_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.29 | 147.47 | AC1-120 | AP_P1-2_PE-500-001_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.24 | 147.4 | AC1-120 | AP_P2-3_PE-500-018C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2901 | 144.86 | 147 | AD1-115 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.95 | 144.24 | AC1-120 | PECO_P4_PEACH025_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.8 | 144.13 | AC1-120 | PECO_P1-2_PBTIE1_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 139.17 | 133.23 | AC1-120 | PECO_P4_PEACH205_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 139.07 | 132.91 | AC1-120 | PECO_P1-2_PBTIE2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 138.12 | 132.03 | AC1-120 | PECO_P4_PEACH055_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 133.44 | 127.62 | AC1-120 | PECO_P4_PEACH015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 128.73 | 126.99 | AC1-120 | DVP_P4-2: 514T595_SRT-SW |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 132.12 | 126.29 | AC1-120 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 126.98 | 125.26 | AC1-120 | DVP_P4-2: 51482_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 126.98 | 125.17 | AC1-120 | AP_P1-2_PE-500-407T_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 126.98 | 125.17 | AC1-120 | DVP_P1-2: LN 514_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 123.02 | 117.64 | AC1-120 | PECO_P4_PEACH225_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 117.18 | 115.26 | AC1-120 | AP_P2-3_PE-500-019C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 99.6 | 103.58 | AC1-120 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 99.6 | 103.58 | AC1-120 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 99.6 | 103.58 | AC1-120 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 98.77 | 100.86 | AC1-120 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2901 | 144.8 | 146.93 | AD1-128 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 153.76 | 158.26 | AC1-122 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.24 | 157.37 | AC1-122 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.24 | 157.37 | AC1-122 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 152.07 | 156.93 | AC1-122 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 161.74 | 154.51 | AC1-122 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 148.71 | 153.28 | AC1-122 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 155.82 | 150.66 | AC1-122 | PN_P1-2_PN-500-010T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.55 | 149.66 | AC1-122 | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.48 | 149.59 | AC1-122 | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.17 | 148.43 | AC1-122 | AP_P2-3_PE-500-016_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.24 | 148.4 | AC1-122 | AP_P2-3_PE-500-015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.13 | 148 | AC1-122 | PJM_500_BG_P4_5_CNSTN_L_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.41 | 147.97 | AC1-122 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.21 | 147.78 | AC1-122 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.23 | 147.77 | AC1-122 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.96 | 147.57 | AC1-122 | PECO_P4_NOTTI85_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.9 | 147.56 | AC1-122 | PECO_P1-2_220-08_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.35 | 147.55 | AC1-122 | AP_P1-2_PE-500-001_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.35 | 147.55 | AC1-122 | AP_P1-2_WP-500-DRT17_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.84 | 147.49 | AC1-122 | PECO_P4_COOPR125_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.3 | 147.48 | AC1-122 | AP_P2-3_PE-500-018C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2901 | 144.77 | 146.89 | AD1-140 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.95 | 144.24 | AC1-122 | PECO_P4_PEACH025_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.82 | 144.15 | AC1-122 | PECO_P1-2_PBTIE1_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 139.2 | 133.26 | AC1-122 | PECO_P4_PEACH205_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 139.09 | 132.93 | AC1-122 | PECO_P1-2_PBTIE2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 138.14 | 132.05 | AC1-122 | PECO_P4_PEACH055_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 133.46 | 127.64 | AC1-122 | PECO_P4_PEACH015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 132.13 | 126.31 | AC1-122 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 123.04 | 117.66 | AC1-122 | PECO_P4_PEACH225_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2901 | 145.47 | 147.71 | AD1-143 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 153.71 | 158.2 | AC1-143 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.21 | 157.34 | AC1-143 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.21 | 157.33 | AC1-143 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 152.03 | 156.88 | AC1-143 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 161.72 | 154.5 | AC1-143 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 148.66 | 153.23 | AC1-143 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 155.79 | 150.63 | AC1-143 | PN_P1-2_PN-500-010T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.5 | 149.61 | AC1-143 | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.43 | 149.53 | AC1-143 | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.11 | 148.35 | AC1-143 | AP_P2-3_PE-500-016_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.18 | 148.32 | AC1-143 | AP_P2-3_PE-500-015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.1 | 147.96 | AC1-143 | PJM_500_BG_P4_5_CNSTN_L_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.4 | 147.96 | AC1-143 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.2 | 147.77 | AC1-143 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.22 | 147.76 | AC1-143 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.95 | 147.56 | AC1-143 | PECO_P4_NOTTI85_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.89 | 147.55 | AC1-143 | PECO_P1-2_220-08_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.83 | 147.48 | AC1-143 | PECO_P4_COOPR125_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.29 | 147.47 | AC1-143 | AP_P1-2_WP-500-DRT17_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.29 | 147.47 | AC1-143 | AP_P1-2_PE-500-001_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.24 | 147.4 | AC1-143 | AP_P2-3_PE-500-018C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2901 | 144.8 | 146.93 | AD1-152 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.95 | 144.24 | AC1-143 | PECO_P4_PEACH025_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.8 | 144.13 | AC1-143 | PECO_P1-2_PBTIE1_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 139.17 | 133.23 | AC1-143 | PECO_P4_PEACH205_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 139.07 | 132.91 | AC1-143 | PECO_P1-2_PBTIE2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 138.12 | 132.03 | AC1-143 | PECO_P4_PEACH055_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 133.44 | 127.62 | AC1-143 | PECO_P4_PEACH015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 128.72 | 126.98 | AC1-143 | DVP_P4-2: 514T595_SRT-SW |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 132.12 | 126.29 | AC1-143 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 126.97 | 125.26 | AC1-143 | DVP_P4-2: 51482_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 126.97 | 125.17 | AC1-143 | AP_P1-2_PE-500-407T_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 126.97 | 125.17 | AC1-143 | DVP_P1-2: LN 514_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 123.02 | 117.64 | AC1-143 | PECO_P4_PEACH225_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 117.18 | 115.25 | AC1-143 | AP_P2-3_PE-500-019C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 99.6 | 103.58 | AC1-143 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 99.6 | 103.58 | AC1-143 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 99.6 | 103.58 | AC1-143 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 98.77 | 100.86 | AC1-143 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2901 | 144.8 | 146.93 | AD1-155 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.31 | 157.44 | AC1-145 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.31 | 157.44 | AC1-145 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 161.82 | 154.6 | AC1-145 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 155.88 | 150.73 | AC1-145 | PN_P1-2_PN-500-010T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.19 | 148.06 | AC1-145 | PJM_500_BG_P4_5_CNSTN_L_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.48 | 148.05 | AC1-145 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.28 | 147.86 | AC1-145 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.31 | 147.84 | AC1-145 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.04 | 147.65 | AC1-145 | PECO_P4_NOTTI85_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.98 | 147.63 | AC1-145 | PECO_P1-2_220-08_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.91 | 147.57 | AC1-145 | PECO_P4_COOPR125_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 151.04 | 144.32 | AC1-145 | PECO_P4_PEACH025_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.91 | 144.23 | AC1-145 | PECO_P1-2_PBTIE1_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 137.17 | 139.13 | AC1-145 | AP_P2-3_WP-500-706T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 136.16 | 138.44 | AC1-145 | ME_P2-3_ME-115-013C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 134.1 | 136.17 | AC1-145 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 134.09 | 136.11 | AC1-145 | PECO_P4_COOPR125_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 134.06 | 136.08 | AC1-145 | PECO_P1-2_220-08_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 134.08 | 136.07 | AC1-145 | PECO_P4_NOTTI85_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 133.96 | 136.03 | AC1-145 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 133.97 | 136.02 | AC1-145 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 133.84 | 135.97 | AC1-145 | PECO_P1-2_220-93_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 133.83 | 135.92 | AC1-145 | BG_P1_2317_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 139.17 | 133.01 | AC1-145 | PECO_P1-2_PBTIE2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 138.22 | 132.12 | AC1-145 | PECO_P4_PEACH055_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 133.55 | 127.72 | AC1-145 | PECO_P4_PEACH015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 132.21 | 126.39 | AC1-145 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 123.12 | 117.74 | AC1-145 | PECO_P4_PEACH225_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 222.96 | 233.04 | AC1-158 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 221.02 | 233.04 | AC1-158 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 221.98 | 231.12 | AC1-158 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 220.04 | 231.12 | AC1-158 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 221.91 | 231.05 | AC1-158 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 221.91 | 231.05 | AC1-158 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 219.98 | 231.05 | AC1-158 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 219.98 | 231.05 | AC1-158 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 211.06 | 223.01 | AC1-158 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 210.12 | 221.15 | AC1-158 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 210.05 | 221.08 | AC1-158 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 210.05 | 221.07 | AC1-158 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 206.81 | 219.77 | AC1-158 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 205.86 | 217.89 | AC1-158 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 205.8 | 217.82 | AC1-158 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 205.8 | 217.82 | AC1-158 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 207.14 | 212.23 | AC1-158 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 205.2 | 212.23 | AC1-158 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 195.78 | 202.85 | AC1-158 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 191.53 | 199.49 | AC1-158 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 334 | 170.97 | 173.53 | AC1-158 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 334 | 170.97 | 173.53 | AC1-158 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 334 | 170.84 | 173.38 | AC1-158 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204539 | 27HUNTRSTN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 334 | 170.52 | 171.86 | AC1-158 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204539 | 27HUNTRSTN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 334 | 170.52 | 171.86 | AC1-158 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204539 | 27HUNTRSTN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 334 | 170.39 | 171.72 | AC1-158 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 235463 | 01TANEY | 1 | 138 | 227/201 | 317 | 174.44 | 168.8 | AC1-158 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 235463 | 01TANEY | 1 | 138 | 227/201 | 317 | 174.44 | 168.8 | AC1-158 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 235463 | 01TANEY | 1 | 138 | 227/201 | 317 | 174.28 | 168.67 | AC1-158 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 170.11 | 165 | AC1-158 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204538 | 27STRABAN | 204544 | 27LINCOLN | 1 | 115 | 227 | 371 | 160.28 | 164.9 | AC1-158 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204538 | 27STRABAN | 204544 | 27LINCOLN | 1 | 115 | 227 | 371 | 160.28 | 164.9 | AC1-158 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204538 | 27STRABAN | 204544 | 27LINCOLN | 1 | 115 | 227 | 371 | 160.15 | 164.76 | AC1-158 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 169.12 | 163.55 | AC1-158 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 169.12 | 163.55 | AC1-158 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 169.1 | 163.54 | AC1-158 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 160.92 | 161.02 | AC1-158 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 204550 | 27ORRTANNA | 1 | 115 | 227 | 189 | 160.9 | 160.61 | AC1-158 | ME_P1-2_ME-115-068_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204529 | 27GERMANTN | 204538 | 27STRABAN | 1 | 115 | 227 | 371 | 154.56 | 160.37 | AC1-158 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204529 | 27GERMANTN | 204538 | 27STRABAN | 1 | 115 | 227 | 371 | 154.56 | 160.37 | AC1-158 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 204550 | 27ORRTANNA | 1 | 115 | 227 | 189 | 159.17 | 160.33 | AC1-158 | ME_P2-3_ME-115-035A_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204529 | 27GERMANTN | 204538 | 27STRABAN | 1 | 115 | 227 | 371 | 154.43 | 160.22 | AC1-158 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2901 | 144.85 | 146.99 | AD2-009 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 221089 | WINDYED1 | 221090 | GLENARM2 | 1 | 115 | 232 | 222 | 155.5 | 159.14 | AC1-158 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 204550 | 27ORRTANNA | 1 | 115 | 227 | 189 | 160.39 | 158.87 | AC1-158 | ME_P1-2_ME-115-067_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 204550 | 27ORRTANNA | 1 | 115 | 227 | 189 | 158.6 | 158.18 | AC1-158 | ME_P2-3_ME-115-013B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 159 | 157.97 | AC1-158 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 159 | 157.97 | AC1-158 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 158.99 | 157.97 | AC1-158 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 204550 | 27ORRTANNA | 1 | 115 | 227 | 189 | 156.87 | 157.9 | AC1-158 | ME_P2-3_ME-115-035B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 204550 | 27ORRTANNA | 1 | 115 | 227 | 189 | 158.29 | 157.86 | AC1-158 | ME_P2-3_ME-115-013A_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 161.2 | 156.38 | AC1-158 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 150.99 | 154.92 | AC1-158 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2901 | 144.58 | 146.68 | AD2-016 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 159.63 | 154.73 | AC1-158 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 159.63 | 154.73 | AC1-158 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 149.34 | 153.62 | AC1-158 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2901 | 144.9 | 147.04 | AD2-072 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 204550 | 27ORRTANNA | 1 | 115 | 227 | 189 | 153.82 | 152.01 | AC1-158 | ME_P2-3_ME-115-0102-A_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 204550 | 27ORRTANNA | 1 | 115 | 227 | 189 | 153.82 | 152.01 | AC1-158 | ME_P2-2_ME-115-0102-4_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 158.8 | 151.66 | AC1-158 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 145.98 | 149.97 | AC1-158 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 903 | 142.02 | 148.39 | AC1-158 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.26 | 148.09 | AC1-158 | PN_P1-2_PN-500-010T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2901 | 144.73 | 146.85 | AD2-074 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 150.1 | 147.93 | AC1-158 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 221089 | WINDYED1 | 221090 | GLENARM2 | 1 | 115 | 232 | 222 | 142.05 | 146.83 | AC1-158 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.91 | 146.53 | AC1-158 | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.84 | 146.46 | AC1-158 | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 334 | 148.43 | 145.98 | AC1-158 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 334 | 148.43 | 145.98 | AC1-158 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 334 | 148.43 | 145.98 | AC1-158 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204539 | 27HUNTRSTN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 334 | 147.98 | 145.92 | AC1-158 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204539 | 27HUNTRSTN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 334 | 147.98 | 145.91 | AC1-158 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204539 | 27HUNTRSTN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 334 | 147.98 | 145.91 | AC1-158 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 903 | 140.45 | 145.8 | AC1-158 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 903 | 140.45 | 145.79 | AC1-158 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 903 | 140.44 | 145.79 | AC1-158 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 334 | 148.24 | 145.73 | AC1-158 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204539 | 27HUNTRSTN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 334 | 147.79 | 145.68 | AC1-158 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 150.6 | 145.47 | AC1-158 | PJM_500_BG_P4_5_CNSTN_L_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 150.85 | 145.45 | AC1-158 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 150.65 | 145.27 | AC1-158 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 150.67 | 145.25 | AC1-158 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 141.5 | 145.11 | AC1-158 | AP_P2-3_PE-500-016_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 141.56 | 145.08 | AC1-158 | AP_P2-3_PE-500-015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 150.4 | 145.06 | AC1-158 | PECO_P4_NOTTI85_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 150.34 | 145.04 | AC1-158 | PECO_P1-2_220-08_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 150.28 | 144.98 | AC1-158 | PECO_P4_COOPR125_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 144.34 | 144.66 | AC1-158 | BG_P7_GRCTN_CNSTN_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 140.68 | 144.26 | AC1-158 | AP_P1-2_PE-500-001_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 140.68 | 144.26 | AC1-158 | AP_P1-2_WP-500-DRT17_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 140.63 | 144.2 | AC1-158 | AP_P2-3_PE-500-018C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2901 | 145.37 | 147.59 | AD2-076 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2901 | 144.89 | 147.03 | AD2-085 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 221092 | FIVE.FOR | 221096 | ROCKRGE1 | 1 | 115 | 232 | 293 | 140.29 | 143.47 | AC1-158 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 148.09 | 141.49 | AC1-158 | PECO_P4_PEACH025_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 147.75 | 141.19 | AC1-158 | PECO_P1-2_PBTIE1_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 911 | 146.46 | 140.72 | AC1-158 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 334 | 141.7 | 140.65 | AC1-158 | ME_P1-2_ME-115-061_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 334 | 141.7 | 140.65 | AC1-158 | ME_P2-3_ME-115-019A-A_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 911 | 145.49 | 139.38 | AC1-158 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 911 | 145.49 | 139.38 | AC1-158 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 911 | 145.47 | 139.37 | AC1-158 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204539 | 27HUNTRSTN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 334 | 141.24 | 139.19 | AC1-158 | ME_P1-2_ME-115-061_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204539 | 27HUNTRSTN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 334 | 141.24 | 139.19 | AC1-158 | ME_P2-3_ME-115-019A-A_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 334 | 139.59 | 138.46 | AC1-158 | ME_P2-3_ME-115-019-B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 138.87 | 138.4 | AC1-158 | PJM_500_BG_P4_5_CNSTN_15_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204502 | 27JACKSON | 204514 | 27TMI | 1 | 230 | 227 | 781 | 131.14 | 138.35 | AC1-158 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204502 | 27JACKSON | 204514 | 27TMI | 1 | 230 | 227 | 781 | 131.14 | 138.35 | AC1-158 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204502 | 27JACKSON | 204514 | 27TMI | 1 | 230 | 227 | 781 | 131.13 | 138.34 | AC1-158 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204502 | 27JACKSON | 204514 | 27TMI | 1 | 230 | 227 | 781 | 130.94 | 138.29 | AC1-158 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2901 | 144.69 | 146.8 | AD2-093 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 221055 | HARRIS1A | 221058 | DOLFD T1 | 1 | 115 | 232 | 201 | 137.77 | 137.77 | AC1-158 | BG_P7_NWEST_GRNITE_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204539 | 27HUNTRSTN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 334 | 140.95 | 137.21 | AC1-158 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204538 | 27STRABAN | 204544 | 27LINCOLN | 1 | 115 | 227 | 371 | 137.42 | 136.79 | AC1-158 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204538 | 27STRABAN | 204544 | 27LINCOLN | 1 | 115 | 227 | 371 | 137.43 | 136.79 | AC1-158 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204538 | 27STRABAN | 204544 | 27LINCOLN | 1 | 115 | 227 | 371 | 137.43 | 136.79 | AC1-158 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204538 | 27STRABAN | 204544 | 27LINCOLN | 1 | 115 | 227 | 371 | 137.24 | 136.54 | AC1-158 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 903 | 133.4 | 136.53 | AC1-158 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200504 | 26CARLISLE | 204528 | 27GARDNERS | 1 | 115 | 226/227 | 190 | 127.4 | 136.17 | AC1-158 | PN_P2-3_PN-115-0331-B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 1031 | 129.05 | 135.94 | AC1-158 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 1031 | 128.55 | 134.93 | AC1-158 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 1031 | 128.55 | 134.93 | AC1-158 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 1031 | 128.54 | 134.92 | AC1-158 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200504 | 26CARLISLE | 204528 | 27GARDNERS | 1 | 115 | 226/227 | 190 | 125.79 | 134.3 | AC1-158 | PN_P1-2_PN-115-094_A_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 203981 | AD2-062_POI | 235188 | 01GREENE | 1 | 138 | 226/201 | 317 | 142.36 | 134.1 | AC1-158 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 203981 | AD2-062_POI | 235188 | 01GREENE | 1 | 138 | 226/201 | 317 | 142.36 | 134.1 | AC1-158 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 221092 | FIVE.FOR | 221096 | ROCKRGE1 | 1 | 115 | 232 | 293 | 130.14 | 134.05 | AC1-158 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 203981 | AD2-062_POI | 235188 | 01GREENE | 1 | 138 | 226/201 | 317 | 142.16 | 133.95 | AC1-158 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200512 | 26LEWISTWN | 200519 | 26REED TAP | 1 | 115 | 226 | 271 | 126.15 | 133.65 | AC1-158 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200512 | 26LEWISTWN | 200519 | 26REED TAP | 1 | 115 | 226 | 271 | 126.15 | 133.64 | AC1-158 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200512 | 26LEWISTWN | 200519 | 26REED TAP | 1 | 115 | 226 | 271 | 126.15 | 133.64 | AC1-158 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200512 | 26LEWISTWN | 200519 | 26REED TAP | 1 | 115 | 226 | 271 | 126.07 | 133.63 | AC1-158 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200504 | 26CARLISLE | 204528 | 27GARDNERS | 1 | 115 | 226/227 | 190 | 125.63 | 133.38 | AC1-158 | PN_P2-3_PN-115-58B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200504 | 26CARLISLE | 204528 | 27GARDNERS | 1 | 115 | 226/227 | 190 | 126.27 | 133.33 | AC1-158 | PN_P2-2_PN-115-030_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200504 | 26CARLISLE | 204528 | 27GARDNERS | 1 | 115 | 226/227 | 190 | 126.27 | 133.33 | AC1-158 | PN_P1-3_PN-115-040_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200504 | 26CARLISLE | 204528 | 27GARDNERS | 1 | 115 | 226/227 | 190 | 125.43 | 133.31 | AC1-158 | PN_P1-2_PN-115-094_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 235463 | 01TANEY | 1 | 138 | 227/201 | 317 | 134.6 | 133 | AC1-158 | AP_P2-3_PE-500-016_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 235463 | 01TANEY | 1 | 138 | 227/201 | 317 | 134.72 | 132.93 | AC1-158 | AP_P2-3_PE-500-015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 911 | 137.65 | 132.9 | AC1-158 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200532 | 26ROXBURY | 203981 | AD2-062_POI | 1 | 138 | 226 | 317 | 141.62 | 132.76 | AC1-158 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200532 | 26ROXBURY | 203981 | AD2-062_POI | 1 | 138 | 226 | 317 | 141.62 | 132.76 | AC1-158 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200532 | 26ROXBURY | 203981 | AD2-062_POI | 1 | 138 | 226 | 317 | 141.41 | 132.61 | AC1-158 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 235463 | 01TANEY | 1 | 138 | 227/201 | 317 | 133.1 | 132.56 | AC1-158 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204529 | 27GERMANTN | 204538 | 27STRABAN | 1 | 115 | 227 | 371 | 131.71 | 132.47 | AC1-158 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204529 | 27GERMANTN | 204538 | 27STRABAN | 1 | 115 | 227 | 371 | 131.71 | 132.47 | AC1-158 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204529 | 27GERMANTN | 204538 | 27STRABAN | 1 | 115 | 227 | 371 | 131.7 | 132.47 | AC1-158 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204529 | 27GERMANTN | 204538 | 27STRABAN | 1 | 115 | 227 | 371 | 131.52 | 132.23 | AC1-158 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 235463 | 01TANEY | 1 | 138 | 227/201 | 317 | 133.32 | 132.14 | AC1-158 | AP_P2-3_PE-500-018D_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 235463 | 01TANEY | 1 | 138 | 227/201 | 317 | 133.32 | 132.14 | AC1-158 | AP_P2-3_PE-500-018C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 235463 | 01TANEY | 1 | 138 | 227/201 | 317 | 132.7 | 131.95 | AC1-158 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 235463 | 01TANEY | 1 | 138 | 227/201 | 317 | 133.16 | 131.86 | AC1-158 | AP_P1-2_PE-500-001_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 207922 | BRIS | 207923 | BRISREAC | RX | 230 | 229 | 676 | 123.37 | 131.34 | AC1-158 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 207923 | BRISREAC | 208132 | WHEM TR1 | 1 | 230 | 229 | 676 | 123.37 | 131.34 | AC1-158 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 221056 | HARRIS0A | 221057 | DOLFD T0 | 1 | 115 | 232 | 201 | 130.79 | 130.67 | AC1-158 | BG_P7_NWEST_GRNITE_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 136.41 | 130.56 | AC1-158 | PECO_P4_PEACH205_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208078 | SAKR | 1 | 230 | 229 | 903 | 123.11 | 130.48 | AC1-158 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 136.25 | 130.2 | AC1-158 | PECO_P1-2_PBTIE2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 207922 | BRIS | 207923 | BRISREAC | RX | 230 | 229 | 676 | 122.6 | 129.9 | AC1-158 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 207922 | BRIS | 207923 | BRISREAC | RX | 230 | 229 | 676 | 122.6 | 129.9 | AC1-158 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 207922 | BRIS | 207923 | BRISREAC | RX | 230 | 229 | 676 | 122.59 | 129.89 | AC1-158 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 207923 | BRISREAC | 208132 | WHEM TR1 | 1 | 230 | 229 | 676 | 122.59 | 129.89 | AC1-158 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 207923 | BRISREAC | 208132 | WHEM TR1 | 1 | 230 | 229 | 676 | 122.6 | 129.89 | AC1-158 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 207923 | BRISREAC | 208132 | WHEM TR1 | 1 | 230 | 229 | 676 | 122.6 | 129.89 | AC1-158 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 135.48 | 129.49 | AC1-158 | PECO_P4_PEACH055_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208078 | SAKR | 1 | 230 | 229 | 903 | 122.34 | 129.13 | AC1-158 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208078 | SAKR | 1 | 230 | 229 | 903 | 122.35 | 129.12 | AC1-158 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208078 | SAKR | 1 | 230 | 229 | 903 | 122.35 | 129.12 | AC1-158 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200504 | 26CARLISLE | 204528 | 27GARDNERS | 1 | 115 | 226/227 | 190 | 123.09 | 128.92 | AC1-158 | PN_P2-3_PN-230-0014-12_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204538 | 27STRABAN | 204544 | 27LINCOLN | 1 | 115 | 227 | 371 | 126.25 | 128.88 | AC1-158 | AP_P2-3_PE-500-016_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204538 | 27STRABAN | 204544 | 27LINCOLN | 1 | 115 | 227 | 371 | 130.31 | 128.82 | AC1-158 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204538 | 27STRABAN | 204544 | 27LINCOLN | 1 | 115 | 227 | 371 | 126.34 | 128.81 | AC1-158 | AP_P2-3_PE-500-015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200519 | 26REED TAP | 200522 | 26SHADE GP | 1 | 115 | 226 | 271 | 118.52 | 128.55 | AC1-158 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200519 | 26REED TAP | 200522 | 26SHADE GP | 1 | 115 | 226 | 271 | 118.52 | 128.54 | AC1-158 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200519 | 26REED TAP | 200522 | 26SHADE GP | 1 | 115 | 226 | 271 | 118.52 | 128.54 | AC1-158 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200519 | 26REED TAP | 200522 | 26SHADE GP | 1 | 115 | 226 | 271 | 118.45 | 128.53 | AC1-158 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200504 | 26CARLISLE | 204528 | 27GARDNERS | 1 | 115 | 226/227 | 190 | 123.08 | 128.5 | AC1-158 | PN_P1-3_PN-230-020A_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200504 | 26CARLISLE | 204528 | 27GARDNERS | 1 | 115 | 226/227 | 190 | 123.08 | 128.5 | AC1-158 | PN_P2-3_PN-230-0014-11_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200504 | 26CARLISLE | 204528 | 27GARDNERS | 1 | 115 | 226/227 | 190 | 123.01 | 128.48 | AC1-158 | PN_P2-2_PN-115-031_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220972 | GRANITE1 | 1 | 230 | 232 | 829 | 132.45 | 128.44 | AC1-158 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204502 | 27JACKSON | 204514 | 27TMI | 1 | 230 | 227 | 781 | 123.52 | 128.31 | AC1-158 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200512 | 26LEWISTWN | 200519 | 26REED TAP | 1 | 115 | 226 | 271 | 123.33 | 127.79 | AC1-158 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 204529 | 27GERMANTN | 1 | 138/115 | 227 | 453 | 122.07 | 127.79 | AC1-158 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 204529 | 27GERMANTN | 1 | 138/115 | 227 | 453 | 122.07 | 127.79 | AC1-158 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220972 | GRANITE1 | 1 | 230 | 232 | 829 | 131.81 | 127.78 | AC1-158 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220972 | GRANITE1 | 1 | 230 | 232 | 829 | 131.81 | 127.78 | AC1-158 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 204529 | 27GERMANTN | 1 | 138/115 | 227 | 453 | 121.96 | 127.66 | AC1-158 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2901 | 144.87 | 147.01 | AD2-134 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 1031 | 122.97 | 126.7 | AC1-158 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220973 | GRANITE6 | 1 | 230 | 232 | 829 | 130.43 | 126.59 | AC1-158 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220973 | GRANITE6 | 1 | 230 | 232 | 829 | 129.83 | 125.97 | AC1-158 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220973 | GRANITE6 | 1 | 230 | 232 | 829 | 129.83 | 125.97 | AC1-158 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2901 | 144.75 | 146.87 | AD2-158 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 125.31 | 125.48 | AC1-158 | BG_P7_GRCTN_CNSTN_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 123.37 | 125.48 | AC1-158 | BG_P7_GRCTN_CNSTN_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 130.46 | 124.75 | AC1-158 | PECO_P4_PEACH015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204539 | 27HUNTRSTN | 204550 | 27ORRTANNA | 1 | 115 | 227 | 264 | 124.89 | 124.69 | AC1-158 | ME_P1-2_ME-115-068_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204539 | 27HUNTRSTN | 204550 | 27ORRTANNA | 1 | 115 | 227 | 264 | 123.65 | 124.48 | AC1-158 | ME_P2-3_ME-115-035A_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204529 | 27GERMANTN | 204538 | 27STRABAN | 1 | 115 | 227 | 371 | 124.59 | 124.46 | AC1-158 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204529 | 27GERMANTN | 204538 | 27STRABAN | 1 | 115 | 227 | 371 | 120.52 | 124.44 | AC1-158 | AP_P2-3_PE-500-016_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204529 | 27GERMANTN | 204538 | 27STRABAN | 1 | 115 | 227 | 371 | 120.62 | 124.36 | AC1-158 | AP_P2-3_PE-500-015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 129.36 | 123.63 | AC1-158 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 911 | 121.31 | 123.59 | AC1-158 | BG_P7_GRCTN_CNSTN_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204539 | 27HUNTRSTN | 204550 | 27ORRTANNA | 1 | 115 | 227 | 264 | 124.52 | 123.34 | AC1-158 | ME_P1-2_ME-115-067_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204539 | 27HUNTRSTN | 204550 | 27ORRTANNA | 1 | 115 | 227 | 264 | 123.24 | 122.93 | AC1-158 | ME_P2-3_ME-115-013B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208394 | PPL-BGE TIE | 221092 | FIVE.FOR | 1 | 115 | 229/232 | 247 | 120.05 | 122.81 | AC1-158 | PL_05_P71_000906_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200519 | 26REED TAP | 200522 | 26SHADE GP | 1 | 115 | 226 | 271 | 115.71 | 122.78 | AC1-158 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204539 | 27HUNTRSTN | 204550 | 27ORRTANNA | 1 | 115 | 227 | 264 | 122 | 122.72 | AC1-158 | ME_P2-3_ME-115-035B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220953 | HOWARD12 | 220972 | GRANITE1 | 1 | 230 | 232 | 772 | 126.79 | 122.72 | AC1-158 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204539 | 27HUNTRSTN | 204550 | 27ORRTANNA | 1 | 115 | 227 | 264 | 123.02 | 122.69 | AC1-158 | ME_P2-3_ME-115-013A_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208020 | MANO TR3 | 1 | 230 | 229 | 793 | 110.2 | 122.52 | AC1-158 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200512 | 26LEWISTWN | 200519 | 26REED TAP | 1 | 115 | 226 | 271 | 119.78 | 122.43 | AC1-158 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200512 | 26LEWISTWN | 200519 | 26REED TAP | 1 | 115 | 226 | 271 | 119.78 | 122.43 | AC1-158 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200512 | 26LEWISTWN | 200519 | 26REED TAP | 1 | 115 | 226 | 271 | 119.72 | 122.35 | AC1-158 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 207923 | BRISREAC | 208132 | WHEM TR1 | 1 | 230 | 229 | 676 | 117.52 | 122.26 | AC1-158 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 207922 | BRIS | 207923 | BRISREAC | RX | 230 | 229 | 676 | 117.52 | 122.26 | AC1-158 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220954 | HOWARD32 | 220973 | GRANITE6 | 1 | 230 | 232 | 772 | 125.8 | 122.18 | AC1-158 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220953 | HOWARD12 | 220972 | GRANITE1 | 1 | 230 | 232 | 772 | 125.86 | 121.74 | AC1-158 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220953 | HOWARD12 | 220972 | GRANITE1 | 1 | 230 | 232 | 772 | 125.86 | 121.74 | AC1-158 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220954 | HOWARD32 | 220973 | GRANITE6 | 1 | 230 | 232 | 772 | 125 | 121.33 | AC1-158 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220954 | HOWARD32 | 220973 | GRANITE6 | 1 | 230 | 232 | 772 | 125 | 121.33 | AC1-158 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 123.1 | 121.31 | AC1-158 | DVP_P4-2: 514T595_SRT-SW |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208020 | MANO TR3 | 1 | 230 | 229 | 793 | 109.35 | 120.96 | AC1-158 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208020 | MANO TR3 | 1 | 230 | 229 | 793 | 109.36 | 120.95 | AC1-158 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208020 | MANO TR3 | 1 | 230 | 229 | 793 | 109.35 | 120.95 | AC1-158 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 793 | 122.54 | 120.71 | AC1-158 | DVP_P4-2: 514T595_SRT-SW |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 2 | 230 | 233 | 793 | 122.54 | 120.71 | AC1-158 | DVP_P4-2: 514T595_SRT-SW |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 117.98 | 120.45 | AC1-158 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 116.04 | 120.45 | AC1-158 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 115.86 | 120.23 | AC1-158 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 117.79 | 120.23 | AC1-158 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 115.86 | 120.23 | AC1-158 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 117.79 | 120.23 | AC1-158 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 203981 | AD2-062_POI | 235188 | 01GREENE | 1 | 138 | 226/201 | 317 | 136.67 | 120 | AC1-158 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208078 | SAKR | 1 | 230 | 229 | 903 | 115.11 | 119.71 | AC1-158 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204512 | 27S.RDG | 204693 | 27BOONETOWN | 1 | 230 | 227 | 607 | 106.44 | 119.61 | AC1-158 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200025 | W CHAPEL | 1 | 500 | 225 | 1732 | 121.39 | 119.49 | AC1-158 | PEPCO_P4_PP41_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 121.21 | 119.4 | AC1-158 | DVP_P4-2: 51482_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 793 | 121.19 | 119.37 | AC1-158 | DVP_P4-2: 51482_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 2 | 230 | 233 | 793 | 121.19 | 119.37 | AC1-158 | DVP_P4-2: 51482_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208031 | MLWD TR2 | 1 | 230 | 229 | 911 | 110.54 | 119.33 | AC1-158 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 121.21 | 119.31 | AC1-158 | DVP_P1-2: LN 514_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 121.21 | 119.31 | AC1-158 | AP_P1-2_PE-500-407T_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 2 | 230 | 233 | 793 | 121.19 | 119.28 | AC1-158 | DVP_P1-2: LN 514_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 2 | 230 | 233 | 793 | 121.19 | 119.28 | AC1-158 | AP_P1-2_PE-500-407T_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 793 | 121.19 | 119.28 | AC1-158 | AP_P1-2_PE-500-407T_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 793 | 121.19 | 119.28 | AC1-158 | DVP_P1-2: LN 514_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204512 | 27S.RDG | 204693 | 27BOONETOWN | 1 | 230 | 227 | 607 | 106.28 | 118.98 | AC1-158 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204512 | 27S.RDG | 204693 | 27BOONETOWN | 1 | 230 | 227 | 607 | 106.26 | 118.94 | AC1-158 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204512 | 27S.RDG | 204693 | 27BOONETOWN | 1 | 230 | 227 | 607 | 106.26 | 118.94 | AC1-158 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 116.77 | 118.88 | AC1-158 | BG_P7_GRCTN_CNSTN_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200532 | 26ROXBURY | 203981 | AD2-062_POI | 1 | 138 | 226 | 317 | 135.92 | 118.68 | AC1-158 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200512 | 26LEWISTWN | 200519 | 26REED TAP | 1 | 115 | 226 | 271 | 119.72 | 118.57 | AC1-158 | ME_P2-3_ME-115-003DT_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200512 | 26LEWISTWN | 200519 | 26REED TAP | 1 | 115 | 226 | 271 | 119.66 | 118.51 | AC1-158 | ME_P2-3_ME-115-003AT_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 203981 | AD2-062_POI | 235188 | 01GREENE | 1 | 138 | 226/201 | 317 | 122.48 | 118.5 | AC1-158 | AP_P2-3_PE-500-016_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204539 | 27HUNTRSTN | 204550 | 27ORRTANNA | 1 | 115 | 227 | 264 | 119.82 | 118.41 | AC1-158 | ME_P2-2_ME-115-0102-4_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204539 | 27HUNTRSTN | 204550 | 27ORRTANNA | 1 | 115 | 227 | 264 | 119.82 | 118.41 | AC1-158 | ME_P2-3_ME-115-0102-A_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 203981 | AD2-062_POI | 235188 | 01GREENE | 1 | 138 | 226/201 | 317 | 122.67 | 118.35 | AC1-158 | AP_P2-3_PE-500-015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208394 | PPL-BGE TIE | 221092 | FIVE.FOR | 1 | 115 | 229/232 | 247 | 117.15 | 118.12 | AC1-158 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208394 | PPL-BGE TIE | 221092 | FIVE.FOR | 1 | 115 | 229/232 | 247 | 117.08 | 118.1 | AC1-158 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208394 | PPL-BGE TIE | 221092 | FIVE.FOR | 1 | 115 | 229/232 | 247 | 117.08 | 118.1 | AC1-158 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208394 | PPL-BGE TIE | 221092 | FIVE.FOR | 1 | 115 | 229/232 | 247 | 117.07 | 118.09 | AC1-158 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208031 | MLWD TR2 | 1 | 230 | 229 | 911 | 109.8 | 117.97 | AC1-158 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208031 | MLWD TR2 | 1 | 230 | 229 | 911 | 109.8 | 117.96 | AC1-158 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208031 | MLWD TR2 | 1 | 230 | 229 | 911 | 109.8 | 117.96 | AC1-158 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 221092 | FIVE.FOR | 221095 | ROCKRGE2 | 1 | 115 | 232 | 340 | 115.6 | 117.77 | AC1-158 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 203981 | AD2-062_POI | 235188 | 01GREENE | 1 | 138 | 226/201 | 317 | 129.88 | 117.74 | AC1-158 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 203981 | AD2-062_POI | 235188 | 01GREENE | 1 | 138 | 226/201 | 317 | 120.46 | 117.7 | AC1-158 | AP_P2-3_PE-500-018C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 203981 | AD2-062_POI | 235188 | 01GREENE | 1 | 138 | 226/201 | 317 | 120.47 | 117.7 | AC1-158 | AP_P2-3_PE-500-018D_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 117.21 | 117.65 | AC1-158 | PJM_500_BG_P4_5_CNSTN_15_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 115.27 | 117.65 | AC1-158 | PJM_500_BG_P4_5_CNSTN_15_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200519 | 26REED TAP | 200522 | 26SHADE GP | 1 | 115 | 226 | 271 | 112.15 | 117.5 | AC1-158 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200519 | 26REED TAP | 200522 | 26SHADE GP | 1 | 115 | 226 | 271 | 112.15 | 117.5 | AC1-158 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200519 | 26REED TAP | 200522 | 26SHADE GP | 1 | 115 | 226 | 271 | 112.09 | 117.42 | AC1-158 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220965 | NEAST339 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 118.03 | 117.34 | AC1-158 | BG_P1_2315_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208393 | FARO DC TIE | 208395 | FARO FF | 1 | 115/69 | 229 | 120 | 122.96 | 117.25 | AC1-158 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208393 | FARO DC TIE | 208395 | FARO FF | 2 | 115/69 | 229 | 120 | 122.96 | 117.25 | AC1-158 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200532 | 26ROXBURY | 203981 | AD2-062_POI | 1 | 138 | 226 | 317 | 121.73 | 117.19 | AC1-158 | AP_P2-3_PE-500-016_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 203981 | AD2-062_POI | 235188 | 01GREENE | 1 | 138 | 226/201 | 317 | 121 | 117.19 | AC1-158 | AP_P2-3_WP-500-DRT19_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220965 | NEAST339 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 117.64 | 117.15 | AC1-158 | BG_P4_5_NEAST_17_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220965 | NEAST339 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 117.79 | 117.15 | AC1-158 | BG_P4_5_NEAST_15_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200532 | 26ROXBURY | 203981 | AD2-062_POI | 1 | 138 | 226 | 317 | 121.92 | 117.05 | AC1-158 | AP_P2-3_PE-500-015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200532 | 26ROXBURY | 200520 | 26ROXBURY | 2 | 138/115 | 226 | 435 | 103.2 | 116.99 | AC1-158 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200532 | 26ROXBURY | 200520 | 26ROXBURY | 2 | 138/115 | 226 | 435 | 103.2 | 116.99 | AC1-158 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2901 | 144.89 | 147.04 | AD2-160 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 911 | 115.98 | 116.86 | AC1-158 | PJM_500_BG_P4_5_CNSTN_15_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200532 | 26ROXBURY | 200520 | 26ROXBURY | 2 | 138/115 | 226 | 435 | 103.05 | 116.82 | AC1-158 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 113.1 | 116.5 | AC1-158 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220979 | NEAST317 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 117.14 | 116.49 | AC1-158 | BG_P1_2337_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200532 | 26ROXBURY | 203981 | AD2-062_POI | 1 | 138 | 226 | 317 | 129.13 | 116.43 | AC1-158 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200532 | 26ROXBURY | 203981 | AD2-062_POI | 1 | 138 | 226 | 317 | 119.73 | 116.37 | AC1-158 | AP_P2-3_PE-500-018D_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200532 | 26ROXBURY | 203981 | AD2-062_POI | 1 | 138 | 226 | 317 | 119.71 | 116.37 | AC1-158 | AP_P2-3_PE-500-018C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208131 | WHEM | 208132 | WHEM TR1 | 1 | 230 | 229 | 691 | 107.74 | 116.31 | AC1-158 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220979 | NEAST317 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 116.83 | 116.24 | AC1-158 | BG_P4_5_NEAST_39_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220979 | NEAST317 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 116.83 | 116.24 | AC1-158 | BG_P4_5_NEAST_37_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 112.77 | 116.17 | AC1-158 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 112.74 | 116.09 | AC1-158 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 112.74 | 116.09 | AC1-158 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200532 | 26ROXBURY | 203981 | AD2-062_POI | 1 | 138 | 226 | 317 | 120.25 | 115.89 | AC1-158 | AP_P1-2_PE-500-004_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 112.42 | 115.77 | AC1-158 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 112.41 | 115.77 | AC1-158 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2901 | 144.77 | 146.89 | AD2-163 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2901 | 144.93 | 147.08 | AD2-180 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 112.52 | 115.04 | AC1-158 | BG_P7_GRCTN_CNSTN_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 120.27 | 115 | AC1-158 | PECO_P4_PEACH225_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208131 | WHEM | 208132 | WHEM TR1 | 1 | 230 | 229 | 691 | 107.01 | 114.97 | AC1-158 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208131 | WHEM | 208132 | WHEM TR1 | 1 | 230 | 229 | 691 | 107 | 114.97 | AC1-158 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208131 | WHEM | 208132 | WHEM TR1 | 1 | 230 | 229 | 691 | 107.01 | 114.97 | AC1-158 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 116.16 | 114.83 | AC1-158 | PL_04_P12_000260_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 116.16 | 114.83 | AC1-158 | PL_04_P42_000564_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208395 | FARO FF | 208396 | FARO | 1 | 69 | 229 | 270 | 111.97 | 114.4 | AC1-158 | PL_05_P71_000906_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 109.69 | 114.04 | AC1-158 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 109.51 | 113.83 | AC1-158 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 109.51 | 113.83 | AC1-158 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200519 | 26REED TAP | 200522 | 26SHADE GP | 1 | 115 | 226 | 271 | 112.09 | 113.72 | AC1-158 | ME_P2-3_ME-115-003DT_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200519 | 26REED TAP | 200522 | 26SHADE GP | 1 | 115 | 226 | 271 | 112.03 | 113.66 | AC1-158 | ME_P2-3_ME-115-003AT_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 2 | 500/230 | 225/232 | 2168 | 108.31 | 113.34 | AC1-158 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2901 | 144.18 | 146.21 | AE1-044 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 2 | 500/230 | 225/232 | 2168 | 108.13 | 113.13 | AC1-158 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 2 | 500/230 | 225/232 | 2168 | 108.13 | 113.13 | AC1-158 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 1 | 500/230 | 225/232 | 2168 | 108.08 | 113.1 | AC1-158 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220964 | GRACETON | 220999 | BAGLEY2 | 13 | 230 | 232 | 1795 | 112.07 | 113 | AC1-158 | BG_P4_5_GRCTN_3T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 1 | 500/230 | 225/232 | 2168 | 107.9 | 112.89 | AC1-158 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 1 | 500/230 | 225/232 | 2168 | 107.9 | 112.89 | AC1-158 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2901 | 144.86 | 147 | AE1-056 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200532 | 26ROXBURY | 200520 | 26ROXBURY | 2 | 138/115 | 226 | 435 | 99.23 | 112.62 | AC1-158 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200532 | 26ROXBURY | 200520 | 26ROXBURY | 2 | 138/115 | 226 | 435 | 99.23 | 112.62 | AC1-158 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200532 | 26ROXBURY | 200520 | 26ROXBURY | 2 | 138/115 | 226 | 435 | 99.23 | 112.62 | AC1-158 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 2 | 230 | 233 | 793 | 115.21 | 112.52 | AC1-158 | PEPCO_P1_PP1_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 793 | 115.21 | 112.52 | AC1-158 | PEPCO_P1_PP2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200532 | 26ROXBURY | 200520 | 26ROXBURY | 2 | 138/115 | 226 | 435 | 99.05 | 112.42 | AC1-158 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204512 | 27S.RDG | 204693 | 27BOONETOWN | 1 | 230 | 227 | 607 | 104.51 | 111.89 | AC1-158 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 108.95 | 111.38 | AC1-158 | PJM_500_BG_P4_5_CNSTN_15_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 221089 | WINDYED1 | 221090 | GLENARM2 | 1 | 115 | 232 | 222 | 105.64 | 111.3 | AC1-158 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 221089 | WINDYED1 | 221090 | GLENARM2 | 1 | 115 | 232 | 222 | 105.47 | 111.12 | AC1-158 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 221089 | WINDYED1 | 221090 | GLENARM2 | 1 | 115 | 232 | 222 | 105.47 | 111.12 | AC1-158 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2901 | 144.8 | 146.93 | AE1-084 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208020 | MANO TR3 | 1 | 230 | 229 | 793 | 102.2 | 111.09 | AC1-158 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208020 | MANO TR3 | 208031 | MLWD TR2 | 1 | 230 | 229 | 903 | 100.74 | 110.75 | AC1-158 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 2 | 500/230 | 225/232 | 2168 | 107.42 | 110.6 | AC1-158 | PJM_500_BG_P4_5_CNSTN_15_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 111.68 | 110.47 | AC1-158 | BG_P4_5_CNSTN_14_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 105.44 | 110.22 | AC1-158 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 105.26 | 110.01 | AC1-158 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 105.26 | 110.01 | AC1-158 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200504 | 26CARLISLE | 200520 | 26ROXBURY | 1 | 115 | 226 | 190 | 99.65 | 109.96 | AC1-158 | PN_P1-2_PN-115-094_A_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208395 | FARO FF | 208396 | FARO | 1 | 69 | 229 | 270 | 109.32 | 109.96 | AC1-158 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208395 | FARO FF | 208396 | FARO | 1 | 69 | 229 | 270 | 109.25 | 109.94 | AC1-158 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208395 | FARO FF | 208396 | FARO | 1 | 69 | 229 | 270 | 109.25 | 109.94 | AC1-158 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208395 | FARO FF | 208396 | FARO | 1 | 69 | 229 | 270 | 109.25 | 109.93 | AC1-158 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220980 | RAPHAEL | 220999 | BAGLEY2 | 13 | 230 | 232 | 1795 | 107.69 | 109.76 | AC1-158 | BG_P4_5_GRCTN_3T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 221092 | FIVE.FOR | 221095 | ROCKRGE2 | 1 | 115 | 232 | 340 | 106.82 | 109.67 | AC1-158 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 105.13 | 109.55 | AC1-158 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 111.57 | 109.54 | AC1-158 | AP_P2-3_PE-500-019C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 105.01 | 109.42 | AC1-158 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208020 | MANO TR3 | 208031 | MLWD TR2 | 1 | 230 | 229 | 903 | 100.01 | 109.32 | AC1-158 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208020 | MANO TR3 | 208031 | MLWD TR2 | 1 | 230 | 229 | 903 | 100.01 | 109.32 | AC1-158 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208020 | MANO TR3 | 208031 | MLWD TR2 | 1 | 230 | 229 | 903 | 100.01 | 109.32 | AC1-158 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200504 | 26CARLISLE | 200520 | 26ROXBURY | 1 | 115 | 226 | 190 | 99.49 | 109.13 | AC1-158 | PN_P2-3_PN-115-58B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200504 | 26CARLISLE | 200520 | 26ROXBURY | 1 | 115 | 226 | 190 | 100.12 | 109.09 | AC1-158 | PN_P2-2_PN-115-030_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200504 | 26CARLISLE | 200520 | 26ROXBURY | 1 | 115 | 226 | 190 | 100.12 | 109.09 | AC1-158 | PN_P1-3_PN-115-040_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208031 | MLWD TR2 | 1 | 230 | 229 | 911 | 103.07 | 109.08 | AC1-158 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200504 | 26CARLISLE | 200520 | 26ROXBURY | 1 | 115 | 226 | 190 | 99.3 | 109.07 | AC1-158 | PN_P1-2_PN-115-094_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2901 | 144.9 | 147.05 | AE1-100 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204512 | 27S.RDG | 204693 | 27BOONETOWN | 1 | 230 | 227 | 607 | 108.77 | 108.08 | AC1-158 | PL_04_P42_101307_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204512 | 27S.RDG | 204693 | 27BOONETOWN | 1 | 230 | 227 | 607 | 108.78 | 108.03 | AC1-158 | PL_24_P42_102306_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208131 | WHEM | 208132 | WHEM TR1 | 1 | 230 | 229 | 691 | 102.24 | 107.93 | AC1-158 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208131 | WHEM | 208133 | WHEM TR2 | 1 | 230 | 229 | 691 | 100.22 | 107.83 | AC1-158 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200101 | VINCO | 200102 | AA1-076 MAIN | 1 | 500 | 225 | 999 | 102.44 | 107.72 | AC1-158 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 104.7 | 107.68 | AC1-158 | PJM_500_BG_P4_5_CNSTN_15_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2901 | 144.61 | 146.71 | AE1-101 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200101 | VINCO | 200102 | AA1-076 MAIN | 1 | 500 | 225 | 999 | 101.45 | 107.09 | AC1-158 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200101 | VINCO | 200102 | AA1-076 MAIN | 1 | 500 | 225 | 999 | 101.45 | 107.09 | AC1-158 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200101 | VINCO | 200102 | AA1-076 MAIN | 1 | 500 | 225 | 999 | 101.45 | 107.09 | AC1-158 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200101 | VINCO | 200102 | AA1-076 MAIN | 1 | 500 | 225 | 999 | 101.45 | 107.03 | AC1-158 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200009 | JUNI | 208004 | JUNI | 2 | 500/230 | 225/229 | 1040 | 107.54 | 106.98 | AC1-158 | PL_10_P42_000140_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 221092 | FIVE.FOR | 221094 | GRACE.-1 | 1 | 115 | 232 | 498 | 106.17 | 106.89 | AC1-158 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208131 | WHEM | 208133 | WHEM TR2 | 1 | 230 | 229 | 691 | 99.49 | 106.52 | AC1-158 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208131 | WHEM | 208133 | WHEM TR2 | 1 | 230 | 229 | 691 | 99.48 | 106.52 | AC1-158 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208131 | WHEM | 208133 | WHEM TR2 | 1 | 230 | 229 | 691 | 99.49 | 106.52 | AC1-158 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204512 | 27S.RDG | 204693 | 27BOONETOWN | 1 | 230 | 227 | 607 | 107.12 | 106.48 | AC1-158 | PL_04_P22_102291_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204512 | 27S.RDG | 204693 | 27BOONETOWN | 1 | 230 | 227 | 607 | 107.12 | 106.48 | AC1-158 | PL_04_P43_102301_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204512 | 27S.RDG | 204693 | 27BOONETOWN | 1 | 230 | 227 | 607 | 107.12 | 106.47 | AC1-158 | PL_04_P43_102300_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 793 | 108.85 | 106.28 | AC1-158 | PEPCO_P4_PP19_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200532 | 26ROXBURY | 200520 | 26ROXBURY | 2 | 138/115 | 226 | 435 | 94.1 | 105.88 | AC1-158 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220973 | GRANITE6 | 1 | 230 | 232 | 829 | 107 | 105.54 | AC1-158 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200504 | 26CARLISLE | 200520 | 26ROXBURY | 1 | 115 | 226 | 190 | 90.39 | 105.52 | AC1-158 | PN_P2-3_PN-115-0331-B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220965 | NEAST339 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 106.66 | 105.15 | AC1-158 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220965 | NEAST339 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 106.56 | 105.03 | AC1-158 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220965 | NEAST339 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 106.56 | 105.03 | AC1-158 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200504 | 26CARLISLE | 200520 | 26ROXBURY | 1 | 115 | 226 | 190 | 97.02 | 104.95 | AC1-158 | PN_P2-3_PN-230-0014-12_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 204529 | 27GERMANTN | 1 | 138/115 | 227 | 453 | 103.35 | 104.59 | AC1-158 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 204529 | 27GERMANTN | 1 | 138/115 | 227 | 453 | 103.35 | 104.59 | AC1-158 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 204529 | 27GERMANTN | 1 | 138/115 | 227 | 453 | 103.35 | 104.59 | AC1-158 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200504 | 26CARLISLE | 200520 | 26ROXBURY | 1 | 115 | 226 | 190 | 97.01 | 104.54 | AC1-158 | PN_P1-3_PN-230-020A_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200504 | 26CARLISLE | 200520 | 26ROXBURY | 1 | 115 | 226 | 190 | 97.01 | 104.54 | AC1-158 | PN_P2-3_PN-230-0014-11_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200504 | 26CARLISLE | 200520 | 26ROXBURY | 1 | 115 | 226 | 190 | 96.94 | 104.51 | AC1-158 | PN_P2-2_PN-115-031_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220972 | GRANITE1 | 1 | 230 | 232 | 829 | 106.13 | 104.46 | AC1-158 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 204529 | 27GERMANTN | 1 | 138/115 | 227 | 453 | 103.2 | 104.39 | AC1-158 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 100.26 | 104.19 | AC1-158 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 100.17 | 104.1 | AC1-158 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200099 | LAUS | 208045 | LAUS | 3 | 500/230 | 225/229 | 1200 | 102.17 | 103.67 | AC1-158 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 793 | 105.65 | 103.66 | AC1-158 | AP_P2-3_PE-500-019C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 2 | 230 | 233 | 793 | 105.65 | 103.66 | AC1-158 | AP_P2-3_PE-500-019C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 101.4 | 103.28 | AC1-158 | BG_P1_2322_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 101.33 | 103.21 | AC1-158 | BG_P1_2310_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200099 | LAUS | 208045 | LAUS | 3 | 500/230 | 225/229 | 1200 | 101.85 | 103.2 | AC1-158 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200099 | LAUS | 208045 | LAUS | 3 | 500/230 | 225/229 | 1200 | 101.85 | 103.2 | AC1-158 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200099 | LAUS | 208045 | LAUS | 3 | 500/230 | 225/229 | 1200 | 101.84 | 103.2 | AC1-158 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 101.34 | 103.18 | AC1-158 | BG_P4_5_NW2322_230-4_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 101.27 | 103.14 | AC1-158 | BG_P4_5_NW2310_230-5_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220972 | GRANITE1 | 1 | 230 | 232 | 829 | 103.96 | 102.62 | AC1-158 | BG_P4_5_NW230-4_2326_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208021 | MANO TR4 | 208133 | WHEM TR2 | 2 | 230 | 229 | 593 | 94.57 | 102.43 | AC1-158 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220979 | NEAST317 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 103.62 | 102.17 | AC1-158 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220973 | GRANITE6 | 1 | 230 | 232 | 829 | 103.62 | 102.07 | AC1-158 | BG_P4_5_NW230-5_2311_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220979 | NEAST317 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 103.53 | 102.06 | AC1-158 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220979 | NEAST317 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 103.53 | 102.06 | AC1-158 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 221088 | WINDYED2 | 221100 | GLENARM1 | 1 | 115 | 232 | 353 | 99.87 | 102 | AC1-158 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 100.03 | 101.95 | AC1-158 | BG_P4_5_NW230-2_2322_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 99.93 | 101.84 | AC1-158 | BG_P4_5_NW2371_2310_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 99.93 | 101.84 | AC1-158 | BG_P4_5_NW230-3_2310_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 98.21 | 101.29 | AC1-158 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 98.21 | 101.29 | AC1-158 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 98.21 | 101.29 | AC1-158 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208021 | MANO TR4 | 208133 | WHEM TR2 | 2 | 230 | 229 | 593 | 93.75 | 101.01 | AC1-158 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208021 | MANO TR4 | 208133 | WHEM TR2 | 2 | 230 | 229 | 593 | 93.75 | 101.01 | AC1-158 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208021 | MANO TR4 | 208133 | WHEM TR2 | 2 | 230 | 229 | 593 | 93.73 | 101.01 | AC1-158 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220964 | GRACETON | 221094 | GRACE.-1 | 1 | 230/115 | 232 | 510 | 103.84 | 100.99 | AC1-158 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 99.06 | 100.91 | AC1-158 | BG_P4_5_CNSTN_14_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220964 | GRACETON | 221000 | BAGLEY | 5 | 230 | 232 | 1795 | 100.24 | 100.91 | AC1-158 | BG_P1_2313_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220964 | GRACETON | 220999 | BAGLEY2 | 13 | 230 | 232 | 1795 | 100.25 | 100.91 | AC1-158 | BG_P1_2305_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204520 | 27ALLEN | 208142 | WIGR-115 | 1 | 115 | 227/229 | 351.4 | 94.18 | 100.86 | AC1-158 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204520 | 27ALLEN | 208142 | WIGR-115 | 1 | 115 | 227/229 | 351.4 | 94.18 | 100.86 | AC1-158 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204520 | 27ALLEN | 208142 | WIGR-115 | 1 | 115 | 227/229 | 351.4 | 94.18 | 100.86 | AC1-158 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208020 | MANO TR3 | 208031 | MLWD TR2 | 1 | 230 | 229 | 903 | 93.66 | 100.77 | AC1-158 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 2 | 500/230 | 225/232 | 2168 | 98.08 | 100.75 | AC1-158 | PJM_500_BG_P2_CNSTN_230-N_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 2 | 500/230 | 225/232 | 2168 | 98.08 | 100.75 | AC1-158 | BG_P1_CNSTN_500-2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204520 | 27ALLEN | 208142 | WIGR-115 | 1 | 115 | 227/229 | 351.4 | 93.93 | 100.67 | AC1-158 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 1 | 500/230 | 225/232 | 2168 | 97.98 | 100.64 | AC1-158 | BG_P1_CNSTN_500-4_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 1 | 500/230 | 225/232 | 2168 | 97.98 | 100.64 | AC1-158 | PJM_500_BG_P2_CNSTN_230-S_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2901 | 146.06 | 148.39 | AE1-104 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220973 | GRANITE6 | 1 | 230 | 232 | 829 | 101.72 | 100.6 | AC1-158 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200532 | 26ROXBURY | 200520 | 26ROXBURY | 2 | 138/115 | 226 | 435 | 88.71 | 100.6 | AC1-158 | AP_P2-3_PE-500-016_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208393 | FARO DC TIE | 208394 | PPL-BGE TIE | 1 | 115 | 229 | 302 | 99.83 | 100.47 | AC1-158 | PL_05_P71_000906_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200532 | 26ROXBURY | 200520 | 26ROXBURY | 2 | 138/115 | 226 | 435 | 88.85 | 100.46 | AC1-158 | AP_P2-3_PE-500-015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220965 | NEAST339 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 101.3 | 100.46 | AC1-158 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 225.82 | 237.87 | AC1-161 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 223.83 | 237.87 | AC1-161 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 224.87 | 235.75 | AC1-161 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 222.88 | 235.75 | AC1-161 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 224.8 | 235.69 | AC1-161 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 222.81 | 235.69 | AC1-161 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 224.8 | 235.69 | AC1-161 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 222.81 | 235.69 | AC1-161 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 213.77 | 227.69 | AC1-161 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 212.85 | 225.63 | AC1-161 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 212.79 | 225.57 | AC1-161 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 212.79 | 225.57 | AC1-161 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 209.51 | 224.49 | AC1-161 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 208.59 | 222.41 | AC1-161 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 208.53 | 222.35 | AC1-161 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 208.53 | 222.35 | AC1-161 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 209.98 | 216.79 | AC1-161 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 207.99 | 216.78 | AC1-161 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 198.47 | 207.24 | AC1-161 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 194.22 | 203.89 | AC1-161 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 172.22 | 167.2 | AC1-161 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 171.25 | 165.85 | AC1-161 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 171.25 | 165.85 | AC1-161 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 171.23 | 165.84 | AC1-161 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 163.08 | 164.14 | AC1-161 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2901 | 145.38 | 147.61 | AE1-129 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 161.2 | 161.08 | AC1-161 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 161.2 | 161.08 | AC1-161 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 161.19 | 161.07 | AC1-161 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 163.31 | 158.42 | AC1-161 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 153.03 | 157.38 | AC1-161 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 161.55 | 156.67 | AC1-161 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 161.55 | 156.67 | AC1-161 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 151.35 | 156.06 | AC1-161 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 160.95 | 153.75 | AC1-161 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 147.99 | 152.41 | AC1-161 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 903 | 143.8 | 151.41 | AC1-161 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 152.27 | 150.56 | AC1-161 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 155.13 | 149.99 | AC1-161 | PN_P1-2_PN-500-010T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 145.85 | 148.83 | AC1-161 | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 145.78 | 148.76 | AC1-161 | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 903 | 142.27 | 148.73 | AC1-161 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 903 | 142.27 | 148.73 | AC1-161 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 903 | 142.25 | 148.72 | AC1-161 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.46 | 147.55 | AC1-161 | AP_P2-3_PE-500-016_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.53 | 147.52 | AC1-161 | AP_P2-3_PE-500-015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.46 | 147.33 | AC1-161 | PJM_500_BG_P4_5_CNSTN_L_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.72 | 147.3 | AC1-161 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.52 | 147.11 | AC1-161 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.55 | 147.1 | AC1-161 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.28 | 146.91 | AC1-161 | PECO_P4_NOTTI85_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.22 | 146.89 | AC1-161 | PECO_P1-2_220-08_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.15 | 146.82 | AC1-161 | PECO_P4_COOPR125_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 142.65 | 146.68 | AC1-161 | AP_P1-2_WP-500-DRT17_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 142.65 | 146.68 | AC1-161 | AP_P1-2_PE-500-001_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 142.6 | 146.61 | AC1-161 | AP_P2-3_PE-500-018C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 145.82 | 146.25 | AC1-161 | BG_P7_GRCTN_CNSTN_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2901 | 144.45 | 146.52 | AE1-153 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.19 | 143.52 | AC1-161 | PECO_P4_PEACH025_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150 | 143.36 | AC1-161 | PECO_P1-2_PBTIE1_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 911 | 148.49 | 142.62 | AC1-161 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 911 | 147.54 | 141.4 | AC1-161 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 911 | 147.54 | 141.4 | AC1-161 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 911 | 147.52 | 141.39 | AC1-161 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204502 | 27JACKSON | 204514 | 27TMI | 1 | 230 | 227 | 781 | 132.48 | 140.99 | AC1-161 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204502 | 27JACKSON | 204514 | 27TMI | 1 | 230 | 227 | 781 | 132.68 | 140.92 | AC1-161 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204502 | 27JACKSON | 204514 | 27TMI | 1 | 230 | 227 | 781 | 132.68 | 140.92 | AC1-161 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204502 | 27JACKSON | 204514 | 27TMI | 1 | 230 | 227 | 781 | 132.67 | 140.91 | AC1-161 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 140.64 | 140.25 | AC1-161 | PJM_500_BG_P4_5_CNSTN_15_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204538 | 27STRABAN | 204544 | 27LINCOLN | 1 | 115 | 227 | 371 | 139.46 | 139.61 | AC1-161 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 903 | 135.2 | 138.94 | AC1-161 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 1031 | 130.48 | 138.55 | AC1-161 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 1031 | 129.98 | 137.44 | AC1-161 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 1031 | 129.98 | 137.44 | AC1-161 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 1031 | 129.97 | 137.43 | AC1-161 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204529 | 27GERMANTN | 204538 | 27STRABAN | 1 | 115 | 227 | 371 | 133.71 | 135.31 | AC1-161 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204529 | 27GERMANTN | 204538 | 27STRABAN | 1 | 115 | 227 | 371 | 133.71 | 135.31 | AC1-161 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204529 | 27GERMANTN | 204538 | 27STRABAN | 1 | 115 | 227 | 371 | 133.7 | 135.3 | AC1-161 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 911 | 139.67 | 134.68 | AC1-161 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 207922 | BRIS | 207923 | BRISREAC | RX | 230 | 229 | 676 | 124.72 | 133.83 | AC1-161 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 207923 | BRISREAC | 208132 | WHEM TR1 | 1 | 230 | 229 | 676 | 124.72 | 133.83 | AC1-161 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208078 | SAKR | 1 | 230 | 229 | 903 | 124.83 | 133.29 | AC1-161 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 138.45 | 132.54 | AC1-161 | PECO_P4_PEACH205_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 207923 | BRISREAC | 208132 | WHEM TR1 | 1 | 230 | 229 | 676 | 123.97 | 132.27 | AC1-161 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 207922 | BRIS | 207923 | BRISREAC | RX | 230 | 229 | 676 | 123.97 | 132.27 | AC1-161 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 207923 | BRISREAC | 208132 | WHEM TR1 | 1 | 230 | 229 | 676 | 123.97 | 132.27 | AC1-161 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 207922 | BRIS | 207923 | BRISREAC | RX | 230 | 229 | 676 | 123.97 | 132.27 | AC1-161 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 207922 | BRIS | 207923 | BRISREAC | RX | 230 | 229 | 676 | 123.96 | 132.27 | AC1-161 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 207923 | BRISREAC | 208132 | WHEM TR1 | 1 | 230 | 229 | 676 | 123.96 | 132.27 | AC1-161 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 138.33 | 132.2 | AC1-161 | PECO_P1-2_PBTIE2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208078 | SAKR | 1 | 230 | 229 | 903 | 124.09 | 131.89 | AC1-161 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208078 | SAKR | 1 | 230 | 229 | 903 | 124.08 | 131.89 | AC1-161 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208078 | SAKR | 1 | 230 | 229 | 903 | 124.08 | 131.89 | AC1-161 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 137.43 | 131.37 | AC1-161 | PECO_P4_PEACH055_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220972 | GRANITE1 | 1 | 230 | 232 | 829 | 134.42 | 130.46 | AC1-161 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204502 | 27JACKSON | 204514 | 27TMI | 1 | 230 | 227 | 781 | 125.04 | 130.45 | AC1-161 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220972 | GRANITE1 | 1 | 230 | 232 | 829 | 133.79 | 129.81 | AC1-161 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220972 | GRANITE1 | 1 | 230 | 232 | 829 | 133.79 | 129.81 | AC1-161 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 1031 | 124.39 | 128.73 | AC1-161 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220973 | GRANITE6 | 1 | 230 | 232 | 829 | 132.36 | 128.58 | AC1-161 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220973 | GRANITE6 | 1 | 230 | 232 | 829 | 131.77 | 127.96 | AC1-161 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220973 | GRANITE6 | 1 | 230 | 232 | 829 | 131.77 | 127.96 | AC1-161 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 132.66 | 126.86 | AC1-161 | PECO_P4_PEACH015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 127.57 | 125.83 | AC1-161 | DVP_P4-2: 514T595_SRT-SW |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 131.39 | 125.6 | AC1-161 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208020 | MANO TR3 | 1 | 230 | 229 | 793 | 111.91 | 125.56 | AC1-161 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 911 | 122.72 | 125.14 | AC1-161 | BG_P7_GRCTN_CNSTN_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220953 | HOWARD12 | 220972 | GRANITE1 | 1 | 230 | 232 | 772 | 129.11 | 125.12 | AC1-161 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220954 | HOWARD32 | 220973 | GRANITE6 | 1 | 230 | 232 | 772 | 127.99 | 124.46 | AC1-161 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 207922 | BRIS | 207923 | BRISREAC | RX | 230 | 229 | 676 | 118.87 | 124.2 | AC1-161 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 207923 | BRISREAC | 208132 | WHEM TR1 | 1 | 230 | 229 | 676 | 118.87 | 124.2 | AC1-161 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 2 | 230 | 233 | 793 | 125.95 | 124.17 | AC1-161 | DVP_P4-2: 514T595_SRT-SW |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 793 | 125.95 | 124.17 | AC1-161 | DVP_P4-2: 514T595_SRT-SW |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220953 | HOWARD12 | 220972 | GRANITE1 | 1 | 230 | 232 | 772 | 128.2 | 124.15 | AC1-161 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220953 | HOWARD12 | 220972 | GRANITE1 | 1 | 230 | 232 | 772 | 128.2 | 124.15 | AC1-161 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 125.79 | 124.03 | AC1-161 | DVP_P4-2: 51482_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 125.79 | 123.93 | AC1-161 | DVP_P1-2: LN 514_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 125.79 | 123.93 | AC1-161 | AP_P1-2_PE-500-407T_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208020 | MANO TR3 | 1 | 230 | 229 | 793 | 111.08 | 123.89 | AC1-161 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208020 | MANO TR3 | 1 | 230 | 229 | 793 | 111.07 | 123.89 | AC1-161 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208020 | MANO TR3 | 1 | 230 | 229 | 793 | 111.08 | 123.89 | AC1-161 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220954 | HOWARD32 | 220973 | GRANITE6 | 1 | 230 | 232 | 772 | 127.2 | 123.61 | AC1-161 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220954 | HOWARD32 | 220973 | GRANITE6 | 1 | 230 | 232 | 772 | 127.2 | 123.61 | AC1-161 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 793 | 124.68 | 122.9 | AC1-161 | DVP_P4-2: 51482_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 2 | 230 | 233 | 793 | 124.68 | 122.9 | AC1-161 | DVP_P4-2: 51482_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 793 | 124.68 | 122.82 | AC1-161 | AP_P1-2_PE-500-407T_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 793 | 124.68 | 122.82 | AC1-161 | DVP_P1-2: LN 514_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 2 | 230 | 233 | 793 | 124.68 | 122.82 | AC1-161 | AP_P1-2_PE-500-407T_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 2 | 230 | 233 | 793 | 124.68 | 122.82 | AC1-161 | DVP_P1-2: LN 514_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 119.6 | 122.32 | AC1-161 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 117.61 | 122.32 | AC1-161 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 119.42 | 122.1 | AC1-161 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 117.43 | 122.1 | AC1-161 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 117.43 | 122.1 | AC1-161 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 119.42 | 122.1 | AC1-161 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208078 | SAKR | 1 | 230 | 229 | 903 | 116.82 | 122.01 | AC1-161 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208031 | MLWD TR2 | 1 | 230 | 229 | 911 | 112.13 | 121.94 | AC1-161 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200025 | W CHAPEL | 1 | 500 | 225 | 1732 | 123.21 | 121.41 | AC1-161 | PEPCO_P4_PP41_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204512 | 27S.RDG | 204693 | 27BOONETOWN | 1 | 230 | 227 | 607 | 107.21 | 121.06 | AC1-161 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204512 | 27S.RDG | 204693 | 27BOONETOWN | 1 | 230 | 227 | 607 | 107.18 | 121.03 | AC1-161 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204512 | 27S.RDG | 204693 | 27BOONETOWN | 1 | 230 | 227 | 607 | 107.18 | 121.03 | AC1-161 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208031 | MLWD TR2 | 1 | 230 | 229 | 911 | 111.41 | 120.58 | AC1-161 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208031 | MLWD TR2 | 1 | 230 | 229 | 911 | 111.41 | 120.58 | AC1-161 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208031 | MLWD TR2 | 1 | 230 | 229 | 911 | 111.4 | 120.58 | AC1-161 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200532 | 26ROXBURY | 200520 | 26ROXBURY | 2 | 138/115 | 226 | 435 | 104.82 | 119.05 | AC1-161 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200532 | 26ROXBURY | 200520 | 26ROXBURY | 2 | 138/115 | 226 | 435 | 104.82 | 119.05 | AC1-161 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200532 | 26ROXBURY | 200520 | 26ROXBURY | 2 | 138/115 | 226 | 435 | 104.67 | 118.88 | AC1-161 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220965 | NEAST339 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 119.44 | 118.78 | AC1-161 | BG_P1_2315_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 911 | 117.67 | 118.65 | AC1-161 | PJM_500_BG_P4_5_CNSTN_15_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208131 | WHEM | 208132 | WHEM TR1 | 1 | 230 | 229 | 691 | 108.99 | 118.6 | AC1-161 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220965 | NEAST339 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 119.02 | 118.58 | AC1-161 | BG_P4_5_NEAST_17_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220965 | NEAST339 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 119.18 | 118.58 | AC1-161 | BG_P4_5_NEAST_15_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 114.41 | 118.05 | AC1-161 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220979 | NEAST317 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 118.52 | 117.91 | AC1-161 | BG_P1_2337_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 114.07 | 117.72 | AC1-161 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220979 | NEAST317 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 118.2 | 117.65 | AC1-161 | BG_P4_5_NEAST_39_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220979 | NEAST317 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 118.2 | 117.65 | AC1-161 | BG_P4_5_NEAST_37_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 114.05 | 117.65 | AC1-161 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 114.05 | 117.65 | AC1-161 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 113.72 | 117.32 | AC1-161 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 113.72 | 117.32 | AC1-161 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208131 | WHEM | 208132 | WHEM TR1 | 1 | 230 | 229 | 691 | 108.28 | 117.16 | AC1-161 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208131 | WHEM | 208132 | WHEM TR1 | 1 | 230 | 229 | 691 | 108.28 | 117.16 | AC1-161 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208131 | WHEM | 208132 | WHEM TR1 | 1 | 230 | 229 | 691 | 108.27 | 117.15 | AC1-161 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 122.3 | 116.95 | AC1-161 | PECO_P4_PEACH225_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 117.74 | 116.47 | AC1-161 | PL_04_P42_000564_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 117.74 | 116.47 | AC1-161 | PL_04_P12_000260_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 111.21 | 115.84 | AC1-161 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 111.03 | 115.63 | AC1-161 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 111.03 | 115.63 | AC1-161 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 2 | 230 | 233 | 793 | 118.1 | 115.33 | AC1-161 | PEPCO_P1_PP1_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 793 | 118.1 | 115.33 | AC1-161 | PEPCO_P1_PP2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200532 | 26ROXBURY | 200520 | 26ROXBURY | 2 | 138/115 | 226 | 435 | 100.75 | 115.26 | AC1-161 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200532 | 26ROXBURY | 200520 | 26ROXBURY | 2 | 138/115 | 226 | 435 | 100.75 | 115.26 | AC1-161 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200532 | 26ROXBURY | 200520 | 26ROXBURY | 2 | 138/115 | 226 | 435 | 100.75 | 115.25 | AC1-161 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 116.74 | 115.12 | AC1-161 | PECO_P4_PEACH205_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 114.75 | 115.12 | AC1-161 | PECO_P4_PEACH205_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200532 | 26ROXBURY | 200520 | 26ROXBURY | 2 | 138/115 | 226 | 435 | 100.58 | 115.1 | AC1-161 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 116.31 | 114.72 | AC1-161 | PECO_P1-2_5014_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 114.32 | 114.72 | AC1-161 | PECO_P1-2_5014_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 2 | 500/230 | 225/232 | 2168 | 109.41 | 114.67 | AC1-161 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 2 | 500/230 | 225/232 | 2168 | 109.23 | 114.45 | AC1-161 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 2 | 500/230 | 225/232 | 2168 | 109.23 | 114.45 | AC1-161 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 1 | 500/230 | 225/232 | 2168 | 109.17 | 114.43 | AC1-161 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 1 | 500/230 | 225/232 | 2168 | 109 | 114.21 | AC1-161 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 1 | 500/230 | 225/232 | 2168 | 109 | 114.21 | AC1-161 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220964 | GRACETON | 220999 | BAGLEY2 | 13 | 230 | 232 | 1795 | 113.18 | 114.19 | AC1-161 | BG_P4_5_GRCTN_3T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 116.03 | 114.05 | AC1-161 | AP_P2-3_PE-500-019C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204512 | 27S.RDG | 204693 | 27BOONETOWN | 1 | 230 | 227 | 607 | 105.43 | 113.61 | AC1-161 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208020 | MANO TR3 | 1 | 230 | 229 | 793 | 103.9 | 113.48 | AC1-161 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208020 | MANO TR3 | 208031 | MLWD TR2 | 1 | 230 | 229 | 903 | 102.25 | 113.2 | AC1-161 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 113.21 | 112.06 | AC1-161 | BG_P4_5_CNSTN_14_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 106.95 | 112.02 | AC1-161 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208020 | MANO TR3 | 208031 | MLWD TR2 | 1 | 230 | 229 | 903 | 101.54 | 111.84 | AC1-161 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208020 | MANO TR3 | 208031 | MLWD TR2 | 1 | 230 | 229 | 903 | 101.53 | 111.84 | AC1-161 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208020 | MANO TR3 | 208031 | MLWD TR2 | 1 | 230 | 229 | 903 | 101.54 | 111.84 | AC1-161 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 106.78 | 111.81 | AC1-161 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 106.78 | 111.81 | AC1-161 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 2 | 500/230 | 225/232 | 2168 | 108.31 | 111.59 | AC1-161 | PJM_500_BG_P4_5_CNSTN_15_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208031 | MLWD TR2 | 1 | 230 | 229 | 911 | 104.66 | 111.18 | AC1-161 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220980 | RAPHAEL | 220999 | BAGLEY2 | 13 | 230 | 232 | 1795 | 108.77 | 110.95 | AC1-161 | BG_P4_5_GRCTN_3T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 106.23 | 110.94 | AC1-161 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 106.1 | 110.8 | AC1-161 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208131 | WHEM | 208133 | WHEM TR2 | 1 | 230 | 229 | 691 | 101.47 | 110.01 | AC1-161 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208131 | WHEM | 208132 | WHEM TR1 | 1 | 230 | 229 | 691 | 103.49 | 109.7 | AC1-161 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 793 | 112.16 | 109.51 | AC1-161 | PEPCO_P4_PP19_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 108.44 | 108.94 | AC1-161 | PECO_P4_PEACH205_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208131 | WHEM | 208133 | WHEM TR2 | 1 | 230 | 229 | 691 | 100.76 | 108.63 | AC1-161 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208131 | WHEM | 208133 | WHEM TR2 | 1 | 230 | 229 | 691 | 100.76 | 108.63 | AC1-161 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208131 | WHEM | 208133 | WHEM TR2 | 1 | 230 | 229 | 691 | 100.75 | 108.62 | AC1-161 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 108.03 | 108.56 | AC1-161 | PECO_P1-2_5014_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200532 | 26ROXBURY | 200520 | 26ROXBURY | 2 | 138/115 | 226 | 435 | 95.61 | 108.07 | AC1-161 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220973 | GRANITE6 | 1 | 230 | 232 | 829 | 108.5 | 107.18 | AC1-161 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 793 | 108.94 | 106.99 | AC1-161 | AP_P2-3_PE-500-019C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 2 | 230 | 233 | 793 | 108.94 | 106.99 | AC1-161 | AP_P2-3_PE-500-019C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 204529 | 27GERMANTN | 1 | 138/115 | 227 | 453 | 104.99 | 106.92 | AC1-161 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 204529 | 27GERMANTN | 1 | 138/115 | 227 | 453 | 104.99 | 106.92 | AC1-161 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 204529 | 27GERMANTN | 1 | 138/115 | 227 | 453 | 104.98 | 106.92 | AC1-161 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220965 | NEAST339 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 108.01 | 106.57 | AC1-161 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220965 | NEAST339 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 107.91 | 106.46 | AC1-161 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220965 | NEAST339 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 107.91 | 106.46 | AC1-161 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220972 | GRANITE1 | 1 | 230 | 232 | 829 | 107.64 | 106.1 | AC1-161 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 101.35 | 105.48 | AC1-161 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 101.26 | 105.39 | AC1-161 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 104.18 | 105.23 | AC1-161 | PECO_P4_PEACH205_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 103.77 | 104.85 | AC1-161 | PECO_P1-2_5014_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200099 | LAUS | 208045 | LAUS | 3 | 500/230 | 225/229 | 1200 | 103.08 | 104.79 | AC1-161 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208021 | MANO TR4 | 208133 | WHEM TR2 | 2 | 230 | 229 | 593 | 95.97 | 104.69 | AC1-161 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 102.47 | 104.46 | AC1-161 | BG_P1_2322_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 102.39 | 104.38 | AC1-161 | BG_P1_2310_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 102.41 | 104.35 | AC1-161 | BG_P4_5_NW2322_230-4_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 102.33 | 104.31 | AC1-161 | BG_P4_5_NW2310_230-5_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200099 | LAUS | 208045 | LAUS | 3 | 500/230 | 225/229 | 1200 | 102.77 | 104.25 | AC1-161 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200099 | LAUS | 208045 | LAUS | 3 | 500/230 | 225/229 | 1200 | 102.77 | 104.25 | AC1-161 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200099 | LAUS | 208045 | LAUS | 3 | 500/230 | 225/229 | 1200 | 102.76 | 104.24 | AC1-161 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220972 | GRANITE1 | 1 | 230 | 232 | 829 | 105.54 | 104.21 | AC1-161 | BG_P4_5_NW230-4_2326_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220973 | GRANITE6 | 1 | 230 | 232 | 829 | 105.21 | 103.67 | AC1-161 | BG_P4_5_NW230-5_2311_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220979 | NEAST317 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 104.91 | 103.54 | AC1-161 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220979 | NEAST317 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 104.81 | 103.42 | AC1-161 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220979 | NEAST317 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 104.81 | 103.42 | AC1-161 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208021 | MANO TR4 | 208133 | WHEM TR2 | 2 | 230 | 229 | 593 | 95.16 | 103.24 | AC1-161 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208021 | MANO TR4 | 208133 | WHEM TR2 | 2 | 230 | 229 | 593 | 95.16 | 103.24 | AC1-161 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208021 | MANO TR4 | 208133 | WHEM TR2 | 2 | 230 | 229 | 593 | 95.15 | 103.23 | AC1-161 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 101.07 | 103.1 | AC1-161 | BG_P4_5_NW230-2_2322_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 99.28 | 103.01 | AC1-161 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 99.27 | 103.01 | AC1-161 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 99.27 | 103.01 | AC1-161 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 100.97 | 102.98 | AC1-161 | BG_P4_5_NW2371_2310_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 100.97 | 102.98 | AC1-161 | BG_P4_5_NW230-3_2310_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208020 | MANO TR3 | 208031 | MLWD TR2 | 1 | 230 | 229 | 903 | 95.17 | 102.71 | AC1-161 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220973 | GRANITE6 | 1 | 230 | 232 | 829 | 103.21 | 102.14 | AC1-161 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 100.09 | 102.04 | AC1-161 | BG_P4_5_CNSTN_14_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220964 | GRACETON | 220999 | BAGLEY2 | 13 | 230 | 232 | 1795 | 101.25 | 101.99 | AC1-161 | BG_P1_2305_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220964 | GRACETON | 221000 | BAGLEY | 5 | 230 | 232 | 1795 | 101.25 | 101.99 | AC1-161 | BG_P1_2313_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220965 | NEAST339 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 102.47 | 101.77 | AC1-161 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 98.34 | 101.7 | AC1-161 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220965 | NEAST339 | 220977 | RIV2339 | 1 | 230 | 232 | 991 | 103.04 | 101.59 | AC1-161 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 2 | 500/230 | 225/232 | 2168 | 98.84 | 101.58 | AC1-161 | BG_P1_CNSTN_500-2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 2 | 500/230 | 225/232 | 2168 | 98.84 | 101.58 | AC1-161 | PJM_500_BG_P2_CNSTN_230-N_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220966 | RIV2317 | 220979 | NEAST317 | 1 | 230 | 232 | 940 | 102.64 | 101.57 | AC1-161 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220965 | NEAST339 | 220977 | RIV2339 | 1 | 230 | 232 | 991 | 103 | 101.53 | AC1-161 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220965 | NEAST339 | 220977 | RIV2339 | 1 | 230 | 232 | 991 | 103 | 101.53 | AC1-161 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220966 | RIV2317 | 220979 | NEAST317 | 1 | 230 | 232 | 940 | 102.59 | 101.51 | AC1-161 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220966 | RIV2317 | 220979 | NEAST317 | 1 | 230 | 232 | 940 | 102.59 | 101.51 | AC1-161 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 1 | 500/230 | 225/232 | 2168 | 98.74 | 101.47 | AC1-161 | PJM_500_BG_P2_CNSTN_230-S_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 1 | 500/230 | 225/232 | 2168 | 98.74 | 101.47 | AC1-161 | BG_P1_CNSTN_500-4_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208131 | WHEM | 208133 | WHEM TR2 | 1 | 230 | 229 | 691 | 95.98 | 101.46 | AC1-161 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220972 | GRANITE1 | 1 | 230 | 232 | 829 | 102.61 | 101.37 | AC1-161 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 223960 | BRG 1T 230 | 1 | 500/230 | 225/233 | 1498 | 100.12 | 100.49 | AC1-161 | PEPCO_P4_PP41_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 98.45 | 100.37 | AC1-161 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 226.11 | 238.33 | AC1-164 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 224.12 | 238.33 | AC1-164 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 225.16 | 236.29 | AC1-164 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 223.17 | 236.29 | AC1-164 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 225.1 | 236.23 | AC1-164 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 223.1 | 236.23 | AC1-164 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 225.1 | 236.23 | AC1-164 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 223.1 | 236.23 | AC1-164 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 214.05 | 228.14 | AC1-164 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 213.13 | 226.15 | AC1-164 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 213.07 | 226.09 | AC1-164 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 213.07 | 226.09 | AC1-164 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 209.79 | 224.94 | AC1-164 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 208.87 | 222.94 | AC1-164 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 208.81 | 222.88 | AC1-164 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 208.81 | 222.88 | AC1-164 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 208.27 | 217.18 | AC1-164 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 210.27 | 217.18 | AC1-164 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 198.75 | 207.64 | AC1-164 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 194.49 | 204.28 | AC1-164 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 172.44 | 167.44 | AC1-164 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 171.47 | 166 | AC1-164 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 171.47 | 166 | AC1-164 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 171.45 | 165.99 | AC1-164 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 163.3 | 164.45 | AC1-164 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2901 | 144.57 | 146.66 | AE1-155 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 161.43 | 161.38 | AC1-164 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 161.43 | 161.38 | AC1-164 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 161.42 | 161.37 | AC1-164 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 163.52 | 158.6 | AC1-164 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 153.22 | 157.62 | AC1-164 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 161.74 | 156.86 | AC1-164 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 161.74 | 156.86 | AC1-164 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 151.54 | 156.3 | AC1-164 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 161.18 | 153.97 | AC1-164 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 148.18 | 152.65 | AC1-164 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 903 | 143.98 | 151.68 | AC1-164 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 152.49 | 150.81 | AC1-164 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 155.32 | 150.17 | AC1-164 | PN_P1-2_PN-500-010T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 903 | 142.45 | 149.08 | AC1-164 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 903 | 142.45 | 149.07 | AC1-164 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 903 | 142.43 | 149.07 | AC1-164 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.04 | 149.06 | AC1-164 | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 145.97 | 148.98 | AC1-164 | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.65 | 147.78 | AC1-164 | AP_P2-3_PE-500-016_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.72 | 147.75 | AC1-164 | AP_P2-3_PE-500-015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.64 | 147.51 | AC1-164 | PJM_500_BG_P4_5_CNSTN_L_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.92 | 147.49 | AC1-164 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.72 | 147.31 | AC1-164 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.75 | 147.29 | AC1-164 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.48 | 147.1 | AC1-164 | PECO_P4_NOTTI85_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.42 | 147.08 | AC1-164 | PECO_P1-2_220-08_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.35 | 147.02 | AC1-164 | PECO_P4_COOPR125_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 142.83 | 146.91 | AC1-164 | AP_P1-2_WP-500-DRT17_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 142.83 | 146.91 | AC1-164 | AP_P1-2_PE-500-001_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 142.78 | 146.84 | AC1-164 | AP_P2-3_PE-500-018C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2901 | 144.58 | 146.68 | AE1-157 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.41 | 143.72 | AC1-164 | PECO_P4_PEACH025_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.23 | 143.58 | AC1-164 | PECO_P1-2_PBTIE1_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 911 | 148.69 | 142.82 | AC1-164 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 911 | 147.74 | 141.51 | AC1-164 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 911 | 147.74 | 141.51 | AC1-164 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 911 | 147.73 | 141.5 | AC1-164 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204502 | 27JACKSON | 204514 | 27TMI | 1 | 230 | 227 | 781 | 132.64 | 141.24 | AC1-164 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204502 | 27JACKSON | 204514 | 27TMI | 1 | 230 | 227 | 781 | 132.84 | 141.23 | AC1-164 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204502 | 27JACKSON | 204514 | 27TMI | 1 | 230 | 227 | 781 | 132.84 | 141.23 | AC1-164 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204502 | 27JACKSON | 204514 | 27TMI | 1 | 230 | 227 | 781 | 132.82 | 141.22 | AC1-164 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 140.81 | 140.43 | AC1-164 | PJM_500_BG_P4_5_CNSTN_15_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 903 | 135.38 | 139.22 | AC1-164 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 1031 | 130.62 | 138.79 | AC1-164 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 1031 | 130.13 | 137.73 | AC1-164 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 1031 | 130.13 | 137.73 | AC1-164 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 1031 | 130.12 | 137.73 | AC1-164 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 911 | 139.87 | 134.84 | AC1-164 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208078 | SAKR | 1 | 230 | 229 | 903 | 125 | 133.56 | AC1-164 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 138.66 | 132.74 | AC1-164 | PECO_P4_PEACH205_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 207922 | BRIS | 207923 | BRISREAC | RX | 230 | 229 | 676 | 124.11 | 132.57 | AC1-164 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 207923 | BRISREAC | 208132 | WHEM TR1 | 1 | 230 | 229 | 676 | 124.11 | 132.57 | AC1-164 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 207922 | BRIS | 207923 | BRISREAC | RX | 230 | 229 | 676 | 124.11 | 132.57 | AC1-164 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 207923 | BRISREAC | 208132 | WHEM TR1 | 1 | 230 | 229 | 676 | 124.11 | 132.57 | AC1-164 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 207923 | BRISREAC | 208132 | WHEM TR1 | 1 | 230 | 229 | 676 | 124.09 | 132.56 | AC1-164 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 207922 | BRIS | 207923 | BRISREAC | RX | 230 | 229 | 676 | 124.09 | 132.56 | AC1-164 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 138.54 | 132.41 | AC1-164 | PECO_P1-2_PBTIE2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208078 | SAKR | 1 | 230 | 229 | 903 | 124.26 | 132.12 | AC1-164 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208078 | SAKR | 1 | 230 | 229 | 903 | 124.26 | 132.12 | AC1-164 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208078 | SAKR | 1 | 230 | 229 | 903 | 124.26 | 132.12 | AC1-164 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 137.63 | 131.56 | AC1-164 | PECO_P4_PEACH055_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204502 | 27JACKSON | 204514 | 27TMI | 1 | 230 | 227 | 781 | 125.19 | 130.69 | AC1-164 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220972 | GRANITE1 | 1 | 230 | 232 | 829 | 134.62 | 130.66 | AC1-164 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220972 | GRANITE1 | 1 | 230 | 232 | 829 | 133.99 | 130 | AC1-164 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220972 | GRANITE1 | 1 | 230 | 232 | 829 | 133.99 | 130 | AC1-164 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 1031 | 124.53 | 128.95 | AC1-164 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220973 | GRANITE6 | 1 | 230 | 232 | 829 | 132.55 | 128.77 | AC1-164 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220973 | GRANITE6 | 1 | 230 | 232 | 829 | 131.96 | 128.15 | AC1-164 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220973 | GRANITE6 | 1 | 230 | 232 | 829 | 131.96 | 128.15 | AC1-164 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 132.89 | 127.08 | AC1-164 | PECO_P4_PEACH015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 127.91 | 126.18 | AC1-164 | DVP_P4-2: 514T595_SRT-SW |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208020 | MANO TR3 | 1 | 230 | 229 | 793 | 112.08 | 125.83 | AC1-164 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 131.6 | 125.8 | AC1-164 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220953 | HOWARD12 | 220972 | GRANITE1 | 1 | 230 | 232 | 772 | 129.34 | 125.35 | AC1-164 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220954 | HOWARD32 | 220973 | GRANITE6 | 1 | 230 | 232 | 772 | 128.2 | 124.67 | AC1-164 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 2 | 230 | 233 | 793 | 126.2 | 124.43 | AC1-164 | DVP_P4-2: 514T595_SRT-SW |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 793 | 126.2 | 124.43 | AC1-164 | DVP_P4-2: 514T595_SRT-SW |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 207923 | BRISREAC | 208132 | WHEM TR1 | 1 | 230 | 229 | 676 | 119.01 | 124.43 | AC1-164 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 207922 | BRIS | 207923 | BRISREAC | RX | 230 | 229 | 676 | 119.01 | 124.43 | AC1-164 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 126.15 | 124.39 | AC1-164 | DVP_P4-2: 51482_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220953 | HOWARD12 | 220972 | GRANITE1 | 1 | 230 | 232 | 772 | 128.42 | 124.38 | AC1-164 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220953 | HOWARD12 | 220972 | GRANITE1 | 1 | 230 | 232 | 772 | 128.42 | 124.38 | AC1-164 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208020 | MANO TR3 | 1 | 230 | 229 | 793 | 111.25 | 124.3 | AC1-164 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208020 | MANO TR3 | 1 | 230 | 229 | 793 | 111.25 | 124.3 | AC1-164 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208020 | MANO TR3 | 1 | 230 | 229 | 793 | 111.25 | 124.3 | AC1-164 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 126.15 | 124.3 | AC1-164 | AP_P1-2_PE-500-407T_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 126.15 | 124.3 | AC1-164 | DVP_P1-2: LN 514_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220954 | HOWARD32 | 220973 | GRANITE6 | 1 | 230 | 232 | 772 | 127.41 | 123.83 | AC1-164 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220954 | HOWARD32 | 220973 | GRANITE6 | 1 | 230 | 232 | 772 | 127.41 | 123.83 | AC1-164 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 793 | 124.94 | 123.17 | AC1-164 | DVP_P4-2: 51482_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 2 | 230 | 233 | 793 | 124.94 | 123.17 | AC1-164 | DVP_P4-2: 51482_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 2 | 230 | 233 | 793 | 124.94 | 123.09 | AC1-164 | AP_P1-2_PE-500-407T_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 793 | 124.94 | 123.09 | AC1-164 | AP_P1-2_PE-500-407T_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 2 | 230 | 233 | 793 | 124.94 | 123.09 | AC1-164 | DVP_P1-2: LN 514_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 793 | 124.94 | 123.09 | AC1-164 | DVP_P1-2: LN 514_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208031 | MLWD TR2 | 1 | 230 | 229 | 911 | 112.29 | 122.2 | AC1-164 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208078 | SAKR | 1 | 230 | 229 | 903 | 117 | 122.17 | AC1-164 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204512 | 27S.RDG | 204693 | 27BOONETOWN | 1 | 230 | 227 | 607 | 107.31 | 122.03 | AC1-164 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204512 | 27S.RDG | 204693 | 27BOONETOWN | 1 | 230 | 227 | 607 | 107.28 | 122 | AC1-164 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204512 | 27S.RDG | 204693 | 27BOONETOWN | 1 | 230 | 227 | 607 | 107.28 | 122 | AC1-164 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200025 | W CHAPEL | 1 | 500 | 225 | 1732 | 123.38 | 121.59 | AC1-164 | PEPCO_P4_PP41_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208031 | MLWD TR2 | 1 | 230 | 229 | 911 | 111.57 | 120.89 | AC1-164 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208031 | MLWD TR2 | 1 | 230 | 229 | 911 | 111.57 | 120.88 | AC1-164 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208031 | MLWD TR2 | 1 | 230 | 229 | 911 | 111.57 | 120.88 | AC1-164 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220965 | NEAST339 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 119.58 | 118.92 | AC1-164 | BG_P1_2315_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 911 | 117.83 | 118.82 | AC1-164 | PJM_500_BG_P4_5_CNSTN_15_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220965 | NEAST339 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 119.16 | 118.71 | AC1-164 | BG_P4_5_NEAST_17_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220965 | NEAST339 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 119.31 | 118.71 | AC1-164 | BG_P4_5_NEAST_15_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 114.53 | 118.2 | AC1-164 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220979 | NEAST317 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 118.66 | 118.05 | AC1-164 | BG_P1_2337_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 114.2 | 117.86 | AC1-164 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 114.18 | 117.8 | AC1-164 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 114.18 | 117.8 | AC1-164 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220979 | NEAST317 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 118.33 | 117.79 | AC1-164 | BG_P4_5_NEAST_39_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220979 | NEAST317 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 118.33 | 117.79 | AC1-164 | BG_P4_5_NEAST_37_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 113.85 | 117.47 | AC1-164 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 113.85 | 117.47 | AC1-164 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208131 | WHEM | 208132 | WHEM TR1 | 1 | 230 | 229 | 691 | 108.41 | 117.43 | AC1-164 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208131 | WHEM | 208132 | WHEM TR1 | 1 | 230 | 229 | 691 | 108.41 | 117.42 | AC1-164 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208131 | WHEM | 208132 | WHEM TR1 | 1 | 230 | 229 | 691 | 108.39 | 117.42 | AC1-164 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 122.51 | 117.15 | AC1-164 | PECO_P4_PEACH225_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 117.9 | 116.63 | AC1-164 | PL_04_P12_000260_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 117.9 | 116.63 | AC1-164 | PL_04_P42_000564_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 793 | 118.31 | 115.54 | AC1-164 | PEPCO_P1_PP2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 2 | 230 | 233 | 793 | 118.31 | 115.54 | AC1-164 | PEPCO_P1_PP1_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 2 | 500/230 | 225/232 | 2168 | 109.51 | 114.79 | AC1-164 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 2 | 500/230 | 225/232 | 2168 | 109.33 | 114.58 | AC1-164 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 2 | 500/230 | 225/232 | 2168 | 109.33 | 114.58 | AC1-164 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 1 | 500/230 | 225/232 | 2168 | 109.28 | 114.55 | AC1-164 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 116.37 | 114.4 | AC1-164 | AP_P2-3_PE-500-019C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 1 | 500/230 | 225/232 | 2168 | 109.1 | 114.34 | AC1-164 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 1 | 500/230 | 225/232 | 2168 | 109.1 | 114.34 | AC1-164 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220964 | GRACETON | 220999 | BAGLEY2 | 13 | 230 | 232 | 1795 | 113.28 | 114.31 | AC1-164 | BG_P4_5_GRCTN_3T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208020 | MANO TR3 | 1 | 230 | 229 | 793 | 104.07 | 113.66 | AC1-164 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208020 | MANO TR3 | 208031 | MLWD TR2 | 1 | 230 | 229 | 903 | 102.4 | 113.45 | AC1-164 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208020 | MANO TR3 | 208031 | MLWD TR2 | 1 | 230 | 229 | 903 | 101.69 | 112.26 | AC1-164 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208020 | MANO TR3 | 208031 | MLWD TR2 | 1 | 230 | 229 | 903 | 101.69 | 112.26 | AC1-164 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208020 | MANO TR3 | 208031 | MLWD TR2 | 1 | 230 | 229 | 903 | 101.69 | 112.26 | AC1-164 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 113.36 | 112.21 | AC1-164 | BG_P4_5_CNSTN_14_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 2 | 500/230 | 225/232 | 2168 | 108.39 | 111.68 | AC1-164 | PJM_500_BG_P4_5_CNSTN_15_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208031 | MLWD TR2 | 1 | 230 | 229 | 911 | 104.82 | 111.34 | AC1-164 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 106.33 | 111.07 | AC1-164 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220980 | RAPHAEL | 220999 | BAGLEY2 | 13 | 230 | 232 | 1795 | 108.87 | 111.07 | AC1-164 | BG_P4_5_GRCTN_3T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 106.21 | 110.94 | AC1-164 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 108.03 | 110.62 | AC1-164 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208131 | WHEM | 208132 | WHEM TR1 | 1 | 230 | 229 | 691 | 103.62 | 109.91 | AC1-164 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 793 | 112.42 | 109.76 | AC1-164 | PEPCO_P4_PP19_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208131 | WHEM | 208133 | WHEM TR2 | 1 | 230 | 229 | 691 | 100.89 | 108.89 | AC1-164 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208131 | WHEM | 208133 | WHEM TR2 | 1 | 230 | 229 | 691 | 100.89 | 108.88 | AC1-164 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208131 | WHEM | 208133 | WHEM TR2 | 1 | 230 | 229 | 691 | 100.87 | 108.88 | AC1-164 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220973 | GRANITE6 | 1 | 230 | 232 | 829 | 108.65 | 107.34 | AC1-164 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 2 | 230 | 233 | 793 | 109.18 | 107.24 | AC1-164 | AP_P2-3_PE-500-019C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 793 | 109.18 | 107.24 | AC1-164 | AP_P2-3_PE-500-019C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220965 | NEAST339 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 108.14 | 106.71 | AC1-164 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220965 | NEAST339 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 108.04 | 106.6 | AC1-164 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220965 | NEAST339 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 108.04 | 106.59 | AC1-164 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220972 | GRANITE1 | 1 | 230 | 232 | 829 | 107.79 | 106.26 | AC1-164 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 101.45 | 105.6 | AC1-164 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 101.37 | 105.51 | AC1-164 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 102.57 | 104.57 | AC1-164 | BG_P1_2322_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 102.5 | 104.5 | AC1-164 | BG_P1_2310_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 102.51 | 104.46 | AC1-164 | BG_P4_5_NW2322_230-4_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 102.44 | 104.43 | AC1-164 | BG_P4_5_NW2310_230-5_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200099 | LAUS | 208045 | LAUS | 3 | 500/230 | 225/229 | 1200 | 102.87 | 104.4 | AC1-164 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200099 | LAUS | 208045 | LAUS | 3 | 500/230 | 225/229 | 1200 | 102.87 | 104.4 | AC1-164 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200099 | LAUS | 208045 | LAUS | 3 | 500/230 | 225/229 | 1200 | 102.85 | 104.39 | AC1-164 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220979 | NEAST317 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 105.04 | 103.67 | AC1-164 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220979 | NEAST317 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 104.94 | 103.55 | AC1-164 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220979 | NEAST317 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 104.94 | 103.55 | AC1-164 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 101.17 | 103.21 | AC1-164 | BG_P4_5_NW230-2_2322_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 99.37 | 103.18 | AC1-164 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 99.36 | 103.18 | AC1-164 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 99.36 | 103.18 | AC1-164 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 101.07 | 103.1 | AC1-164 | BG_P4_5_NW2371_2310_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 101.07 | 103.09 | AC1-164 | BG_P4_5_NW230-3_2310_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208020 | MANO TR3 | 208031 | MLWD TR2 | 1 | 230 | 229 | 903 | 95.32 | 102.87 | AC1-164 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 100.19 | 102.15 | AC1-164 | BG_P4_5_CNSTN_14_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220964 | GRACETON | 220999 | BAGLEY2 | 13 | 230 | 232 | 1795 | 101.35 | 102.09 | AC1-164 | BG_P1_2305_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220964 | GRACETON | 221000 | BAGLEY | 5 | 230 | 232 | 1795 | 101.35 | 102.09 | AC1-164 | BG_P1_2313_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220965 | NEAST339 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 102.59 | 101.89 | AC1-164 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 98.43 | 101.85 | AC1-164 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220965 | NEAST339 | 220977 | RIV2339 | 1 | 230 | 232 | 991 | 103.19 | 101.75 | AC1-164 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220966 | RIV2317 | 220979 | NEAST317 | 1 | 230 | 232 | 940 | 102.79 | 101.73 | AC1-164 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220965 | NEAST339 | 220977 | RIV2339 | 1 | 230 | 232 | 991 | 103.15 | 101.69 | AC1-164 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220965 | NEAST339 | 220977 | RIV2339 | 1 | 230 | 232 | 991 | 103.15 | 101.69 | AC1-164 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220966 | RIV2317 | 220979 | NEAST317 | 1 | 230 | 232 | 940 | 102.75 | 101.67 | AC1-164 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220966 | RIV2317 | 220979 | NEAST317 | 1 | 230 | 232 | 940 | 102.75 | 101.67 | AC1-164 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208131 | WHEM | 208133 | WHEM TR2 | 1 | 230 | 229 | 691 | 96.11 | 101.66 | AC1-164 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 2 | 500/230 | 225/232 | 2168 | 98.92 | 101.66 | AC1-164 | BG_P1_CNSTN_500-2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 2 | 500/230 | 225/232 | 2168 | 98.92 | 101.66 | AC1-164 | PJM_500_BG_P2_CNSTN_230-N_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 1 | 500/230 | 225/232 | 2168 | 98.81 | 101.55 | AC1-164 | BG_P1_CNSTN_500-4_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 1 | 500/230 | 225/232 | 2168 | 98.81 | 101.55 | AC1-164 | PJM_500_BG_P2_CNSTN_230-S_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 223960 | BRG 1T 230 | 1 | 500/230 | 225/233 | 1498 | 100.22 | 100.59 | AC1-164 | PEPCO_P4_PP41_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 98.54 | 100.51 | AC1-164 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 144.32 | 139.17 | AC1-165 | PL_10_P42_100570_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 144.32 | 139.17 | AC1-165 | PL_10_P42_100570_A_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 143.51 | 138.38 | AC1-165 | PL_10_P12_000085_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 143.41 | 138.29 | AC1-165 | PN_P2-3_PN-500-004-DRT-008_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 143.41 | 138.29 | AC1-165 | PN_P2-3_PN-500-DRT31_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 143.04 | 137.92 | AC1-165 | PL_30_P42_000131_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 144.32 | 139.17 | AC1-166 | PL_10_P42_100570_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 144.32 | 139.17 | AC1-166 | PL_10_P42_100570_A_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 143.51 | 138.38 | AC1-166 | PL_10_P12_000085_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 143.41 | 138.29 | AC1-166 | PN_P2-3_PN-500-004-DRT-008_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 143.41 | 138.29 | AC1-166 | PN_P2-3_PN-500-DRT31_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 143.04 | 137.92 | AC1-166 | PL_30_P42_000131_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 144.32 | 139.17 | AC1-167 | PL_10_P42_100570_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 144.32 | 139.17 | AC1-167 | PL_10_P42_100570_A_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 143.51 | 138.38 | AC1-167 | PL_10_P12_000085_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 143.41 | 138.29 | AC1-167 | PN_P2-3_PN-500-004-DRT-008_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 143.41 | 138.29 | AC1-167 | PN_P2-3_PN-500-DRT31_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 143.04 | 137.92 | AC1-167 | PL_30_P42_000131_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 144.32 | 139.18 | AC1-168 | PL_10_P42_100570_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 144.32 | 139.18 | AC1-168 | PL_10_P42_100570_A_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 143.51 | 138.38 | AC1-168 | PL_10_P12_000085_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 143.42 | 138.29 | AC1-168 | PN_P2-3_PN-500-004-DRT-008_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 143.42 | 138.29 | AC1-168 | PN_P2-3_PN-500-DRT31_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 143.04 | 137.92 | AC1-168 | PL_30_P42_000131_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2901 | 144.77 | 146.89 | AE1-191 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 153.79 | 158.29 | AC1-174 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.25 | 157.38 | AC1-174 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.25 | 157.38 | AC1-174 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 152.1 | 156.97 | AC1-174 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 161.73 | 154.5 | AC1-174 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 148.74 | 153.32 | AC1-174 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 155.83 | 150.68 | AC1-174 | PN_P1-2_PN-500-010T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.57 | 149.69 | AC1-174 | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.5 | 149.62 | AC1-174 | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.21 | 148.49 | AC1-174 | AP_P2-3_PE-500-016_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.27 | 148.46 | AC1-174 | AP_P2-3_PE-500-015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.14 | 148.01 | AC1-174 | PJM_500_BG_P4_5_CNSTN_L_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.4 | 147.96 | AC1-174 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.2 | 147.77 | AC1-174 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.22 | 147.76 | AC1-174 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.39 | 147.6 | AC1-174 | AP_P1-2_PE-500-001_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.39 | 147.6 | AC1-174 | AP_P1-2_WP-500-DRT17_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.95 | 147.56 | AC1-174 | PECO_P4_NOTTI85_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.89 | 147.55 | AC1-174 | PECO_P1-2_220-08_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.34 | 147.53 | AC1-174 | AP_P2-3_PE-500-018C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.83 | 147.48 | AC1-174 | PECO_P4_COOPR125_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2901 | 144.88 | 147.03 | AE1-212 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.93 | 144.22 | AC1-174 | PECO_P4_PEACH025_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.81 | 144.14 | AC1-174 | PECO_P1-2_PBTIE1_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 139.19 | 133.25 | AC1-174 | PECO_P4_PEACH205_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 139.08 | 132.92 | AC1-174 | PECO_P1-2_PBTIE2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 138.13 | 132.04 | AC1-174 | PECO_P4_PEACH055_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 133.46 | 127.64 | AC1-174 | PECO_P4_PEACH015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 132.13 | 126.31 | AC1-174 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204512 | 27S.RDG | 204693 | 27BOONETOWN | 1 | 230 | 227 | 607 | 107.68 | 123.45 | AC1-174 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 123.03 | 117.66 | AC1-174 | PECO_P4_PEACH225_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2901 | 145.86 | 148.16 | AE1-229 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 153.79 | 158.29 | AC1-175 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.25 | 157.38 | AC1-175 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.25 | 157.38 | AC1-175 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 152.1 | 156.97 | AC1-175 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 161.73 | 154.5 | AC1-175 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 148.74 | 153.32 | AC1-175 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 155.83 | 150.68 | AC1-175 | PN_P1-2_PN-500-010T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.57 | 149.69 | AC1-175 | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.5 | 149.62 | AC1-175 | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.21 | 148.49 | AC1-175 | AP_P2-3_PE-500-016_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.27 | 148.46 | AC1-175 | AP_P2-3_PE-500-015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.14 | 148.01 | AC1-175 | PJM_500_BG_P4_5_CNSTN_L_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.4 | 147.96 | AC1-175 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.2 | 147.77 | AC1-175 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.22 | 147.76 | AC1-175 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.39 | 147.6 | AC1-175 | AP_P1-2_PE-500-001_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.39 | 147.6 | AC1-175 | AP_P1-2_WP-500-DRT17_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.95 | 147.56 | AC1-175 | PECO_P4_NOTTI85_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.89 | 147.55 | AC1-175 | PECO_P1-2_220-08_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.34 | 147.53 | AC1-175 | AP_P2-3_PE-500-018C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.83 | 147.48 | AC1-175 | PECO_P4_COOPR125_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2901 | 144.93 | 147.08 | AE1-237 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.93 | 144.22 | AC1-175 | PECO_P4_PEACH025_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.81 | 144.14 | AC1-175 | PECO_P1-2_PBTIE1_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 139.19 | 133.25 | AC1-175 | PECO_P4_PEACH205_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 139.08 | 132.92 | AC1-175 | PECO_P1-2_PBTIE2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 138.13 | 132.04 | AC1-175 | PECO_P4_PEACH055_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 133.46 | 127.64 | AC1-175 | PECO_P4_PEACH015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 132.13 | 126.31 | AC1-175 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204512 | 27S.RDG | 204693 | 27BOONETOWN | 1 | 230 | 227 | 607 | 107.68 | 123.45 | AC1-175 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 123.03 | 117.66 | AC1-175 | PECO_P4_PEACH225_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2901 | 145.35 | 147.57 | AE1-240 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 153.68 | 158.15 | AC1-189 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.17 | 157.29 | AC1-189 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.17 | 157.29 | AC1-189 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 151.99 | 156.83 | AC1-189 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 161.66 | 154.44 | AC1-189 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 148.63 | 153.18 | AC1-189 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 155.74 | 150.59 | AC1-189 | PN_P1-2_PN-500-010T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.46 | 149.56 | AC1-189 | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.39 | 149.49 | AC1-189 | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.08 | 148.32 | AC1-189 | AP_P2-3_PE-500-016_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.15 | 148.29 | AC1-189 | AP_P2-3_PE-500-015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.05 | 147.92 | AC1-189 | PJM_500_BG_P4_5_CNSTN_L_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.34 | 147.9 | AC1-189 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.14 | 147.72 | AC1-189 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.17 | 147.7 | AC1-189 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.9 | 147.51 | AC1-189 | PECO_P4_NOTTI85_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.84 | 147.49 | AC1-189 | PECO_P1-2_220-08_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.26 | 147.44 | AC1-189 | AP_P1-2_WP-500-DRT17_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.26 | 147.44 | AC1-189 | AP_P1-2_PE-500-001_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.77 | 147.43 | AC1-189 | PECO_P4_COOPR125_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.21 | 147.37 | AC1-189 | AP_P2-3_PE-500-018C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2901 | 146.86 | 149.32 | AE2-000 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.88 | 144.17 | AC1-189 | PECO_P4_PEACH025_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.74 | 144.07 | AC1-189 | PECO_P1-2_PBTIE1_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 139.12 | 133.18 | AC1-189 | PECO_P4_PEACH205_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 139.01 | 132.86 | AC1-189 | PECO_P1-2_PBTIE2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 138.07 | 131.98 | AC1-189 | PECO_P4_PEACH055_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 133.38 | 127.56 | AC1-189 | PECO_P4_PEACH015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 128.79 | 127.05 | AC1-189 | DVP_P4-2: 514T595_SRT-SW |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 132.06 | 126.24 | AC1-189 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 127.04 | 125.34 | AC1-189 | DVP_P4-2: 51482_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 127.04 | 125.24 | AC1-189 | DVP_P1-2: LN 514_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 127.04 | 125.24 | AC1-189 | AP_P1-2_PE-500-407T_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 122.96 | 117.59 | AC1-189 | PECO_P4_PEACH225_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 117.24 | 115.33 | AC1-189 | AP_P2-3_PE-500-019C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 225.77 | 237.26 | AC1-191 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 223.76 | 237.26 | AC1-191 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 225.7 | 237.2 | AC1-191 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 223.69 | 237.19 | AC1-191 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 225.7 | 237.19 | AC1-191 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 223.69 | 237.19 | AC1-191 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 213.7 | 227.09 | AC1-191 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 213.64 | 227.03 | AC1-191 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 213.64 | 227.03 | AC1-191 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 209.44 | 223.89 | AC1-191 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 209.38 | 223.83 | AC1-191 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 209.38 | 223.82 | AC1-191 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 172.87 | 167.9 | AC1-191 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2901 | 146.53 | 148.95 | AE2-020 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 153.63 | 158.1 | AC1-191 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.13 | 157.25 | AC1-191 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.13 | 157.25 | AC1-191 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 151.95 | 156.78 | AC1-191 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 161.63 | 154.4 | AC1-191 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 148.58 | 153.13 | AC1-191 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 155.71 | 150.55 | AC1-191 | PN_P1-2_PN-500-010T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.42 | 149.51 | AC1-191 | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.35 | 149.44 | AC1-191 | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.04 | 148.26 | AC1-191 | AP_P2-3_PE-500-016_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.1 | 148.23 | AC1-191 | AP_P2-3_PE-500-015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.02 | 147.89 | AC1-191 | PJM_500_BG_P4_5_CNSTN_L_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.31 | 147.88 | AC1-191 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.11 | 147.69 | AC1-191 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.14 | 147.68 | AC1-191 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.87 | 147.48 | AC1-191 | PECO_P4_NOTTI85_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.81 | 147.46 | AC1-191 | PECO_P1-2_220-08_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.74 | 147.4 | AC1-191 | PECO_P4_COOPR125_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.22 | 147.38 | AC1-191 | AP_P1-2_WP-500-DRT17_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.22 | 147.38 | AC1-191 | AP_P1-2_PE-500-001_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.17 | 147.31 | AC1-191 | AP_P2-3_PE-500-018C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2901 | 146.53 | 148.95 | AE2-021 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.85 | 144.14 | AC1-191 | PECO_P4_PEACH025_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.7 | 144.03 | AC1-191 | PECO_P1-2_PBTIE1_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 911 | 149.1 | 143.22 | AC1-191 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 139.08 | 133.15 | AC1-191 | PECO_P4_PEACH205_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 138.98 | 132.82 | AC1-191 | PECO_P1-2_PBTIE2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 138.04 | 131.95 | AC1-191 | PECO_P4_PEACH055_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 133.35 | 127.53 | AC1-191 | PECO_P4_PEACH015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 128.66 | 126.96 | AC1-191 | DVP_P4-2: 514T595_SRT-SW |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 132.03 | 126.2 | AC1-191 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 126.91 | 125.19 | AC1-191 | DVP_P4-2: 51482_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 126.91 | 125.09 | AC1-191 | AP_P1-2_PE-500-407T_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 126.91 | 125.09 | AC1-191 | DVP_P1-2: LN 514_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200025 | W CHAPEL | 1 | 500 | 225 | 1732 | 123.75 | 121.97 | AC1-191 | PEPCO_P4_PP41_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 122.93 | 117.56 | AC1-191 | PECO_P4_PEACH225_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 117.11 | 115.18 | AC1-191 | AP_P2-3_PE-500-019C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 99.56 | 103.51 | AC1-191 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 99.56 | 103.51 | AC1-191 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 99.56 | 103.51 | AC1-191 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 98.64 | 102.19 | AC1-191 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 98.73 | 100.81 | AC1-191 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2901 | 145.81 | 148.1 | AE2-022 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 153.75 | 158.25 | AC1-194 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.21 | 157.33 | AC1-194 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.21 | 157.33 | AC1-194 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 152.06 | 156.92 | AC1-194 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 161.66 | 154.44 | AC1-194 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 148.7 | 153.27 | AC1-194 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 155.78 | 150.63 | AC1-194 | PN_P1-2_PN-500-010T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.53 | 149.65 | AC1-194 | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.46 | 149.57 | AC1-194 | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.18 | 148.45 | AC1-194 | AP_P2-3_PE-500-016_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.24 | 148.42 | AC1-194 | AP_P2-3_PE-500-015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.09 | 147.97 | AC1-194 | PJM_500_BG_P4_5_CNSTN_L_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.34 | 147.91 | AC1-194 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.14 | 147.72 | AC1-194 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.17 | 147.7 | AC1-194 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.35 | 147.57 | AC1-194 | AP_P1-2_WP-500-DRT17_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.35 | 147.57 | AC1-194 | AP_P1-2_PE-500-001_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.89 | 147.51 | AC1-194 | PECO_P4_NOTTI85_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.3 | 147.5 | AC1-194 | AP_P2-3_PE-500-018C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.83 | 147.49 | AC1-194 | PECO_P1-2_220-08_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.77 | 147.43 | AC1-194 | PECO_P4_COOPR125_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2901 | 144.61 | 146.71 | AE2-027 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.86 | 144.15 | AC1-194 | PECO_P4_PEACH025_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.75 | 144.07 | AC1-194 | PECO_P1-2_PBTIE1_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 139.14 | 133.2 | AC1-194 | PECO_P4_PEACH205_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 139.02 | 132.86 | AC1-194 | PECO_P1-2_PBTIE2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 138.08 | 131.99 | AC1-194 | PECO_P4_PEACH055_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 133.4 | 127.58 | AC1-194 | PECO_P4_PEACH015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 132.07 | 126.25 | AC1-194 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 122.98 | 117.61 | AC1-194 | PECO_P4_PEACH225_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2901 | 144.91 | 147.06 | AE2-029 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 153.69 | 158.17 | AC1-208 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.18 | 157.3 | AC1-208 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.18 | 157.3 | AC1-208 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 152 | 156.85 | AC1-208 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 161.68 | 154.45 | AC1-208 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 148.64 | 153.2 | AC1-208 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 155.75 | 150.6 | AC1-208 | PN_P1-2_PN-500-010T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.48 | 149.58 | AC1-208 | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.41 | 149.51 | AC1-208 | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.1 | 148.33 | AC1-208 | AP_P2-3_PE-500-016_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.16 | 148.3 | AC1-208 | AP_P2-3_PE-500-015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.07 | 147.93 | AC1-208 | PJM_500_BG_P4_5_CNSTN_L_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.35 | 147.92 | AC1-208 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.15 | 147.73 | AC1-208 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.18 | 147.72 | AC1-208 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.91 | 147.52 | AC1-208 | PECO_P4_NOTTI85_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.85 | 147.51 | AC1-208 | PECO_P1-2_220-08_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.27 | 147.45 | AC1-208 | AP_P1-2_PE-500-001_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.27 | 147.45 | AC1-208 | AP_P1-2_WP-500-DRT17_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.78 | 147.44 | AC1-208 | PECO_P4_COOPR125_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.23 | 147.38 | AC1-208 | AP_P2-3_PE-500-018C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2901 | 145.36 | 147.58 | AE2-042 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.9 | 144.19 | AC1-208 | PECO_P4_PEACH025_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.75 | 144.08 | AC1-208 | PECO_P1-2_PBTIE1_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 139.13 | 133.19 | AC1-208 | PECO_P4_PEACH205_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 139.02 | 132.87 | AC1-208 | PECO_P1-2_PBTIE2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 138.08 | 132 | AC1-208 | PECO_P4_PEACH055_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 133.4 | 127.58 | AC1-208 | PECO_P4_PEACH015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 128.81 | 127.07 | AC1-208 | DVP_P4-2: 514T595_SRT-SW |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 132.07 | 126.25 | AC1-208 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 127.06 | 125.36 | AC1-208 | DVP_P4-2: 51482_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 127.06 | 125.26 | AC1-208 | DVP_P1-2: LN 514_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 127.06 | 125.26 | AC1-208 | AP_P1-2_PE-500-407T_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 122.98 | 117.6 | AC1-208 | PECO_P4_PEACH225_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 117.26 | 115.35 | AC1-208 | AP_P2-3_PE-500-019C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 144.32 | 139.17 | AC1-214 | PL_10_P42_100570_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 144.32 | 139.17 | AC1-214 | PL_10_P42_100570_A_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 143.51 | 138.38 | AC1-214 | PL_10_P12_000085_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 143.41 | 138.29 | AC1-214 | PN_P2-3_PN-500-004-DRT-008_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 143.41 | 138.29 | AC1-214 | PN_P2-3_PN-500-DRT31_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 143.04 | 137.92 | AC1-214 | PL_30_P42_000131_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 225.7 | 237.15 | AC1-216 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 223.69 | 237.15 | AC1-216 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 225.63 | 237.09 | AC1-216 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 223.62 | 237.09 | AC1-216 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 225.63 | 237.09 | AC1-216 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 223.62 | 237.09 | AC1-216 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 213.64 | 226.99 | AC1-216 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 213.57 | 226.93 | AC1-216 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 213.57 | 226.93 | AC1-216 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 209.38 | 223.78 | AC1-216 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 209.31 | 223.72 | AC1-216 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 209.31 | 223.72 | AC1-216 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 210.79 | 217.94 | AC1-216 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 208.79 | 217.94 | AC1-216 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 199.24 | 208.38 | AC1-216 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 194.99 | 205.03 | AC1-216 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 172.82 | 167.84 | AC1-216 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 163.69 | 165.02 | AC1-216 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2901 | 145.31 | 147.52 | AE2-046 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 161.84 | 161.92 | AC1-216 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 161.83 | 161.92 | AC1-216 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 161.82 | 161.91 | AC1-216 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 153.59 | 158.05 | AC1-216 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.09 | 157.21 | AC1-216 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.09 | 157.21 | AC1-216 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 151.9 | 156.73 | AC1-216 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 161.57 | 154.35 | AC1-216 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 148.54 | 153.07 | AC1-216 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 155.66 | 150.51 | AC1-216 | PN_P1-2_PN-500-010T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 903 | 142.79 | 149.61 | AC1-216 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 903 | 142.79 | 149.61 | AC1-216 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 903 | 142.77 | 149.6 | AC1-216 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.38 | 149.46 | AC1-216 | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.31 | 149.39 | AC1-216 | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144 | 148.21 | AC1-216 | AP_P2-3_PE-500-016_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.06 | 148.18 | AC1-216 | AP_P2-3_PE-500-015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.98 | 147.84 | AC1-216 | PJM_500_BG_P4_5_CNSTN_L_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.27 | 147.83 | AC1-216 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.07 | 147.64 | AC1-216 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.09 | 147.63 | AC1-216 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.82 | 147.43 | AC1-216 | PECO_P4_NOTTI85_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.76 | 147.42 | AC1-216 | PECO_P1-2_220-08_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.7 | 147.35 | AC1-216 | PECO_P4_COOPR125_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.18 | 147.33 | AC1-216 | AP_P1-2_PE-500-001_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.18 | 147.33 | AC1-216 | AP_P1-2_WP-500-DRT17_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.13 | 147.26 | AC1-216 | AP_P2-3_PE-500-018C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2901 | 145.35 | 147.57 | AE2-093 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.8 | 144.09 | AC1-216 | PECO_P4_PEACH025_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.65 | 143.98 | AC1-216 | PECO_P1-2_PBTIE1_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 911 | 149.06 | 143.18 | AC1-216 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 1031 | 130.39 | 138.2 | AC1-216 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 1031 | 130.39 | 138.2 | AC1-216 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 1031 | 130.38 | 138.19 | AC1-216 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 139.04 | 133.1 | AC1-216 | PECO_P4_PEACH205_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 138.93 | 132.78 | AC1-216 | PECO_P1-2_PBTIE2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208078 | SAKR | 1 | 230 | 229 | 903 | 124.57 | 132.64 | AC1-216 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 137.99 | 131.91 | AC1-216 | PECO_P4_PEACH055_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 133.29 | 127.48 | AC1-216 | PECO_P4_PEACH015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 128.59 | 126.9 | AC1-216 | DVP_P4-2: 514T595_SRT-SW |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 131.98 | 126.16 | AC1-216 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 126.84 | 125.12 | AC1-216 | DVP_P4-2: 51482_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 126.84 | 125.03 | AC1-216 | DVP_P1-2: LN 514_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 126.84 | 125.03 | AC1-216 | AP_P1-2_PE-500-407T_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208020 | MANO TR3 | 1 | 230 | 229 | 793 | 111.57 | 124.75 | AC1-216 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208020 | MANO TR3 | 1 | 230 | 229 | 793 | 111.56 | 124.75 | AC1-216 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208020 | MANO TR3 | 1 | 230 | 229 | 793 | 111.57 | 124.74 | AC1-216 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200025 | W CHAPEL | 1 | 500 | 225 | 1732 | 123.72 | 121.93 | AC1-216 | PEPCO_P4_PP41_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 122.88 | 117.51 | AC1-216 | PECO_P4_PEACH225_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 117.04 | 115.11 | AC1-216 | AP_P2-3_PE-500-019C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 2 | 500/230 | 225/232 | 2168 | 109.71 | 115.03 | AC1-216 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 2 | 500/230 | 225/232 | 2168 | 109.53 | 114.81 | AC1-216 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 2 | 500/230 | 225/232 | 2168 | 109.53 | 114.81 | AC1-216 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 1 | 500/230 | 225/232 | 2168 | 109.48 | 114.78 | AC1-216 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 1 | 500/230 | 225/232 | 2168 | 109.3 | 114.57 | AC1-216 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 1 | 500/230 | 225/232 | 2168 | 109.3 | 114.57 | AC1-216 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 99.55 | 103.48 | AC1-216 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 99.54 | 103.48 | AC1-216 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 99.54 | 103.48 | AC1-216 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 98.62 | 102.16 | AC1-216 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 98.72 | 100.78 | AC1-216 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2901 | 144.89 | 147.04 | AE2-104 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 153.77 | 158.26 | AC1-221 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.25 | 157.38 | AC1-221 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.25 | 157.37 | AC1-221 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 152.08 | 156.94 | AC1-221 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 161.75 | 154.53 | AC1-221 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 148.71 | 153.29 | AC1-221 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 155.82 | 150.67 | AC1-221 | PN_P1-2_PN-500-010T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.55 | 149.66 | AC1-221 | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.48 | 149.59 | AC1-221 | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.17 | 148.43 | AC1-221 | AP_P2-3_PE-500-016_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.24 | 148.4 | AC1-221 | AP_P2-3_PE-500-015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.14 | 148 | AC1-221 | PJM_500_BG_P4_5_CNSTN_L_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.42 | 147.99 | AC1-221 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.22 | 147.8 | AC1-221 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.25 | 147.78 | AC1-221 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.98 | 147.59 | AC1-221 | PECO_P4_NOTTI85_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.92 | 147.57 | AC1-221 | PECO_P1-2_220-08_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.35 | 147.55 | AC1-221 | AP_P1-2_WP-500-DRT17_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.35 | 147.55 | AC1-221 | AP_P1-2_PE-500-001_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.85 | 147.51 | AC1-221 | PECO_P4_COOPR125_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.3 | 147.48 | AC1-221 | AP_P2-3_PE-500-018C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2901 | 144.83 | 146.96 | AE2-206 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.97 | 144.26 | AC1-221 | PECO_P4_PEACH025_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.84 | 144.16 | AC1-221 | PECO_P1-2_PBTIE1_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 139.21 | 133.27 | AC1-221 | PECO_P4_PEACH205_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 139.1 | 132.94 | AC1-221 | PECO_P1-2_PBTIE2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 138.15 | 132.06 | AC1-221 | PECO_P4_PEACH055_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 133.48 | 127.65 | AC1-221 | PECO_P4_PEACH015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 132.15 | 126.32 | AC1-221 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 127.23 | 125.53 | AC1-221 | DVP_P4-2: 51482_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 127.23 | 125.44 | AC1-221 | AP_P1-2_PE-500-407T_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 127.23 | 125.44 | AC1-221 | DVP_P1-2: LN 514_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 123.05 | 117.68 | AC1-221 | PECO_P4_PEACH225_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2901 | 144.75 | 146.87 | AE2-217 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 153.76 | 158.26 | AC1-222 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.25 | 157.37 | AC1-222 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.25 | 157.37 | AC1-222 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 152.07 | 156.93 | AC1-222 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 161.75 | 154.52 | AC1-222 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 148.71 | 153.28 | AC1-222 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 155.82 | 150.67 | AC1-222 | PN_P1-2_PN-500-010T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.54 | 149.66 | AC1-222 | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.47 | 149.59 | AC1-222 | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.17 | 148.42 | AC1-222 | AP_P2-3_PE-500-016_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.23 | 148.39 | AC1-222 | AP_P2-3_PE-500-015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.13 | 148 | AC1-222 | PJM_500_BG_P4_5_CNSTN_L_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.42 | 147.98 | AC1-222 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.22 | 147.8 | AC1-222 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.25 | 147.78 | AC1-222 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.98 | 147.59 | AC1-222 | PECO_P4_NOTTI85_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.92 | 147.57 | AC1-222 | PECO_P1-2_220-08_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.34 | 147.54 | AC1-222 | AP_P1-2_WP-500-DRT17_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.34 | 147.54 | AC1-222 | AP_P1-2_PE-500-001_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.85 | 147.51 | AC1-222 | PECO_P4_COOPR125_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.29 | 147.47 | AC1-222 | AP_P2-3_PE-500-018C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2901 | 144.74 | 146.86 | AE2-218 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.97 | 144.26 | AC1-222 | PECO_P4_PEACH025_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.83 | 144.16 | AC1-222 | PECO_P1-2_PBTIE1_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 139.21 | 133.26 | AC1-222 | PECO_P4_PEACH205_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 139.1 | 132.94 | AC1-222 | PECO_P1-2_PBTIE2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 138.15 | 132.06 | AC1-222 | PECO_P4_PEACH055_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 133.47 | 127.65 | AC1-222 | PECO_P4_PEACH015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 128.96 | 127.23 | AC1-222 | DVP_P4-2: 514T595_SRT-SW |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 132.14 | 126.32 | AC1-222 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 127.22 | 125.51 | AC1-222 | DVP_P4-2: 51482_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 127.22 | 125.42 | AC1-222 | DVP_P1-2: LN 514_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 127.22 | 125.42 | AC1-222 | AP_P1-2_PE-500-407T_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 123.05 | 117.67 | AC1-222 | PECO_P4_PEACH225_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 117.41 | 115.5 | AC1-222 | AP_P2-3_PE-500-019C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 225.39 | 236.66 | AC2-012 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 223.39 | 236.66 | AC2-012 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 225.33 | 236.62 | AC2-012 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 223.33 | 236.62 | AC2-012 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 225.33 | 236.61 | AC2-012 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 223.33 | 236.61 | AC2-012 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 213.35 | 226.51 | AC2-012 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 213.29 | 226.47 | AC2-012 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 213.28 | 226.47 | AC2-012 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 209.09 | 223.3 | AC2-012 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 209.03 | 223.25 | AC2-012 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 209.03 | 223.25 | AC2-012 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 210.49 | 217.54 | AC2-012 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 208.49 | 217.53 | AC2-012 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 198.96 | 207.97 | AC2-012 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 194.7 | 204.63 | AC2-012 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 172.6 | 167.62 | AC2-012 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 171.64 | 166.18 | AC2-012 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 171.64 | 166.18 | AC2-012 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 171.62 | 166.17 | AC2-012 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 163.47 | 164.7 | AC2-012 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2901 | 144.52 | 146.61 | AE2-221 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 161.6 | 161.62 | AC2-012 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 161.6 | 161.62 | AC2-012 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 161.59 | 161.62 | AC2-012 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 163.69 | 158.71 | AC2-012 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 153.38 | 157.81 | AC2-012 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 161.89 | 157.01 | AC2-012 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 161.89 | 157.01 | AC2-012 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 151.7 | 156.49 | AC2-012 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 161.35 | 154.13 | AC2-012 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 148.34 | 152.83 | AC2-012 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 903 | 144.13 | 151.93 | AC2-012 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 152.66 | 151.01 | AC2-012 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 155.47 | 150.32 | AC2-012 | PN_P1-2_PN-500-010T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 903 | 142.6 | 149.32 | AC2-012 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 903 | 142.6 | 149.32 | AC2-012 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 903 | 142.58 | 149.3 | AC2-012 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.19 | 149.24 | AC2-012 | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.12 | 149.16 | AC2-012 | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.8 | 147.97 | AC2-012 | AP_P2-3_PE-500-016_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.87 | 147.94 | AC2-012 | AP_P2-3_PE-500-015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.79 | 147.66 | AC2-012 | PJM_500_BG_P4_5_CNSTN_L_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.07 | 147.64 | AC2-012 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.87 | 147.45 | AC2-012 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.89 | 147.44 | AC2-012 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.62 | 147.24 | AC2-012 | PECO_P4_NOTTI85_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.56 | 147.23 | AC2-012 | PECO_P1-2_220-08_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.5 | 147.16 | AC2-012 | PECO_P4_COOPR125_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 142.98 | 147.1 | AC2-012 | AP_P1-2_PE-500-001_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 142.98 | 147.1 | AC2-012 | AP_P1-2_WP-500-DRT17_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 142.93 | 147.03 | AC2-012 | AP_P2-3_PE-500-018C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2901 | 144.6 | 146.7 | AE2-230 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.58 | 143.88 | AC2-012 | PECO_P4_PEACH025_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.41 | 143.76 | AC2-012 | PECO_P1-2_PBTIE1_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 911 | 148.85 | 142.98 | AC2-012 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 911 | 147.91 | 141.66 | AC2-012 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 911 | 147.91 | 141.66 | AC2-012 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 911 | 147.89 | 141.66 | AC2-012 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204502 | 27JACKSON | 204514 | 27TMI | 1 | 230 | 227 | 781 | 132.95 | 141.45 | AC2-012 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204502 | 27JACKSON | 204514 | 27TMI | 1 | 230 | 227 | 781 | 132.95 | 141.45 | AC2-012 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204502 | 27JACKSON | 204514 | 27TMI | 1 | 230 | 227 | 781 | 132.94 | 141.43 | AC2-012 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 903 | 135.52 | 139.46 | AC2-012 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 1031 | 130.73 | 139 | AC2-012 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 1031 | 130.24 | 137.94 | AC2-012 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 1031 | 130.24 | 137.94 | AC2-012 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 1031 | 130.23 | 137.92 | AC2-012 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 911 | 140.04 | 134.93 | AC2-012 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 138.82 | 132.9 | AC2-012 | PECO_P4_PEACH205_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 138.71 | 132.57 | AC2-012 | PECO_P1-2_PBTIE2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208078 | SAKR | 1 | 230 | 229 | 903 | 124.4 | 132.35 | AC2-012 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208078 | SAKR | 1 | 230 | 229 | 903 | 124.4 | 132.35 | AC2-012 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208078 | SAKR | 1 | 230 | 229 | 903 | 124.39 | 132.34 | AC2-012 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 137.79 | 131.71 | AC2-012 | PECO_P4_PEACH055_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204502 | 27JACKSON | 204514 | 27TMI | 1 | 230 | 227 | 781 | 125.31 | 130.88 | AC2-012 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 1031 | 124.64 | 129.14 | AC2-012 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 133.06 | 127.25 | AC2-012 | PECO_P4_PEACH015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 128.22 | 126.5 | AC2-012 | DVP_P4-2: 514T595_SRT-SW |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 131.76 | 125.96 | AC2-012 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220953 | HOWARD12 | 220972 | GRANITE1 | 1 | 230 | 232 | 772 | 129.52 | 125.54 | AC2-012 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220954 | HOWARD32 | 220973 | GRANITE6 | 1 | 230 | 232 | 772 | 128.38 | 124.85 | AC2-012 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 126.46 | 124.71 | AC2-012 | DVP_P4-2: 51482_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 793 | 126.43 | 124.68 | AC2-012 | DVP_P4-2: 514T595_SRT-SW |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 2 | 230 | 233 | 793 | 126.43 | 124.68 | AC2-012 | DVP_P4-2: 514T595_SRT-SW |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 126.46 | 124.62 | AC2-012 | DVP_P1-2: LN 514_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 126.46 | 124.62 | AC2-012 | AP_P1-2_PE-500-407T_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220953 | HOWARD12 | 220972 | GRANITE1 | 1 | 230 | 232 | 772 | 128.61 | 124.57 | AC2-012 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220953 | HOWARD12 | 220972 | GRANITE1 | 1 | 230 | 232 | 772 | 128.61 | 124.57 | AC2-012 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208020 | MANO TR3 | 1 | 230 | 229 | 793 | 111.39 | 124.52 | AC2-012 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208020 | MANO TR3 | 1 | 230 | 229 | 793 | 111.39 | 124.52 | AC2-012 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208020 | MANO TR3 | 1 | 230 | 229 | 793 | 111.38 | 124.52 | AC2-012 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 793 | 125.18 | 123.42 | AC2-012 | DVP_P4-2: 51482_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 2 | 230 | 233 | 793 | 125.18 | 123.42 | AC2-012 | DVP_P4-2: 51482_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 793 | 125.18 | 123.34 | AC2-012 | AP_P1-2_PE-500-407T_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 793 | 125.18 | 123.34 | AC2-012 | DVP_P1-2: LN 514_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 2 | 230 | 233 | 793 | 125.18 | 123.34 | AC2-012 | DVP_P1-2: LN 514_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 2 | 230 | 233 | 793 | 125.18 | 123.34 | AC2-012 | AP_P1-2_PE-500-407T_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208078 | SAKR | 1 | 230 | 229 | 903 | 117.13 | 122.37 | AC2-012 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200025 | W CHAPEL | 1 | 500 | 225 | 1732 | 123.53 | 121.75 | AC2-012 | PEPCO_P4_PP41_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208031 | MLWD TR2 | 1 | 230 | 229 | 911 | 111.7 | 121.1 | AC2-012 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208031 | MLWD TR2 | 1 | 230 | 229 | 911 | 111.7 | 121.09 | AC2-012 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208031 | MLWD TR2 | 1 | 230 | 229 | 911 | 111.69 | 121.09 | AC2-012 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220965 | NEAST339 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 119.69 | 119.04 | AC2-012 | BG_P1_2315_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220965 | NEAST339 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 119.27 | 118.83 | AC2-012 | BG_P4_5_NEAST_17_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220965 | NEAST339 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 119.43 | 118.83 | AC2-012 | BG_P4_5_NEAST_15_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 114.64 | 118.32 | AC2-012 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220979 | NEAST317 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 118.77 | 118.17 | AC2-012 | BG_P1_2337_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 114.3 | 117.99 | AC2-012 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 114.28 | 117.92 | AC2-012 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 114.28 | 117.92 | AC2-012 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220979 | NEAST317 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 118.44 | 117.9 | AC2-012 | BG_P4_5_NEAST_39_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220979 | NEAST317 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 118.44 | 117.9 | AC2-012 | BG_P4_5_NEAST_37_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 113.95 | 117.59 | AC2-012 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 113.95 | 117.59 | AC2-012 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 122.67 | 117.31 | AC2-012 | PECO_P4_PEACH225_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 2 | 230 | 233 | 793 | 118.52 | 115.74 | AC2-012 | PEPCO_P1_PP1_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 793 | 118.52 | 115.74 | AC2-012 | PEPCO_P1_PP2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 2 | 500/230 | 225/232 | 2168 | 109.6 | 114.9 | AC2-012 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 116.67 | 114.72 | AC2-012 | AP_P2-3_PE-500-019C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 2 | 500/230 | 225/232 | 2168 | 109.42 | 114.68 | AC2-012 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 2 | 500/230 | 225/232 | 2168 | 109.42 | 114.68 | AC2-012 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 1 | 500/230 | 225/232 | 2168 | 109.37 | 114.65 | AC2-012 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 1 | 500/230 | 225/232 | 2168 | 109.19 | 114.44 | AC2-012 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 1 | 500/230 | 225/232 | 2168 | 109.19 | 114.44 | AC2-012 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220964 | GRACETON | 220999 | BAGLEY2 | 13 | 230 | 232 | 1795 | 113.37 | 114.41 | AC2-012 | BG_P4_5_GRCTN_3T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208020 | MANO TR3 | 1 | 230 | 229 | 793 | 104.2 | 113.95 | AC2-012 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208020 | MANO TR3 | 208031 | MLWD TR2 | 1 | 230 | 229 | 903 | 102.52 | 113.64 | AC2-012 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208020 | MANO TR3 | 208031 | MLWD TR2 | 1 | 230 | 229 | 903 | 101.81 | 112.46 | AC2-012 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208020 | MANO TR3 | 208031 | MLWD TR2 | 1 | 230 | 229 | 903 | 101.81 | 112.46 | AC2-012 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208020 | MANO TR3 | 208031 | MLWD TR2 | 1 | 230 | 229 | 903 | 101.81 | 112.45 | AC2-012 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 2 | 500/230 | 225/232 | 2168 | 108.46 | 111.76 | AC2-012 | PJM_500_BG_P4_5_CNSTN_15_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208031 | MLWD TR2 | 1 | 230 | 229 | 911 | 104.94 | 111.6 | AC2-012 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 106.42 | 111.18 | AC2-012 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220980 | RAPHAEL | 220999 | BAGLEY2 | 13 | 230 | 232 | 1795 | 108.96 | 111.16 | AC2-012 | BG_P4_5_GRCTN_3T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 106.29 | 111.05 | AC2-012 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 793 | 112.65 | 109.99 | AC2-012 | PEPCO_P4_PP19_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 793 | 109.41 | 107.48 | AC2-012 | AP_P2-3_PE-500-019C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 2 | 230 | 233 | 793 | 109.41 | 107.48 | AC2-012 | AP_P2-3_PE-500-019C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220965 | NEAST339 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 108.25 | 106.82 | AC2-012 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220965 | NEAST339 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 108.15 | 106.71 | AC2-012 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220965 | NEAST339 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 108.15 | 106.71 | AC2-012 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 101.54 | 105.7 | AC2-012 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 101.45 | 105.61 | AC2-012 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220979 | NEAST317 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 105.14 | 103.77 | AC2-012 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220979 | NEAST317 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 105.04 | 103.66 | AC2-012 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220979 | NEAST317 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 105.04 | 103.66 | AC2-012 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 99.45 | 103.32 | AC2-012 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 99.45 | 103.32 | AC2-012 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 99.44 | 103.32 | AC2-012 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208020 | MANO TR3 | 208031 | MLWD TR2 | 1 | 230 | 229 | 903 | 95.44 | 103.23 | AC2-012 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220964 | GRACETON | 221000 | BAGLEY | 5 | 230 | 232 | 1795 | 101.43 | 102.18 | AC2-012 | BG_P1_2313_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220964 | GRACETON | 220999 | BAGLEY2 | 13 | 230 | 232 | 1795 | 101.43 | 102.18 | AC2-012 | BG_P1_2305_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220965 | NEAST339 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 102.68 | 102 | AC2-012 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 98.52 | 101.99 | AC2-012 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 98.62 | 100.63 | AC2-012 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 225.9 | 240.28 | AC2-023 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 227.93 | 240.27 | AC2-023 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 215.77 | 230.01 | AC2-023 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 211.5 | 226.82 | AC2-023 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 212.09 | 219.66 | AC2-023 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 210.06 | 219.66 | AC2-023 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 200.47 | 210.04 | AC2-023 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 196.21 | 206.71 | AC2-023 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2901 | 144.7 | 146.81 | AE2-253 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 154.26 | 158.85 | AC2-023 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.81 | 157.93 | AC2-023 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.81 | 157.93 | AC2-023 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 152.57 | 157.53 | AC2-023 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 162.5 | 155.25 | AC2-023 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 149.21 | 153.88 | AC2-023 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 156.38 | 151.23 | AC2-023 | PN_P1-2_PN-500-010T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 147.03 | 150.23 | AC2-023 | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.95 | 150.16 | AC2-023 | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.62 | 148.96 | AC2-023 | AP_P2-3_PE-500-016_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.68 | 148.93 | AC2-023 | AP_P2-3_PE-500-015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 154.07 | 148.62 | AC2-023 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.67 | 148.53 | AC2-023 | PJM_500_BG_P4_5_CNSTN_L_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.87 | 148.43 | AC2-023 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.89 | 148.42 | AC2-023 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.62 | 148.22 | AC2-023 | PECO_P4_NOTTI85_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.56 | 148.21 | AC2-023 | PECO_P1-2_220-08_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.5 | 148.14 | AC2-023 | PECO_P4_COOPR125_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.79 | 148.08 | AC2-023 | AP_P1-2_WP-500-DRT17_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.79 | 148.08 | AC2-023 | AP_P1-2_PE-500-001_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.75 | 148.01 | AC2-023 | AP_P2-3_PE-500-018C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2901 | 144.79 | 146.92 | AE2-297 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 151.85 | 145.1 | AC2-023 | PECO_P4_PEACH025_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 151.65 | 144.94 | AC2-023 | PECO_P1-2_PBTIE1_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 139.82 | 133.86 | AC2-023 | PECO_P4_PEACH205_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 139.85 | 133.66 | AC2-023 | PECO_P1-2_PBTIE2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 138.88 | 132.76 | AC2-023 | PECO_P4_PEACH055_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 134.28 | 128.43 | AC2-023 | PECO_P4_PEACH015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 132.88 | 127.02 | AC2-023 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 123.79 | 118.39 | AC2-023 | PECO_P4_PEACH225_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 209.42 | 223.94 | AC2-059 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2901 | 144.9 | 147.04 | AE2-318 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 153.71 | 158.2 | AC2-059 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.16 | 157.29 | AC2-059 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.16 | 157.29 | AC2-059 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 152.02 | 156.88 | AC2-059 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 161.6 | 154.39 | AC2-059 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 148.66 | 153.22 | AC2-059 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 155.74 | 150.59 | AC2-059 | PN_P1-2_PN-500-010T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.49 | 149.6 | AC2-059 | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.42 | 149.53 | AC2-059 | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.14 | 148.42 | AC2-059 | AP_P2-3_PE-500-016_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.21 | 148.39 | AC2-059 | AP_P2-3_PE-500-015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.05 | 147.92 | AC2-059 | PJM_500_BG_P4_5_CNSTN_L_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.29 | 147.85 | AC2-059 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.09 | 147.67 | AC2-059 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.11 | 147.65 | AC2-059 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.32 | 147.53 | AC2-059 | AP_P1-2_PE-500-001_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.32 | 147.53 | AC2-059 | AP_P1-2_WP-500-DRT17_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.27 | 147.46 | AC2-059 | AP_P2-3_PE-500-018C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.84 | 147.46 | AC2-059 | PECO_P4_NOTTI85_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.78 | 147.44 | AC2-059 | PECO_P1-2_220-08_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.72 | 147.38 | AC2-059 | PECO_P4_COOPR125_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2901 | 144.9 | 147.05 | AE2-319 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.8 | 144.09 | AC2-059 | PECO_P4_PEACH025_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.69 | 144.02 | AC2-059 | PECO_P1-2_PBTIE1_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 139.09 | 133.15 | AC2-059 | PECO_P4_PEACH205_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 138.96 | 132.81 | AC2-059 | PECO_P1-2_PBTIE2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 138.03 | 131.94 | AC2-059 | PECO_P4_PEACH055_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 133.34 | 127.52 | AC2-059 | PECO_P4_PEACH015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 132.02 | 126.2 | AC2-059 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 122.92 | 117.56 | AC2-059 | PECO_P4_PEACH225_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2901 | 144.69 | 146.8 | AE2-333 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 153.74 | 158.24 | AC2-060 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.21 | 157.33 | AC2-060 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.2 | 157.33 | AC2-060 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 152.06 | 156.92 | AC2-060 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 161.66 | 154.44 | AC2-060 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 148.69 | 153.27 | AC2-060 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 155.78 | 150.63 | AC2-060 | PN_P1-2_PN-500-010T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.53 | 149.65 | AC2-060 | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.46 | 149.57 | AC2-060 | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.17 | 148.45 | AC2-060 | AP_P2-3_PE-500-016_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.24 | 148.42 | AC2-060 | AP_P2-3_PE-500-015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.09 | 147.96 | AC2-060 | PJM_500_BG_P4_5_CNSTN_L_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.34 | 147.91 | AC2-060 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.14 | 147.72 | AC2-060 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.17 | 147.71 | AC2-060 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.35 | 147.57 | AC2-060 | AP_P1-2_WP-500-DRT17_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.35 | 147.57 | AC2-060 | AP_P1-2_PE-500-001_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.9 | 147.51 | AC2-060 | PECO_P4_NOTTI85_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.3 | 147.5 | AC2-060 | AP_P2-3_PE-500-018C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.83 | 147.49 | AC2-060 | PECO_P1-2_220-08_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.77 | 147.43 | AC2-060 | PECO_P4_COOPR125_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2901 | 145.31 | 147.53 | AE2-334 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.86 | 144.15 | AC2-060 | PECO_P4_PEACH025_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.75 | 144.08 | AC2-060 | PECO_P1-2_PBTIE1_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 139.14 | 133.2 | AC2-060 | PECO_P4_PEACH205_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 139.02 | 132.86 | AC2-060 | PECO_P1-2_PBTIE2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 138.08 | 131.99 | AC2-060 | PECO_P4_PEACH055_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 133.4 | 127.58 | AC2-060 | PECO_P4_PEACH015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 132.07 | 126.25 | AC2-060 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 122.98 | 117.61 | AC2-060 | PECO_P4_PEACH225_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2901 | 144.93 | 147.09 | AE2-343 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 153.75 | 158.24 | AC2-061 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.21 | 157.34 | AC2-061 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.21 | 157.33 | AC2-061 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 152.06 | 156.92 | AC2-061 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 161.67 | 154.45 | AC2-061 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 148.7 | 153.27 | AC2-061 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 155.78 | 150.63 | AC2-061 | PN_P1-2_PN-500-010T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.53 | 149.65 | AC2-061 | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.46 | 149.57 | AC2-061 | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.17 | 148.45 | AC2-061 | AP_P2-3_PE-500-016_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.24 | 148.42 | AC2-061 | AP_P2-3_PE-500-015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.09 | 147.97 | AC2-061 | PJM_500_BG_P4_5_CNSTN_L_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.34 | 147.91 | AC2-061 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.14 | 147.72 | AC2-061 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.17 | 147.71 | AC2-061 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.35 | 147.57 | AC2-061 | AP_P1-2_WP-500-DRT17_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.35 | 147.57 | AC2-061 | AP_P1-2_PE-500-001_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.9 | 147.51 | AC2-061 | PECO_P4_NOTTI85_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.84 | 147.5 | AC2-061 | PECO_P1-2_220-08_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.3 | 147.5 | AC2-061 | AP_P2-3_PE-500-018C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.77 | 147.43 | AC2-061 | PECO_P4_COOPR125_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2901 | 144.89 | 147.04 | AF1-042 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.87 | 144.16 | AC2-061 | PECO_P4_PEACH025_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.75 | 144.08 | AC2-061 | PECO_P1-2_PBTIE1_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 139.14 | 133.2 | AC2-061 | PECO_P4_PEACH205_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 139.02 | 132.87 | AC2-061 | PECO_P1-2_PBTIE2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 138.08 | 131.99 | AC2-061 | PECO_P4_PEACH055_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 133.4 | 127.58 | AC2-061 | PECO_P4_PEACH015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 132.08 | 126.25 | AC2-061 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 122.98 | 117.61 | AC2-061 | PECO_P4_PEACH225_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2901 | 144.6 | 146.69 | AF1-147 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.5 | 148.07 | AC2-067 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.3 | 147.88 | AC2-067 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.33 | 147.86 | AC2-067 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.06 | 147.67 | AC2-067 | PECO_P4_NOTTI85_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153 | 147.65 | AC2-067 | PECO_P1-2_220-08_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.93 | 147.59 | AC2-067 | PECO_P4_COOPR125_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.59 | 147.4 | AC2-067 | PECO_P1-2_220-93_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 148.47 | 143.24 | AC2-067 | AP_P2-2_WP-500-DRT16_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 148.47 | 143.24 | AC2-067 | AP_P2-3_WP-500-465_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 148.47 | 143.24 | AC2-067 | AP_P2-3_WP-500-DRT20_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 225.78 | 237.29 | AC2-079 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 223.77 | 237.28 | AC2-079 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 213.71 | 227.12 | AC2-079 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 213.65 | 227.06 | AC2-079 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 213.65 | 227.06 | AC2-079 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 209.45 | 223.91 | AC2-079 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 209.39 | 223.85 | AC2-079 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 209.39 | 223.85 | AC2-079 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2901 | 144.93 | 147.08 | AF1-173 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 153.65 | 158.12 | AC2-079 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.14 | 157.26 | AC2-079 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.14 | 157.26 | AC2-079 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 151.96 | 156.8 | AC2-079 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 161.64 | 154.41 | AC2-079 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 148.6 | 153.14 | AC2-079 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 155.72 | 150.56 | AC2-079 | PN_P1-2_PN-500-010T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.44 | 149.53 | AC2-079 | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.37 | 149.46 | AC2-079 | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.05 | 148.28 | AC2-079 | AP_P2-3_PE-500-016_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.12 | 148.25 | AC2-079 | AP_P2-3_PE-500-015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.03 | 147.9 | AC2-079 | PJM_500_BG_P4_5_CNSTN_L_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.32 | 147.88 | AC2-079 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.12 | 147.7 | AC2-079 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.15 | 147.68 | AC2-079 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.88 | 147.49 | AC2-079 | PECO_P4_NOTTI85_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.82 | 147.47 | AC2-079 | PECO_P1-2_220-08_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.75 | 147.41 | AC2-079 | PECO_P4_COOPR125_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.23 | 147.4 | AC2-079 | AP_P1-2_PE-500-001_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.23 | 147.4 | AC2-079 | AP_P1-2_WP-500-DRT17_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.18 | 147.33 | AC2-079 | AP_P2-3_PE-500-018C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2901 | 144.43 | 146.51 | AF1-227 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.86 | 144.15 | AC2-079 | PECO_P4_PEACH025_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.71 | 144.04 | AC2-079 | PECO_P1-2_PBTIE1_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 139.09 | 133.16 | AC2-079 | PECO_P4_PEACH205_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 138.98 | 132.83 | AC2-079 | PECO_P1-2_PBTIE2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 138.05 | 131.96 | AC2-079 | PECO_P4_PEACH055_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 133.36 | 127.54 | AC2-079 | PECO_P4_PEACH015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 128.7 | 127.01 | AC2-079 | DVP_P4-2: 514T595_SRT-SW |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 132.04 | 126.21 | AC2-079 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 126.95 | 125.24 | AC2-079 | DVP_P4-2: 51482_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 126.95 | 125.14 | AC2-079 | AP_P1-2_PE-500-407T_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 126.95 | 125.14 | AC2-079 | DVP_P1-2: LN 514_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200025 | W CHAPEL | 1 | 500 | 225 | 1732 | 123.77 | 121.99 | AC2-079 | PEPCO_P4_PP41_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 122.94 | 117.57 | AC2-079 | PECO_P4_PEACH225_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 117.15 | 115.23 | AC2-079 | AP_P2-3_PE-500-019C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 99.57 | 103.53 | AC2-079 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 99.57 | 103.53 | AC2-079 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 99.57 | 103.53 | AC2-079 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 98.74 | 100.82 | AC2-079 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2901 | 145.32 | 147.54 | AF2-144 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 153.76 | 158.25 | AC2-084 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.25 | 157.37 | AC2-084 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.24 | 157.37 | AC2-084 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 152.07 | 156.93 | AC2-084 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 161.75 | 154.53 | AC2-084 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 148.71 | 153.28 | AC2-084 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 155.82 | 150.67 | AC2-084 | PN_P1-2_PN-500-010T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.54 | 149.65 | AC2-084 | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.47 | 149.58 | AC2-084 | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.16 | 148.41 | AC2-084 | AP_P2-3_PE-500-016_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.22 | 148.38 | AC2-084 | AP_P2-3_PE-500-015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.13 | 148 | AC2-084 | PJM_500_BG_P4_5_CNSTN_L_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.42 | 147.98 | AC2-084 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.22 | 147.8 | AC2-084 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.25 | 147.78 | AC2-084 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.98 | 147.59 | AC2-084 | PECO_P4_NOTTI85_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.92 | 147.57 | AC2-084 | PECO_P1-2_220-08_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.34 | 147.53 | AC2-084 | AP_P1-2_WP-500-DRT17_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.34 | 147.53 | AC2-084 | AP_P1-2_PE-500-001_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.85 | 147.51 | AC2-084 | PECO_P4_COOPR125_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.29 | 147.46 | AC2-084 | AP_P2-3_PE-500-018C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2901 | 144.9 | 147.05 | AG1-086 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.97 | 144.26 | AC2-084 | PECO_P4_PEACH025_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.83 | 144.16 | AC2-084 | PECO_P1-2_PBTIE1_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 139.21 | 133.26 | AC2-084 | PECO_P4_PEACH205_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 139.1 | 132.94 | AC2-084 | PECO_P1-2_PBTIE2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 138.15 | 132.06 | AC2-084 | PECO_P4_PEACH055_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 133.47 | 127.65 | AC2-084 | PECO_P4_PEACH015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 128.92 | 127.19 | AC2-084 | DVP_P4-2: 514T595_SRT-SW |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 132.15 | 126.32 | AC2-084 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 127.18 | 125.48 | AC2-084 | DVP_P4-2: 51482_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 127.18 | 125.38 | AC2-084 | AP_P1-2_PE-500-407T_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 127.18 | 125.38 | AC2-084 | DVP_P1-2: LN 514_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 123.05 | 117.67 | AC2-084 | PECO_P4_PEACH225_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 117.37 | 115.46 | AC2-084 | AP_P2-3_PE-500-019C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2901 | 144.65 | 146.76 | AG1-397 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.29 | 157.42 | AC2-088 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.29 | 157.42 | AC2-088 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 161.78 | 154.55 | AC2-088 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 155.87 | 150.71 | AC2-088 | PN_P1-2_PN-500-010T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.18 | 148.05 | AC2-088 | PJM_500_BG_P4_5_CNSTN_L_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.44 | 148.01 | AC2-088 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.24 | 147.82 | AC2-088 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.27 | 147.81 | AC2-088 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153 | 147.61 | AC2-088 | PECO_P4_NOTTI85_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.94 | 147.6 | AC2-088 | PECO_P1-2_220-08_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.87 | 147.53 | AC2-088 | PECO_P4_COOPR125_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2901 | 150.95 | 154.15 | AG2-055 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.99 | 144.27 | AC2-088 | PECO_P4_PEACH025_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.87 | 144.19 | AC2-088 | PECO_P1-2_PBTIE1_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 138.97 | 141.27 | AC2-088 | AP_P2-2_WP-500-DRT16_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 138.97 | 141.27 | AC2-088 | AP_P2-3_WP-500-465_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 138.97 | 141.27 | AC2-088 | AP_P2-3_WP-500-DRT20_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 138.97 | 141.27 | AC2-088 | AP_P1-2_WP-500-DRT21_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 138.97 | 141.27 | AC2-088 | AP_P1-2_WP-500-005A_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 138.74 | 140.9 | AC2-088 | AP_P1-2_WP-500-008_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 138.74 | 140.9 | AC2-088 | AP_P2-3_WP-500-DRT45_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 137.14 | 139.13 | AC2-088 | AP_P2-3_WP-500-696_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 137.14 | 139.13 | AC2-088 | AP_P2-3_WP-500-707T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 137.16 | 139.12 | AC2-088 | AP_P2-3_WP-500-706T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 139.24 | 133.3 | AC2-088 | PECO_P4_PEACH205_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 139.13 | 132.97 | AC2-088 | PECO_P1-2_PBTIE2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 138.18 | 132.09 | AC2-088 | PECO_P4_PEACH055_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 133.51 | 127.69 | AC2-088 | PECO_P4_PEACH015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 132.18 | 126.35 | AC2-088 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 123.08 | 117.71 | AC2-088 | PECO_P4_PEACH225_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2901 | 145.29 | 147.5 | ALDENE_AB | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 153.78 | 158.28 | AC2-100 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.26 | 157.39 | AC2-100 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.26 | 157.39 | AC2-100 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 152.09 | 156.95 | AC2-100 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 161.77 | 154.54 | AC2-100 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 148.73 | 153.3 | AC2-100 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 155.84 | 150.68 | AC2-100 | PN_P1-2_PN-500-010T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.56 | 149.68 | AC2-100 | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.49 | 149.61 | AC2-100 | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.18 | 148.44 | AC2-100 | AP_P2-3_PE-500-016_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.25 | 148.42 | AC2-100 | AP_P2-3_PE-500-015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.15 | 148.02 | AC2-100 | PJM_500_BG_P4_5_CNSTN_L_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.44 | 148 | AC2-100 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.24 | 147.81 | AC2-100 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.26 | 147.8 | AC2-100 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.99 | 147.6 | AC2-100 | PECO_P4_NOTTI85_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.93 | 147.59 | AC2-100 | PECO_P1-2_220-08_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.36 | 147.56 | AC2-100 | AP_P1-2_WP-500-DRT17_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.36 | 147.56 | AC2-100 | AP_P1-2_PE-500-001_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.86 | 147.52 | AC2-100 | PECO_P4_COOPR125_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.31 | 147.49 | AC2-100 | AP_P2-3_PE-500-018C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2901 | 144.8 | 146.93 | BIGSKY | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.99 | 144.27 | AC2-100 | PECO_P4_PEACH025_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.85 | 144.18 | AC2-100 | PECO_P1-2_PBTIE1_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 139.22 | 133.28 | AC2-100 | PECO_P4_PEACH205_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 139.11 | 132.96 | AC2-100 | PECO_P1-2_PBTIE2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 138.17 | 132.08 | AC2-100 | PECO_P4_PEACH055_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 133.49 | 127.67 | AC2-100 | PECO_P4_PEACH015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 132.16 | 126.34 | AC2-100 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 123.06 | 117.69 | AC2-100 | PECO_P4_PEACH225_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2901 | 144.85 | 146.98 | BISHOP | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 153.74 | 158.24 | AC2-103 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.18 | 157.31 | AC2-103 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.18 | 157.31 | AC2-103 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 152.05 | 156.92 | AC2-103 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 161.6 | 154.38 | AC2-103 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 148.69 | 153.27 | AC2-103 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 155.75 | 150.61 | AC2-103 | PN_P1-2_PN-500-010T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.53 | 149.64 | AC2-103 | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.46 | 149.57 | AC2-103 | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.18 | 148.47 | AC2-103 | AP_P2-3_PE-500-016_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.25 | 148.44 | AC2-103 | AP_P2-3_PE-500-015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.06 | 147.94 | AC2-103 | PJM_500_BG_P4_5_CNSTN_L_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.28 | 147.84 | AC2-103 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.08 | 147.66 | AC2-103 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.1 | 147.64 | AC2-103 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.36 | 147.58 | AC2-103 | AP_P1-2_WP-500-DRT17_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.36 | 147.58 | AC2-103 | AP_P1-2_PE-500-001_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.31 | 147.51 | AC2-103 | AP_P2-3_PE-500-018C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.83 | 147.45 | AC2-103 | PECO_P4_NOTTI85_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.77 | 147.43 | AC2-103 | PECO_P1-2_220-08_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.71 | 147.37 | AC2-103 | PECO_P4_COOPR125_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2901 | 144.91 | 147.05 | CAMPGROVE;RU | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.77 | 144.06 | AC2-103 | PECO_P4_PEACH025_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.68 | 144.01 | AC2-103 | PECO_P1-2_PBTIE1_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 139.09 | 133.15 | AC2-103 | PECO_P4_PEACH205_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 138.96 | 132.81 | AC2-103 | PECO_P1-2_PBTIE2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 138.02 | 131.94 | AC2-103 | PECO_P4_PEACH055_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 133.34 | 127.52 | AC2-103 | PECO_P4_PEACH015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 132.02 | 126.2 | AC2-103 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 122.92 | 117.55 | AC2-103 | PECO_P4_PEACH225_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2901 | 144.73 | 146.85 | CAYUGA | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.29 | 157.42 | AC2-111 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.29 | 157.42 | AC2-111 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 161.78 | 154.55 | AC2-111 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 155.87 | 150.71 | AC2-111 | PN_P1-2_PN-500-010T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.17 | 148.05 | AC2-111 | PJM_500_BG_P4_5_CNSTN_L_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.44 | 148.01 | AC2-111 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.24 | 147.82 | AC2-111 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.27 | 147.81 | AC2-111 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153 | 147.61 | AC2-111 | PECO_P4_NOTTI85_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.94 | 147.59 | AC2-111 | PECO_P1-2_220-08_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.87 | 147.53 | AC2-111 | PECO_P4_COOPR125_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2901 | 145.26 | 147.47 | D05 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.98 | 144.27 | AC2-111 | PECO_P4_PEACH025_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.87 | 144.19 | AC2-111 | PECO_P1-2_PBTIE1_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 138.97 | 141.27 | AC2-111 | AP_P2-3_WP-500-465_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 138.97 | 141.27 | AC2-111 | AP_P2-3_WP-500-DRT20_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 138.97 | 141.27 | AC2-111 | AP_P1-2_WP-500-DRT21_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 138.97 | 141.27 | AC2-111 | AP_P1-2_WP-500-005A_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 138.97 | 141.27 | AC2-111 | AP_P2-2_WP-500-DRT16_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 138.74 | 140.9 | AC2-111 | AP_P2-3_WP-500-DRT45_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 138.74 | 140.9 | AC2-111 | AP_P1-2_WP-500-008_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 137.14 | 139.13 | AC2-111 | AP_P2-3_WP-500-696_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 137.14 | 139.13 | AC2-111 | AP_P2-3_WP-500-707T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 137.16 | 139.12 | AC2-111 | AP_P2-3_WP-500-706T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 139.24 | 133.3 | AC2-111 | PECO_P4_PEACH205_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 139.13 | 132.97 | AC2-111 | PECO_P1-2_PBTIE2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 138.18 | 132.09 | AC2-111 | PECO_P4_PEACH055_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 133.51 | 127.69 | AC2-111 | PECO_P4_PEACH015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 132.18 | 126.35 | AC2-111 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 123.08 | 117.7 | AC2-111 | PECO_P4_PEACH225_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 225.47 | 236.79 | AC2-112 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 223.47 | 236.79 | AC2-112 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 225.41 | 236.73 | AC2-112 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 223.41 | 236.73 | AC2-112 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 225.41 | 236.73 | AC2-112 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 223.41 | 236.73 | AC2-112 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 213.43 | 226.64 | AC2-112 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 213.36 | 226.58 | AC2-112 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 213.36 | 226.58 | AC2-112 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 209.17 | 223.43 | AC2-112 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 209.1 | 223.37 | AC2-112 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 209.1 | 223.37 | AC2-112 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 210.58 | 217.65 | AC2-112 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 208.57 | 217.65 | AC2-112 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 199.04 | 208.09 | AC2-112 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 194.78 | 204.74 | AC2-112 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 172.68 | 167.7 | AC2-112 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 171.72 | 166.26 | AC2-112 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 171.72 | 166.26 | AC2-112 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 171.7 | 166.25 | AC2-112 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 163.55 | 164.81 | AC2-112 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2901 | 145.25 | 147.45 | DC1 NUG | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 161.68 | 161.72 | AC2-112 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 161.68 | 161.72 | AC2-112 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 161.67 | 161.72 | AC2-112 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 163.77 | 158.8 | AC2-112 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 153.46 | 157.89 | AC2-112 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 161.95 | 157.07 | AC2-112 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 161.95 | 157.07 | AC2-112 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 151.77 | 156.57 | AC2-112 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 161.41 | 154.19 | AC2-112 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 148.41 | 152.92 | AC2-112 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 903 | 144.2 | 152.03 | AC2-112 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 152.74 | 151.1 | AC2-112 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 155.53 | 150.38 | AC2-112 | PN_P1-2_PN-500-010T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 903 | 142.67 | 149.41 | AC2-112 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 903 | 142.67 | 149.4 | AC2-112 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 903 | 142.65 | 149.4 | AC2-112 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.26 | 149.31 | AC2-112 | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.18 | 149.24 | AC2-112 | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.88 | 148.06 | AC2-112 | AP_P2-3_PE-500-016_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.95 | 148.04 | AC2-112 | AP_P2-3_PE-500-015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.85 | 147.72 | AC2-112 | PJM_500_BG_P4_5_CNSTN_L_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.12 | 147.68 | AC2-112 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.92 | 147.5 | AC2-112 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.94 | 147.48 | AC2-112 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.67 | 147.29 | AC2-112 | PECO_P4_NOTTI85_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.61 | 147.27 | AC2-112 | PECO_P1-2_220-08_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.55 | 147.21 | AC2-112 | PECO_P4_COOPR125_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.06 | 147.19 | AC2-112 | AP_P1-2_PE-500-001_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.06 | 147.19 | AC2-112 | AP_P1-2_WP-500-DRT17_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.01 | 147.12 | AC2-112 | AP_P2-3_PE-500-018C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2901 | 145.25 | 147.45 | DC2 NUG | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.63 | 143.92 | AC2-112 | PECO_P4_PEACH025_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.47 | 143.81 | AC2-112 | PECO_P1-2_PBTIE1_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 911 | 148.93 | 143.06 | AC2-112 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204502 | 27JACKSON | 204514 | 27TMI | 1 | 230 | 227 | 781 | 132.99 | 141.51 | AC2-112 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204502 | 27JACKSON | 204514 | 27TMI | 1 | 230 | 227 | 781 | 132.99 | 141.51 | AC2-112 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204502 | 27JACKSON | 204514 | 27TMI | 1 | 230 | 227 | 781 | 132.98 | 141.5 | AC2-112 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 903 | 135.59 | 139.55 | AC2-112 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 1031 | 130.29 | 138.01 | AC2-112 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 1031 | 130.29 | 138 | AC2-112 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 1031 | 130.28 | 138 | AC2-112 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 138.88 | 132.95 | AC2-112 | PECO_P4_PEACH205_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 138.77 | 132.62 | AC2-112 | PECO_P1-2_PBTIE2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208078 | SAKR | 1 | 230 | 229 | 903 | 124.46 | 132.42 | AC2-112 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208078 | SAKR | 1 | 230 | 229 | 903 | 124.45 | 132.42 | AC2-112 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208078 | SAKR | 1 | 230 | 229 | 903 | 124.45 | 132.42 | AC2-112 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 137.84 | 131.76 | AC2-112 | PECO_P4_PEACH055_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 1031 | 124.69 | 129.21 | AC2-112 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 133.13 | 127.31 | AC2-112 | PECO_P4_PEACH015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 128.6 | 126.86 | AC2-112 | DVP_P4-2: 514T595_SRT-SW |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 131.82 | 126.01 | AC2-112 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 126.85 | 125.14 | AC2-112 | DVP_P4-2: 51482_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 126.85 | 125.05 | AC2-112 | DVP_P1-2: LN 514_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 126.85 | 125.05 | AC2-112 | AP_P1-2_PE-500-407T_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208020 | MANO TR3 | 1 | 230 | 229 | 793 | 111.44 | 124.6 | AC2-112 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208020 | MANO TR3 | 1 | 230 | 229 | 793 | 111.44 | 124.59 | AC2-112 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208020 | MANO TR3 | 1 | 230 | 229 | 793 | 111.44 | 124.59 | AC2-112 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208078 | SAKR | 1 | 230 | 229 | 903 | 117.19 | 122.44 | AC2-112 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200025 | W CHAPEL | 1 | 500 | 225 | 1732 | 123.65 | 121.85 | AC2-112 | PEPCO_P4_PP41_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208031 | MLWD TR2 | 1 | 230 | 229 | 911 | 111.75 | 121.17 | AC2-112 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208031 | MLWD TR2 | 1 | 230 | 229 | 911 | 111.74 | 121.17 | AC2-112 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208031 | MLWD TR2 | 1 | 230 | 229 | 911 | 111.75 | 121.17 | AC2-112 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 114.69 | 118.38 | AC2-112 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 114.35 | 118.04 | AC2-112 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 114.34 | 117.98 | AC2-112 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 114.34 | 117.98 | AC2-112 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 114.01 | 117.65 | AC2-112 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 114 | 117.65 | AC2-112 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 122.73 | 117.36 | AC2-112 | PECO_P4_PEACH225_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 117.05 | 115.13 | AC2-112 | AP_P2-3_PE-500-019C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 2 | 500/230 | 225/232 | 2168 | 109.64 | 114.95 | AC2-112 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 2 | 500/230 | 225/232 | 2168 | 109.47 | 114.73 | AC2-112 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 2 | 500/230 | 225/232 | 2168 | 109.46 | 114.73 | AC2-112 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 1 | 500/230 | 225/232 | 2168 | 109.41 | 114.71 | AC2-112 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 1 | 500/230 | 225/232 | 2168 | 109.23 | 114.49 | AC2-112 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 1 | 500/230 | 225/232 | 2168 | 109.23 | 114.49 | AC2-112 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208020 | MANO TR3 | 1 | 230 | 229 | 793 | 104.26 | 114.02 | AC2-112 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208020 | MANO TR3 | 208031 | MLWD TR2 | 1 | 230 | 229 | 903 | 101.86 | 112.53 | AC2-112 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208020 | MANO TR3 | 208031 | MLWD TR2 | 1 | 230 | 229 | 903 | 101.86 | 112.52 | AC2-112 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208020 | MANO TR3 | 208031 | MLWD TR2 | 1 | 230 | 229 | 903 | 101.86 | 112.52 | AC2-112 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208031 | MLWD TR2 | 1 | 230 | 229 | 911 | 104.99 | 111.68 | AC2-112 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 99.51 | 103.4 | AC2-112 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 99.51 | 103.4 | AC2-112 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 99.51 | 103.4 | AC2-112 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208020 | MANO TR3 | 208031 | MLWD TR2 | 1 | 230 | 229 | 903 | 95.49 | 103.29 | AC2-112 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 98.58 | 102.07 | AC2-112 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 98.68 | 100.71 | AC2-112 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2901 | 145.45 | 147.69 | FAIRLAWN_AB | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 153.82 | 158.33 | AC2-120 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.31 | 157.43 | AC2-120 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.3 | 157.43 | AC2-120 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 152.14 | 157.01 | AC2-120 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 161.84 | 154.61 | AC2-120 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 148.77 | 153.36 | AC2-120 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 155.88 | 150.72 | AC2-120 | PN_P1-2_PN-500-010T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.19 | 148.06 | AC2-120 | PJM_500_BG_P4_5_CNSTN_L_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.49 | 148.06 | AC2-120 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.29 | 147.87 | AC2-120 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.32 | 147.85 | AC2-120 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.05 | 147.66 | AC2-120 | PECO_P4_NOTTI85_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.99 | 147.64 | AC2-120 | PECO_P1-2_220-08_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.92 | 147.58 | AC2-120 | PECO_P4_COOPR125_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.92 | 144.24 | AC2-120 | PECO_P1-2_PBTIE1_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 136.81 | 139.44 | AC2-120 | DVP_P4-2: 536T550_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 136.17 | 138.45 | AC2-120 | ME_P2-3_ME-115-013C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 133.04 | 135.09 | AC2-120 | AP_P2-3_MP-500-012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 131.21 | 133.2 | AC2-120 | DVP_P4-2: 560T571_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 131.13 | 133.12 | AC2-120 | DVP_P4-2: H1T560_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 131.13 | 133.11 | AC2-120 | DVP_P4-2: H2T560_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 131.12 | 133.1 | AC2-120 | PEPCO_P1_5070_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 139.18 | 133.02 | AC2-120 | PECO_P1-2_PBTIE2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 133.56 | 127.73 | AC2-120 | PECO_P4_PEACH015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 132.22 | 126.39 | AC2-120 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 123.12 | 117.74 | AC2-120 | PECO_P4_PEACH225_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2901 | 144.54 | 146.63 | G07 NFTWR | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 153.79 | 158.3 | AC2-123 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.27 | 157.4 | AC2-123 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.27 | 157.39 | AC2-123 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 152.1 | 156.97 | AC2-123 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 161.76 | 154.54 | AC2-123 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 148.74 | 153.32 | AC2-123 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 155.84 | 150.69 | AC2-123 | PN_P1-2_PN-500-010T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.58 | 149.7 | AC2-123 | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.51 | 149.63 | AC2-123 | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.21 | 148.48 | AC2-123 | AP_P2-3_PE-500-016_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.27 | 148.45 | AC2-123 | AP_P2-3_PE-500-015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.15 | 148.02 | AC2-123 | PJM_500_BG_P4_5_CNSTN_L_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.43 | 147.99 | AC2-123 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.23 | 147.81 | AC2-123 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.26 | 147.79 | AC2-123 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.99 | 147.6 | AC2-123 | PECO_P4_NOTTI85_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.38 | 147.6 | AC2-123 | AP_P1-2_WP-500-DRT17_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.38 | 147.6 | AC2-123 | AP_P1-2_PE-500-001_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.93 | 147.58 | AC2-123 | PECO_P1-2_220-08_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.33 | 147.53 | AC2-123 | AP_P2-3_PE-500-018C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.86 | 147.52 | AC2-123 | PECO_P4_COOPR125_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2901 | 145.23 | 147.43 | GLOUCSTR_26 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.98 | 144.26 | AC2-123 | PECO_P4_PEACH025_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.85 | 144.17 | AC2-123 | PECO_P1-2_PBTIE1_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 139.22 | 133.28 | AC2-123 | PECO_P4_PEACH205_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 139.11 | 132.95 | AC2-123 | PECO_P1-2_PBTIE2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 138.16 | 132.07 | AC2-123 | PECO_P4_PEACH055_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 133.49 | 127.67 | AC2-123 | PECO_P4_PEACH015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 132.16 | 126.34 | AC2-123 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 123.06 | 117.69 | AC2-123 | PECO_P4_PEACH225_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 144.32 | 139.17 | AC2-154 | PL_10_P42_100570_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 144.32 | 139.17 | AC2-154 | PL_10_P42_100570_A_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 143.51 | 138.38 | AC2-154 | PL_10_P12_000085_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 143.41 | 138.29 | AC2-154 | PN_P2-3_PN-500-004-DRT-008_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 143.41 | 138.29 | AC2-154 | PN_P2-3_PN-500-DRT31_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 225.69 | 237.15 | AC2-165 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 223.69 | 237.15 | AC2-165 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 225.63 | 237.09 | AC2-165 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 223.62 | 237.09 | AC2-165 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 225.63 | 237.09 | AC2-165 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 223.62 | 237.09 | AC2-165 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 213.63 | 226.99 | AC2-165 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 213.57 | 226.93 | AC2-165 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 213.57 | 226.93 | AC2-165 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 209.37 | 223.78 | AC2-165 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 209.31 | 223.72 | AC2-165 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 209.31 | 223.72 | AC2-165 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 210.79 | 217.94 | AC2-165 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 208.78 | 217.94 | AC2-165 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 199.24 | 208.37 | AC2-165 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 194.98 | 205.02 | AC2-165 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 172.82 | 167.84 | AC2-165 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 163.7 | 165.02 | AC2-165 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2901 | 144.72 | 146.84 | GR RIDGE | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 161.84 | 161.92 | AC2-165 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 161.83 | 161.92 | AC2-165 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 161.82 | 161.91 | AC2-165 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 153.59 | 158.05 | AC2-165 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.09 | 157.21 | AC2-165 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.09 | 157.21 | AC2-165 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 151.9 | 156.73 | AC2-165 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 161.57 | 154.35 | AC2-165 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 148.54 | 153.08 | AC2-165 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 155.66 | 150.51 | AC2-165 | PN_P1-2_PN-500-010T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 903 | 142.79 | 149.61 | AC2-165 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 903 | 142.79 | 149.61 | AC2-165 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 903 | 142.77 | 149.6 | AC2-165 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.38 | 149.46 | AC2-165 | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.31 | 149.39 | AC2-165 | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144 | 148.21 | AC2-165 | AP_P2-3_PE-500-016_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.06 | 148.18 | AC2-165 | AP_P2-3_PE-500-015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.98 | 147.84 | AC2-165 | PJM_500_BG_P4_5_CNSTN_L_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.27 | 147.83 | AC2-165 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.06 | 147.64 | AC2-165 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.09 | 147.63 | AC2-165 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.82 | 147.43 | AC2-165 | PECO_P4_NOTTI85_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.76 | 147.42 | AC2-165 | PECO_P1-2_220-08_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.69 | 147.35 | AC2-165 | PECO_P4_COOPR125_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.18 | 147.33 | AC2-165 | AP_P1-2_PE-500-001_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.18 | 147.33 | AC2-165 | AP_P1-2_WP-500-DRT17_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.13 | 147.26 | AC2-165 | AP_P2-3_PE-500-018C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2901 | 144.88 | 147.03 | KELLY CRK;1U | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.8 | 144.09 | AC2-165 | PECO_P4_PEACH025_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.65 | 143.98 | AC2-165 | PECO_P1-2_PBTIE1_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 911 | 149.06 | 143.18 | AC2-165 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 1031 | 130.39 | 138.2 | AC2-165 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 1031 | 130.39 | 138.2 | AC2-165 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 1031 | 130.38 | 138.19 | AC2-165 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 139.04 | 133.1 | AC2-165 | PECO_P4_PEACH205_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 138.92 | 132.77 | AC2-165 | PECO_P1-2_PBTIE2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208078 | SAKR | 1 | 230 | 229 | 903 | 124.57 | 132.64 | AC2-165 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 137.99 | 131.9 | AC2-165 | PECO_P4_PEACH055_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 133.29 | 127.47 | AC2-165 | PECO_P4_PEACH015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 128.62 | 126.92 | AC2-165 | DVP_P4-2: 514T595_SRT-SW |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 131.98 | 126.16 | AC2-165 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 126.87 | 125.15 | AC2-165 | DVP_P4-2: 51482_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 126.87 | 125.05 | AC2-165 | AP_P1-2_PE-500-407T_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 126.87 | 125.05 | AC2-165 | DVP_P1-2: LN 514_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208020 | MANO TR3 | 1 | 230 | 229 | 793 | 111.57 | 124.74 | AC2-165 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208020 | MANO TR3 | 1 | 230 | 229 | 793 | 111.56 | 124.74 | AC2-165 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208020 | MANO TR3 | 1 | 230 | 229 | 793 | 111.57 | 124.74 | AC2-165 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200025 | W CHAPEL | 1 | 500 | 225 | 1732 | 123.73 | 121.94 | AC2-165 | PEPCO_P4_PP41_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 122.88 | 117.51 | AC2-165 | PECO_P4_PEACH225_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 117.07 | 115.14 | AC2-165 | AP_P2-3_PE-500-019C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 2 | 500/230 | 225/232 | 2168 | 109.71 | 115.03 | AC2-165 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 2 | 500/230 | 225/232 | 2168 | 109.53 | 114.81 | AC2-165 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 2 | 500/230 | 225/232 | 2168 | 109.53 | 114.81 | AC2-165 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 1 | 500/230 | 225/232 | 2168 | 109.48 | 114.78 | AC2-165 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 1 | 500/230 | 225/232 | 2168 | 109.3 | 114.57 | AC2-165 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 1 | 500/230 | 225/232 | 2168 | 109.3 | 114.57 | AC2-165 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 99.55 | 103.48 | AC2-165 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 99.55 | 103.48 | AC2-165 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 99.55 | 103.48 | AC2-165 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 98.62 | 102.16 | AC2-165 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 98.72 | 100.78 | AC2-165 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2901 | 144.82 | 146.96 | M24 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.3 | 157.43 | AC2-176 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.3 | 157.43 | AC2-176 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 161.79 | 154.56 | AC2-176 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 155.87 | 150.72 | AC2-176 | PN_P1-2_PN-500-010T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.18 | 148.05 | AC2-176 | PJM_500_BG_P4_5_CNSTN_L_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.45 | 148.02 | AC2-176 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.25 | 147.83 | AC2-176 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.28 | 147.81 | AC2-176 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.01 | 147.62 | AC2-176 | PECO_P4_NOTTI85_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.95 | 147.6 | AC2-176 | PECO_P1-2_220-08_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.88 | 147.54 | AC2-176 | PECO_P4_COOPR125_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.99 | 144.28 | AC2-176 | PECO_P4_PEACH025_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.88 | 144.2 | AC2-176 | PECO_P1-2_PBTIE1_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 138.98 | 141.28 | AC2-176 | AP_P1-2_WP-500-DRT21_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 138.98 | 141.28 | AC2-176 | AP_P2-2_WP-500-DRT16_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 138.98 | 141.28 | AC2-176 | AP_P2-3_WP-500-465_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 138.98 | 141.28 | AC2-176 | AP_P1-2_WP-500-005A_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 138.98 | 141.28 | AC2-176 | AP_P2-3_WP-500-DRT20_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 138.75 | 140.91 | AC2-176 | AP_P1-2_WP-500-008_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 138.75 | 140.91 | AC2-176 | AP_P2-3_WP-500-DRT45_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 137.16 | 139.13 | AC2-176 | AP_P2-3_WP-500-706T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 136.66 | 138.86 | AC2-176 | PN_P2-3_PN-500-DRT32_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 136.66 | 138.86 | AC2-176 | PN_P2-3_PN-500-004-DRT-002_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 139.25 | 133.31 | AC2-176 | PECO_P4_PEACH205_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 139.14 | 132.98 | AC2-176 | PECO_P1-2_PBTIE2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 138.19 | 132.1 | AC2-176 | PECO_P4_PEACH055_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 133.52 | 127.7 | AC2-176 | PECO_P4_PEACH015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 132.19 | 126.36 | AC2-176 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 123.09 | 117.71 | AC2-176 | PECO_P4_PEACH225_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2901 | 144.85 | 146.99 | MINONK ;1U | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 154.21 | 158.79 | AC2-185 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.74 | 157.86 | AC2-185 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.74 | 157.86 | AC2-185 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 152.51 | 157.46 | AC2-185 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 162.41 | 155.16 | AC2-185 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 149.15 | 153.81 | AC2-185 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 156.32 | 151.16 | AC2-185 | PN_P1-2_PN-500-010T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.97 | 150.16 | AC2-185 | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.9 | 150.09 | AC2-185 | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.57 | 148.9 | AC2-185 | AP_P2-3_PE-500-016_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.63 | 148.87 | AC2-185 | AP_P2-3_PE-500-015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.99 | 148.54 | AC2-185 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.61 | 148.47 | AC2-185 | PJM_500_BG_P4_5_CNSTN_L_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.78 | 148.35 | AC2-185 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.81 | 148.34 | AC2-185 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.54 | 148.14 | AC2-185 | PECO_P4_NOTTI85_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.48 | 148.12 | AC2-185 | PECO_P1-2_220-08_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.41 | 148.06 | AC2-185 | PECO_P4_COOPR125_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.75 | 148.02 | AC2-185 | AP_P1-2_WP-500-DRT17_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.75 | 148.02 | AC2-185 | AP_P1-2_PE-500-001_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.7 | 147.95 | AC2-185 | AP_P2-3_PE-500-018C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2901 | 144.83 | 146.97 | O09 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 151.73 | 144.98 | AC2-185 | PECO_P4_PEACH025_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 151.54 | 144.84 | AC2-185 | PECO_P1-2_PBTIE1_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 139.75 | 133.79 | AC2-185 | PECO_P4_PEACH205_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 139.75 | 133.57 | AC2-185 | PECO_P1-2_PBTIE2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 138.78 | 132.67 | AC2-185 | PECO_P4_PEACH055_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 134.18 | 128.33 | AC2-185 | PECO_P4_PEACH015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 132.79 | 126.93 | AC2-185 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 123.7 | 118.29 | AC2-185 | PECO_P4_PEACH225_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2901 | 144.82 | 146.95 | O29 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.61 | 157.73 | AC2-187 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.61 | 157.73 | AC2-187 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 162.22 | 154.97 | AC2-187 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 156.18 | 151.02 | AC2-187 | PN_P1-2_PN-500-010T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.82 | 148.38 | AC2-187 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.48 | 148.34 | AC2-187 | PJM_500_BG_P4_5_CNSTN_L_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.62 | 148.19 | AC2-187 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.65 | 148.18 | AC2-187 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.38 | 147.98 | AC2-187 | PECO_P4_NOTTI85_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.32 | 147.97 | AC2-187 | PECO_P1-2_220-08_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.25 | 147.9 | AC2-187 | PECO_P4_COOPR125_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 151.49 | 144.75 | AC2-187 | PECO_P4_PEACH025_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 151.33 | 144.63 | AC2-187 | PECO_P1-2_PBTIE1_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 139.55 | 133.38 | AC2-187 | PECO_P1-2_PBTIE2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 138.59 | 132.48 | AC2-187 | PECO_P4_PEACH055_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 133.96 | 128.12 | AC2-187 | PECO_P4_PEACH015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 132.59 | 126.74 | AC2-187 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204512 | 27S.RDG | 204693 | 27BOONETOWN | 1 | 230 | 227 | 607 | 107.72 | 122.16 | AC2-187 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 123.5 | 118.11 | AC2-187 | PECO_P4_PEACH225_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2901 | 141.52 | 143.15 | O66 NFTWR | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.61 | 157.73 | AC2-188 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.61 | 157.73 | AC2-188 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 162.22 | 154.97 | AC2-188 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 156.18 | 151.02 | AC2-188 | PN_P1-2_PN-500-010T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.82 | 148.38 | AC2-188 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.48 | 148.34 | AC2-188 | PJM_500_BG_P4_5_CNSTN_L_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.62 | 148.19 | AC2-188 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.65 | 148.18 | AC2-188 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.38 | 147.98 | AC2-188 | PECO_P4_NOTTI85_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.32 | 147.97 | AC2-188 | PECO_P1-2_220-08_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.25 | 147.9 | AC2-188 | PECO_P4_COOPR125_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 151.49 | 144.75 | AC2-188 | PECO_P4_PEACH025_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 151.33 | 144.63 | AC2-188 | PECO_P1-2_PBTIE1_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 139.55 | 133.38 | AC2-188 | PECO_P1-2_PBTIE2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 138.59 | 132.48 | AC2-188 | PECO_P4_PEACH055_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 133.96 | 128.12 | AC2-188 | PECO_P4_PEACH015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 132.59 | 126.74 | AC2-188 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204512 | 27S.RDG | 204693 | 27BOONETOWN | 1 | 230 | 227 | 607 | 107.72 | 122.16 | AC2-188 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 123.5 | 118.11 | AC2-188 | PECO_P4_PEACH225_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2901 | 145.32 | 147.54 | P28 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 153.81 | 158.32 | AC2-195 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.27 | 157.4 | AC2-195 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.27 | 157.4 | AC2-195 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 152.12 | 157 | AC2-195 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 161.75 | 154.52 | AC2-195 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 148.76 | 153.35 | AC2-195 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 155.85 | 150.7 | AC2-195 | PN_P1-2_PN-500-010T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.59 | 149.72 | AC2-195 | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.52 | 149.65 | AC2-195 | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.16 | 148.03 | AC2-195 | PJM_500_BG_P4_5_CNSTN_L_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.41 | 147.98 | AC2-195 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.21 | 147.79 | AC2-195 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.24 | 147.78 | AC2-195 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.97 | 147.58 | AC2-195 | PECO_P4_NOTTI85_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.91 | 147.57 | AC2-195 | PECO_P1-2_220-08_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.84 | 147.5 | AC2-195 | PECO_P4_COOPR125_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2901 | 144.21 | 146.24 | Q01/Q03 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 142.88 | 147 | AC2-195 | AP_P1-2_WP-500-006_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 142.88 | 147 | AC2-195 | AP_P1-2_PE-500-004_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 142.88 | 147 | AC2-195 | AP_P2-3_WP-500-DRT19_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 142.88 | 147 | AC2-195 | AP_P2-3_WP-500-466_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 142.88 | 146.99 | AC2-195 | AP_P2-3_PE-500-014_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.95 | 144.23 | AC2-195 | PECO_P4_PEACH025_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.84 | 144.16 | AC2-195 | PECO_P1-2_PBTIE1_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 139.22 | 133.28 | AC2-195 | PECO_P4_PEACH205_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 139.1 | 132.94 | AC2-195 | PECO_P1-2_PBTIE2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 138.15 | 132.06 | AC2-195 | PECO_P4_PEACH055_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 133.48 | 127.66 | AC2-195 | PECO_P4_PEACH015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 132.15 | 126.33 | AC2-195 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204512 | 27S.RDG | 204693 | 27BOONETOWN | 1 | 230 | 227 | 607 | 107.68 | 123.47 | AC2-195 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 123.05 | 117.68 | AC2-195 | PECO_P4_PEACH225_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 226.04 | 237.17 | AD1-020 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 224.03 | 237.17 | AD1-020 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 225.97 | 237.11 | AD1-020 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 223.96 | 237.11 | AD1-020 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 225.97 | 237.11 | AD1-020 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 223.96 | 237.11 | AD1-020 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 213.96 | 227.01 | AD1-020 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 213.9 | 226.95 | AD1-020 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 213.9 | 226.95 | AD1-020 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 209.7 | 223.8 | AD1-020 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 209.64 | 223.74 | AD1-020 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 209.64 | 223.74 | AD1-020 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 334 | 181.28 | 184.56 | AD1-020 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 334 | 181.28 | 184.56 | AD1-020 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 334 | 181.15 | 184.41 | AD1-020 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 235463 | 01TANEY | 1 | 138 | 227/201 | 317 | 184.22 | 178.51 | AD1-020 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 235463 | 01TANEY | 1 | 138 | 227/201 | 317 | 184.22 | 178.5 | AD1-020 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 235463 | 01TANEY | 1 | 138 | 227/201 | 317 | 184.07 | 178.37 | AD1-020 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204538 | 27STRABAN | 204544 | 27LINCOLN | 1 | 115 | 227 | 371 | 168.85 | 174.47 | AD1-020 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204538 | 27STRABAN | 204544 | 27LINCOLN | 1 | 115 | 227 | 371 | 168.85 | 174.47 | AD1-020 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204538 | 27STRABAN | 204544 | 27LINCOLN | 1 | 115 | 227 | 371 | 168.72 | 174.32 | AD1-020 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204529 | 27GERMANTN | 204538 | 27STRABAN | 1 | 115 | 227 | 371 | 162.94 | 169.91 | AD1-020 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204529 | 27GERMANTN | 204538 | 27STRABAN | 1 | 115 | 227 | 371 | 162.94 | 169.91 | AD1-020 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 204550 | 27ORRTANNA | 1 | 115 | 227 | 189 | 170.26 | 169.83 | AD1-020 | ME_P1-2_ME-115-068_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204529 | 27GERMANTN | 204538 | 27STRABAN | 1 | 115 | 227 | 371 | 162.81 | 169.76 | AD1-020 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 174.08 | 169.29 | AD1-020 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 173.13 | 167.9 | AD1-020 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 173.13 | 167.9 | AD1-020 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 173.11 | 167.89 | AD1-020 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 204550 | 27ORRTANNA | 1 | 115 | 227 | 189 | 167.96 | 167.39 | AD1-020 | ME_P2-3_ME-115-013B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 204550 | 27ORRTANNA | 1 | 115 | 227 | 189 | 167.65 | 167.06 | AD1-020 | ME_P2-3_ME-115-013A_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 165.22 | 166.68 | AD1-020 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2901 | 145.33 | 147.55 | Q27 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 163.38 | 163.62 | AD1-020 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 163.38 | 163.62 | AD1-020 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 163.37 | 163.61 | AD1-020 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 165.18 | 160.38 | AD1-020 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 154.38 | 159 | AD1-020 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2901 | 144.8 | 146.93 | Q57 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 152.69 | 157.68 | AD1-020 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 334 | 158.09 | 157.58 | AD1-020 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 334 | 158.09 | 157.58 | AD1-020 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 334 | 158.08 | 157.57 | AD1-020 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 334 | 157.9 | 157.39 | AD1-020 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 903 | 146.53 | 154.42 | AD1-020 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 149.33 | 154.03 | AD1-020 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2901 | 144.92 | 147.07 | R49 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 154.44 | 152.95 | AD1-020 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 903 | 145.03 | 151.75 | AD1-020 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 903 | 145.03 | 151.75 | AD1-020 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 903 | 145.01 | 151.74 | AD1-020 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 155.81 | 150.63 | AD1-020 | PN_P1-2_PN-500-010T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 147.11 | 150.32 | AD1-020 | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 147.03 | 150.25 | AD1-020 | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 334 | 150.33 | 149.3 | AD1-020 | ME_P1-2_ME-115-061_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 334 | 150.33 | 149.3 | AD1-020 | ME_P2-3_ME-115-019A-A_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.69 | 149.04 | AD1-020 | AP_P2-3_PE-500-016_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.76 | 149.01 | AD1-020 | AP_P2-3_PE-500-015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 334 | 151.04 | 148.75 | AD1-020 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204539 | 27HUNTRSTN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 334 | 146.02 | 148.47 | AD1-020 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204539 | 27HUNTRSTN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 334 | 146.02 | 148.47 | AD1-020 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204539 | 27HUNTRSTN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 334 | 145.89 | 148.33 | AD1-020 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.87 | 148.16 | AD1-020 | AP_P1-2_PE-500-001_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.87 | 148.16 | AD1-020 | AP_P1-2_WP-500-DRT17_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.82 | 148.09 | AD1-020 | AP_P2-3_PE-500-018C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2901 | 144.71 | 146.83 | R60 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 147.42 | 147.9 | AD1-020 | BG_P7_GRCTN_CNSTN_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2901 | 144.85 | 146.99 | S06 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204538 | 27STRABAN | 204544 | 27LINCOLN | 1 | 115 | 227 | 371 | 145.33 | 146.74 | AD1-020 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204538 | 27STRABAN | 204544 | 27LINCOLN | 1 | 115 | 227 | 371 | 145.33 | 146.74 | AD1-020 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204538 | 27STRABAN | 204544 | 27LINCOLN | 1 | 115 | 227 | 371 | 145.33 | 146.74 | AD1-020 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204538 | 27STRABAN | 204544 | 27LINCOLN | 1 | 115 | 227 | 371 | 145.15 | 146.55 | AD1-020 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 911 | 150.29 | 144.6 | AD1-020 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 151.04 | 144.32 | AD1-020 | PECO_P4_PEACH025_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 911 | 149.36 | 143.34 | AD1-020 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 911 | 149.36 | 143.34 | AD1-020 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 911 | 149.34 | 143.33 | AD1-020 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 142.89 | 142.53 | AD1-020 | PJM_500_BG_P4_5_CNSTN_15_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204529 | 27GERMANTN | 204538 | 27STRABAN | 1 | 115 | 227 | 371 | 139.42 | 142.39 | AD1-020 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204529 | 27GERMANTN | 204538 | 27STRABAN | 1 | 115 | 227 | 371 | 139.42 | 142.39 | AD1-020 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204529 | 27GERMANTN | 204538 | 27STRABAN | 1 | 115 | 227 | 371 | 139.42 | 142.38 | AD1-020 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204529 | 27GERMANTN | 204538 | 27STRABAN | 1 | 115 | 227 | 371 | 139.24 | 142.19 | AD1-020 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 903 | 137.95 | 141.87 | AD1-020 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 235463 | 01TANEY | 1 | 138 | 227/201 | 317 | 143.35 | 141.83 | AD1-020 | AP_P2-3_PE-500-016_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 147 | 141.81 | AD1-020 | ME_P2-3_ME-230-018A_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 235463 | 01TANEY | 1 | 138 | 227/201 | 317 | 143.46 | 141.76 | AD1-020 | AP_P2-3_PE-500-015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200504 | 26CARLISLE | 204528 | 27GARDNERS | 1 | 115 | 226/227 | 190 | 132.58 | 141.73 | AD1-020 | PN_P2-3_PN-115-0331-B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 146.89 | 141.7 | AD1-020 | ME_P1-2_ME-230-008_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 146.89 | 141.7 | AD1-020 | ME_P2-3_ME-230-DTR030_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 146.89 | 141.7 | AD1-020 | ME_P2-3_ME-230-007C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 146.86 | 141.68 | AD1-020 | ME_P2-3_ME-230-007D_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 235463 | 01TANEY | 1 | 138 | 227/201 | 317 | 141.85 | 141.47 | AD1-020 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 235463 | 01TANEY | 1 | 138 | 227/201 | 317 | 142.04 | 140.93 | AD1-020 | AP_P2-3_PE-500-018D_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 235463 | 01TANEY | 1 | 138 | 227/201 | 317 | 142.03 | 140.92 | AD1-020 | AP_P2-3_PE-500-018C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 235463 | 01TANEY | 1 | 138 | 227/201 | 317 | 141.44 | 140.85 | AD1-020 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 235463 | 01TANEY | 1 | 138 | 227/201 | 317 | 141.89 | 140.67 | AD1-020 | AP_P1-2_PE-500-001_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 145.59 | 140.36 | AD1-020 | ME_P2-4_ME-115-0102-B134_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200504 | 26CARLISLE | 204528 | 27GARDNERS | 1 | 115 | 226/227 | 190 | 130.99 | 140.26 | AD1-020 | PN_P1-2_PN-115-094_A_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 145.19 | 140.07 | AD1-020 | ME_P2-3_ME-230-007A_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 145.17 | 140.02 | AD1-020 | ME_P7-1_ME-230-003_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 145.16 | 140 | AD1-020 | ME_P1-2_ME-115-067_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200504 | 26CARLISLE | 204528 | 27GARDNERS | 1 | 115 | 226/227 | 190 | 130.85 | 139.34 | AD1-020 | PN_P2-3_PN-115-58B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200504 | 26CARLISLE | 204528 | 27GARDNERS | 1 | 115 | 226/227 | 190 | 131.51 | 139.3 | AD1-020 | PN_P2-2_PN-115-030_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200504 | 26CARLISLE | 204528 | 27GARDNERS | 1 | 115 | 226/227 | 190 | 131.51 | 139.3 | AD1-020 | PN_P1-3_PN-115-040_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200504 | 26CARLISLE | 204528 | 27GARDNERS | 1 | 115 | 226/227 | 190 | 130.65 | 139.28 | AD1-020 | PN_P1-2_PN-115-094_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 1031 | 130.25 | 138.41 | AD1-020 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204502 | 27JACKSON | 204514 | 27TMI | 1 | 230 | 227 | 781 | 129.97 | 138.35 | AD1-020 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204502 | 27JACKSON | 204514 | 27TMI | 1 | 230 | 227 | 781 | 130.17 | 138.28 | AD1-020 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204502 | 27JACKSON | 204514 | 27TMI | 1 | 230 | 227 | 781 | 130.17 | 138.28 | AD1-020 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204502 | 27JACKSON | 204514 | 27TMI | 1 | 230 | 227 | 781 | 130.15 | 138.27 | AD1-020 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204538 | 27STRABAN | 204544 | 27LINCOLN | 1 | 115 | 227 | 371 | 138.19 | 137.98 | AD1-020 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 1031 | 129.76 | 137.31 | AD1-020 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 1031 | 129.76 | 137.31 | AD1-020 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 1031 | 129.75 | 137.3 | AD1-020 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204538 | 27STRABAN | 204544 | 27LINCOLN | 1 | 115 | 227 | 371 | 133.92 | 137.17 | AD1-020 | AP_P2-3_PE-500-016_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204538 | 27STRABAN | 204544 | 27LINCOLN | 1 | 115 | 227 | 371 | 134.02 | 137.1 | AD1-020 | AP_P2-3_PE-500-015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 911 | 141.49 | 136.54 | AD1-020 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 204529 | 27GERMANTN | 1 | 138/115 | 227 | 453 | 128.91 | 135.61 | AD1-020 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 204529 | 27GERMANTN | 1 | 138/115 | 227 | 453 | 128.91 | 135.61 | AD1-020 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 204529 | 27GERMANTN | 1 | 138/115 | 227 | 453 | 128.81 | 135.48 | AD1-020 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200504 | 26CARLISLE | 204528 | 27GARDNERS | 1 | 115 | 226/227 | 190 | 128.29 | 134.76 | AD1-020 | PN_P2-3_PN-230-0014-12_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200504 | 26CARLISLE | 204528 | 27GARDNERS | 1 | 115 | 226/227 | 190 | 128.28 | 134.33 | AD1-020 | PN_P1-3_PN-230-020A_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200504 | 26CARLISLE | 204528 | 27GARDNERS | 1 | 115 | 226/227 | 190 | 128.28 | 134.33 | AD1-020 | PN_P2-3_PN-230-0014-11_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200504 | 26CARLISLE | 204528 | 27GARDNERS | 1 | 115 | 226/227 | 190 | 128.21 | 134.32 | AD1-020 | PN_P2-2_PN-115-031_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204529 | 27GERMANTN | 204538 | 27STRABAN | 1 | 115 | 227 | 371 | 132.28 | 133.59 | AD1-020 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204529 | 27GERMANTN | 204538 | 27STRABAN | 1 | 115 | 227 | 371 | 128.01 | 132.71 | AD1-020 | AP_P2-3_PE-500-016_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204529 | 27GERMANTN | 204538 | 27STRABAN | 1 | 115 | 227 | 371 | 128.11 | 132.63 | AD1-020 | AP_P2-3_PE-500-015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204539 | 27HUNTRSTN | 204550 | 27ORRTANNA | 1 | 115 | 227 | 264 | 131.57 | 131.34 | AD1-020 | ME_P1-2_ME-115-068_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204539 | 27HUNTRSTN | 204550 | 27ORRTANNA | 1 | 115 | 227 | 264 | 129.93 | 129.57 | AD1-020 | ME_P2-3_ME-115-013B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204539 | 27HUNTRSTN | 204550 | 27ORRTANNA | 1 | 115 | 227 | 264 | 129.71 | 129.33 | AD1-020 | ME_P2-3_ME-115-013A_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 1031 | 124.16 | 128.56 | AD1-020 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 129.99 | 128.26 | AD1-020 | DVP_P4-2: 514T595_SRT-SW |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 204550 | 27ORRTANNA | 1 | 115 | 227 | 189 | 130.34 | 127.92 | AD1-020 | ME_P1-2_ME-115-067_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204502 | 27JACKSON | 204514 | 27TMI | 1 | 230 | 227 | 781 | 122.52 | 127.83 | AD1-020 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 911 | 124.27 | 126.76 | AD1-020 | BG_P7_GRCTN_CNSTN_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 128.27 | 126.57 | AD1-020 | DVP_P4-2: 51482_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 128.27 | 126.48 | AD1-020 | DVP_P1-2: LN 514_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 128.27 | 126.48 | AD1-020 | AP_P1-2_PE-500-407T_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208020 | MANO TR3 | 1 | 230 | 229 | 793 | 111.72 | 124.76 | AD1-020 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208020 | MANO TR3 | 1 | 230 | 229 | 793 | 111.71 | 124.76 | AD1-020 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208020 | MANO TR3 | 1 | 230 | 229 | 793 | 111.72 | 124.76 | AD1-020 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 203981 | AD2-062_POI | 235188 | 01GREENE | 1 | 138 | 226/201 | 317 | 141.03 | 123.14 | AD1-020 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 203981 | AD2-062_POI | 235188 | 01GREENE | 1 | 138 | 226/201 | 317 | 141.03 | 123.14 | AD1-020 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 203981 | AD2-062_POI | 235188 | 01GREENE | 1 | 138 | 226/201 | 317 | 141.03 | 123.13 | AD1-020 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200025 | W CHAPEL | 1 | 500 | 225 | 1732 | 124.42 | 122.66 | AD1-020 | PEPCO_P4_PP41_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2901 | 144.88 | 147.02 | S36 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200532 | 26ROXBURY | 203981 | AD2-062_POI | 1 | 138 | 226 | 317 | 140.32 | 121.84 | AD1-020 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200532 | 26ROXBURY | 203981 | AD2-062_POI | 1 | 138 | 226 | 317 | 140.32 | 121.84 | AD1-020 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200532 | 26ROXBURY | 203981 | AD2-062_POI | 1 | 138 | 226 | 317 | 140.32 | 121.84 | AD1-020 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 204550 | 27ORRTANNA | 1 | 115 | 227 | 189 | 124.49 | 121.75 | AD1-020 | ME_P2-2_ME-115-0102-4_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 204550 | 27ORRTANNA | 1 | 115 | 227 | 189 | 124.49 | 121.75 | AD1-020 | ME_P2-3_ME-115-0102-A_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200532 | 26ROXBURY | 200520 | 26ROXBURY | 2 | 138/115 | 226 | 435 | 106.46 | 121.46 | AD1-020 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200532 | 26ROXBURY | 200520 | 26ROXBURY | 2 | 138/115 | 226 | 435 | 106.46 | 121.46 | AD1-020 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200532 | 26ROXBURY | 200520 | 26ROXBURY | 2 | 138/115 | 226 | 435 | 106.31 | 121.29 | AD1-020 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204512 | 27S.RDG | 204693 | 27BOONETOWN | 1 | 230 | 227 | 607 | 107.28 | 121.28 | AD1-020 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204512 | 27S.RDG | 204693 | 27BOONETOWN | 1 | 230 | 227 | 607 | 107.25 | 121.25 | AD1-020 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204512 | 27S.RDG | 204693 | 27BOONETOWN | 1 | 230 | 227 | 607 | 107.25 | 121.25 | AD1-020 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 203981 | AD2-062_POI | 235188 | 01GREENE | 1 | 138 | 226/201 | 317 | 133.97 | 121.02 | AD1-020 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 911 | 119.85 | 120.88 | AD1-020 | PJM_500_BG_P4_5_CNSTN_15_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220965 | NEAST339 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 120.5 | 119.86 | AD1-020 | BG_P1_2315_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200532 | 26ROXBURY | 203981 | AD2-062_POI | 1 | 138 | 226 | 317 | 133.26 | 119.73 | AD1-020 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204539 | 27HUNTRSTN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 334 | 122.83 | 119.7 | AD1-020 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204539 | 27HUNTRSTN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 334 | 122.83 | 119.7 | AD1-020 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204539 | 27HUNTRSTN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 334 | 122.83 | 119.69 | AD1-020 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220965 | NEAST339 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 120.07 | 119.65 | AD1-020 | BG_P4_5_NEAST_17_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220965 | NEAST339 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 120.23 | 119.65 | AD1-020 | BG_P4_5_NEAST_15_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204539 | 27HUNTRSTN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 334 | 122.65 | 119.49 | AD1-020 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2901 | 145.31 | 147.52 | SALEM G3 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204539 | 27HUNTRSTN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 334 | 121.73 | 119.33 | AD1-020 | PJM_GEN_P-1-1: AD1-020_C_BUS_205916_ID_1_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220979 | NEAST317 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 119.57 | 118.99 | AD1-020 | BG_P1_2337_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220979 | NEAST317 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 119.23 | 118.71 | AD1-020 | BG_P4_5_NEAST_39_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220979 | NEAST317 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 119.23 | 118.71 | AD1-020 | BG_P4_5_NEAST_37_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 119.9 | 118.59 | AD1-020 | PL_04_P42_000564_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 119.9 | 118.59 | AD1-020 | PL_04_P12_000260_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 2 | 230 | 233 | 793 | 119.92 | 117.19 | AD1-020 | PEPCO_P1_PP1_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 793 | 119.92 | 117.19 | AD1-020 | PEPCO_P1_PP2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 118.49 | 116.58 | AD1-020 | AP_P2-3_PE-500-019C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200504 | 26CARLISLE | 200520 | 26ROXBURY | 1 | 115 | 226 | 190 | 104.71 | 115.72 | AD1-020 | PN_P1-2_PN-115-094_A_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220964 | GRACETON | 220999 | BAGLEY2 | 13 | 230 | 232 | 1795 | 114.01 | 115.09 | AD1-020 | BG_P4_5_GRCTN_3T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200504 | 26CARLISLE | 200520 | 26ROXBURY | 1 | 115 | 226 | 190 | 104.57 | 114.9 | AD1-020 | PN_P2-3_PN-115-58B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200504 | 26CARLISLE | 200520 | 26ROXBURY | 1 | 115 | 226 | 190 | 105.22 | 114.85 | AD1-020 | PN_P2-2_PN-115-030_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200504 | 26CARLISLE | 200520 | 26ROXBURY | 1 | 115 | 226 | 190 | 105.22 | 114.85 | AD1-020 | PN_P1-3_PN-115-040_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200504 | 26CARLISLE | 200520 | 26ROXBURY | 1 | 115 | 226 | 190 | 104.38 | 114.84 | AD1-020 | PN_P1-2_PN-115-094_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204539 | 27HUNTRSTN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 334 | 115.07 | 114.56 | AD1-020 | ME_P1-2_ME-115-061_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204539 | 27HUNTRSTN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 334 | 115.07 | 114.56 | AD1-020 | ME_P2-3_ME-115-019A-A_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 115.34 | 114.19 | AD1-020 | BG_P4_5_CNSTN_14_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204512 | 27S.RDG | 204693 | 27BOONETOWN | 1 | 230 | 227 | 607 | 105.5 | 113.76 | AD1-020 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 204529 | 27GERMANTN | 1 | 138/115 | 227 | 453 | 109.65 | 112.77 | AD1-020 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 204529 | 27GERMANTN | 1 | 138/115 | 227 | 453 | 109.65 | 112.77 | AD1-020 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 204529 | 27GERMANTN | 1 | 138/115 | 227 | 453 | 109.65 | 112.76 | AD1-020 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 204529 | 27GERMANTN | 1 | 138/115 | 227 | 453 | 109.5 | 112.6 | AD1-020 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200532 | 26ROXBURY | 203981 | AD2-062_POI | 1 | 138 | 226 | 317 | 114.85 | 112.38 | AD1-020 | ME_P1-2_ME-115-240T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200504 | 26CARLISLE | 200520 | 26ROXBURY | 1 | 115 | 226 | 190 | 95.57 | 112.03 | AD1-020 | PN_P2-3_PN-115-0331-B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 107.04 | 111.95 | AD1-020 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220980 | RAPHAEL | 220999 | BAGLEY2 | 13 | 230 | 232 | 1795 | 109.58 | 111.85 | AD1-020 | BG_P4_5_GRCTN_3T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 106.91 | 111.81 | AD1-020 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 793 | 114.23 | 111.6 | AD1-020 | PEPCO_P4_PP19_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2901 | 145.27 | 147.48 | SEWAREN_IM | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200504 | 26CARLISLE | 200520 | 26ROXBURY | 1 | 115 | 226 | 190 | 102.08 | 110.59 | AD1-020 | PN_P2-3_PN-230-0014-12_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200504 | 26CARLISLE | 200520 | 26ROXBURY | 1 | 115 | 226 | 190 | 102.07 | 110.17 | AD1-020 | PN_P1-3_PN-230-020A_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200504 | 26CARLISLE | 200520 | 26ROXBURY | 1 | 115 | 226 | 190 | 102.07 | 110.17 | AD1-020 | PN_P2-3_PN-230-0014-11_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200504 | 26CARLISLE | 200520 | 26ROXBURY | 1 | 115 | 226 | 190 | 102 | 110.15 | AD1-020 | PN_P2-2_PN-115-031_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2901 | 144.85 | 146.99 | T126 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200009 | JUNI | 208004 | JUNI | 2 | 500/230 | 225/229 | 1040 | 107.42 | 106.86 | AD1-020 | PL_10_P42_000140_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 204529 | 27GERMANTN | 1 | 138/115 | 227 | 453 | 103.8 | 105.57 | AD1-020 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 204529 | 27GERMANTN | 1 | 138/115 | 227 | 453 | 100.31 | 105.15 | AD1-020 | AP_P2-3_PE-500-016_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 204529 | 27GERMANTN | 1 | 138/115 | 227 | 453 | 100.39 | 105.09 | AD1-020 | AP_P2-3_PE-500-015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200099 | LAUS | 208045 | LAUS | 3 | 500/230 | 225/229 | 1200 | 103.05 | 104.77 | AD1-020 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200099 | LAUS | 208045 | LAUS | 3 | 500/230 | 225/229 | 1200 | 102.75 | 104.22 | AD1-020 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200099 | LAUS | 208045 | LAUS | 3 | 500/230 | 225/229 | 1200 | 102.75 | 104.22 | AD1-020 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200099 | LAUS | 208045 | LAUS | 3 | 500/230 | 225/229 | 1200 | 102.74 | 104.21 | AD1-020 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 100.07 | 104.07 | AD1-020 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 100.06 | 104.07 | AD1-020 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 100.07 | 104.07 | AD1-020 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220964 | GRACETON | 221000 | BAGLEY | 5 | 230 | 232 | 1795 | 102.02 | 102.8 | AD1-020 | BG_P1_2313_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220964 | GRACETON | 220999 | BAGLEY2 | 13 | 230 | 232 | 1795 | 102.02 | 102.8 | AD1-020 | BG_P1_2305_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 99.15 | 102.77 | AD1-020 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 99.24 | 101.37 | AD1-020 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204539 | 27HUNTRSTN | 204550 | 27ORRTANNA | 1 | 115 | 227 | 264 | 103 | 101.21 | AD1-020 | ME_P1-2_ME-115-067_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204520 | 27ALLEN | 208142 | WIGR-115 | 1 | 115 | 227/229 | 351.4 | 93.04 | 100.3 | AD1-020 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204520 | 27ALLEN | 208142 | WIGR-115 | 1 | 115 | 227/229 | 351.4 | 93.04 | 100.3 | AD1-020 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204520 | 27ALLEN | 208142 | WIGR-115 | 1 | 115 | 227/229 | 351.4 | 93.04 | 100.3 | AD1-020 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204520 | 27ALLEN | 208142 | WIGR-115 | 1 | 115 | 227/229 | 351.4 | 92.81 | 100.15 | AD1-020 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2901 | 144.86 | 146.99 | T127 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 153.67 | 158.15 | AD1-022 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.16 | 157.29 | AD1-022 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.16 | 157.29 | AD1-022 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 151.98 | 156.83 | AD1-022 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 161.66 | 154.44 | AD1-022 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 148.62 | 153.17 | AD1-022 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 155.74 | 150.59 | AD1-022 | PN_P1-2_PN-500-010T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.46 | 149.56 | AD1-022 | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.39 | 149.48 | AD1-022 | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.08 | 148.31 | AD1-022 | AP_P2-3_PE-500-016_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.14 | 148.28 | AD1-022 | AP_P2-3_PE-500-015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.05 | 147.92 | AD1-022 | PJM_500_BG_P4_5_CNSTN_L_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.34 | 147.9 | AD1-022 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.14 | 147.72 | AD1-022 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.17 | 147.7 | AD1-022 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.9 | 147.51 | AD1-022 | PECO_P4_NOTTI85_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.84 | 147.49 | AD1-022 | PECO_P1-2_220-08_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.26 | 147.43 | AD1-022 | AP_P1-2_WP-500-DRT17_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.26 | 147.43 | AD1-022 | AP_P1-2_PE-500-001_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.77 | 147.43 | AD1-022 | PECO_P4_COOPR125_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.21 | 147.36 | AD1-022 | AP_P2-3_PE-500-018C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2901 | 144.87 | 147.01 | T157 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.88 | 144.17 | AD1-022 | PECO_P4_PEACH025_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.74 | 144.07 | AD1-022 | PECO_P1-2_PBTIE1_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 139.12 | 133.18 | AD1-022 | PECO_P4_PEACH205_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 139.01 | 132.86 | AD1-022 | PECO_P1-2_PBTIE2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 138.07 | 131.98 | AD1-022 | PECO_P4_PEACH055_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 133.38 | 127.56 | AD1-022 | PECO_P4_PEACH015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 128.76 | 127.02 | AD1-022 | DVP_P4-2: 514T595_SRT-SW |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 132.06 | 126.24 | AD1-022 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 127.01 | 125.3 | AD1-022 | DVP_P4-2: 51482_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 127.01 | 125.21 | AD1-022 | DVP_P1-2: LN 514_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 127.01 | 125.21 | AD1-022 | AP_P1-2_PE-500-407T_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 122.96 | 117.59 | AD1-022 | PECO_P4_PEACH225_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 117.21 | 115.29 | AD1-022 | AP_P2-3_PE-500-019C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 225.37 | 236.63 | AD1-025 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 223.37 | 236.63 | AD1-025 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 225.31 | 236.57 | AD1-025 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 223.31 | 236.57 | AD1-025 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 225.31 | 236.57 | AD1-025 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 223.31 | 236.57 | AD1-025 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 213.33 | 226.48 | AD1-025 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 213.27 | 226.42 | AD1-025 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 213.27 | 226.42 | AD1-025 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 209.07 | 223.27 | AD1-025 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 209.01 | 223.21 | AD1-025 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 209.01 | 223.21 | AD1-025 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 210.47 | 217.51 | AD1-025 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 208.47 | 217.5 | AD1-025 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 198.94 | 207.95 | AD1-025 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 194.69 | 204.6 | AD1-025 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 172.59 | 167.61 | AD1-025 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 171.62 | 166.17 | AD1-025 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 171.62 | 166.17 | AD1-025 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 171.6 | 166.16 | AD1-025 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 163.45 | 164.68 | AD1-025 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2901 | 144.74 | 146.86 | TOP CROP | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 161.59 | 161.6 | AD1-025 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 161.59 | 161.6 | AD1-025 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 161.58 | 161.6 | AD1-025 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 163.68 | 158.7 | AD1-025 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 153.37 | 157.79 | AD1-025 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 161.88 | 157 | AD1-025 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 161.88 | 157 | AD1-025 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 151.69 | 156.47 | AD1-025 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 161.33 | 154.12 | AD1-025 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 148.33 | 152.82 | AD1-025 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 903 | 144.11 | 151.91 | AD1-025 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 152.65 | 150.99 | AD1-025 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 155.46 | 150.31 | AD1-025 | PN_P1-2_PN-500-010T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 903 | 142.59 | 149.29 | AD1-025 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 903 | 142.59 | 149.29 | AD1-025 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 903 | 142.57 | 149.28 | AD1-025 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.17 | 149.22 | AD1-025 | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.1 | 149.15 | AD1-025 | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.79 | 147.96 | AD1-025 | AP_P2-3_PE-500-016_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.86 | 147.93 | AD1-025 | AP_P2-3_PE-500-015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.77 | 147.64 | AD1-025 | PJM_500_BG_P4_5_CNSTN_L_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.06 | 147.63 | AD1-025 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.85 | 147.44 | AD1-025 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.88 | 147.42 | AD1-025 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.61 | 147.23 | AD1-025 | PECO_P4_NOTTI85_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.55 | 147.21 | AD1-025 | PECO_P1-2_220-08_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.48 | 147.15 | AD1-025 | PECO_P4_COOPR125_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 142.97 | 147.08 | AD1-025 | AP_P1-2_PE-500-001_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 142.97 | 147.08 | AD1-025 | AP_P1-2_WP-500-DRT17_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 142.92 | 147.02 | AD1-025 | AP_P2-3_PE-500-018C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2901 | 144.62 | 146.72 | TWINGROVE | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.56 | 143.87 | AD1-025 | PECO_P4_PEACH025_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.4 | 143.74 | AD1-025 | PECO_P1-2_PBTIE1_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 911 | 148.84 | 142.97 | AD1-025 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 911 | 147.89 | 141.66 | AD1-025 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 911 | 147.89 | 141.65 | AD1-025 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 911 | 147.87 | 141.65 | AD1-025 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204502 | 27JACKSON | 204514 | 27TMI | 1 | 230 | 227 | 781 | 132.94 | 141.42 | AD1-025 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204502 | 27JACKSON | 204514 | 27TMI | 1 | 230 | 227 | 781 | 132.94 | 141.42 | AD1-025 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204502 | 27JACKSON | 204514 | 27TMI | 1 | 230 | 227 | 781 | 132.93 | 141.41 | AD1-025 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 903 | 135.51 | 139.44 | AD1-025 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 1031 | 130.72 | 138.98 | AD1-025 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 1031 | 130.23 | 137.91 | AD1-025 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 1031 | 130.23 | 137.91 | AD1-025 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 1031 | 130.22 | 137.91 | AD1-025 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 911 | 140.02 | 134.91 | AD1-025 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 138.81 | 132.88 | AD1-025 | PECO_P4_PEACH205_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 207923 | BRISREAC | 208132 | WHEM TR1 | 1 | 230 | 229 | 676 | 124.19 | 132.73 | AD1-025 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 207922 | BRIS | 207923 | BRISREAC | RX | 230 | 229 | 676 | 124.19 | 132.73 | AD1-025 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 138.69 | 132.56 | AD1-025 | PECO_P1-2_PBTIE2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208078 | SAKR | 1 | 230 | 229 | 903 | 124.39 | 132.32 | AD1-025 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208078 | SAKR | 1 | 230 | 229 | 903 | 124.39 | 132.32 | AD1-025 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208078 | SAKR | 1 | 230 | 229 | 903 | 124.38 | 132.32 | AD1-025 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 137.77 | 131.7 | AD1-025 | PECO_P4_PEACH055_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204502 | 27JACKSON | 204514 | 27TMI | 1 | 230 | 227 | 781 | 125.3 | 130.87 | AD1-025 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 1031 | 124.63 | 129.13 | AD1-025 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 133.05 | 127.24 | AD1-025 | PECO_P4_PEACH015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 128.19 | 126.48 | AD1-025 | DVP_P4-2: 514T595_SRT-SW |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 131.75 | 125.94 | AD1-025 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220953 | HOWARD12 | 220972 | GRANITE1 | 1 | 230 | 232 | 772 | 129.5 | 125.53 | AD1-025 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220954 | HOWARD32 | 220973 | GRANITE6 | 1 | 230 | 232 | 772 | 128.36 | 124.84 | AD1-025 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 126.43 | 124.69 | AD1-025 | DVP_P4-2: 51482_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 793 | 126.41 | 124.66 | AD1-025 | DVP_P4-2: 514T595_SRT-SW |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 2 | 230 | 233 | 793 | 126.41 | 124.66 | AD1-025 | DVP_P4-2: 514T595_SRT-SW |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 126.43 | 124.6 | AD1-025 | DVP_P1-2: LN 514_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 126.43 | 124.6 | AD1-025 | AP_P1-2_PE-500-407T_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220953 | HOWARD12 | 220972 | GRANITE1 | 1 | 230 | 232 | 772 | 128.59 | 124.56 | AD1-025 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220953 | HOWARD12 | 220972 | GRANITE1 | 1 | 230 | 232 | 772 | 128.59 | 124.56 | AD1-025 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208020 | MANO TR3 | 1 | 230 | 229 | 793 | 111.38 | 124.5 | AD1-025 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208020 | MANO TR3 | 1 | 230 | 229 | 793 | 111.37 | 124.5 | AD1-025 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208020 | MANO TR3 | 1 | 230 | 229 | 793 | 111.38 | 124.5 | AD1-025 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220954 | HOWARD32 | 220973 | GRANITE6 | 1 | 230 | 232 | 772 | 127.57 | 124 | AD1-025 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220954 | HOWARD32 | 220973 | GRANITE6 | 1 | 230 | 232 | 772 | 127.57 | 124 | AD1-025 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 793 | 125.16 | 123.4 | AD1-025 | DVP_P4-2: 51482_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 2 | 230 | 233 | 793 | 125.16 | 123.4 | AD1-025 | DVP_P4-2: 51482_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 2 | 230 | 233 | 793 | 125.16 | 123.32 | AD1-025 | AP_P1-2_PE-500-407T_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 793 | 125.16 | 123.32 | AD1-025 | AP_P1-2_PE-500-407T_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 793 | 125.16 | 123.32 | AD1-025 | DVP_P1-2: LN 514_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 2 | 230 | 233 | 793 | 125.16 | 123.32 | AD1-025 | DVP_P1-2: LN 514_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208078 | SAKR | 1 | 230 | 229 | 903 | 117.12 | 122.35 | AD1-025 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200025 | W CHAPEL | 1 | 500 | 225 | 1732 | 123.52 | 121.73 | AD1-025 | PEPCO_P4_PP41_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208031 | MLWD TR2 | 1 | 230 | 229 | 911 | 111.69 | 121.07 | AD1-025 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208031 | MLWD TR2 | 1 | 230 | 229 | 911 | 111.68 | 121.07 | AD1-025 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208031 | MLWD TR2 | 1 | 230 | 229 | 911 | 111.69 | 121.07 | AD1-025 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220965 | NEAST339 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 119.68 | 119.03 | AD1-025 | BG_P1_2315_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220965 | NEAST339 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 119.26 | 118.82 | AD1-025 | BG_P4_5_NEAST_17_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220965 | NEAST339 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 119.42 | 118.82 | AD1-025 | BG_P4_5_NEAST_15_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 114.63 | 118.31 | AD1-025 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220979 | NEAST317 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 118.76 | 118.16 | AD1-025 | BG_P1_2337_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 114.29 | 117.98 | AD1-025 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 114.28 | 117.91 | AD1-025 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 114.28 | 117.91 | AD1-025 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220979 | NEAST317 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 118.43 | 117.89 | AD1-025 | BG_P4_5_NEAST_39_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220979 | NEAST317 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 118.43 | 117.89 | AD1-025 | BG_P4_5_NEAST_37_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 113.94 | 117.58 | AD1-025 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 113.94 | 117.58 | AD1-025 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 122.65 | 117.29 | AD1-025 | PECO_P4_PEACH225_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 793 | 118.5 | 115.72 | AD1-025 | PEPCO_P1_PP2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 2 | 230 | 233 | 793 | 118.5 | 115.72 | AD1-025 | PEPCO_P1_PP1_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 2 | 500/230 | 225/232 | 2168 | 109.59 | 114.89 | AD1-025 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 116.65 | 114.69 | AD1-025 | AP_P2-3_PE-500-019C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 2 | 500/230 | 225/232 | 2168 | 109.41 | 114.67 | AD1-025 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 2 | 500/230 | 225/232 | 2168 | 109.41 | 114.67 | AD1-025 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 1 | 500/230 | 225/232 | 2168 | 109.36 | 114.65 | AD1-025 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 1 | 500/230 | 225/232 | 2168 | 109.18 | 114.43 | AD1-025 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 1 | 500/230 | 225/232 | 2168 | 109.18 | 114.43 | AD1-025 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220964 | GRACETON | 220999 | BAGLEY2 | 13 | 230 | 232 | 1795 | 113.36 | 114.4 | AD1-025 | BG_P4_5_GRCTN_3T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208020 | MANO TR3 | 1 | 230 | 229 | 793 | 104.19 | 113.93 | AD1-025 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208020 | MANO TR3 | 208031 | MLWD TR2 | 1 | 230 | 229 | 903 | 102.51 | 113.63 | AD1-025 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208020 | MANO TR3 | 208031 | MLWD TR2 | 1 | 230 | 229 | 903 | 101.8 | 112.44 | AD1-025 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208020 | MANO TR3 | 208031 | MLWD TR2 | 1 | 230 | 229 | 903 | 101.8 | 112.44 | AD1-025 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208020 | MANO TR3 | 208031 | MLWD TR2 | 1 | 230 | 229 | 903 | 101.8 | 112.44 | AD1-025 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 2 | 500/230 | 225/232 | 2168 | 108.46 | 111.75 | AD1-025 | PJM_500_BG_P4_5_CNSTN_15_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208031 | MLWD TR2 | 1 | 230 | 229 | 911 | 104.93 | 111.59 | AD1-025 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 106.41 | 111.17 | AD1-025 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220980 | RAPHAEL | 220999 | BAGLEY2 | 13 | 230 | 232 | 1795 | 108.95 | 111.15 | AD1-025 | BG_P4_5_GRCTN_3T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 106.29 | 111.04 | AD1-025 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 793 | 112.63 | 109.97 | AD1-025 | PEPCO_P4_PP19_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 2 | 230 | 233 | 793 | 109.39 | 107.46 | AD1-025 | AP_P2-3_PE-500-019C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 793 | 109.39 | 107.46 | AD1-025 | AP_P2-3_PE-500-019C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220965 | NEAST339 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 108.24 | 106.81 | AD1-025 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220965 | NEAST339 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 108.14 | 106.7 | AD1-025 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220965 | NEAST339 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 108.14 | 106.7 | AD1-025 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 101.53 | 105.69 | AD1-025 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 101.45 | 105.6 | AD1-025 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220979 | NEAST317 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 105.13 | 103.77 | AD1-025 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220979 | NEAST317 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 105.03 | 103.65 | AD1-025 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220979 | NEAST317 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 105.03 | 103.65 | AD1-025 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 99.44 | 103.3 | AD1-025 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 99.44 | 103.3 | AD1-025 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 99.44 | 103.3 | AD1-025 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208020 | MANO TR3 | 208031 | MLWD TR2 | 1 | 230 | 229 | 903 | 95.43 | 103.21 | AD1-025 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220964 | GRACETON | 221000 | BAGLEY | 5 | 230 | 232 | 1795 | 101.42 | 102.17 | AD1-025 | BG_P1_2313_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220964 | GRACETON | 220999 | BAGLEY2 | 13 | 230 | 232 | 1795 | 101.43 | 102.17 | AD1-025 | BG_P1_2305_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220965 | NEAST339 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 102.67 | 101.99 | AD1-025 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 98.51 | 101.97 | AD1-025 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 98.61 | 100.62 | AD1-025 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2901 | 144.82 | 146.96 | U2-072 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 153.7 | 158.18 | AD1-033 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.2 | 157.32 | AD1-033 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.19 | 157.32 | AD1-033 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 152.01 | 156.86 | AD1-033 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 161.7 | 154.47 | AD1-033 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 148.65 | 153.21 | AD1-033 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 155.77 | 150.62 | AD1-033 | PN_P1-2_PN-500-010T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.49 | 149.59 | AD1-033 | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.42 | 149.52 | AD1-033 | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.11 | 148.34 | AD1-033 | AP_P2-3_PE-500-016_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.17 | 148.31 | AD1-033 | AP_P2-3_PE-500-015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.08 | 147.95 | AD1-033 | PJM_500_BG_P4_5_CNSTN_L_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.38 | 147.94 | AD1-033 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.17 | 147.75 | AD1-033 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.2 | 147.74 | AD1-033 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.93 | 147.54 | AD1-033 | PECO_P4_NOTTI85_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.87 | 147.53 | AD1-033 | PECO_P1-2_220-08_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.28 | 147.46 | AD1-033 | AP_P1-2_PE-500-001_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.28 | 147.46 | AD1-033 | AP_P1-2_WP-500-DRT17_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.8 | 147.46 | AD1-033 | PECO_P4_COOPR125_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.23 | 147.39 | AD1-033 | AP_P2-3_PE-500-018C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2901 | 144.88 | 147.02 | U2-073 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.92 | 144.21 | AD1-033 | PECO_P4_PEACH025_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.78 | 144.1 | AD1-033 | PECO_P1-2_PBTIE1_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 139.15 | 133.21 | AD1-033 | PECO_P4_PEACH205_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 139.04 | 132.89 | AD1-033 | PECO_P1-2_PBTIE2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 138.1 | 132.01 | AD1-033 | PECO_P4_PEACH055_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 133.42 | 127.6 | AD1-033 | PECO_P4_PEACH015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 128.8 | 127.06 | AD1-033 | DVP_P4-2: 514T595_SRT-SW |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 132.09 | 126.27 | AD1-033 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 127.05 | 125.34 | AD1-033 | DVP_P4-2: 51482_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 127.05 | 125.25 | AD1-033 | DVP_P1-2: LN 514_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 127.05 | 125.25 | AD1-033 | AP_P1-2_PE-500-407T_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 123 | 117.62 | AD1-033 | PECO_P4_PEACH225_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 117.25 | 115.33 | AD1-033 | AP_P2-3_PE-500-019C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2901 | 144.86 | 147 | U2-090 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 153.77 | 158.27 | AD1-041 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.27 | 157.39 | AD1-041 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.26 | 157.39 | AD1-041 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 152.08 | 156.95 | AD1-041 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 161.78 | 154.55 | AD1-041 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 148.72 | 153.3 | AD1-041 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 155.84 | 150.68 | AD1-041 | PN_P1-2_PN-500-010T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.56 | 149.67 | AD1-041 | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.49 | 149.6 | AD1-041 | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.17 | 148.42 | AD1-041 | AP_P2-3_PE-500-016_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.24 | 148.4 | AD1-041 | AP_P2-3_PE-500-015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.15 | 148.02 | AD1-041 | PJM_500_BG_P4_5_CNSTN_L_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.45 | 148.01 | AD1-041 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.25 | 147.82 | AD1-041 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.27 | 147.81 | AD1-041 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153 | 147.61 | AD1-041 | PECO_P4_NOTTI85_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.94 | 147.6 | AD1-041 | PECO_P1-2_220-08_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.35 | 147.54 | AD1-041 | AP_P1-2_WP-500-DRT17_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.35 | 147.54 | AD1-041 | AP_P1-2_PE-500-001_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.87 | 147.53 | AD1-041 | PECO_P4_COOPR125_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.3 | 147.47 | AD1-041 | AP_P2-3_PE-500-018C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2901 | 144.74 | 146.87 | U3-002 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 151 | 144.29 | AD1-041 | PECO_P4_PEACH025_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.86 | 144.19 | AD1-041 | PECO_P1-2_PBTIE1_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 139.23 | 133.29 | AD1-041 | PECO_P4_PEACH205_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 139.12 | 132.97 | AD1-041 | PECO_P1-2_PBTIE2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 138.18 | 132.09 | AD1-041 | PECO_P4_PEACH055_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 133.5 | 127.68 | AD1-041 | PECO_P4_PEACH015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 128.92 | 127.18 | AD1-041 | DVP_P4-2: 514T595_SRT-SW |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 132.17 | 126.34 | AD1-041 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 127.17 | 125.47 | AD1-041 | DVP_P4-2: 51482_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 127.17 | 125.37 | AD1-041 | DVP_P1-2: LN 514_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 127.17 | 125.37 | AD1-041 | AP_P1-2_PE-500-407T_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 123.07 | 117.7 | AD1-041 | PECO_P4_PEACH225_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 117.37 | 115.45 | AD1-041 | AP_P2-3_PE-500-019C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 225.58 | 237.11 | AD1-070 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 223.58 | 237.11 | AD1-070 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 225.52 | 237.05 | AD1-070 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 223.51 | 237.05 | AD1-070 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 225.52 | 237.04 | AD1-070 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 223.51 | 237.04 | AD1-070 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 213.53 | 226.95 | AD1-070 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 213.46 | 226.89 | AD1-070 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 213.46 | 226.88 | AD1-070 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 209.27 | 223.74 | AD1-070 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 209.21 | 223.68 | AD1-070 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 209.21 | 223.67 | AD1-070 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 208.69 | 217.92 | AD1-070 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 210.69 | 217.92 | AD1-070 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 199.15 | 208.35 | AD1-070 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 194.89 | 205 | AD1-070 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 172.85 | 167.92 | AD1-070 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 161.83 | 161.99 | AD1-070 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 161.83 | 161.99 | AD1-070 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 161.82 | 161.98 | AD1-070 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2901 | 144.85 | 146.99 | V3-007 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 153.65 | 158.14 | AD1-070 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.09 | 157.22 | AD1-070 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.09 | 157.22 | AD1-070 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 151.97 | 156.81 | AD1-070 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 161.49 | 154.28 | AD1-070 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 148.6 | 153.16 | AD1-070 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 155.67 | 150.52 | AD1-070 | PN_P1-2_PN-500-010T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.44 | 149.54 | AD1-070 | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.37 | 149.47 | AD1-070 | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.1 | 148.37 | AD1-070 | AP_P2-3_PE-500-016_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.17 | 148.34 | AD1-070 | AP_P2-3_PE-500-015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.98 | 147.86 | AD1-070 | PJM_500_BG_P4_5_CNSTN_L_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.18 | 147.75 | AD1-070 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.98 | 147.57 | AD1-070 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.01 | 147.55 | AD1-070 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.28 | 147.49 | AD1-070 | AP_P1-2_WP-500-DRT17_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.28 | 147.49 | AD1-070 | AP_P1-2_PE-500-001_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.23 | 147.42 | AD1-070 | AP_P2-3_PE-500-018C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.74 | 147.36 | AD1-070 | PECO_P4_NOTTI85_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.68 | 147.34 | AD1-070 | PECO_P1-2_220-08_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.61 | 147.28 | AD1-070 | PECO_P4_COOPR125_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2901 | 144.53 | 146.62 | V3-028 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.66 | 143.96 | AD1-070 | PECO_P4_PEACH025_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.57 | 143.91 | AD1-070 | PECO_P1-2_PBTIE1_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 911 | 149.1 | 143.26 | AD1-070 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 138.99 | 133.06 | AD1-070 | PECO_P4_PEACH205_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 138.86 | 132.71 | AD1-070 | PECO_P1-2_PBTIE2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 137.93 | 131.84 | AD1-070 | PECO_P4_PEACH055_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 133.23 | 127.42 | AD1-070 | PECO_P4_PEACH015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 131.92 | 126.1 | AD1-070 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208020 | MANO TR3 | 1 | 230 | 229 | 793 | 111.54 | 124.76 | AD1-070 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208020 | MANO TR3 | 1 | 230 | 229 | 793 | 111.54 | 124.76 | AD1-070 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208020 | MANO TR3 | 1 | 230 | 229 | 793 | 111.54 | 124.76 | AD1-070 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 122.82 | 117.46 | AD1-070 | PECO_P4_PEACH225_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2901 | 145.24 | 147.44 | W1-003 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 153.71 | 158.2 | AD1-082 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.21 | 157.33 | AD1-082 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.2 | 157.33 | AD1-082 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 152.02 | 156.88 | AD1-082 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 161.71 | 154.48 | AD1-082 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 148.66 | 153.22 | AD1-082 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 155.78 | 150.63 | AD1-082 | PN_P1-2_PN-500-010T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.5 | 149.6 | AD1-082 | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.43 | 149.53 | AD1-082 | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.12 | 148.35 | AD1-082 | AP_P2-3_PE-500-016_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.18 | 148.33 | AD1-082 | AP_P2-3_PE-500-015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.09 | 147.96 | AD1-082 | PJM_500_BG_P4_5_CNSTN_L_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.38 | 147.95 | AD1-082 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.18 | 147.76 | AD1-082 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.21 | 147.75 | AD1-082 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.94 | 147.55 | AD1-082 | PECO_P4_NOTTI85_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.88 | 147.54 | AD1-082 | PECO_P1-2_220-08_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.3 | 147.48 | AD1-082 | AP_P1-2_PE-500-001_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.3 | 147.48 | AD1-082 | AP_P1-2_WP-500-DRT17_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.81 | 147.47 | AD1-082 | PECO_P4_COOPR125_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.25 | 147.41 | AD1-082 | AP_P2-3_PE-500-018C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2901 | 145.24 | 147.44 | W1-004 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.93 | 144.22 | AD1-082 | PECO_P4_PEACH025_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.79 | 144.12 | AD1-082 | PECO_P1-2_PBTIE1_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 139.16 | 133.22 | AD1-082 | PECO_P4_PEACH205_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 139.06 | 132.9 | AD1-082 | PECO_P1-2_PBTIE2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 138.11 | 132.02 | AD1-082 | PECO_P4_PEACH055_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 133.43 | 127.61 | AD1-082 | PECO_P4_PEACH015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 128.82 | 127.08 | AD1-082 | DVP_P4-2: 514T595_SRT-SW |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 132.1 | 126.28 | AD1-082 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 127.08 | 125.37 | AD1-082 | DVP_P4-2: 51482_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 127.08 | 125.27 | AD1-082 | DVP_P1-2: LN 514_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 127.08 | 125.27 | AD1-082 | AP_P1-2_PE-500-407T_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 123.01 | 117.63 | AD1-082 | PECO_P4_PEACH225_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 117.27 | 115.36 | AD1-082 | AP_P2-3_PE-500-019C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 225.68 | 237.14 | AD1-083 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 223.68 | 237.14 | AD1-083 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 225.62 | 237.08 | AD1-083 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 223.61 | 237.08 | AD1-083 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 225.62 | 237.08 | AD1-083 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 223.61 | 237.08 | AD1-083 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 213.62 | 226.98 | AD1-083 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 213.56 | 226.92 | AD1-083 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 213.56 | 226.92 | AD1-083 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 209.36 | 223.77 | AD1-083 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 209.3 | 223.71 | AD1-083 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 209.3 | 223.71 | AD1-083 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 210.78 | 217.93 | AD1-083 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 208.77 | 217.93 | AD1-083 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 199.23 | 208.37 | AD1-083 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 194.97 | 205.02 | AD1-083 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 172.83 | 167.85 | AD1-083 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 163.7 | 165.02 | AD1-083 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2901 | 145.24 | 147.44 | W1-005 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 161.84 | 161.92 | AD1-083 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 161.83 | 161.92 | AD1-083 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 161.82 | 161.91 | AD1-083 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 153.59 | 158.04 | AD1-083 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.08 | 157.2 | AD1-083 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.08 | 157.2 | AD1-083 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 151.9 | 156.72 | AD1-083 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 161.56 | 154.34 | AD1-083 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 148.54 | 153.07 | AD1-083 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 155.66 | 150.51 | AD1-083 | PN_P1-2_PN-500-010T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 903 | 142.8 | 149.62 | AD1-083 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 903 | 142.8 | 149.62 | AD1-083 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 903 | 142.78 | 149.61 | AD1-083 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.38 | 149.46 | AD1-083 | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.31 | 149.39 | AD1-083 | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144 | 148.21 | AD1-083 | AP_P2-3_PE-500-016_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.06 | 148.18 | AD1-083 | AP_P2-3_PE-500-015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.97 | 147.84 | AD1-083 | PJM_500_BG_P4_5_CNSTN_L_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.26 | 147.82 | AD1-083 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.05 | 147.63 | AD1-083 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.08 | 147.62 | AD1-083 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.81 | 147.42 | AD1-083 | PECO_P4_NOTTI85_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.75 | 147.41 | AD1-083 | PECO_P1-2_220-08_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.68 | 147.34 | AD1-083 | PECO_P4_COOPR125_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.18 | 147.33 | AD1-083 | AP_P1-2_PE-500-001_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.18 | 147.33 | AD1-083 | AP_P1-2_WP-500-DRT17_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.13 | 147.27 | AD1-083 | AP_P2-3_PE-500-018C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2901 | 145.24 | 147.44 | W1-006 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.78 | 144.08 | AD1-083 | PECO_P4_PEACH025_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.64 | 143.97 | AD1-083 | PECO_P1-2_PBTIE1_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 911 | 149.06 | 143.19 | AD1-083 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 1031 | 130.38 | 138.19 | AD1-083 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 1031 | 130.38 | 138.19 | AD1-083 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 1031 | 130.37 | 138.19 | AD1-083 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 139.03 | 133.09 | AD1-083 | PECO_P4_PEACH205_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 138.91 | 132.76 | AD1-083 | PECO_P1-2_PBTIE2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208078 | SAKR | 1 | 230 | 229 | 903 | 124.57 | 132.64 | AD1-083 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 137.98 | 131.9 | AD1-083 | PECO_P4_PEACH055_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 133.28 | 127.46 | AD1-083 | PECO_P4_PEACH015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 128.88 | 127.17 | AD1-083 | DVP_P4-2: 514T595_SRT-SW |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 131.97 | 126.15 | AD1-083 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 127.14 | 125.45 | AD1-083 | DVP_P4-2: 51482_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 127.14 | 125.31 | AD1-083 | AP_P1-2_PE-500-407T_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 127.14 | 125.31 | AD1-083 | DVP_P1-2: LN 514_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208020 | MANO TR3 | 1 | 230 | 229 | 793 | 111.56 | 124.74 | AD1-083 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208020 | MANO TR3 | 1 | 230 | 229 | 793 | 111.56 | 124.74 | AD1-083 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208020 | MANO TR3 | 1 | 230 | 229 | 793 | 111.56 | 124.74 | AD1-083 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200025 | W CHAPEL | 1 | 500 | 225 | 1732 | 123.78 | 121.98 | AD1-083 | PEPCO_P4_PP41_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 122.87 | 117.5 | AD1-083 | PECO_P4_PEACH225_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 117.33 | 115.44 | AD1-083 | AP_P2-3_PE-500-019C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 2 | 500/230 | 225/232 | 2168 | 109.71 | 115.03 | AD1-083 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 2 | 500/230 | 225/232 | 2168 | 109.53 | 114.82 | AD1-083 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 2 | 500/230 | 225/232 | 2168 | 109.53 | 114.82 | AD1-083 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 1 | 500/230 | 225/232 | 2168 | 109.48 | 114.79 | AD1-083 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 1 | 500/230 | 225/232 | 2168 | 109.3 | 114.57 | AD1-083 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 1 | 500/230 | 225/232 | 2168 | 109.3 | 114.57 | AD1-083 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 99.56 | 103.5 | AD1-083 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 99.56 | 103.5 | AD1-083 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 99.56 | 103.49 | AD1-083 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 98.63 | 102.17 | AD1-083 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 98.73 | 100.79 | AD1-083 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2901 | 144.59 | 146.69 | W1-029 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 153.74 | 158.24 | AD1-087 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.24 | 157.36 | AD1-087 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.23 | 157.36 | AD1-087 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 152.06 | 156.91 | AD1-087 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 161.74 | 154.51 | AD1-087 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 148.69 | 153.26 | AD1-087 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 155.81 | 150.65 | AD1-087 | PN_P1-2_PN-500-010T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.53 | 149.64 | AD1-087 | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.46 | 149.57 | AD1-087 | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.15 | 148.4 | AD1-087 | AP_P2-3_PE-500-016_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.21 | 148.37 | AD1-087 | AP_P2-3_PE-500-015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.12 | 147.99 | AD1-087 | PJM_500_BG_P4_5_CNSTN_L_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.41 | 147.97 | AD1-087 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.21 | 147.79 | AD1-087 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.24 | 147.77 | AD1-087 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.97 | 147.58 | AD1-087 | PECO_P4_NOTTI85_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.91 | 147.56 | AD1-087 | PECO_P1-2_220-08_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.33 | 147.52 | AD1-087 | AP_P1-2_WP-500-DRT17_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.33 | 147.52 | AD1-087 | AP_P1-2_PE-500-001_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.84 | 147.5 | AD1-087 | PECO_P4_COOPR125_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.28 | 147.45 | AD1-087 | AP_P2-3_PE-500-018C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2901 | 144.72 | 146.84 | W4-005 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.96 | 144.25 | AD1-087 | PECO_P4_PEACH025_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.82 | 144.15 | AD1-087 | PECO_P1-2_PBTIE1_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 139.19 | 133.25 | AD1-087 | PECO_P4_PEACH205_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 139.09 | 132.93 | AD1-087 | PECO_P1-2_PBTIE2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 138.14 | 132.05 | AD1-087 | PECO_P4_PEACH055_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 133.46 | 127.64 | AD1-087 | PECO_P4_PEACH015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 128.91 | 127.17 | AD1-087 | DVP_P4-2: 514T595_SRT-SW |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 132.13 | 126.31 | AD1-087 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 127.16 | 125.46 | AD1-087 | DVP_P4-2: 51482_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 127.16 | 125.36 | AD1-087 | DVP_P1-2: LN 514_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 127.16 | 125.36 | AD1-087 | AP_P1-2_PE-500-407T_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 123.04 | 117.66 | AD1-087 | PECO_P4_PEACH225_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 117.36 | 115.45 | AD1-087 | AP_P2-3_PE-500-019C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 223.64 | 237.09 | AD1-088 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 225.65 | 237.09 | AD1-088 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 223.58 | 237.03 | AD1-088 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 225.58 | 237.03 | AD1-088 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 223.57 | 237.03 | AD1-088 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 225.58 | 237.03 | AD1-088 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 213.59 | 226.93 | AD1-088 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 213.53 | 226.87 | AD1-088 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 213.52 | 226.87 | AD1-088 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 209.33 | 223.72 | AD1-088 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 209.27 | 223.66 | AD1-088 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 209.27 | 223.66 | AD1-088 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 210.74 | 217.89 | AD1-088 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 208.74 | 217.89 | AD1-088 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 199.2 | 208.32 | AD1-088 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 194.94 | 204.97 | AD1-088 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 172.8 | 167.82 | AD1-088 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 163.67 | 164.98 | AD1-088 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2901 | 144.86 | 147 | X2-022 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 161.8 | 161.89 | AD1-088 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 161.8 | 161.88 | AD1-088 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 161.79 | 161.88 | AD1-088 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 153.57 | 158.02 | AD1-088 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.06 | 157.18 | AD1-088 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.06 | 157.18 | AD1-088 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 151.88 | 156.7 | AD1-088 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 161.54 | 154.32 | AD1-088 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 148.52 | 153.05 | AD1-088 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 152.86 | 151.25 | AD1-088 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 155.64 | 150.49 | AD1-088 | PN_P1-2_PN-500-010T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 903 | 142.77 | 149.59 | AD1-088 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 903 | 142.77 | 149.59 | AD1-088 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 903 | 142.75 | 149.58 | AD1-088 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.36 | 149.44 | AD1-088 | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.29 | 149.37 | AD1-088 | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.98 | 148.19 | AD1-088 | AP_P2-3_PE-500-016_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.05 | 148.16 | AD1-088 | AP_P2-3_PE-500-015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.95 | 147.82 | AD1-088 | PJM_500_BG_P4_5_CNSTN_L_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.23 | 147.8 | AD1-088 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.03 | 147.61 | AD1-088 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.06 | 147.6 | AD1-088 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.79 | 147.4 | AD1-088 | PECO_P4_NOTTI85_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.73 | 147.39 | AD1-088 | PECO_P1-2_220-08_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.66 | 147.32 | AD1-088 | PECO_P4_COOPR125_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.16 | 147.31 | AD1-088 | AP_P1-2_WP-500-DRT17_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.16 | 147.31 | AD1-088 | AP_P1-2_PE-500-001_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.11 | 147.24 | AD1-088 | AP_P2-3_PE-500-018C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2901 | 144.84 | 146.98 | X2-060 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.76 | 144.05 | AD1-088 | PECO_P4_PEACH025_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.61 | 143.94 | AD1-088 | PECO_P1-2_PBTIE1_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 911 | 149.03 | 143.16 | AD1-088 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 1031 | 130.37 | 138.17 | AD1-088 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 1031 | 130.37 | 138.17 | AD1-088 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 1031 | 130.36 | 138.16 | AD1-088 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 139 | 133.07 | AD1-088 | PECO_P4_PEACH205_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 138.89 | 132.74 | AD1-088 | PECO_P1-2_PBTIE2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208078 | SAKR | 1 | 230 | 229 | 903 | 124.55 | 132.61 | AD1-088 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208078 | SAKR | 1 | 230 | 229 | 903 | 124.55 | 132.61 | AD1-088 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208078 | SAKR | 1 | 230 | 229 | 903 | 124.55 | 132.61 | AD1-088 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 137.96 | 131.87 | AD1-088 | PECO_P4_PEACH055_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 133.26 | 127.44 | AD1-088 | PECO_P4_PEACH015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 128.6 | 126.86 | AD1-088 | DVP_P4-2: 514T595_SRT-SW |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 131.94 | 126.13 | AD1-088 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 126.85 | 125.14 | AD1-088 | DVP_P4-2: 51482_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 126.85 | 125.04 | AD1-088 | AP_P1-2_PE-500-407T_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 126.85 | 125.04 | AD1-088 | DVP_P1-2: LN 514_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208020 | MANO TR3 | 1 | 230 | 229 | 793 | 111.54 | 124.71 | AD1-088 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208020 | MANO TR3 | 1 | 230 | 229 | 793 | 111.54 | 124.71 | AD1-088 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208020 | MANO TR3 | 1 | 230 | 229 | 793 | 111.54 | 124.71 | AD1-088 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200025 | W CHAPEL | 1 | 500 | 225 | 1732 | 123.71 | 121.92 | AD1-088 | PEPCO_P4_PP41_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 122.85 | 117.48 | AD1-088 | PECO_P4_PEACH225_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 117.05 | 115.13 | AD1-088 | AP_P2-3_PE-500-019C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 2 | 500/230 | 225/232 | 2168 | 109.7 | 115.02 | AD1-088 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 2 | 500/230 | 225/232 | 2168 | 109.52 | 114.8 | AD1-088 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 2 | 500/230 | 225/232 | 2168 | 109.52 | 114.8 | AD1-088 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 1 | 500/230 | 225/232 | 2168 | 109.46 | 114.77 | AD1-088 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 1 | 500/230 | 225/232 | 2168 | 109.29 | 114.56 | AD1-088 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 1 | 500/230 | 225/232 | 2168 | 109.29 | 114.56 | AD1-088 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 99.55 | 103.48 | AD1-088 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 99.54 | 103.48 | AD1-088 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 99.55 | 103.48 | AD1-088 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 98.62 | 102.15 | AD1-088 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 98.72 | 100.78 | AD1-088 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 144.32 | 139.17 | AD1-101 | PL_10_P42_100570_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 144.32 | 139.17 | AD1-101 | PL_10_P42_100570_A_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 143.51 | 138.38 | AD1-101 | PL_10_P12_000085_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 143.42 | 138.29 | AD1-101 | PN_P2-3_PN-500-004-DRT-008_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 143.42 | 138.29 | AD1-101 | PN_P2-3_PN-500-DRT31_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 143.04 | 137.92 | AD1-101 | PL_30_P42_000131_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2901 | 144.37 | 146.43 | Z1-036 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 153.66 | 158.13 | AD1-105 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.16 | 157.28 | AD1-105 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.16 | 157.28 | AD1-105 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 151.97 | 156.81 | AD1-105 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 161.66 | 154.43 | AD1-105 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 148.61 | 153.16 | AD1-105 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 155.73 | 150.58 | AD1-105 | PN_P1-2_PN-500-010T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.45 | 149.54 | AD1-105 | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.38 | 149.47 | AD1-105 | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.07 | 148.29 | AD1-105 | AP_P2-3_PE-500-016_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.13 | 148.26 | AD1-105 | AP_P2-3_PE-500-015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.04 | 147.91 | AD1-105 | PJM_500_BG_P4_5_CNSTN_L_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.34 | 147.9 | AD1-105 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.14 | 147.71 | AD1-105 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.16 | 147.7 | AD1-105 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.89 | 147.5 | AD1-105 | PECO_P4_NOTTI85_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.83 | 147.49 | AD1-105 | PECO_P1-2_220-08_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.77 | 147.42 | AD1-105 | PECO_P4_COOPR125_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.24 | 147.41 | AD1-105 | AP_P1-2_WP-500-DRT17_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.24 | 147.41 | AD1-105 | AP_P1-2_PE-500-001_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.19 | 147.34 | AD1-105 | AP_P2-3_PE-500-018C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2901 | 144.84 | 146.98 | Z2-087 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.88 | 144.17 | AD1-105 | PECO_P4_PEACH025_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.73 | 144.06 | AD1-105 | PECO_P1-2_PBTIE1_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 139.11 | 133.17 | AD1-105 | PECO_P4_PEACH205_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 139 | 132.85 | AD1-105 | PECO_P1-2_PBTIE2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 138.06 | 131.98 | AD1-105 | PECO_P4_PEACH055_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 133.38 | 127.55 | AD1-105 | PECO_P4_PEACH015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 128.7 | 126.96 | AD1-105 | DVP_P4-2: 514T595_SRT-SW |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 132.05 | 126.23 | AD1-105 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 126.96 | 125.24 | AD1-105 | DVP_P4-2: 51482_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 126.96 | 125.15 | AD1-105 | DVP_P1-2: LN 514_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 126.96 | 125.15 | AD1-105 | AP_P1-2_PE-500-407T_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200025 | W CHAPEL | 1 | 500 | 225 | 1732 | 123.78 | 121.99 | AD1-105 | PEPCO_P4_PP41_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 122.96 | 117.58 | AD1-105 | PECO_P4_PEACH225_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 117.16 | 115.24 | AD1-105 | AP_P2-3_PE-500-019C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 2901 | 144.74 | 146.86 | Z2-088 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 161.85 | 154.62 | AD1-106 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.5 | 148.06 | AD1-106 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.3 | 147.88 | AD1-106 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.33 | 147.86 | AD1-106 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.06 | 147.67 | AD1-106 | PECO_P4_NOTTI85_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153 | 147.65 | AD1-106 | PECO_P1-2_220-08_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.93 | 147.59 | AD1-106 | PECO_P4_COOPR125_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.59 | 147.4 | AD1-106 | PECO_P1-2_220-93_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 151.05 | 144.34 | AD1-106 | PECO_P4_PEACH025_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 148.47 | 143.24 | AD1-106 | AP_P2-2_WP-500-DRT16_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 148.47 | 143.24 | AD1-106 | AP_P2-3_WP-500-465_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 148.47 | 143.24 | AD1-106 | AP_P2-3_WP-500-DRT20_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3464 | 168.29 | 162.28 | 01CROSSCHOOL | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 153.75 | 158.24 | AD1-115 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.24 | 157.37 | AD1-115 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.24 | 157.36 | AD1-115 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 152.06 | 156.91 | AD1-115 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 161.76 | 154.53 | AD1-115 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 148.7 | 153.26 | AD1-115 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 155.81 | 150.66 | AD1-115 | PN_P1-2_PN-500-010T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.53 | 149.64 | AD1-115 | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.46 | 149.57 | AD1-115 | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.14 | 148.39 | AD1-115 | AP_P2-3_PE-500-016_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.21 | 148.36 | AD1-115 | AP_P2-3_PE-500-015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.13 | 147.99 | AD1-115 | PJM_500_BG_P4_5_CNSTN_L_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.43 | 147.99 | AD1-115 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.23 | 147.8 | AD1-115 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.25 | 147.79 | AD1-115 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.98 | 147.59 | AD1-115 | PECO_P4_NOTTI85_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.92 | 147.58 | AD1-115 | PECO_P1-2_220-08_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.85 | 147.51 | AD1-115 | PECO_P4_COOPR125_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.32 | 147.51 | AD1-115 | AP_P1-2_PE-500-001_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.32 | 147.51 | AD1-115 | AP_P1-2_WP-500-DRT17_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.27 | 147.44 | AD1-115 | AP_P2-3_PE-500-018C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3464 | 167.8 | 161.8 | 01GRNGAP | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.98 | 144.27 | AD1-115 | PECO_P4_PEACH025_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.84 | 144.16 | AD1-115 | PECO_P1-2_PBTIE1_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 139.21 | 133.26 | AD1-115 | PECO_P4_PEACH205_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 139.1 | 132.94 | AD1-115 | PECO_P1-2_PBTIE2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 138.15 | 132.06 | AD1-115 | PECO_P4_PEACH055_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 133.48 | 127.65 | AD1-115 | PECO_P4_PEACH015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 128.79 | 127.05 | AD1-115 | DVP_P4-2: 514T595_SRT-SW |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 132.15 | 126.32 | AD1-115 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 127.04 | 125.33 | AD1-115 | DVP_P4-2: 51482_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 127.04 | 125.24 | AD1-115 | AP_P1-2_PE-500-407T_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 127.04 | 125.24 | AD1-115 | DVP_P1-2: LN 514_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 123.05 | 117.67 | AD1-115 | PECO_P4_PEACH225_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 117.24 | 115.32 | AD1-115 | AP_P2-3_PE-500-019C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 144.32 | 139.17 | AD1-119 | PL_10_P42_100570_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 144.32 | 139.17 | AD1-119 | PL_10_P42_100570_A_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 143.51 | 138.38 | AD1-119 | PL_10_P12_000085_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 143.41 | 138.29 | AD1-119 | PN_P2-3_PN-500-004-DRT-008_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 143.41 | 138.29 | AD1-119 | PN_P2-3_PN-500-DRT31_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 143.04 | 137.92 | AD1-119 | PL_30_P42_000131_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3464 | 168.18 | 162.17 | 05CELAN | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.34 | 157.46 | AD1-125 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.34 | 157.46 | AD1-125 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.51 | 148.07 | AD1-125 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.3 | 147.88 | AD1-125 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.33 | 147.87 | AD1-125 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.06 | 147.67 | AD1-125 | PECO_P4_NOTTI85_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153 | 147.65 | AD1-125 | PECO_P1-2_220-08_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.93 | 147.59 | AD1-125 | PECO_P4_COOPR125_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.59 | 147.4 | AD1-125 | PECO_P1-2_220-93_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 142.88 | 146.95 | AD1-125 | AP_P1-2_WP-500-006_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 142.88 | 146.95 | AD1-125 | AP_P2-3_WP-500-DRT19_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 142.88 | 146.95 | AD1-125 | AP_P2-3_WP-500-466_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 142.88 | 146.95 | AD1-125 | AP_P1-2_PE-500-004_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 142.88 | 146.95 | AD1-125 | AP_P2-3_PE-500-014_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 150.97 | 146.59 | AD1-125 | AP_P2-3_WP-500-DRT19_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 225.72 | 237.28 | AD1-128 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 223.71 | 237.28 | AD1-128 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 225.65 | 237.21 | AD1-128 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 223.64 | 237.21 | AD1-128 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 225.65 | 237.21 | AD1-128 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 223.64 | 237.21 | AD1-128 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 213.65 | 227.11 | AD1-128 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 213.59 | 227.05 | AD1-128 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 213.59 | 227.05 | AD1-128 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 209.39 | 223.91 | AD1-128 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 209.33 | 223.84 | AD1-128 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 209.33 | 223.84 | AD1-128 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3464 | 168.29 | 162.28 | 05NTRDAM | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 153.69 | 158.18 | AD1-128 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.15 | 157.28 | AD1-128 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.15 | 157.27 | AD1-128 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 152 | 156.86 | AD1-128 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 161.59 | 154.37 | AD1-128 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 148.64 | 153.2 | AD1-128 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 155.72 | 150.58 | AD1-128 | PN_P1-2_PN-500-010T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.48 | 149.58 | AD1-128 | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.41 | 149.51 | AD1-128 | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.13 | 148.4 | AD1-128 | AP_P2-3_PE-500-016_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.19 | 148.37 | AD1-128 | AP_P2-3_PE-500-015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.04 | 147.91 | AD1-128 | PJM_500_BG_P4_5_CNSTN_L_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.27 | 147.84 | AD1-128 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.07 | 147.65 | AD1-128 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.1 | 147.64 | AD1-128 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.3 | 147.51 | AD1-128 | AP_P1-2_WP-500-DRT17_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.3 | 147.51 | AD1-128 | AP_P1-2_PE-500-001_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.83 | 147.44 | AD1-128 | PECO_P4_NOTTI85_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.26 | 147.44 | AD1-128 | AP_P2-3_PE-500-018C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.77 | 147.43 | AD1-128 | PECO_P1-2_220-08_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.7 | 147.36 | AD1-128 | PECO_P4_COOPR125_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3464 | 167.91 | 161.91 | 08HLCRTG | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.78 | 144.07 | AD1-128 | PECO_P4_PEACH025_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.67 | 144 | AD1-128 | PECO_P1-2_PBTIE1_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 139.07 | 133.14 | AD1-128 | PECO_P4_PEACH205_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 138.95 | 132.8 | AD1-128 | PECO_P1-2_PBTIE2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 138.01 | 131.92 | AD1-128 | PECO_P4_PEACH055_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 133.32 | 127.51 | AD1-128 | PECO_P4_PEACH015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 132 | 126.18 | AD1-128 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 122.91 | 117.54 | AD1-128 | PECO_P4_PEACH225_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 225.64 | 237.17 | AD1-140 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 223.63 | 237.16 | AD1-140 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 225.57 | 237.1 | AD1-140 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 223.57 | 237.1 | AD1-140 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 225.57 | 237.1 | AD1-140 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 223.57 | 237.1 | AD1-140 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 213.58 | 227.01 | AD1-140 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 213.52 | 226.95 | AD1-140 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 213.52 | 226.94 | AD1-140 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 209.32 | 223.8 | AD1-140 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 209.26 | 223.74 | AD1-140 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 209.26 | 223.73 | AD1-140 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 172.87 | 167.94 | AD1-140 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3464 | 168.7 | 162.68 | 09GRNVIL | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 153.66 | 158.14 | AD1-140 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.11 | 157.23 | AD1-140 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.1 | 157.23 | AD1-140 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 151.97 | 156.82 | AD1-140 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 161.53 | 154.31 | AD1-140 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 148.61 | 153.16 | AD1-140 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 155.68 | 150.54 | AD1-140 | PN_P1-2_PN-500-010T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.45 | 149.55 | AD1-140 | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.37 | 149.47 | AD1-140 | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.1 | 148.37 | AD1-140 | AP_P2-3_PE-500-016_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.17 | 148.34 | AD1-140 | AP_P2-3_PE-500-015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153 | 147.87 | AD1-140 | PJM_500_BG_P4_5_CNSTN_L_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.22 | 147.79 | AD1-140 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.02 | 147.6 | AD1-140 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.05 | 147.59 | AD1-140 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.28 | 147.48 | AD1-140 | AP_P1-2_WP-500-DRT17_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.28 | 147.48 | AD1-140 | AP_P1-2_PE-500-001_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.23 | 147.41 | AD1-140 | AP_P2-3_PE-500-018C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.78 | 147.39 | AD1-140 | PECO_P4_NOTTI85_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.72 | 147.38 | AD1-140 | PECO_P1-2_220-08_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.65 | 147.31 | AD1-140 | PECO_P4_COOPR125_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3464 | 168.24 | 162.23 | 1DOMTR10 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.71 | 144.01 | AD1-140 | PECO_P4_PEACH025_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.61 | 143.94 | AD1-140 | PECO_P1-2_PBTIE1_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 911 | 149.11 | 143.27 | AD1-140 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 139.02 | 133.09 | AD1-140 | PECO_P4_PEACH205_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 138.89 | 132.74 | AD1-140 | PECO_P1-2_PBTIE2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 137.96 | 131.87 | AD1-140 | PECO_P4_PEACH055_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 133.26 | 127.45 | AD1-140 | PECO_P4_PEACH015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 131.95 | 126.13 | AD1-140 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 122.85 | 117.49 | AD1-140 | PECO_P4_PEACH225_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 212.08 | 219.78 | AD1-143 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 210.05 | 219.78 | AD1-143 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 200.47 | 210.16 | AD1-143 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 196.21 | 206.82 | AD1-143 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 172.8 | 167.59 | AD1-143 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 172.82 | 167.59 | AD1-143 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 172.82 | 167.59 | AD1-143 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 162.85 | 163.26 | AD1-143 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 162.85 | 163.26 | AD1-143 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 162.83 | 163.26 | AD1-143 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3464 | 168.28 | 162.27 | 1DOMTR9 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 154.38 | 159 | AD1-143 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.88 | 158 | AD1-143 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.88 | 158 | AD1-143 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 152.68 | 157.67 | AD1-143 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 162.59 | 155.33 | AD1-143 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 149.32 | 154.02 | AD1-143 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 153.9 | 152.49 | AD1-143 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 156.45 | 151.29 | AD1-143 | PN_P1-2_PN-500-010T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 147.13 | 150.35 | AD1-143 | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 147.06 | 150.28 | AD1-143 | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.72 | 149.08 | AD1-143 | AP_P2-3_PE-500-016_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.78 | 149.05 | AD1-143 | AP_P2-3_PE-500-015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 154.13 | 148.68 | AD1-143 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.74 | 148.61 | AD1-143 | PJM_500_BG_P4_5_CNSTN_L_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.93 | 148.49 | AD1-143 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.95 | 148.48 | AD1-143 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.68 | 148.28 | AD1-143 | PECO_P4_NOTTI85_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.62 | 148.27 | AD1-143 | PECO_P1-2_220-08_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.55 | 148.2 | AD1-143 | PECO_P4_COOPR125_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.89 | 148.19 | AD1-143 | AP_P1-2_WP-500-DRT17_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.89 | 148.19 | AD1-143 | AP_P1-2_PE-500-001_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.85 | 148.12 | AD1-143 | AP_P2-3_PE-500-018C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3464 | 168.22 | 162.21 | 1EDGECMA | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 151.79 | 145.04 | AD1-143 | PECO_P4_PEACH025_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 151.75 | 145.03 | AD1-143 | PECO_P1-2_PBTIE1_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 911 | 149.04 | 142.99 | AD1-143 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 911 | 149.06 | 142.98 | AD1-143 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 911 | 149.06 | 142.98 | AD1-143 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 903 | 136.51 | 140.8 | AD1-143 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 140.05 | 134.08 | AD1-143 | PECO_P4_PEACH205_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 139.94 | 133.75 | AD1-143 | PECO_P1-2_PBTIE2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 138.91 | 132.79 | AD1-143 | PECO_P4_PEACH055_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 1031 | 125.43 | 130.32 | AD1-143 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 134.39 | 128.53 | AD1-143 | PECO_P4_PEACH015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 129.65 | 127.92 | AD1-143 | DVP_P4-2: 514T595_SRT-SW |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 132.98 | 127.11 | AD1-143 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 127.92 | 126.22 | AD1-143 | DVP_P4-2: 51482_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 127.92 | 126.13 | AD1-143 | AP_P1-2_PE-500-407T_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 127.92 | 126.13 | AD1-143 | DVP_P1-2: LN 514_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208078 | SAKR | 1 | 230 | 229 | 903 | 118.17 | 123.83 | AD1-143 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200025 | W CHAPEL | 1 | 500 | 225 | 1732 | 124.42 | 122.66 | AD1-143 | PEPCO_P4_PP41_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 123.89 | 118.48 | AD1-143 | PECO_P4_PEACH225_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 118.1 | 116.2 | AD1-143 | AP_P2-3_PE-500-019C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208020 | MANO TR3 | 1 | 230 | 229 | 793 | 105.23 | 115.4 | AD1-143 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208031 | MLWD TR2 | 1 | 230 | 229 | 911 | 105.9 | 112.98 | AD1-143 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208020 | MANO TR3 | 208031 | MLWD TR2 | 1 | 230 | 229 | 903 | 96.35 | 104.53 | AD1-143 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 98.98 | 101.23 | AD1-143 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3464 | 168.09 | 162.08 | 1HOLLOMANSOL | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 153.69 | 158.17 | AD1-152 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.18 | 157.3 | AD1-152 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.18 | 157.3 | AD1-152 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 152 | 156.85 | AD1-152 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 161.67 | 154.45 | AD1-152 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 148.64 | 153.19 | AD1-152 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 155.75 | 150.6 | AD1-152 | PN_P1-2_PN-500-010T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.47 | 149.58 | AD1-152 | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.4 | 149.5 | AD1-152 | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.09 | 148.33 | AD1-152 | AP_P2-3_PE-500-016_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.16 | 148.3 | AD1-152 | AP_P2-3_PE-500-015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.07 | 147.93 | AD1-152 | PJM_500_BG_P4_5_CNSTN_L_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.35 | 147.92 | AD1-152 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.15 | 147.73 | AD1-152 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.18 | 147.72 | AD1-152 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.91 | 147.52 | AD1-152 | PECO_P4_NOTTI85_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.85 | 147.5 | AD1-152 | PECO_P1-2_220-08_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.27 | 147.45 | AD1-152 | AP_P1-2_WP-500-DRT17_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.27 | 147.45 | AD1-152 | AP_P1-2_PE-500-001_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.78 | 147.44 | AD1-152 | PECO_P4_COOPR125_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.22 | 147.38 | AD1-152 | AP_P2-3_PE-500-018C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3464 | 168.28 | 162.27 | 1STONECA | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.9 | 144.19 | AD1-152 | PECO_P4_PEACH025_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.75 | 144.08 | AD1-152 | PECO_P1-2_PBTIE1_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 139.13 | 133.19 | AD1-152 | PECO_P4_PEACH205_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 139.02 | 132.87 | AD1-152 | PECO_P1-2_PBTIE2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 138.08 | 131.99 | AD1-152 | PECO_P4_PEACH055_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 133.4 | 127.58 | AD1-152 | PECO_P4_PEACH015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 128.81 | 127.07 | AD1-152 | DVP_P4-2: 514T595_SRT-SW |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 132.07 | 126.25 | AD1-152 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 127.06 | 125.35 | AD1-152 | DVP_P4-2: 51482_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 127.06 | 125.26 | AD1-152 | AP_P1-2_PE-500-407T_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 127.06 | 125.26 | AD1-152 | DVP_P1-2: LN 514_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 122.98 | 117.6 | AD1-152 | PECO_P4_PEACH225_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 117.26 | 115.34 | AD1-152 | AP_P2-3_PE-500-019C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3464 | 168.61 | 162.59 | 28MDLSEXCO | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 153.69 | 158.17 | AD1-155 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.19 | 157.31 | AD1-155 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.19 | 157.31 | AD1-155 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 152 | 156.85 | AD1-155 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 161.69 | 154.46 | AD1-155 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 148.64 | 153.2 | AD1-155 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 155.76 | 150.61 | AD1-155 | PN_P1-2_PN-500-010T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.48 | 149.58 | AD1-155 | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.41 | 149.51 | AD1-155 | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.09 | 148.33 | AD1-155 | AP_P2-3_PE-500-016_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.16 | 148.3 | AD1-155 | AP_P2-3_PE-500-015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.07 | 147.94 | AD1-155 | PJM_500_BG_P4_5_CNSTN_L_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.37 | 147.93 | AD1-155 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.16 | 147.74 | AD1-155 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.19 | 147.73 | AD1-155 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.92 | 147.53 | AD1-155 | PECO_P4_NOTTI85_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.86 | 147.52 | AD1-155 | PECO_P1-2_220-08_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.28 | 147.45 | AD1-155 | AP_P1-2_PE-500-001_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.28 | 147.45 | AD1-155 | AP_P1-2_WP-500-DRT17_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.79 | 147.45 | AD1-155 | PECO_P4_COOPR125_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.23 | 147.39 | AD1-155 | AP_P2-3_PE-500-018C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3464 | 168.13 | 162.12 | 3MURPHYS | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.91 | 144.2 | AD1-155 | PECO_P4_PEACH025_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.77 | 144.09 | AD1-155 | PECO_P1-2_PBTIE1_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 139.14 | 133.2 | AD1-155 | PECO_P4_PEACH205_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 139.03 | 132.88 | AD1-155 | PECO_P1-2_PBTIE2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 138.09 | 132 | AD1-155 | PECO_P4_PEACH055_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 133.41 | 127.59 | AD1-155 | PECO_P4_PEACH015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 132.08 | 126.26 | AD1-155 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 122.99 | 117.61 | AD1-155 | PECO_P4_PEACH225_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 99.6 | 103.57 | AD1-155 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 99.6 | 103.57 | AD1-155 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 98.77 | 100.86 | AD1-155 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3464 | 168.3 | 162.29 | 3UNCAMP | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 153.75 | 158.24 | AD2-009 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.23 | 157.35 | AD2-009 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.23 | 157.35 | AD2-009 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 152.06 | 156.92 | AD2-009 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 161.74 | 154.51 | AD2-009 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 148.7 | 153.26 | AD2-009 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 155.79 | 150.63 | AD2-009 | PN_P1-2_PN-500-010T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.53 | 149.64 | AD2-009 | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.46 | 149.57 | AD2-009 | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.12 | 148.34 | AD2-009 | AP_P2-3_PE-500-016_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.18 | 148.32 | AD2-009 | AP_P2-3_PE-500-015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.11 | 147.98 | AD2-009 | PJM_500_BG_P4_5_CNSTN_L_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.41 | 147.97 | AD2-009 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.21 | 147.78 | AD2-009 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.23 | 147.77 | AD2-009 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.96 | 147.57 | AD2-009 | PECO_P4_NOTTI85_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.9 | 147.56 | AD2-009 | PECO_P1-2_220-08_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.84 | 147.49 | AD2-009 | PECO_P4_COOPR125_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.3 | 147.47 | AD2-009 | AP_P1-2_PE-500-001_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.3 | 147.47 | AD2-009 | AP_P1-2_WP-500-DRT17_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.26 | 147.41 | AD2-009 | AP_P2-3_PE-500-018C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3464 | 168.26 | 162.25 | 4E MILL | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.95 | 144.25 | AD2-009 | PECO_P4_PEACH025_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.82 | 144.14 | AD2-009 | PECO_P1-2_PBTIE1_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200512 | 26LEWISTWN | 200519 | 26REED TAP | 1 | 115 | 226 | 271 | 126.84 | 135.8 | AD2-009 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200512 | 26LEWISTWN | 200519 | 26REED TAP | 1 | 115 | 226 | 271 | 126.84 | 135.8 | AD2-009 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200512 | 26LEWISTWN | 200519 | 26REED TAP | 1 | 115 | 226 | 271 | 126.84 | 135.8 | AD2-009 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200504 | 26CARLISLE | 204528 | 27GARDNERS | 1 | 115 | 226/227 | 190 | 127.19 | 135.65 | AD2-009 | PN_P2-3_PN-115-0331-B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 203981 | AD2-062_POI | 235188 | 01GREENE | 1 | 138 | 226/201 | 317 | 143.17 | 134.65 | AD2-009 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 203981 | AD2-062_POI | 235188 | 01GREENE | 1 | 138 | 226/201 | 317 | 143.17 | 134.65 | AD2-009 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 203981 | AD2-062_POI | 235188 | 01GREENE | 1 | 138 | 226/201 | 317 | 142.96 | 134.51 | AD2-009 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200504 | 26CARLISLE | 204528 | 27GARDNERS | 1 | 115 | 226/227 | 190 | 125.59 | 133.77 | AD2-009 | PN_P1-2_PN-115-094_A_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200532 | 26ROXBURY | 203981 | AD2-062_POI | 1 | 138 | 226 | 317 | 142.42 | 133.33 | AD2-009 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200532 | 26ROXBURY | 203981 | AD2-062_POI | 1 | 138 | 226 | 317 | 142.42 | 133.33 | AD2-009 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 139.19 | 133.25 | AD2-009 | PECO_P4_PEACH205_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200532 | 26ROXBURY | 203981 | AD2-062_POI | 1 | 138 | 226 | 317 | 142.22 | 133.19 | AD2-009 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 139.08 | 132.93 | AD2-009 | PECO_P1-2_PBTIE2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200504 | 26CARLISLE | 204528 | 27GARDNERS | 1 | 115 | 226/227 | 190 | 125.43 | 132.84 | AD2-009 | PN_P2-3_PN-115-58B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200504 | 26CARLISLE | 204528 | 27GARDNERS | 1 | 115 | 226/227 | 190 | 126.07 | 132.8 | AD2-009 | PN_P1-3_PN-115-040_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200504 | 26CARLISLE | 204528 | 27GARDNERS | 1 | 115 | 226/227 | 190 | 126.07 | 132.8 | AD2-009 | PN_P2-2_PN-115-030_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200504 | 26CARLISLE | 204528 | 27GARDNERS | 1 | 115 | 226/227 | 190 | 125.23 | 132.78 | AD2-009 | PN_P1-2_PN-115-094_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 138.14 | 132.05 | AD2-009 | PECO_P4_PEACH055_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200519 | 26REED TAP | 200522 | 26SHADE GP | 1 | 115 | 226 | 271 | 119.2 | 130.66 | AD2-009 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200519 | 26REED TAP | 200522 | 26SHADE GP | 1 | 115 | 226 | 271 | 119.2 | 130.66 | AD2-009 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200519 | 26REED TAP | 200522 | 26SHADE GP | 1 | 115 | 226 | 271 | 119.2 | 130.66 | AD2-009 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200512 | 26LEWISTWN | 200519 | 26REED TAP | 1 | 115 | 226 | 271 | 124.01 | 129.42 | AD2-009 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200504 | 26CARLISLE | 204528 | 27GARDNERS | 1 | 115 | 226/227 | 190 | 122.89 | 128.37 | AD2-009 | PN_P2-3_PN-230-0014-12_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 129.94 | 128.19 | AD2-009 | DVP_P4-2: 514T595_SRT-SW |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200504 | 26CARLISLE | 204528 | 27GARDNERS | 1 | 115 | 226/227 | 190 | 122.88 | 127.95 | AD2-009 | PN_P1-3_PN-230-020A_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200504 | 26CARLISLE | 204528 | 27GARDNERS | 1 | 115 | 226/227 | 190 | 122.88 | 127.95 | AD2-009 | PN_P2-3_PN-230-0014-11_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200504 | 26CARLISLE | 204528 | 27GARDNERS | 1 | 115 | 226/227 | 190 | 122.81 | 127.93 | AD2-009 | PN_P2-2_PN-115-031_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 133.46 | 127.64 | AD2-009 | PECO_P4_PEACH015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3464 | 168.27 | 162.26 | 6BUCKING | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 128.22 | 126.5 | AD2-009 | DVP_P4-2: 51482_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 128.22 | 126.41 | AD2-009 | AP_P1-2_PE-500-407T_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 128.22 | 126.41 | AD2-009 | DVP_P1-2: LN 514_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 132.13 | 126.31 | AD2-009 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 2 | 230 | 233 | 793 | 128.01 | 126.25 | AD2-009 | DVP_P4-2: 514T595_SRT-SW |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 793 | 128.01 | 126.25 | AD2-009 | DVP_P4-2: 514T595_SRT-SW |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3464 | 168.26 | 162.25 | 6ELIZ CT | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 793 | 126.78 | 125.06 | AD2-009 | DVP_P4-2: 51482_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 2 | 230 | 233 | 793 | 126.78 | 125.06 | AD2-009 | DVP_P4-2: 51482_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 2 | 230 | 233 | 793 | 126.78 | 124.98 | AD2-009 | DVP_P1-2: LN 514_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 793 | 126.78 | 124.98 | AD2-009 | DVP_P1-2: LN 514_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 793 | 126.78 | 124.98 | AD2-009 | AP_P1-2_PE-500-407T_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 2 | 230 | 233 | 793 | 126.78 | 124.98 | AD2-009 | AP_P1-2_PE-500-407T_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200519 | 26REED TAP | 200522 | 26SHADE GP | 1 | 115 | 226 | 271 | 116.37 | 124.38 | AD2-009 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 203981 | AD2-062_POI | 235188 | 01GREENE | 1 | 138 | 226/201 | 317 | 137.54 | 119.67 | AD2-009 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 203981 | AD2-062_POI | 235188 | 01GREENE | 1 | 138 | 226/201 | 317 | 137.54 | 119.67 | AD2-009 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 203981 | AD2-062_POI | 235188 | 01GREENE | 1 | 138 | 226/201 | 317 | 137.54 | 119.67 | AD2-009 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 203981 | AD2-062_POI | 235188 | 01GREENE | 1 | 138 | 226/201 | 317 | 137.31 | 119.31 | AD2-009 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 203981 | AD2-062_POI | 235188 | 01GREENE | 1 | 138 | 226/201 | 317 | 122.81 | 118.81 | AD2-009 | AP_P2-3_PE-500-016_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200512 | 26LEWISTWN | 200519 | 26REED TAP | 1 | 115 | 226 | 271 | 119.92 | 118.69 | AD2-009 | ME_P2-3_ME-115-003DT_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 203981 | AD2-062_POI | 235188 | 01GREENE | 1 | 138 | 226/201 | 317 | 123.01 | 118.68 | AD2-009 | AP_P2-3_PE-500-015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200512 | 26LEWISTWN | 200519 | 26REED TAP | 1 | 115 | 226 | 271 | 119.85 | 118.63 | AD2-009 | ME_P2-3_ME-115-003AT_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200512 | 26LEWISTWN | 200519 | 26REED TAP | 1 | 115 | 226 | 271 | 119.85 | 118.62 | AD2-009 | ME_P2-3_ME-115-003BT_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200512 | 26LEWISTWN | 200519 | 26REED TAP | 1 | 115 | 226 | 271 | 119.85 | 118.62 | AD2-009 | ME_P2-2_ME-115-002T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200512 | 26LEWISTWN | 200519 | 26REED TAP | 1 | 115 | 226 | 271 | 119.6 | 118.39 | AD2-009 | ME_P1-2_ME-115-058T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200532 | 26ROXBURY | 203981 | AD2-062_POI | 1 | 138 | 226 | 317 | 136.8 | 118.38 | AD2-009 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200532 | 26ROXBURY | 203981 | AD2-062_POI | 1 | 138 | 226 | 317 | 136.8 | 118.38 | AD2-009 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200532 | 26ROXBURY | 203981 | AD2-062_POI | 1 | 138 | 226 | 317 | 136.79 | 118.38 | AD2-009 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200532 | 26ROXBURY | 203981 | AD2-062_POI | 1 | 138 | 226 | 317 | 136.56 | 118.02 | AD2-009 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 203981 | AD2-062_POI | 235188 | 01GREENE | 1 | 138 | 226/201 | 317 | 120.69 | 117.86 | AD2-009 | AP_P2-3_PE-500-018D_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200532 | 26ROXBURY | 200520 | 26ROXBURY | 2 | 138/115 | 226 | 435 | 103.79 | 117.85 | AD2-009 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200532 | 26ROXBURY | 200520 | 26ROXBURY | 2 | 138/115 | 226 | 435 | 103.79 | 117.85 | AD2-009 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200532 | 26ROXBURY | 200520 | 26ROXBURY | 2 | 138/115 | 226 | 435 | 103.64 | 117.7 | AD2-009 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 123.04 | 117.66 | AD2-009 | PECO_P4_PEACH225_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200532 | 26ROXBURY | 203981 | AD2-062_POI | 1 | 138 | 226 | 317 | 122.06 | 117.53 | AD2-009 | AP_P2-3_PE-500-016_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 793 | 120.27 | 117.52 | AD2-009 | PEPCO_P1_PP2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 2 | 230 | 233 | 793 | 120.27 | 117.52 | AD2-009 | PEPCO_P1_PP1_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200532 | 26ROXBURY | 203981 | AD2-062_POI | 1 | 138 | 226 | 317 | 122.26 | 117.4 | AD2-009 | AP_P2-3_PE-500-015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200532 | 26ROXBURY | 203981 | AD2-062_POI | 1 | 138 | 226 | 317 | 119.94 | 116.55 | AD2-009 | AP_P2-3_PE-500-018D_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 118.44 | 116.51 | AD2-009 | AP_P2-3_PE-500-019C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200512 | 26LEWISTWN | 200519 | 26REED TAP | 1 | 115 | 226 | 271 | 116.78 | 115.79 | AD2-009 | PN_P2-3_PN-115-10T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200532 | 26ROXBURY | 200520 | 26ROXBURY | 2 | 138/115 | 226 | 435 | 99.69 | 114.12 | AD2-009 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200532 | 26ROXBURY | 200520 | 26ROXBURY | 2 | 138/115 | 226 | 435 | 99.69 | 114.12 | AD2-009 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200532 | 26ROXBURY | 200520 | 26ROXBURY | 2 | 138/115 | 226 | 435 | 99.68 | 114.12 | AD2-009 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200532 | 26ROXBURY | 200520 | 26ROXBURY | 2 | 138/115 | 226 | 435 | 99.52 | 113.95 | AD2-009 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200519 | 26REED TAP | 200522 | 26SHADE GP | 1 | 115 | 226 | 271 | 112.27 | 113.84 | AD2-009 | ME_P2-3_ME-115-003DT_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200519 | 26REED TAP | 200522 | 26SHADE GP | 1 | 115 | 226 | 271 | 112.21 | 113.78 | AD2-009 | ME_P2-3_ME-115-003AT_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200519 | 26REED TAP | 200522 | 26SHADE GP | 1 | 115 | 226 | 271 | 112.21 | 113.77 | AD2-009 | ME_P2-2_ME-115-002T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200519 | 26REED TAP | 200522 | 26SHADE GP | 1 | 115 | 226 | 271 | 112.21 | 113.77 | AD2-009 | ME_P2-3_ME-115-003BT_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200519 | 26REED TAP | 200522 | 26SHADE GP | 1 | 115 | 226 | 271 | 111.96 | 113.55 | AD2-009 | ME_P1-2_ME-115-058T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 793 | 114.41 | 111.76 | AD2-009 | PEPCO_P4_PP19_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200519 | 26REED TAP | 200522 | 26SHADE GP | 1 | 115 | 226 | 271 | 109.14 | 110.95 | AD2-009 | PN_P2-3_PN-115-10T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200504 | 26CARLISLE | 200520 | 26ROXBURY | 1 | 115 | 226 | 190 | 99.46 | 109.44 | AD2-009 | PN_P1-2_PN-115-094_A_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 2 | 230 | 233 | 793 | 111.02 | 109.13 | AD2-009 | AP_P2-3_PE-500-019C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 793 | 111.02 | 109.13 | AD2-009 | AP_P2-3_PE-500-019C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200504 | 26CARLISLE | 200520 | 26ROXBURY | 1 | 115 | 226 | 190 | 99.3 | 108.6 | AD2-009 | PN_P2-3_PN-115-58B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200504 | 26CARLISLE | 200520 | 26ROXBURY | 1 | 115 | 226 | 190 | 99.93 | 108.56 | AD2-009 | PN_P1-3_PN-115-040_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200504 | 26CARLISLE | 200520 | 26ROXBURY | 1 | 115 | 226 | 190 | 99.93 | 108.56 | AD2-009 | PN_P2-2_PN-115-030_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200504 | 26CARLISLE | 200520 | 26ROXBURY | 1 | 115 | 226 | 190 | 99.11 | 108.54 | AD2-009 | PN_P1-2_PN-115-094_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200532 | 26ROXBURY | 200520 | 26ROXBURY | 2 | 138/115 | 226 | 435 | 94.54 | 106.88 | AD2-009 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200504 | 26CARLISLE | 200520 | 26ROXBURY | 1 | 115 | 226 | 190 | 90.19 | 104.98 | AD2-009 | PN_P2-3_PN-115-0331-B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200504 | 26CARLISLE | 200520 | 26ROXBURY | 1 | 115 | 226 | 190 | 96.82 | 104.4 | AD2-009 | PN_P2-3_PN-230-0014-12_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200504 | 26CARLISLE | 200520 | 26ROXBURY | 1 | 115 | 226 | 190 | 96.81 | 103.99 | AD2-009 | PN_P2-3_PN-230-0014-11_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200504 | 26CARLISLE | 200520 | 26ROXBURY | 1 | 115 | 226 | 190 | 96.81 | 103.99 | AD2-009 | PN_P1-3_PN-230-020A_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200504 | 26CARLISLE | 200520 | 26ROXBURY | 1 | 115 | 226 | 190 | 96.74 | 103.97 | AD2-009 | PN_P2-2_PN-115-031_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 99.62 | 103.59 | AD2-009 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 99.62 | 103.59 | AD2-009 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 99.62 | 103.59 | AD2-009 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200532 | 26ROXBURY | 200520 | 26ROXBURY | 2 | 138/115 | 226 | 435 | 88.95 | 101.02 | AD2-009 | AP_P2-3_PE-500-016_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200532 | 26ROXBURY | 200520 | 26ROXBURY | 2 | 138/115 | 226 | 435 | 89.1 | 100.89 | AD2-009 | AP_P2-3_PE-500-015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 98.79 | 100.88 | AD2-009 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 143.04 | 137.93 | AD2-014 | PL_30_P42_000131_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 225.27 | 236.62 | AD2-016 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 223.27 | 236.61 | AD2-016 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 225.21 | 236.57 | AD2-016 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 223.21 | 236.57 | AD2-016 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 225.2 | 236.57 | AD2-016 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 223.21 | 236.57 | AD2-016 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 213.23 | 226.47 | AD2-016 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 213.17 | 226.43 | AD2-016 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 213.17 | 226.42 | AD2-016 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 208.97 | 223.26 | AD2-016 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 208.91 | 223.21 | AD2-016 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 208.91 | 223.21 | AD2-016 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 210.39 | 217.52 | AD2-016 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 208.39 | 217.52 | AD2-016 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 198.86 | 207.96 | AD2-016 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 194.6 | 204.61 | AD2-016 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 172.65 | 167.73 | AD2-016 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 163.49 | 164.81 | AD2-016 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3464 | 168.17 | 162.16 | 6EVERETS | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 161.61 | 161.72 | AD2-016 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 161.61 | 161.72 | AD2-016 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 161.6 | 161.71 | AD2-016 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 153.47 | 157.91 | AD2-016 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 161.9 | 157.03 | AD2-016 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 161.9 | 157.03 | AD2-016 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 151.78 | 156.59 | AD2-016 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 161.25 | 154.05 | AD2-016 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 148.42 | 152.94 | AD2-016 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 903 | 144.2 | 152.07 | AD2-016 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 152.68 | 151.11 | AD2-016 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 155.48 | 150.34 | AD2-016 | PN_P1-2_PN-500-010T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 903 | 142.66 | 149.44 | AD2-016 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 903 | 142.66 | 149.44 | AD2-016 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 903 | 142.64 | 149.42 | AD2-016 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.26 | 149.33 | AD2-016 | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.19 | 149.26 | AD2-016 | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.94 | 148.19 | AD2-016 | AP_P2-3_PE-500-016_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.01 | 148.16 | AD2-016 | AP_P2-3_PE-500-015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.8 | 147.67 | AD2-016 | PJM_500_BG_P4_5_CNSTN_L_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.98 | 147.55 | AD2-016 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.78 | 147.36 | AD2-016 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.8 | 147.35 | AD2-016 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.12 | 147.3 | AD2-016 | AP_P1-2_PE-500-001_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.12 | 147.3 | AD2-016 | AP_P1-2_WP-500-DRT17_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.07 | 147.23 | AD2-016 | AP_P2-3_PE-500-018C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.53 | 147.15 | AD2-016 | PECO_P4_NOTTI85_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.47 | 147.14 | AD2-016 | PECO_P1-2_220-08_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.4 | 147.07 | AD2-016 | PECO_P4_COOPR125_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3464 | 168.3 | 162.29 | 6HICKORY | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.42 | 143.73 | AD2-016 | PECO_P4_PEACH025_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.33 | 143.67 | AD2-016 | PECO_P1-2_PBTIE1_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 911 | 148.91 | 143.09 | AD2-016 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204502 | 27JACKSON | 204514 | 27TMI | 1 | 230 | 227 | 781 | 132.9 | 141.44 | AD2-016 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204502 | 27JACKSON | 204514 | 27TMI | 1 | 230 | 227 | 781 | 132.9 | 141.44 | AD2-016 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204502 | 27JACKSON | 204514 | 27TMI | 1 | 230 | 227 | 781 | 132.88 | 141.42 | AD2-016 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 903 | 135.59 | 139.6 | AD2-016 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 1031 | 130.24 | 137.98 | AD2-016 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 1031 | 130.24 | 137.98 | AD2-016 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 1031 | 130.23 | 137.97 | AD2-016 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 138.77 | 132.85 | AD2-016 | PECO_P4_PEACH205_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 138.63 | 132.49 | AD2-016 | PECO_P1-2_PBTIE2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208078 | SAKR | 1 | 230 | 229 | 903 | 124.39 | 132.39 | AD2-016 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208078 | SAKR | 1 | 230 | 229 | 903 | 124.39 | 132.39 | AD2-016 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208078 | SAKR | 1 | 230 | 229 | 903 | 124.38 | 132.38 | AD2-016 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 137.71 | 131.64 | AD2-016 | PECO_P4_PEACH055_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204502 | 27JACKSON | 204514 | 27TMI | 1 | 230 | 227 | 781 | 125.26 | 130.89 | AD2-016 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 1031 | 124.64 | 129.2 | AD2-016 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 132.99 | 127.19 | AD2-016 | PECO_P4_PEACH015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 131.7 | 125.89 | AD2-016 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208020 | MANO TR3 | 1 | 230 | 229 | 793 | 111.36 | 124.55 | AD2-016 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208020 | MANO TR3 | 1 | 230 | 229 | 793 | 111.36 | 124.55 | AD2-016 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208020 | MANO TR3 | 1 | 230 | 229 | 793 | 111.36 | 124.54 | AD2-016 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208078 | SAKR | 1 | 230 | 229 | 903 | 117.13 | 122.42 | AD2-016 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204512 | 27S.RDG | 204693 | 27BOONETOWN | 1 | 230 | 227 | 607 | 107.28 | 122.14 | AD2-016 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200025 | W CHAPEL | 1 | 500 | 225 | 1732 | 123.73 | 121.93 | AD2-016 | PEPCO_P4_PP41_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208031 | MLWD TR2 | 1 | 230 | 229 | 911 | 111.68 | 121.13 | AD2-016 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208031 | MLWD TR2 | 1 | 230 | 229 | 911 | 111.68 | 121.13 | AD2-016 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208031 | MLWD TR2 | 1 | 230 | 229 | 911 | 111.68 | 121.12 | AD2-016 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 122.61 | 117.25 | AD2-016 | PECO_P4_PEACH225_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 2 | 500/230 | 225/232 | 2168 | 109.66 | 114.99 | AD2-016 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 2 | 500/230 | 225/232 | 2168 | 109.48 | 114.78 | AD2-016 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 2 | 500/230 | 225/232 | 2168 | 109.48 | 114.78 | AD2-016 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 1 | 500/230 | 225/232 | 2168 | 109.43 | 114.75 | AD2-016 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 1 | 500/230 | 225/232 | 2168 | 109.25 | 114.54 | AD2-016 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 1 | 500/230 | 225/232 | 2168 | 109.25 | 114.54 | AD2-016 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208020 | MANO TR3 | 1 | 230 | 229 | 793 | 104.19 | 113.99 | AD2-016 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208020 | MANO TR3 | 208031 | MLWD TR2 | 1 | 230 | 229 | 903 | 102.5 | 113.68 | AD2-016 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208020 | MANO TR3 | 208031 | MLWD TR2 | 1 | 230 | 229 | 903 | 101.79 | 112.49 | AD2-016 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208020 | MANO TR3 | 208031 | MLWD TR2 | 1 | 230 | 229 | 903 | 101.79 | 112.49 | AD2-016 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208020 | MANO TR3 | 208031 | MLWD TR2 | 1 | 230 | 229 | 903 | 101.79 | 112.48 | AD2-016 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208031 | MLWD TR2 | 1 | 230 | 229 | 911 | 104.93 | 111.65 | AD2-016 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 99.67 | 103.59 | AD2-016 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 99.67 | 103.59 | AD2-016 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 99.66 | 103.58 | AD2-016 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208020 | MANO TR3 | 208031 | MLWD TR2 | 1 | 230 | 229 | 903 | 95.43 | 103.27 | AD2-016 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 98.84 | 100.9 | AD2-016 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 144.31 | 139.17 | AD2-031 | PL_10_P42_100570_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 144.31 | 139.17 | AD2-031 | PL_10_P42_100570_A_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 143.51 | 138.38 | AD2-031 | PL_10_P12_000085_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 143.41 | 138.29 | AD2-031 | PN_P2-3_PN-500-004-DRT-008_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 143.41 | 138.29 | AD2-031 | PN_P2-3_PN-500-DRT31_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3464 | 168.13 | 162.12 | 6HORNRTN | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.31 | 157.44 | AD2-048 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.31 | 157.44 | AD2-048 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 161.8 | 154.58 | AD2-048 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 155.88 | 150.73 | AD2-048 | PN_P1-2_PN-500-010T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.19 | 148.06 | AD2-048 | PJM_500_BG_P4_5_CNSTN_L_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.47 | 148.03 | AD2-048 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.27 | 147.84 | AD2-048 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.29 | 147.83 | AD2-048 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.02 | 147.63 | AD2-048 | PECO_P4_NOTTI85_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.96 | 147.62 | AD2-048 | PECO_P1-2_220-08_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.89 | 147.55 | AD2-048 | PECO_P4_COOPR125_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 151.01 | 144.3 | AD2-048 | PECO_P4_PEACH025_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.89 | 144.21 | AD2-048 | PECO_P1-2_PBTIE1_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 138.99 | 141.28 | AD2-048 | AP_P2-3_WP-500-DRT20_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 138.99 | 141.28 | AD2-048 | AP_P2-2_WP-500-DRT16_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 138.99 | 141.28 | AD2-048 | AP_P1-2_WP-500-005A_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 138.99 | 141.28 | AD2-048 | AP_P2-3_WP-500-465_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 138.99 | 141.28 | AD2-048 | AP_P1-2_WP-500-DRT21_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 138.76 | 140.92 | AD2-048 | AP_P1-2_WP-500-008_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 138.76 | 140.92 | AD2-048 | AP_P2-3_WP-500-DRT45_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 137.17 | 139.13 | AD2-048 | AP_P2-3_WP-500-706T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 136.67 | 138.87 | AD2-048 | PN_P2-3_PN-500-DRT32_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 136.67 | 138.87 | AD2-048 | PN_P2-3_PN-500-004-DRT-002_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 139.26 | 133.32 | AD2-048 | PECO_P4_PEACH205_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 139.15 | 132.99 | AD2-048 | PECO_P1-2_PBTIE2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 138.2 | 132.11 | AD2-048 | PECO_P4_PEACH055_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 133.53 | 127.71 | AD2-048 | PECO_P4_PEACH015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 132.2 | 126.37 | AD2-048 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 123.1 | 117.73 | AD2-048 | PECO_P4_PEACH225_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.33 | 157.46 | AD2-062 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.33 | 157.45 | AD2-062 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 203981 | AD2-062_POI | 235188 | 01GREENE | 1 | 138 | 226/201 | 317 | 161.31 | 154.05 | AD2-062 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 203981 | AD2-062_POI | 235188 | 01GREENE | 1 | 138 | 226/201 | 317 | 161.31 | 154.05 | AD2-062 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 203981 | AD2-062_POI | 235188 | 01GREENE | 1 | 138 | 226/201 | 317 | 161.1 | 153.9 | AD2-062 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 155.88 | 150.71 | AD2-062 | PN_P1-2_PN-500-010T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3464 | 168.19 | 162.18 | 6OLDCHRC | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.51 | 148.07 | AD2-062 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.3 | 147.88 | AD2-062 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.33 | 147.86 | AD2-062 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.06 | 147.67 | AD2-062 | PECO_P4_NOTTI85_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153 | 147.65 | AD2-062 | PECO_P1-2_220-08_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.93 | 147.59 | AD2-062 | PECO_P4_COOPR125_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 151.77 | 147.43 | AD2-062 | AP_P2-3_PE-500-016_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 151.04 | 144.32 | AD2-062 | PECO_P4_PEACH025_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204502 | 27JACKSON | 204514 | 27TMI | 1 | 230 | 227 | 781 | 132.95 | 141.5 | AD2-062 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204502 | 27JACKSON | 204514 | 27TMI | 1 | 230 | 227 | 781 | 132.95 | 141.49 | AD2-062 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204502 | 27JACKSON | 204514 | 27TMI | 1 | 230 | 227 | 781 | 132.94 | 141.49 | AD2-062 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 203981 | AD2-062_POI | 235188 | 01GREENE | 1 | 138 | 226/201 | 317 | 155.66 | 139.45 | AD2-062 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 203981 | AD2-062_POI | 235188 | 01GREENE | 1 | 138 | 226/201 | 317 | 155.66 | 139.45 | AD2-062 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 203981 | AD2-062_POI | 235188 | 01GREENE | 1 | 138 | 226/201 | 317 | 155.66 | 139.45 | AD2-062 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 203981 | AD2-062_POI | 235188 | 01GREENE | 1 | 138 | 226/201 | 317 | 155.43 | 139.11 | AD2-062 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 203981 | AD2-062_POI | 235188 | 01GREENE | 1 | 138 | 226/201 | 317 | 140.92 | 137.56 | AD2-062 | AP_P2-3_PE-500-016_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 135.05 | 137.49 | AD2-062 | AP_P1-2_WP-138-340AT_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 203981 | AD2-062_POI | 235188 | 01GREENE | 1 | 138 | 226/201 | 317 | 141.12 | 137.41 | AD2-062 | AP_P2-3_PE-500-015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 134.8 | 137.21 | AD2-062 | AP_P2-3_WP-138-272T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 203981 | AD2-062_POI | 235188 | 01GREENE | 1 | 138 | 226/201 | 317 | 148.6 | 136.86 | AD2-062 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 134.51 | 136.86 | AD2-062 | AP_P1-2_WP-138-340BT_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 134.51 | 136.86 | AD2-062 | PN_P1-3_PN-115-118_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 134.47 | 136.8 | AD2-062 | PN_P2-3_PN-115-0331-D_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 134.42 | 136.77 | AD2-062 | PN_P2-3_PN-115-0331-A_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 133.69 | 136.02 | AD2-062 | AP_P1-3_WP-138-055_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 133.69 | 136.02 | AD2-062 | AP_P2-2_WP-138-074_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 133.69 | 136.02 | AD2-062 | AP_P2-3_WP-138-271_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 133.14 | 135.33 | AD2-062 | PN_P1-2_PN-115-094_A_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200512 | 26LEWISTWN | 200519 | 26REED TAP | 1 | 115 | 226 | 271 | 122.85 | 131.52 | AD2-062 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200512 | 26LEWISTWN | 200519 | 26REED TAP | 1 | 115 | 226 | 271 | 122.93 | 131.47 | AD2-062 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200512 | 26LEWISTWN | 200519 | 26REED TAP | 1 | 115 | 226 | 271 | 122.93 | 131.47 | AD2-062 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200512 | 26LEWISTWN | 200519 | 26REED TAP | 1 | 115 | 226 | 271 | 122.93 | 131.47 | AD2-062 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204502 | 27JACKSON | 204514 | 27TMI | 1 | 230 | 227 | 781 | 125.3 | 130.91 | AD2-062 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200532 | 26ROXBURY | 203981 | AD2-062_POI | 1 | 138 | 226 | 317 | 136.27 | 128.75 | AD2-062 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200532 | 26ROXBURY | 203981 | AD2-062_POI | 1 | 138 | 226 | 317 | 136.27 | 128.75 | AD2-062 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200532 | 26ROXBURY | 203981 | AD2-062_POI | 1 | 138 | 226 | 317 | 136.07 | 128.6 | AD2-062 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 129.97 | 128.24 | AD2-062 | DVP_P4-2: 514T595_SRT-SW |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200504 | 26CARLISLE | 204528 | 27GARDNERS | 1 | 115 | 226/227 | 190 | 119.54 | 126.78 | AD2-062 | PN_P2-3_PN-115-0331-B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 128.25 | 126.55 | AD2-062 | DVP_P4-2: 51482_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 128.25 | 126.46 | AD2-062 | DVP_P1-2: LN 514_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 128.25 | 126.46 | AD2-062 | AP_P1-2_PE-500-407T_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200519 | 26REED TAP | 200522 | 26SHADE GP | 1 | 115 | 226 | 271 | 115.44 | 126.43 | AD2-062 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200519 | 26REED TAP | 200522 | 26SHADE GP | 1 | 115 | 226 | 271 | 115.51 | 126.39 | AD2-062 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200519 | 26REED TAP | 200522 | 26SHADE GP | 1 | 115 | 226 | 271 | 115.51 | 126.39 | AD2-062 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200519 | 26REED TAP | 200522 | 26SHADE GP | 1 | 115 | 226 | 271 | 115.51 | 126.38 | AD2-062 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 2 | 230 | 233 | 793 | 127.99 | 126.24 | AD2-062 | DVP_P4-2: 514T595_SRT-SW |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 793 | 127.99 | 126.24 | AD2-062 | DVP_P4-2: 514T595_SRT-SW |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200512 | 26LEWISTWN | 200519 | 26REED TAP | 1 | 115 | 226 | 271 | 120.1 | 125.19 | AD2-062 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200504 | 26CARLISLE | 204528 | 27GARDNERS | 1 | 115 | 226/227 | 190 | 117.91 | 125.07 | AD2-062 | PN_P1-2_PN-115-094_A_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 793 | 126.77 | 125.05 | AD2-062 | DVP_P4-2: 51482_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 2 | 230 | 233 | 793 | 126.77 | 125.05 | AD2-062 | DVP_P4-2: 51482_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 793 | 126.77 | 124.98 | AD2-062 | DVP_P1-2: LN 514_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 793 | 126.77 | 124.98 | AD2-062 | AP_P1-2_PE-500-407T_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 2 | 230 | 233 | 793 | 126.77 | 124.98 | AD2-062 | DVP_P1-2: LN 514_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 2 | 230 | 233 | 793 | 126.77 | 124.98 | AD2-062 | AP_P1-2_PE-500-407T_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200504 | 26CARLISLE | 204528 | 27GARDNERS | 1 | 115 | 226/227 | 190 | 117.68 | 124.14 | AD2-062 | PN_P2-3_PN-115-58B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200504 | 26CARLISLE | 204528 | 27GARDNERS | 1 | 115 | 226/227 | 190 | 118.26 | 124.09 | AD2-062 | PN_P1-3_PN-115-040_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200504 | 26CARLISLE | 204528 | 27GARDNERS | 1 | 115 | 226/227 | 190 | 118.26 | 124.09 | AD2-062 | PN_P2-2_PN-115-030_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200504 | 26CARLISLE | 204528 | 27GARDNERS | 1 | 115 | 226/227 | 190 | 117.49 | 124.06 | AD2-062 | PN_P1-2_PN-115-094_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200519 | 26REED TAP | 200522 | 26SHADE GP | 1 | 115 | 226 | 271 | 112.69 | 120.19 | AD2-062 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200504 | 26CARLISLE | 204528 | 27GARDNERS | 1 | 115 | 226/227 | 190 | 115.22 | 119.99 | AD2-062 | PN_P2-3_PN-230-0014-12_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200504 | 26CARLISLE | 204528 | 27GARDNERS | 1 | 115 | 226/227 | 190 | 115.14 | 119.57 | AD2-062 | PN_P2-2_PN-115-031_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200504 | 26CARLISLE | 204528 | 27GARDNERS | 1 | 115 | 226/227 | 190 | 115.21 | 119.43 | AD2-062 | PN_P1-3_PN-230-020A_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200504 | 26CARLISLE | 204528 | 27GARDNERS | 1 | 115 | 226/227 | 190 | 115.21 | 119.43 | AD2-062 | PN_P2-3_PN-230-0014-11_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200512 | 26LEWISTWN | 200519 | 26REED TAP | 1 | 115 | 226 | 271 | 116.49 | 119.06 | AD2-062 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200512 | 26LEWISTWN | 200519 | 26REED TAP | 1 | 115 | 226 | 271 | 116.49 | 119.06 | AD2-062 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200512 | 26LEWISTWN | 200519 | 26REED TAP | 1 | 115 | 226 | 271 | 116.43 | 118.98 | AD2-062 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3464 | 168.29 | 162.27 | 6PAPERMILL | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 793 | 120.26 | 117.52 | AD2-062 | PEPCO_P1_PP2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 2 | 230 | 233 | 793 | 120.26 | 117.52 | AD2-062 | PEPCO_P1_PP1_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 118.48 | 116.57 | AD2-062 | AP_P2-3_PE-500-019C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200519 | 26REED TAP | 200522 | 26SHADE GP | 1 | 115 | 226 | 271 | 109.08 | 114.16 | AD2-062 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200519 | 26REED TAP | 200522 | 26SHADE GP | 1 | 115 | 226 | 271 | 109.08 | 114.16 | AD2-062 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200532 | 26ROXBURY | 203981 | AD2-062_POI | 1 | 138 | 226 | 317 | 130.63 | 114.12 | AD2-062 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200532 | 26ROXBURY | 203981 | AD2-062_POI | 1 | 138 | 226 | 317 | 130.63 | 114.12 | AD2-062 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200532 | 26ROXBURY | 203981 | AD2-062_POI | 1 | 138 | 226 | 317 | 130.62 | 114.12 | AD2-062 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200519 | 26REED TAP | 200522 | 26SHADE GP | 1 | 115 | 226 | 271 | 109.02 | 114.08 | AD2-062 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200532 | 26ROXBURY | 203981 | AD2-062_POI | 1 | 138 | 226 | 317 | 130.4 | 113.77 | AD2-062 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200512 | 26LEWISTWN | 200519 | 26REED TAP | 1 | 115 | 226 | 271 | 114.57 | 113.03 | AD2-062 | ME_P2-3_ME-115-003DT_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200512 | 26LEWISTWN | 200519 | 26REED TAP | 1 | 115 | 226 | 271 | 114.51 | 112.96 | AD2-062 | ME_P2-3_ME-115-003AT_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3464 | 168.3 | 162.28 | 6POWHATN | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200532 | 26ROXBURY | 203981 | AD2-062_POI | 1 | 138 | 226 | 317 | 115.89 | 112.21 | AD2-062 | AP_P2-3_PE-500-016_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200532 | 26ROXBURY | 203981 | AD2-062_POI | 1 | 138 | 226 | 317 | 116.09 | 112.05 | AD2-062 | AP_P2-3_PE-500-015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200532 | 26ROXBURY | 200520 | 26ROXBURY | 2 | 138/115 | 226 | 435 | 99.31 | 112.01 | AD2-062 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200532 | 26ROXBURY | 200520 | 26ROXBURY | 2 | 138/115 | 226 | 435 | 99.31 | 112.01 | AD2-062 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200532 | 26ROXBURY | 200520 | 26ROXBURY | 2 | 138/115 | 226 | 435 | 99.16 | 111.84 | AD2-062 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 793 | 114.43 | 111.8 | AD2-062 | PEPCO_P4_PP19_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200532 | 26ROXBURY | 203981 | AD2-062_POI | 1 | 138 | 226 | 317 | 123.57 | 111.52 | AD2-062 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 2 | 230 | 233 | 793 | 111.02 | 109.13 | AD2-062 | AP_P2-3_PE-500-019C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 793 | 111.02 | 109.13 | AD2-062 | AP_P2-3_PE-500-019C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3464 | 168.28 | 162.27 | 6WINFALL | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200519 | 26REED TAP | 200522 | 26SHADE GP | 1 | 115 | 226 | 271 | 107.16 | 108.21 | AD2-062 | ME_P2-3_ME-115-003DT_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200519 | 26REED TAP | 200522 | 26SHADE GP | 1 | 115 | 226 | 271 | 107.09 | 108.15 | AD2-062 | ME_P2-3_ME-115-003AT_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200532 | 26ROXBURY | 200520 | 26ROXBURY | 2 | 138/115 | 226 | 435 | 95.19 | 108.01 | AD2-062 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200532 | 26ROXBURY | 200520 | 26ROXBURY | 2 | 138/115 | 226 | 435 | 95.19 | 108.01 | AD2-062 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200532 | 26ROXBURY | 200520 | 26ROXBURY | 2 | 138/115 | 226 | 435 | 95.19 | 108 | AD2-062 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200532 | 26ROXBURY | 200520 | 26ROXBURY | 2 | 138/115 | 226 | 435 | 95.02 | 107.84 | AD2-062 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200009 | JUNI | 208004 | JUNI | 2 | 500/230 | 225/229 | 1040 | 107.7 | 107.12 | AD2-062 | PL_10_P42_000140_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204520 | 27ALLEN | 208142 | WIGR-115 | 1 | 115 | 227/229 | 351.4 | 93.99 | 101.6 | AD2-062 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204520 | 27ALLEN | 208142 | WIGR-115 | 1 | 115 | 227/229 | 351.4 | 93.99 | 101.6 | AD2-062 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204520 | 27ALLEN | 208142 | WIGR-115 | 1 | 115 | 227/229 | 351.4 | 93.99 | 101.6 | AD2-062 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204520 | 27ALLEN | 208142 | WIGR-115 | 1 | 115 | 227/229 | 351.4 | 93.76 | 101.43 | AD2-062 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200504 | 26CARLISLE | 200520 | 26ROXBURY | 1 | 115 | 226 | 190 | 91.95 | 101.09 | AD2-062 | PN_P1-2_PN-115-094_A_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200532 | 26ROXBURY | 200520 | 26ROXBURY | 2 | 138/115 | 226 | 435 | 90.05 | 100.89 | AD2-062 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200504 | 26CARLISLE | 200520 | 26ROXBURY | 1 | 115 | 226 | 190 | 91.72 | 100.24 | AD2-062 | PN_P2-3_PN-115-58B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200504 | 26CARLISLE | 200520 | 26ROXBURY | 1 | 115 | 226 | 190 | 92.29 | 100.19 | AD2-062 | PN_P2-2_PN-115-030_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200504 | 26CARLISLE | 200520 | 26ROXBURY | 1 | 115 | 226 | 190 | 92.29 | 100.19 | AD2-062 | PN_P1-3_PN-115-040_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200504 | 26CARLISLE | 200520 | 26ROXBURY | 1 | 115 | 226 | 190 | 91.54 | 100.17 | AD2-062 | PN_P1-2_PN-115-094_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3464 | 168.23 | 162.21 | 6WINTERP | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 153.79 | 158.29 | AD2-072 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.25 | 157.38 | AD2-072 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.25 | 157.38 | AD2-072 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 152.1 | 156.97 | AD2-072 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 161.73 | 154.51 | AD2-072 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 148.73 | 153.32 | AD2-072 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 155.83 | 150.68 | AD2-072 | PN_P1-2_PN-500-010T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.57 | 149.69 | AD2-072 | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.5 | 149.62 | AD2-072 | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.21 | 148.48 | AD2-072 | AP_P2-3_PE-500-016_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.27 | 148.45 | AD2-072 | AP_P2-3_PE-500-015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.14 | 148.01 | AD2-072 | PJM_500_BG_P4_5_CNSTN_L_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.4 | 147.97 | AD2-072 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.2 | 147.78 | AD2-072 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.23 | 147.77 | AD2-072 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.38 | 147.6 | AD2-072 | AP_P1-2_PE-500-001_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.38 | 147.6 | AD2-072 | AP_P1-2_WP-500-DRT17_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.96 | 147.57 | AD2-072 | PECO_P4_NOTTI85_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.9 | 147.55 | AD2-072 | PECO_P1-2_220-08_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.33 | 147.53 | AD2-072 | AP_P2-3_PE-500-018C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.83 | 147.49 | AD2-072 | PECO_P4_COOPR125_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3464 | 168.21 | 162.2 | AA1-018 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.94 | 144.22 | AD2-072 | PECO_P4_PEACH025_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.82 | 144.14 | AD2-072 | PECO_P1-2_PBTIE1_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 139.2 | 133.26 | AD2-072 | PECO_P4_PEACH205_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 139.08 | 132.93 | AD2-072 | PECO_P1-2_PBTIE2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 138.14 | 132.05 | AD2-072 | PECO_P4_PEACH055_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 133.46 | 127.64 | AD2-072 | PECO_P4_PEACH015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 132.13 | 126.31 | AD2-072 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204512 | 27S.RDG | 204693 | 27BOONETOWN | 1 | 230 | 227 | 607 | 107.68 | 123.46 | AD2-072 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 123.04 | 117.66 | AD2-072 | PECO_P4_PEACH225_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 223.73 | 237.22 | AD2-074 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 225.74 | 237.22 | AD2-074 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 225.67 | 237.15 | AD2-074 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 223.67 | 237.15 | AD2-074 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 225.67 | 237.15 | AD2-074 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 223.67 | 237.15 | AD2-074 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 213.68 | 227.06 | AD2-074 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 213.61 | 226.99 | AD2-074 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 213.61 | 226.99 | AD2-074 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 209.42 | 223.85 | AD2-074 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 209.35 | 223.78 | AD2-074 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 209.35 | 223.78 | AD2-074 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 172.85 | 167.87 | AD2-074 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3464 | 168.28 | 162.26 | AA1-038 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 161.86 | 161.99 | AD2-074 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 161.86 | 161.98 | AD2-074 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 161.85 | 161.95 | AD2-074 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 153.61 | 158.08 | AD2-074 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.11 | 157.24 | AD2-074 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.11 | 157.23 | AD2-074 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 151.93 | 156.76 | AD2-074 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 161.61 | 154.38 | AD2-074 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 148.56 | 153.1 | AD2-074 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 155.69 | 150.53 | AD2-074 | PN_P1-2_PN-500-010T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 903 | 142.81 | 149.62 | AD2-074 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 903 | 142.81 | 149.62 | AD2-074 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.4 | 149.49 | AD2-074 | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.33 | 149.42 | AD2-074 | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.02 | 148.23 | AD2-074 | AP_P2-3_PE-500-016_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.08 | 148.2 | AD2-074 | AP_P2-3_PE-500-015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153 | 147.87 | AD2-074 | PJM_500_BG_P4_5_CNSTN_L_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.3 | 147.86 | AD2-074 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.09 | 147.67 | AD2-074 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.12 | 147.66 | AD2-074 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.85 | 147.46 | AD2-074 | PECO_P4_NOTTI85_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.79 | 147.45 | AD2-074 | PECO_P1-2_220-08_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.72 | 147.38 | AD2-074 | PECO_P4_COOPR125_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.2 | 147.36 | AD2-074 | AP_P1-2_WP-500-DRT17_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.2 | 147.36 | AD2-074 | AP_P1-2_PE-500-001_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.15 | 147.28 | AD2-074 | AP_P2-3_PE-500-018C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3464 | 168.62 | 162.6 | AA1-060 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.84 | 144.13 | AD2-074 | PECO_P4_PEACH025_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.68 | 144.01 | AD2-074 | PECO_P1-2_PBTIE1_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 911 | 149.08 | 143.2 | AD2-074 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 139.07 | 133.13 | AD2-074 | PECO_P4_PEACH205_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 138.96 | 132.8 | AD2-074 | PECO_P1-2_PBTIE2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 138.02 | 131.93 | AD2-074 | PECO_P4_PEACH055_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 133.32 | 127.51 | AD2-074 | PECO_P4_PEACH015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 128.61 | 126.92 | AD2-074 | DVP_P4-2: 514T595_SRT-SW |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 132.01 | 126.19 | AD2-074 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 126.86 | 125.14 | AD2-074 | DVP_P4-2: 51482_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 126.86 | 125.05 | AD2-074 | AP_P1-2_PE-500-407T_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 126.86 | 125.05 | AD2-074 | DVP_P1-2: LN 514_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208020 | MANO TR3 | 1 | 230 | 229 | 793 | 111.59 | 124.78 | AD2-074 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200025 | W CHAPEL | 1 | 500 | 225 | 1732 | 123.73 | 121.95 | AD2-074 | PEPCO_P4_PP41_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 122.91 | 117.54 | AD2-074 | PECO_P4_PEACH225_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 117.07 | 115.14 | AD2-074 | AP_P2-3_PE-500-019C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 2 | 500/230 | 225/232 | 2168 | 109.72 | 115.04 | AD2-074 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 1 | 500/230 | 225/232 | 2168 | 109.49 | 114.8 | AD2-074 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 99.55 | 103.5 | AD2-074 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 99.55 | 103.5 | AD2-074 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 99.55 | 103.5 | AD2-074 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 98.63 | 102.17 | AD2-074 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 98.72 | 100.79 | AD2-074 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 225.97 | 240.37 | AD2-076 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 228.01 | 240.36 | AD2-076 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 215.84 | 230.1 | AD2-076 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 211.58 | 226.91 | AD2-076 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 212.17 | 219.75 | AD2-076 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 210.13 | 219.75 | AD2-076 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 200.55 | 210.13 | AD2-076 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 196.28 | 206.79 | AD2-076 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3464 | 168.15 | 162.14 | AA1-063 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 154.27 | 158.86 | AD2-076 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.81 | 157.93 | AD2-076 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.81 | 157.93 | AD2-076 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 152.58 | 157.54 | AD2-076 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 162.51 | 155.25 | AD2-076 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 149.21 | 153.89 | AD2-076 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 156.39 | 151.23 | AD2-076 | PN_P1-2_PN-500-010T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 147.03 | 150.24 | AD2-076 | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.96 | 150.16 | AD2-076 | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.62 | 148.97 | AD2-076 | AP_P2-3_PE-500-016_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.69 | 148.94 | AD2-076 | AP_P2-3_PE-500-015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 154.08 | 148.63 | AD2-076 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.67 | 148.53 | AD2-076 | PJM_500_BG_P4_5_CNSTN_L_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.88 | 148.44 | AD2-076 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.91 | 148.43 | AD2-076 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.63 | 148.23 | AD2-076 | PECO_P4_NOTTI85_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.57 | 148.22 | AD2-076 | PECO_P1-2_220-08_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.51 | 148.15 | AD2-076 | PECO_P4_COOPR125_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.8 | 148.08 | AD2-076 | AP_P1-2_WP-500-DRT17_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.8 | 148.08 | AD2-076 | AP_P1-2_PE-500-001_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.75 | 148.01 | AD2-076 | AP_P2-3_PE-500-018C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3464 | 169.84 | 163.8 | AA1-102 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 151.86 | 145.11 | AD2-076 | PECO_P4_PEACH025_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 151.65 | 144.95 | AD2-076 | PECO_P1-2_PBTIE1_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 139.83 | 133.86 | AD2-076 | PECO_P4_PEACH205_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 139.85 | 133.67 | AD2-076 | PECO_P1-2_PBTIE2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 138.89 | 132.77 | AD2-076 | PECO_P4_PEACH055_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 134.29 | 128.44 | AD2-076 | PECO_P4_PEACH015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 132.89 | 127.02 | AD2-076 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 123.8 | 118.4 | AD2-076 | PECO_P4_PEACH225_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3464 | 167.95 | 161.95 | AA1-139 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 153.78 | 158.28 | AD2-085 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.27 | 157.39 | AD2-085 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.27 | 157.39 | AD2-085 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 152.09 | 156.95 | AD2-085 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 161.78 | 154.55 | AD2-085 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 148.73 | 153.3 | AD2-085 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 155.84 | 150.69 | AD2-085 | PN_P1-2_PN-500-010T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.56 | 149.68 | AD2-085 | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.49 | 149.61 | AD2-085 | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.18 | 148.43 | AD2-085 | AP_P2-3_PE-500-016_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.24 | 148.4 | AD2-085 | AP_P2-3_PE-500-015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.15 | 148.02 | AD2-085 | PJM_500_BG_P4_5_CNSTN_L_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.45 | 148.01 | AD2-085 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.25 | 147.82 | AD2-085 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.27 | 147.81 | AD2-085 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153 | 147.61 | AD2-085 | PECO_P4_NOTTI85_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.94 | 147.6 | AD2-085 | PECO_P1-2_220-08_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.36 | 147.55 | AD2-085 | AP_P1-2_PE-500-001_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.36 | 147.55 | AD2-085 | AP_P1-2_WP-500-DRT17_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.88 | 147.53 | AD2-085 | PECO_P4_COOPR125_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.31 | 147.48 | AD2-085 | AP_P2-3_PE-500-018C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3464 | 168.13 | 162.12 | AA2-053 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 151.01 | 144.29 | AD2-085 | PECO_P4_PEACH025_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.87 | 144.19 | AD2-085 | PECO_P1-2_PBTIE1_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 139.23 | 133.29 | AD2-085 | PECO_P4_PEACH205_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 139.13 | 132.97 | AD2-085 | PECO_P1-2_PBTIE2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 138.18 | 132.09 | AD2-085 | PECO_P4_PEACH055_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 133.5 | 127.68 | AD2-085 | PECO_P4_PEACH015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 128.94 | 127.2 | AD2-085 | DVP_P4-2: 514T595_SRT-SW |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 132.17 | 126.35 | AD2-085 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 127.2 | 125.49 | AD2-085 | DVP_P4-2: 51482_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 127.2 | 125.4 | AD2-085 | AP_P1-2_PE-500-407T_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 127.2 | 125.4 | AD2-085 | DVP_P1-2: LN 514_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 123.08 | 117.7 | AD2-085 | PECO_P4_PEACH225_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 117.39 | 115.48 | AD2-085 | AP_P2-3_PE-500-019C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 223.46 | 236.94 | AD2-093 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 225.46 | 236.94 | AD2-093 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 225.4 | 236.84 | AD2-093 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 223.39 | 236.84 | AD2-093 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 225.4 | 236.84 | AD2-093 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 223.39 | 236.84 | AD2-093 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 213.41 | 226.78 | AD2-093 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 213.35 | 226.69 | AD2-093 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 213.35 | 226.69 | AD2-093 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 209.15 | 223.57 | AD2-093 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 209.09 | 223.48 | AD2-093 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 209.09 | 223.48 | AD2-093 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 208.57 | 217.76 | AD2-093 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 210.57 | 217.75 | AD2-093 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 199.04 | 208.19 | AD2-093 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 194.78 | 204.84 | AD2-093 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 172.77 | 167.84 | AD2-093 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 163.62 | 164.97 | AD2-093 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 161.74 | 161.88 | AD2-093 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 161.74 | 161.88 | AD2-093 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 161.73 | 161.87 | AD2-093 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3464 | 168.16 | 162.15 | AA2-057 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 153.57 | 158.04 | AD2-093 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.01 | 157.14 | AD2-093 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.01 | 157.14 | AD2-093 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 151.89 | 156.72 | AD2-093 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 161.4 | 154.19 | AD2-093 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 148.52 | 153.07 | AD2-093 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 152.81 | 151.26 | AD2-093 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 155.59 | 150.44 | AD2-093 | PN_P1-2_PN-500-010T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 903 | 142.74 | 149.61 | AD2-093 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 903 | 142.76 | 149.59 | AD2-093 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 903 | 142.76 | 149.59 | AD2-093 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.37 | 149.45 | AD2-093 | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.29 | 149.38 | AD2-093 | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.03 | 148.29 | AD2-093 | AP_P2-3_PE-500-016_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.1 | 148.26 | AD2-093 | AP_P2-3_PE-500-015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.9 | 147.78 | AD2-093 | PJM_500_BG_P4_5_CNSTN_L_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.1 | 147.67 | AD2-093 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.9 | 147.49 | AD2-093 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.93 | 147.47 | AD2-093 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.21 | 147.41 | AD2-093 | AP_P1-2_PE-500-001_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.21 | 147.41 | AD2-093 | AP_P1-2_WP-500-DRT17_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.16 | 147.34 | AD2-093 | AP_P2-3_PE-500-018C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.66 | 147.28 | AD2-093 | PECO_P4_NOTTI85_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.6 | 147.26 | AD2-093 | PECO_P1-2_220-08_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.53 | 147.2 | AD2-093 | PECO_P4_COOPR125_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3464 | 168.05 | 162.04 | AA2-088 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.57 | 143.87 | AD2-093 | PECO_P4_PEACH025_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.48 | 143.81 | AD2-093 | PECO_P1-2_PBTIE1_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 911 | 149.02 | 143.2 | AD2-093 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204502 | 27JACKSON | 204514 | 27TMI | 1 | 230 | 227 | 781 | 132.98 | 141.6 | AD2-093 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204502 | 27JACKSON | 204514 | 27TMI | 1 | 230 | 227 | 781 | 132.99 | 141.59 | AD2-093 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204502 | 27JACKSON | 204514 | 27TMI | 1 | 230 | 227 | 781 | 132.99 | 141.59 | AD2-093 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 1031 | 130.31 | 138.14 | AD2-093 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 1031 | 130.32 | 138.12 | AD2-093 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 1031 | 130.32 | 138.12 | AD2-093 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 138.9 | 132.97 | AD2-093 | PECO_P4_PEACH205_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 138.77 | 132.62 | AD2-093 | PECO_P1-2_PBTIE2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208078 | SAKR | 1 | 230 | 229 | 903 | 124.49 | 132.57 | AD2-093 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208078 | SAKR | 1 | 230 | 229 | 903 | 124.49 | 132.54 | AD2-093 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208078 | SAKR | 1 | 230 | 229 | 903 | 124.49 | 132.54 | AD2-093 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 137.84 | 131.76 | AD2-093 | PECO_P4_PEACH055_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 133.14 | 127.33 | AD2-093 | PECO_P4_PEACH015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 131.83 | 126.02 | AD2-093 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208020 | MANO TR3 | 1 | 230 | 229 | 793 | 111.47 | 124.7 | AD2-093 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208020 | MANO TR3 | 1 | 230 | 229 | 793 | 111.47 | 124.7 | AD2-093 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208020 | MANO TR3 | 1 | 230 | 229 | 793 | 111.46 | 124.66 | AD2-093 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208078 | SAKR | 1 | 230 | 229 | 903 | 117.23 | 122.56 | AD2-093 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200025 | W CHAPEL | 1 | 500 | 225 | 1732 | 123.8 | 122.01 | AD2-093 | PEPCO_P4_PP41_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208031 | MLWD TR2 | 1 | 230 | 229 | 911 | 111.78 | 121.27 | AD2-093 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208031 | MLWD TR2 | 1 | 230 | 229 | 911 | 111.78 | 121.27 | AD2-093 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 122.74 | 117.38 | AD2-093 | PECO_P4_PEACH225_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 99.69 | 103.65 | AD2-093 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 99.69 | 103.64 | AD2-093 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 99.69 | 103.64 | AD2-093 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3464 | 168.13 | 162.12 | AA2-178 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 153.76 | 158.26 | AD2-134 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.22 | 157.35 | AD2-134 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.22 | 157.35 | AD2-134 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 152.07 | 156.93 | AD2-134 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 161.69 | 154.47 | AD2-134 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 148.71 | 153.28 | AD2-134 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 155.8 | 150.65 | AD2-134 | PN_P1-2_PN-500-010T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.54 | 149.66 | AD2-134 | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.47 | 149.59 | AD2-134 | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.18 | 148.46 | AD2-134 | AP_P2-3_PE-500-016_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.25 | 148.43 | AD2-134 | AP_P2-3_PE-500-015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.11 | 147.98 | AD2-134 | PJM_500_BG_P4_5_CNSTN_L_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.36 | 147.93 | AD2-134 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.16 | 147.74 | AD2-134 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.19 | 147.73 | AD2-134 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.36 | 147.57 | AD2-134 | AP_P1-2_WP-500-DRT17_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.36 | 147.57 | AD2-134 | AP_P1-2_PE-500-001_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.92 | 147.53 | AD2-134 | PECO_P4_NOTTI85_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.86 | 147.52 | AD2-134 | PECO_P1-2_220-08_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.31 | 147.5 | AD2-134 | AP_P2-3_PE-500-018C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.79 | 147.45 | AD2-134 | PECO_P4_COOPR125_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3464 | 168.61 | 162.59 | AA2-184 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.89 | 144.18 | AD2-134 | PECO_P4_PEACH025_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.77 | 144.1 | AD2-134 | PECO_P1-2_PBTIE1_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 139.16 | 133.22 | AD2-134 | PECO_P4_PEACH205_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 139.04 | 132.89 | AD2-134 | PECO_P1-2_PBTIE2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 138.1 | 132.01 | AD2-134 | PECO_P4_PEACH055_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 133.42 | 127.6 | AD2-134 | PECO_P4_PEACH015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 132.09 | 126.27 | AD2-134 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204512 | 27S.RDG | 204693 | 27BOONETOWN | 1 | 230 | 227 | 607 | 107.66 | 123.4 | AD2-134 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 123 | 117.63 | AD2-134 | PECO_P4_PEACH225_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 225.78 | 237.26 | AD2-158 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 223.77 | 237.26 | AD2-158 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 225.71 | 237.19 | AD2-158 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 223.71 | 237.19 | AD2-158 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 225.71 | 237.19 | AD2-158 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 223.7 | 237.19 | AD2-158 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 213.71 | 227.09 | AD2-158 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 213.65 | 227.03 | AD2-158 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 213.65 | 227.03 | AD2-158 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 209.45 | 223.89 | AD2-158 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 209.39 | 223.82 | AD2-158 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 209.39 | 223.82 | AD2-158 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 172.89 | 167.92 | AD2-158 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3464 | 168.13 | 162.12 | AB1-006 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 153.63 | 158.1 | AD2-158 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.14 | 157.26 | AD2-158 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.14 | 157.26 | AD2-158 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 151.95 | 156.78 | AD2-158 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 161.63 | 154.41 | AD2-158 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 148.59 | 153.13 | AD2-158 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 155.71 | 150.55 | AD2-158 | PN_P1-2_PN-500-010T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.42 | 149.51 | AD2-158 | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.35 | 149.44 | AD2-158 | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.02 | 148.23 | AD2-158 | AP_P2-3_PE-500-016_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.08 | 148.19 | AD2-158 | AP_P2-3_PE-500-015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.02 | 147.89 | AD2-158 | PJM_500_BG_P4_5_CNSTN_L_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.32 | 147.88 | AD2-158 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.12 | 147.69 | AD2-158 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.14 | 147.68 | AD2-158 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.87 | 147.48 | AD2-158 | PECO_P4_NOTTI85_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.81 | 147.47 | AD2-158 | PECO_P1-2_220-08_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.75 | 147.4 | AD2-158 | PECO_P4_COOPR125_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.2 | 147.34 | AD2-158 | AP_P1-2_WP-500-DRT17_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.2 | 147.34 | AD2-158 | AP_P1-2_PE-500-001_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.16 | 147.29 | AD2-158 | AP_P2-3_PE-500-018C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3464 | 169.72 | 163.68 | AB1-056 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.86 | 144.15 | AD2-158 | PECO_P4_PEACH025_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.71 | 144.04 | AD2-158 | PECO_P1-2_PBTIE1_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 911 | 149.13 | 143.25 | AD2-158 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 139.09 | 133.15 | AD2-158 | PECO_P4_PEACH205_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 138.98 | 132.83 | AD2-158 | PECO_P1-2_PBTIE2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 138.04 | 131.96 | AD2-158 | PECO_P4_PEACH055_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 133.35 | 127.53 | AD2-158 | PECO_P4_PEACH015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 132.03 | 126.21 | AD2-158 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 122.93 | 117.56 | AD2-158 | PECO_P4_PEACH225_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 793 | 119.93 | 117.2 | AD2-158 | PEPCO_P1_PP2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 2 | 230 | 233 | 793 | 119.93 | 117.2 | AD2-158 | PEPCO_P1_PP1_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 99.57 | 103.51 | AD2-158 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 99.56 | 103.51 | AD2-158 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 99.57 | 103.51 | AD2-158 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 98.64 | 102.18 | AD2-158 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 98.74 | 100.81 | AD2-158 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3464 | 168.14 | 162.13 | AB1-081 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 153.78 | 158.28 | AD2-160 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.27 | 157.4 | AD2-160 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.27 | 157.39 | AD2-160 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 152.09 | 156.96 | AD2-160 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 161.79 | 154.56 | AD2-160 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 148.73 | 153.31 | AD2-160 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 155.84 | 150.69 | AD2-160 | PN_P1-2_PN-500-010T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.56 | 149.68 | AD2-160 | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.49 | 149.61 | AD2-160 | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.18 | 148.44 | AD2-160 | AP_P2-3_PE-500-016_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.25 | 148.41 | AD2-160 | AP_P2-3_PE-500-015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.16 | 148.02 | AD2-160 | PJM_500_BG_P4_5_CNSTN_L_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.45 | 148.01 | AD2-160 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.25 | 147.83 | AD2-160 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.28 | 147.81 | AD2-160 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.01 | 147.62 | AD2-160 | PECO_P4_NOTTI85_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.95 | 147.6 | AD2-160 | PECO_P1-2_220-08_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.36 | 147.55 | AD2-160 | AP_P1-2_PE-500-001_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.36 | 147.55 | AD2-160 | AP_P1-2_WP-500-DRT17_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.88 | 147.54 | AD2-160 | PECO_P4_COOPR125_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.31 | 147.49 | AD2-160 | AP_P2-3_PE-500-018C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3464 | 167.98 | 161.97 | AB1-132 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 151.01 | 144.29 | AD2-160 | PECO_P4_PEACH025_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.87 | 144.19 | AD2-160 | PECO_P1-2_PBTIE1_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 139.24 | 133.29 | AD2-160 | PECO_P4_PEACH205_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 139.13 | 132.97 | AD2-160 | PECO_P1-2_PBTIE2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 138.18 | 132.09 | AD2-160 | PECO_P4_PEACH055_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 133.51 | 127.68 | AD2-160 | PECO_P4_PEACH015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 128.94 | 127.21 | AD2-160 | DVP_P4-2: 514T595_SRT-SW |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 132.18 | 126.35 | AD2-160 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 127.2 | 125.49 | AD2-160 | DVP_P4-2: 51482_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 127.2 | 125.4 | AD2-160 | AP_P1-2_PE-500-407T_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 127.2 | 125.4 | AD2-160 | DVP_P1-2: LN 514_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 123.08 | 117.7 | AD2-160 | PECO_P4_PEACH225_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 117.4 | 115.48 | AD2-160 | AP_P2-3_PE-500-019C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 225.63 | 237.15 | AD2-163 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 223.62 | 237.15 | AD2-163 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 225.56 | 237.09 | AD2-163 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 223.56 | 237.09 | AD2-163 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 225.56 | 237.09 | AD2-163 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 223.55 | 237.09 | AD2-163 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 213.57 | 226.99 | AD2-163 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 213.51 | 226.93 | AD2-163 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 213.5 | 226.93 | AD2-163 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 209.31 | 223.78 | AD2-163 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 209.25 | 223.72 | AD2-163 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 209.25 | 223.72 | AD2-163 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 208.73 | 217.96 | AD2-163 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 210.73 | 217.96 | AD2-163 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 199.19 | 208.39 | AD2-163 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 194.93 | 205.04 | AD2-163 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 172.86 | 167.93 | AD2-163 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3464 | 168.64 | 162.62 | AB1-141 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 153.65 | 158.14 | AD2-163 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.1 | 157.23 | AD2-163 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.1 | 157.23 | AD2-163 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 151.97 | 156.81 | AD2-163 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 161.52 | 154.3 | AD2-163 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 148.6 | 153.16 | AD2-163 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 155.68 | 150.53 | AD2-163 | PN_P1-2_PN-500-010T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.44 | 149.54 | AD2-163 | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.37 | 149.47 | AD2-163 | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.1 | 148.37 | AD2-163 | AP_P2-3_PE-500-016_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.17 | 148.34 | AD2-163 | AP_P2-3_PE-500-015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.99 | 147.87 | AD2-163 | PJM_500_BG_P4_5_CNSTN_L_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.21 | 147.78 | AD2-163 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.01 | 147.59 | AD2-163 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.04 | 147.58 | AD2-163 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.28 | 147.48 | AD2-163 | AP_P1-2_WP-500-DRT17_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.28 | 147.48 | AD2-163 | AP_P1-2_PE-500-001_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.23 | 147.41 | AD2-163 | AP_P2-3_PE-500-018C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.77 | 147.38 | AD2-163 | PECO_P4_NOTTI85_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.71 | 147.37 | AD2-163 | PECO_P1-2_220-08_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.64 | 147.3 | AD2-163 | PECO_P4_COOPR125_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3464 | 168.64 | 162.62 | AB1-142 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.7 | 144 | AD2-163 | PECO_P4_PEACH025_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.6 | 143.93 | AD2-163 | PECO_P1-2_PBTIE1_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 911 | 149.11 | 143.27 | AD2-163 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 139.01 | 133.08 | AD2-163 | PECO_P4_PEACH205_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 138.88 | 132.73 | AD2-163 | PECO_P1-2_PBTIE2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 137.95 | 131.87 | AD2-163 | PECO_P4_PEACH055_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 133.26 | 127.44 | AD2-163 | PECO_P4_PEACH015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 131.94 | 126.13 | AD2-163 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 122.85 | 117.48 | AD2-163 | PECO_P4_PEACH225_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 144.31 | 139.17 | AD2-172 | PL_10_P42_100570_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 144.31 | 139.17 | AD2-172 | PL_10_P42_100570_A_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 143.41 | 138.28 | AD2-172 | PN_P2-3_PN-500-004-DRT-008_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 143.41 | 138.28 | AD2-172 | PN_P2-3_PN-500-DRT31_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3464 | 168.22 | 162.2 | AB1-173 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.3 | 157.42 | AD2-180 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.3 | 157.42 | AD2-180 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 161.8 | 154.57 | AD2-180 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 155.87 | 150.72 | AD2-180 | PN_P1-2_PN-500-010T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.18 | 148.05 | AD2-180 | PJM_500_BG_P4_5_CNSTN_L_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.46 | 148.02 | AD2-180 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.26 | 147.84 | AD2-180 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.29 | 147.82 | AD2-180 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.02 | 147.63 | AD2-180 | PECO_P4_NOTTI85_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.95 | 147.61 | AD2-180 | PECO_P1-2_220-08_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.89 | 147.55 | AD2-180 | PECO_P4_COOPR125_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3464 | 168.64 | 162.62 | AB2-032 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 142.84 | 146.91 | AD2-180 | AP_P2-3_WP-500-DRT19_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 142.84 | 146.91 | AD2-180 | AP_P2-3_WP-500-466_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 142.84 | 146.91 | AD2-180 | AP_P1-2_WP-500-006_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 142.84 | 146.91 | AD2-180 | AP_P1-2_PE-500-004_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 142.84 | 146.91 | AD2-180 | AP_P2-3_PE-500-014_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 151.01 | 144.29 | AD2-180 | PECO_P4_PEACH025_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.88 | 144.21 | AD2-180 | PECO_P1-2_PBTIE1_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 139.27 | 142.08 | AD2-180 | DVP_P4-2: 551TB3_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 139.22 | 142 | AD2-180 | AP_P1-2_PE-500-402AT_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 139.27 | 141.98 | AD2-180 | DVP_P4-2: 551TB4_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 139.26 | 141.97 | AD2-180 | AP_P1-2_PE-500-402BT_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 138.92 | 141.68 | AD2-180 | AP_P2-3_PE-500-019D_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 139.25 | 133.31 | AD2-180 | PECO_P4_PEACH205_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 139.14 | 132.99 | AD2-180 | PECO_P1-2_PBTIE2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 138.2 | 132.1 | AD2-180 | PECO_P4_PEACH055_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 133.53 | 127.7 | AD2-180 | PECO_P4_PEACH015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 132.19 | 126.37 | AD2-180 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 123.1 | 117.72 | AD2-180 | PECO_P4_PEACH225_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3464 | 169.32 | 163.29 | AB2-036 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 162.17 | 154.93 | AD2-213 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.78 | 148.34 | AD2-213 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.58 | 148.15 | AD2-213 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.61 | 148.14 | AD2-213 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.34 | 147.94 | AD2-213 | PECO_P4_NOTTI85_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.28 | 147.93 | AD2-213 | PECO_P1-2_220-08_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.21 | 147.86 | AD2-213 | PECO_P4_COOPR125_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.05 | 147.72 | AD2-213 | AP_P2-3_PE-500-016_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.09 | 147.7 | AD2-213 | AP_P2-3_PE-500-015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.87 | 147.67 | AD2-213 | PECO_P1-2_220-93_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 151.57 | 147.24 | AD2-213 | AP_P1-2_PE-500-001_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 151.4 | 144.67 | AD2-213 | PECO_P4_PEACH025_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 151.28 | 144.59 | AD2-213 | PECO_P1-2_PBTIE1_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 139.51 | 133.34 | AD2-213 | PECO_P1-2_PBTIE2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 133.92 | 128.08 | AD2-213 | PECO_P4_PEACH015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 123.46 | 118.06 | AD2-213 | PECO_P4_PEACH225_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 144.32 | 139.17 | AE1-040 | PL_10_P42_100570_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 144.32 | 139.17 | AE1-040 | PL_10_P42_100570_A_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 143.51 | 138.38 | AE1-040 | PL_10_P12_000085_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 143.42 | 138.29 | AE1-040 | PN_P2-3_PN-500-004-DRT-008_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 143.42 | 138.29 | AE1-040 | PN_P2-3_PN-500-DRT31_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 143.04 | 137.92 | AE1-040 | PL_30_P42_000131_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 225.9 | 237.96 | AE1-044 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 223.9 | 237.96 | AE1-044 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 222.95 | 235.86 | AE1-044 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 224.94 | 235.86 | AE1-044 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 224.88 | 235.79 | AE1-044 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 222.89 | 235.79 | AE1-044 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 224.88 | 235.79 | AE1-044 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 222.89 | 235.79 | AE1-044 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 213.84 | 227.77 | AE1-044 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 212.92 | 225.73 | AE1-044 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 212.86 | 225.67 | AE1-044 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 212.86 | 225.67 | AE1-044 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 209.58 | 224.57 | AE1-044 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 208.67 | 222.51 | AE1-044 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 208.6 | 222.45 | AE1-044 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 208.6 | 222.45 | AE1-044 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 210.05 | 216.88 | AE1-044 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 208.06 | 216.87 | AE1-044 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 198.54 | 207.33 | AE1-044 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 194.29 | 203.97 | AE1-044 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 172.26 | 167.25 | AE1-044 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 171.29 | 165.88 | AE1-044 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 171.29 | 165.88 | AE1-044 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 171.27 | 165.87 | AE1-044 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 163.12 | 164.17 | AE1-044 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3464 | 170.43 | 164.38 | AB2-037 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 161.25 | 161.13 | AE1-044 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 161.25 | 161.13 | AE1-044 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 161.23 | 161.12 | AE1-044 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 163.35 | 158.45 | AE1-044 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 153.05 | 157.4 | AE1-044 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 161.58 | 156.7 | AE1-044 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 161.58 | 156.7 | AE1-044 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 151.37 | 156.08 | AE1-044 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 161.01 | 153.81 | AE1-044 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 148.01 | 152.43 | AE1-044 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 903 | 143.83 | 151.45 | AE1-044 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 152.31 | 150.6 | AE1-044 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 155.17 | 150.02 | AE1-044 | PN_P1-2_PN-500-010T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 145.87 | 148.85 | AE1-044 | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 145.8 | 148.78 | AE1-044 | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 903 | 142.3 | 148.77 | AE1-044 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 903 | 142.3 | 148.77 | AE1-044 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 903 | 142.28 | 148.76 | AE1-044 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.47 | 147.56 | AE1-044 | AP_P2-3_PE-500-016_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.53 | 147.53 | AE1-044 | AP_P2-3_PE-500-015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.49 | 147.36 | AE1-044 | PJM_500_BG_P4_5_CNSTN_L_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.78 | 147.35 | AE1-044 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.58 | 147.16 | AE1-044 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.6 | 147.15 | AE1-044 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.33 | 146.96 | AE1-044 | PECO_P4_NOTTI85_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.27 | 146.94 | AE1-044 | PECO_P1-2_220-08_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.21 | 146.87 | AE1-044 | PECO_P4_COOPR125_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 142.65 | 146.68 | AE1-044 | AP_P1-2_WP-500-DRT17_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 142.65 | 146.68 | AE1-044 | AP_P1-2_PE-500-001_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 142.6 | 146.62 | AE1-044 | AP_P2-3_PE-500-018C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 145.83 | 146.26 | AE1-044 | BG_P7_GRCTN_CNSTN_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3464 | 168.13 | 162.12 | AB2-040 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.26 | 143.58 | AE1-044 | PECO_P4_PEACH025_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.06 | 143.41 | AE1-044 | PECO_P1-2_PBTIE1_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 911 | 148.52 | 142.67 | AE1-044 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 911 | 147.57 | 141.42 | AE1-044 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 911 | 147.57 | 141.42 | AE1-044 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 911 | 147.56 | 141.41 | AE1-044 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204502 | 27JACKSON | 204514 | 27TMI | 1 | 230 | 227 | 781 | 132.52 | 141.03 | AE1-044 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204502 | 27JACKSON | 204514 | 27TMI | 1 | 230 | 227 | 781 | 132.72 | 140.98 | AE1-044 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204502 | 27JACKSON | 204514 | 27TMI | 1 | 230 | 227 | 781 | 132.72 | 140.98 | AE1-044 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204502 | 27JACKSON | 204514 | 27TMI | 1 | 230 | 227 | 781 | 132.7 | 140.97 | AE1-044 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 140.66 | 140.27 | AE1-044 | PJM_500_BG_P4_5_CNSTN_15_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 903 | 135.22 | 138.97 | AE1-044 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 1031 | 130.51 | 138.59 | AE1-044 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 1031 | 130.01 | 137.48 | AE1-044 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 1031 | 130.01 | 137.48 | AE1-044 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 1031 | 130 | 137.48 | AE1-044 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 911 | 139.71 | 134.71 | AE1-044 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 207922 | BRIS | 207923 | BRISREAC | RX | 230 | 229 | 676 | 124.74 | 133.85 | AE1-044 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 207923 | BRISREAC | 208132 | WHEM TR1 | 1 | 230 | 229 | 676 | 124.74 | 133.85 | AE1-044 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208078 | SAKR | 1 | 230 | 229 | 903 | 124.86 | 133.35 | AE1-044 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 138.5 | 132.58 | AE1-044 | PECO_P4_PEACH205_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 207923 | BRISREAC | 208132 | WHEM TR1 | 1 | 230 | 229 | 676 | 123.99 | 132.31 | AE1-044 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 207922 | BRIS | 207923 | BRISREAC | RX | 230 | 229 | 676 | 123.99 | 132.31 | AE1-044 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 207923 | BRISREAC | 208132 | WHEM TR1 | 1 | 230 | 229 | 676 | 123.99 | 132.31 | AE1-044 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 207922 | BRIS | 207923 | BRISREAC | RX | 230 | 229 | 676 | 123.99 | 132.31 | AE1-044 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 207922 | BRIS | 207923 | BRISREAC | RX | 230 | 229 | 676 | 123.98 | 132.3 | AE1-044 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 207923 | BRISREAC | 208132 | WHEM TR1 | 1 | 230 | 229 | 676 | 123.98 | 132.3 | AE1-044 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 138.38 | 132.25 | AE1-044 | PECO_P1-2_PBTIE2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208078 | SAKR | 1 | 230 | 229 | 903 | 124.12 | 131.94 | AE1-044 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208078 | SAKR | 1 | 230 | 229 | 903 | 124.12 | 131.94 | AE1-044 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208078 | SAKR | 1 | 230 | 229 | 903 | 124.12 | 131.94 | AE1-044 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 137.48 | 131.42 | AE1-044 | PECO_P4_PEACH055_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204502 | 27JACKSON | 204514 | 27TMI | 1 | 230 | 227 | 781 | 125.07 | 130.5 | AE1-044 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220972 | GRANITE1 | 1 | 230 | 232 | 829 | 134.45 | 130.49 | AE1-044 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220972 | GRANITE1 | 1 | 230 | 232 | 829 | 133.82 | 129.83 | AE1-044 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220972 | GRANITE1 | 1 | 230 | 232 | 829 | 133.82 | 129.83 | AE1-044 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 1031 | 124.41 | 128.77 | AE1-044 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220973 | GRANITE6 | 1 | 230 | 232 | 829 | 132.39 | 128.6 | AE1-044 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220973 | GRANITE6 | 1 | 230 | 232 | 829 | 131.79 | 127.98 | AE1-044 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220973 | GRANITE6 | 1 | 230 | 232 | 829 | 131.79 | 127.98 | AE1-044 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 132.71 | 126.91 | AE1-044 | PECO_P4_PEACH015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 131.44 | 125.65 | AE1-044 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208020 | MANO TR3 | 1 | 230 | 229 | 793 | 111.94 | 125.5 | AE1-044 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 127.25 | 125.47 | AE1-044 | DVP_P4-2: 514T595_SRT-SW |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 911 | 122.73 | 125.15 | AE1-044 | BG_P7_GRCTN_CNSTN_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220953 | HOWARD12 | 220972 | GRANITE1 | 1 | 230 | 232 | 772 | 129.14 | 125.15 | AE1-044 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220954 | HOWARD32 | 220973 | GRANITE6 | 1 | 230 | 232 | 772 | 128.02 | 124.48 | AE1-044 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 207922 | BRIS | 207923 | BRISREAC | RX | 230 | 229 | 676 | 118.89 | 124.23 | AE1-044 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 207923 | BRISREAC | 208132 | WHEM TR1 | 1 | 230 | 229 | 676 | 118.89 | 124.23 | AE1-044 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220953 | HOWARD12 | 220972 | GRANITE1 | 1 | 230 | 232 | 772 | 128.22 | 124.18 | AE1-044 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220953 | HOWARD12 | 220972 | GRANITE1 | 1 | 230 | 232 | 772 | 128.22 | 124.18 | AE1-044 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208020 | MANO TR3 | 1 | 230 | 229 | 793 | 111.12 | 123.95 | AE1-044 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208020 | MANO TR3 | 1 | 230 | 229 | 793 | 111.11 | 123.95 | AE1-044 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208020 | MANO TR3 | 1 | 230 | 229 | 793 | 111.12 | 123.95 | AE1-044 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 793 | 125.7 | 123.89 | AE1-044 | DVP_P4-2: 514T595_SRT-SW |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 2 | 230 | 233 | 793 | 125.7 | 123.89 | AE1-044 | DVP_P4-2: 514T595_SRT-SW |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 125.47 | 123.71 | AE1-044 | DVP_P4-2: 51482_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220954 | HOWARD32 | 220973 | GRANITE6 | 1 | 230 | 232 | 772 | 127.22 | 123.64 | AE1-044 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220954 | HOWARD32 | 220973 | GRANITE6 | 1 | 230 | 232 | 772 | 127.22 | 123.63 | AE1-044 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 125.47 | 123.57 | AE1-044 | DVP_P1-2: LN 514_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 125.47 | 123.57 | AE1-044 | AP_P1-2_PE-500-407T_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 2 | 230 | 233 | 793 | 124.43 | 122.66 | AE1-044 | DVP_P4-2: 51482_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 793 | 124.43 | 122.66 | AE1-044 | DVP_P4-2: 51482_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 793 | 124.43 | 122.53 | AE1-044 | AP_P1-2_PE-500-407T_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 2 | 230 | 233 | 793 | 124.43 | 122.53 | AE1-044 | AP_P1-2_PE-500-407T_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 2 | 230 | 233 | 793 | 124.43 | 122.53 | AE1-044 | DVP_P1-2: LN 514_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 793 | 124.43 | 122.53 | AE1-044 | DVP_P1-2: LN 514_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 119.64 | 122.36 | AE1-044 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 117.65 | 122.36 | AE1-044 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 117.47 | 122.14 | AE1-044 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 119.46 | 122.14 | AE1-044 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 119.46 | 122.14 | AE1-044 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 117.47 | 122.14 | AE1-044 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208078 | SAKR | 1 | 230 | 229 | 903 | 116.86 | 122.05 | AE1-044 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208031 | MLWD TR2 | 1 | 230 | 229 | 911 | 112.16 | 122.04 | AE1-044 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200025 | W CHAPEL | 1 | 500 | 225 | 1732 | 123.27 | 121.46 | AE1-044 | PEPCO_P4_PP41_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204512 | 27S.RDG | 204693 | 27BOONETOWN | 1 | 230 | 227 | 607 | 107.24 | 121.13 | AE1-044 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204512 | 27S.RDG | 204693 | 27BOONETOWN | 1 | 230 | 227 | 607 | 107.22 | 121.1 | AE1-044 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204512 | 27S.RDG | 204693 | 27BOONETOWN | 1 | 230 | 227 | 607 | 107.22 | 121.1 | AE1-044 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208031 | MLWD TR2 | 1 | 230 | 229 | 911 | 111.44 | 120.63 | AE1-044 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208031 | MLWD TR2 | 1 | 230 | 229 | 911 | 111.44 | 120.63 | AE1-044 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208031 | MLWD TR2 | 1 | 230 | 229 | 911 | 111.44 | 120.63 | AE1-044 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200532 | 26ROXBURY | 200520 | 26ROXBURY | 2 | 138/115 | 226 | 435 | 104.83 | 119.05 | AE1-044 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200532 | 26ROXBURY | 200520 | 26ROXBURY | 2 | 138/115 | 226 | 435 | 104.83 | 119.05 | AE1-044 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200532 | 26ROXBURY | 200520 | 26ROXBURY | 2 | 138/115 | 226 | 435 | 104.68 | 118.88 | AE1-044 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220965 | NEAST339 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 119.46 | 118.8 | AE1-044 | BG_P1_2315_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208131 | WHEM | 208132 | WHEM TR1 | 1 | 230 | 229 | 691 | 109.01 | 118.67 | AE1-044 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 911 | 117.68 | 118.66 | AE1-044 | PJM_500_BG_P4_5_CNSTN_15_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220965 | NEAST339 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 119.04 | 118.6 | AE1-044 | BG_P4_5_NEAST_17_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220965 | NEAST339 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 119.2 | 118.6 | AE1-044 | BG_P4_5_NEAST_15_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 114.42 | 118.07 | AE1-044 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220979 | NEAST317 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 118.54 | 117.94 | AE1-044 | BG_P1_2337_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 114.08 | 117.73 | AE1-044 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220979 | NEAST317 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 118.22 | 117.67 | AE1-044 | BG_P4_5_NEAST_39_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220979 | NEAST317 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 118.22 | 117.67 | AE1-044 | BG_P4_5_NEAST_37_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 114.07 | 117.67 | AE1-044 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 114.07 | 117.67 | AE1-044 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 113.74 | 117.34 | AE1-044 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 113.74 | 117.34 | AE1-044 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208131 | WHEM | 208132 | WHEM TR1 | 1 | 230 | 229 | 691 | 108.3 | 117.2 | AE1-044 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208131 | WHEM | 208132 | WHEM TR1 | 1 | 230 | 229 | 691 | 108.3 | 117.2 | AE1-044 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208131 | WHEM | 208132 | WHEM TR1 | 1 | 230 | 229 | 691 | 108.29 | 117.19 | AE1-044 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 122.35 | 117 | AE1-044 | PECO_P4_PEACH225_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 117.76 | 116.49 | AE1-044 | PL_04_P42_000564_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 117.76 | 116.49 | AE1-044 | PL_04_P12_000260_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 111.25 | 115.88 | AE1-044 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 111.07 | 115.67 | AE1-044 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 111.07 | 115.67 | AE1-044 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200532 | 26ROXBURY | 200520 | 26ROXBURY | 2 | 138/115 | 226 | 435 | 100.76 | 115.27 | AE1-044 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200532 | 26ROXBURY | 200520 | 26ROXBURY | 2 | 138/115 | 226 | 435 | 100.76 | 115.27 | AE1-044 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200532 | 26ROXBURY | 200520 | 26ROXBURY | 2 | 138/115 | 226 | 435 | 100.76 | 115.27 | AE1-044 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 793 | 117.92 | 115.15 | AE1-044 | PEPCO_P1_PP2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 2 | 230 | 233 | 793 | 117.92 | 115.15 | AE1-044 | PEPCO_P1_PP1_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200532 | 26ROXBURY | 200520 | 26ROXBURY | 2 | 138/115 | 226 | 435 | 100.59 | 115.11 | AE1-044 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 2 | 500/230 | 225/232 | 2168 | 109.42 | 114.68 | AE1-044 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 2 | 500/230 | 225/232 | 2168 | 109.24 | 114.47 | AE1-044 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 2 | 500/230 | 225/232 | 2168 | 109.24 | 114.47 | AE1-044 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 1 | 500/230 | 225/232 | 2168 | 109.19 | 114.44 | AE1-044 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 1 | 500/230 | 225/232 | 2168 | 109.01 | 114.23 | AE1-044 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 1 | 500/230 | 225/232 | 2168 | 109.01 | 114.22 | AE1-044 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220964 | GRACETON | 220999 | BAGLEY2 | 13 | 230 | 232 | 1795 | 113.19 | 114.21 | AE1-044 | BG_P4_5_GRCTN_3T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 115.71 | 113.75 | AE1-044 | AP_P2-3_PE-500-019C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204512 | 27S.RDG | 204693 | 27BOONETOWN | 1 | 230 | 227 | 607 | 105.46 | 113.66 | AE1-044 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208020 | MANO TR3 | 1 | 230 | 229 | 793 | 103.94 | 113.53 | AE1-044 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208020 | MANO TR3 | 208031 | MLWD TR2 | 1 | 230 | 229 | 903 | 102.28 | 113.37 | AE1-044 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 113.23 | 112.07 | AE1-044 | BG_P4_5_CNSTN_14_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 106.99 | 112.06 | AE1-044 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208020 | MANO TR3 | 208031 | MLWD TR2 | 1 | 230 | 229 | 903 | 101.57 | 111.89 | AE1-044 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208020 | MANO TR3 | 208031 | MLWD TR2 | 1 | 230 | 229 | 903 | 101.57 | 111.89 | AE1-044 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208020 | MANO TR3 | 208031 | MLWD TR2 | 1 | 230 | 229 | 903 | 101.57 | 111.89 | AE1-044 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 106.81 | 111.85 | AE1-044 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 106.81 | 111.85 | AE1-044 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 2 | 500/230 | 225/232 | 2168 | 108.32 | 111.6 | AE1-044 | PJM_500_BG_P4_5_CNSTN_15_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208031 | MLWD TR2 | 1 | 230 | 229 | 911 | 104.69 | 111.23 | AE1-044 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220980 | RAPHAEL | 220999 | BAGLEY2 | 13 | 230 | 232 | 1795 | 108.78 | 110.97 | AE1-044 | BG_P4_5_GRCTN_3T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 106.24 | 110.95 | AE1-044 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 106.12 | 110.82 | AE1-044 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208131 | WHEM | 208133 | WHEM TR2 | 1 | 230 | 229 | 691 | 101.49 | 110.08 | AE1-044 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208131 | WHEM | 208132 | WHEM TR1 | 1 | 230 | 229 | 691 | 103.51 | 109.72 | AE1-044 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 793 | 111.96 | 109.3 | AE1-044 | PEPCO_P4_PP19_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208131 | WHEM | 208133 | WHEM TR2 | 1 | 230 | 229 | 691 | 100.78 | 108.67 | AE1-044 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208131 | WHEM | 208133 | WHEM TR2 | 1 | 230 | 229 | 691 | 100.78 | 108.66 | AE1-044 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208131 | WHEM | 208133 | WHEM TR2 | 1 | 230 | 229 | 691 | 100.77 | 108.66 | AE1-044 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200532 | 26ROXBURY | 200520 | 26ROXBURY | 2 | 138/115 | 226 | 435 | 95.62 | 108.08 | AE1-044 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220973 | GRANITE6 | 1 | 230 | 232 | 829 | 108.52 | 107.2 | AE1-044 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 204529 | 27GERMANTN | 1 | 138/115 | 227 | 453 | 104.99 | 106.93 | AE1-044 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 2 | 230 | 233 | 793 | 108.7 | 106.76 | AE1-044 | AP_P2-3_PE-500-019C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 793 | 108.7 | 106.76 | AE1-044 | AP_P2-3_PE-500-019C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220965 | NEAST339 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 108.02 | 106.59 | AE1-044 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220965 | NEAST339 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 107.93 | 106.47 | AE1-044 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220965 | NEAST339 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 107.93 | 106.47 | AE1-044 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220972 | GRANITE1 | 1 | 230 | 232 | 829 | 107.66 | 106.12 | AE1-044 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 101.36 | 105.49 | AE1-044 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 101.28 | 105.4 | AE1-044 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200099 | LAUS | 208045 | LAUS | 3 | 500/230 | 225/229 | 1200 | 103.1 | 104.81 | AE1-044 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 102.48 | 104.47 | AE1-044 | BG_P1_2322_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 102.41 | 104.4 | AE1-044 | BG_P1_2310_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 102.42 | 104.37 | AE1-044 | BG_P4_5_NW2322_230-4_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 102.35 | 104.33 | AE1-044 | BG_P4_5_NW2310_230-5_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200099 | LAUS | 208045 | LAUS | 3 | 500/230 | 225/229 | 1200 | 102.79 | 104.27 | AE1-044 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200099 | LAUS | 208045 | LAUS | 3 | 500/230 | 225/229 | 1200 | 102.79 | 104.26 | AE1-044 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200099 | LAUS | 208045 | LAUS | 3 | 500/230 | 225/229 | 1200 | 102.78 | 104.25 | AE1-044 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220972 | GRANITE1 | 1 | 230 | 232 | 829 | 105.56 | 104.23 | AE1-044 | BG_P4_5_NW230-4_2326_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220973 | GRANITE6 | 1 | 230 | 232 | 829 | 105.23 | 103.69 | AE1-044 | BG_P4_5_NW230-5_2311_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220979 | NEAST317 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 104.93 | 103.55 | AE1-044 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220979 | NEAST317 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 104.83 | 103.44 | AE1-044 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220979 | NEAST317 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 104.83 | 103.44 | AE1-044 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208021 | MANO TR4 | 208133 | WHEM TR2 | 2 | 230 | 229 | 593 | 95.19 | 103.28 | AE1-044 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208021 | MANO TR4 | 208133 | WHEM TR2 | 2 | 230 | 229 | 593 | 95.19 | 103.27 | AE1-044 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208021 | MANO TR4 | 208133 | WHEM TR2 | 2 | 230 | 229 | 593 | 95.17 | 103.27 | AE1-044 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 101.08 | 103.11 | AE1-044 | BG_P4_5_NW230-2_2322_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 100.98 | 103 | AE1-044 | BG_P4_5_NW2371_2310_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 99.26 | 103 | AE1-044 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 99.26 | 103 | AE1-044 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 99.26 | 103 | AE1-044 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 100.98 | 103 | AE1-044 | BG_P4_5_NW230-3_2310_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208020 | MANO TR3 | 208031 | MLWD TR2 | 1 | 230 | 229 | 903 | 95.2 | 102.75 | AE1-044 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220973 | GRANITE6 | 1 | 230 | 232 | 829 | 103.23 | 102.16 | AE1-044 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 100.1 | 102.06 | AE1-044 | BG_P4_5_CNSTN_14_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220964 | GRACETON | 221000 | BAGLEY | 5 | 230 | 232 | 1795 | 101.27 | 102 | AE1-044 | BG_P1_2313_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220964 | GRACETON | 220999 | BAGLEY2 | 13 | 230 | 232 | 1795 | 101.27 | 102 | AE1-044 | BG_P1_2305_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220965 | NEAST339 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 102.49 | 101.78 | AE1-044 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 98.33 | 101.68 | AE1-044 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220965 | NEAST339 | 220977 | RIV2339 | 1 | 230 | 232 | 991 | 103.06 | 101.61 | AE1-044 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220966 | RIV2317 | 220979 | NEAST317 | 1 | 230 | 232 | 940 | 102.66 | 101.59 | AE1-044 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 2 | 500/230 | 225/232 | 2168 | 98.85 | 101.59 | AE1-044 | BG_P1_CNSTN_500-2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 2 | 500/230 | 225/232 | 2168 | 98.85 | 101.59 | AE1-044 | PJM_500_BG_P2_CNSTN_230-N_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220965 | NEAST339 | 220977 | RIV2339 | 1 | 230 | 232 | 991 | 103.02 | 101.55 | AE1-044 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220965 | NEAST339 | 220977 | RIV2339 | 1 | 230 | 232 | 991 | 103.02 | 101.55 | AE1-044 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220966 | RIV2317 | 220979 | NEAST317 | 1 | 230 | 232 | 940 | 102.62 | 101.53 | AE1-044 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220966 | RIV2317 | 220979 | NEAST317 | 1 | 230 | 232 | 940 | 102.61 | 101.53 | AE1-044 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208131 | WHEM | 208133 | WHEM TR2 | 1 | 230 | 229 | 691 | 96 | 101.48 | AE1-044 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 1 | 500/230 | 225/232 | 2168 | 98.75 | 101.48 | AE1-044 | BG_P1_CNSTN_500-4_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 1 | 500/230 | 225/232 | 2168 | 98.75 | 101.48 | AE1-044 | PJM_500_BG_P2_CNSTN_230-S_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220972 | GRANITE1 | 1 | 230 | 232 | 829 | 102.63 | 101.39 | AE1-044 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 223960 | BRG 1T 230 | 1 | 500/230 | 225/233 | 1498 | 100.11 | 100.47 | AE1-044 | PEPCO_P4_PP41_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 98.43 | 100.36 | AE1-044 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3464 | 168.26 | 162.25 | AB2-043 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 153.74 | 158.24 | AE1-056 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.24 | 157.36 | AE1-056 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.23 | 157.36 | AE1-056 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 152.06 | 156.91 | AE1-056 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 161.74 | 154.51 | AE1-056 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 148.69 | 153.26 | AE1-056 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 155.81 | 150.65 | AE1-056 | PN_P1-2_PN-500-010T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.53 | 149.64 | AE1-056 | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.46 | 149.57 | AE1-056 | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.15 | 148.4 | AE1-056 | AP_P2-3_PE-500-016_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.21 | 148.37 | AE1-056 | AP_P2-3_PE-500-015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.12 | 147.99 | AE1-056 | PJM_500_BG_P4_5_CNSTN_L_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.41 | 147.97 | AE1-056 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.21 | 147.79 | AE1-056 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.24 | 147.77 | AE1-056 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.97 | 147.58 | AE1-056 | PECO_P4_NOTTI85_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.91 | 147.56 | AE1-056 | PECO_P1-2_220-08_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.33 | 147.52 | AE1-056 | AP_P1-2_WP-500-DRT17_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.33 | 147.52 | AE1-056 | AP_P1-2_PE-500-001_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.84 | 147.5 | AE1-056 | PECO_P4_COOPR125_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.28 | 147.45 | AE1-056 | AP_P2-3_PE-500-018C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3464 | 168.04 | 162.03 | AB2-047 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.96 | 144.25 | AE1-056 | PECO_P4_PEACH025_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.82 | 144.15 | AE1-056 | PECO_P1-2_PBTIE1_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 139.19 | 133.25 | AE1-056 | PECO_P4_PEACH205_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 139.09 | 132.93 | AE1-056 | PECO_P1-2_PBTIE2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 138.14 | 132.05 | AE1-056 | PECO_P4_PEACH055_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 133.46 | 127.64 | AE1-056 | PECO_P4_PEACH015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 128.91 | 127.17 | AE1-056 | DVP_P4-2: 514T595_SRT-SW |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 132.13 | 126.31 | AE1-056 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 127.17 | 125.46 | AE1-056 | DVP_P4-2: 51482_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 127.17 | 125.37 | AE1-056 | AP_P1-2_PE-500-407T_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 127.17 | 125.37 | AE1-056 | DVP_P1-2: LN 514_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 123.04 | 117.66 | AE1-056 | PECO_P4_PEACH225_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 117.36 | 115.45 | AE1-056 | AP_P2-3_PE-500-019C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 144.58 | 139.43 | AE1-060 | PL_10_P42_100570_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 144.58 | 139.43 | AE1-060 | PL_10_P42_100570_A_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 143.78 | 138.64 | AE1-060 | PL_10_P12_000085_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 143.68 | 138.55 | AE1-060 | PN_P2-3_PN-500-DRT31_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 143.31 | 138.18 | AE1-060 | PL_30_P42_000131_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 203981 | AD2-062_POI | 235188 | 01GREENE | 1 | 138 | 226/201 | 317 | 158.28 | 151.16 | AE1-071 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 203981 | AD2-062_POI | 235188 | 01GREENE | 1 | 138 | 226/201 | 317 | 158.27 | 151.16 | AE1-071 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 203981 | AD2-062_POI | 235188 | 01GREENE | 1 | 138 | 226/201 | 317 | 158.07 | 151.01 | AE1-071 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200532 | 26ROXBURY | 203981 | AD2-062_POI | 1 | 138 | 226 | 317 | 157.71 | 149.82 | AE1-071 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200532 | 26ROXBURY | 203981 | AD2-062_POI | 1 | 138 | 226 | 317 | 157.71 | 149.82 | AE1-071 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200532 | 26ROXBURY | 203981 | AD2-062_POI | 1 | 138 | 226 | 317 | 157.5 | 149.66 | AE1-071 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3464 | 168.07 | 162.06 | AB2-059 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3464 | 168.14 | 162.13 | AB2-060 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 146.85 | 141.83 | AE1-071 | PN_P2-3_PN-115-0331-A_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 146.78 | 141.76 | AE1-071 | PN_P2-3_PN-115-0331-D_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 146.66 | 141.65 | AE1-071 | AP_P1-2_WP-138-340BT_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 146.66 | 141.65 | AE1-071 | PN_P1-3_PN-115-118_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 146.59 | 141.61 | AE1-071 | AP_P1-2_WP-138-340AT_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204502 | 27JACKSON | 204514 | 27TMI | 1 | 230 | 227 | 781 | 132.97 | 141.52 | AE1-071 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204502 | 27JACKSON | 204514 | 27TMI | 1 | 230 | 227 | 781 | 132.97 | 141.52 | AE1-071 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204502 | 27JACKSON | 204514 | 27TMI | 1 | 230 | 227 | 781 | 132.96 | 141.51 | AE1-071 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 146.36 | 141.38 | AE1-071 | AP_P2-3_WP-138-272T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 146.07 | 141.02 | AE1-071 | PN_P1-2_PN-115-094_A_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 146.05 | 141.01 | AE1-071 | PN_P2-3_PN-115-0331-B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 145.68 | 140.61 | AE1-071 | PN_P1-2_PN-115-094_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 145.74 | 140.6 | AE1-071 | PN_P2-3_PN-115-58B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 135.18 | 137.58 | AE1-071 | AP_P1-2_WP-138-340BT_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 135.18 | 137.58 | AE1-071 | PN_P1-3_PN-115-118_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 135.11 | 137.55 | AE1-071 | AP_P1-2_WP-138-340AT_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 135.1 | 137.48 | AE1-071 | PN_P2-3_PN-115-0331-D_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 135.05 | 137.43 | AE1-071 | PN_P2-3_PN-115-0331-A_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 134.86 | 137.27 | AE1-071 | AP_P2-3_WP-138-272T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 203981 | AD2-062_POI | 235188 | 01GREENE | 1 | 138 | 226/201 | 317 | 152.61 | 136.85 | AE1-071 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 203981 | AD2-062_POI | 235188 | 01GREENE | 1 | 138 | 226/201 | 317 | 152.61 | 136.85 | AE1-071 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 203981 | AD2-062_POI | 235188 | 01GREENE | 1 | 138 | 226/201 | 317 | 152.61 | 136.84 | AE1-071 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 203981 | AD2-062_POI | 235188 | 01GREENE | 1 | 138 | 226/201 | 317 | 152.38 | 136.51 | AE1-071 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 133.77 | 136.11 | AE1-071 | AP_P2-2_WP-138-074_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 133.77 | 136.11 | AE1-071 | AP_P2-3_WP-138-271_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 133.77 | 136.11 | AE1-071 | AP_P1-3_WP-138-055_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 133.57 | 135.78 | AE1-071 | PN_P1-2_PN-115-094_A_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200532 | 26ROXBURY | 203981 | AD2-062_POI | 1 | 138 | 226 | 317 | 152.05 | 135.53 | AE1-071 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200532 | 26ROXBURY | 203981 | AD2-062_POI | 1 | 138 | 226 | 317 | 152.05 | 135.53 | AE1-071 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200532 | 26ROXBURY | 203981 | AD2-062_POI | 1 | 138 | 226 | 317 | 152.04 | 135.53 | AE1-071 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200532 | 26ROXBURY | 203981 | AD2-062_POI | 1 | 138 | 226 | 317 | 151.82 | 135.19 | AE1-071 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 203981 | AD2-062_POI | 235188 | 01GREENE | 1 | 138 | 226/201 | 317 | 137.86 | 134.59 | AE1-071 | AP_P2-3_PE-500-016_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 203981 | AD2-062_POI | 235188 | 01GREENE | 1 | 138 | 226/201 | 317 | 138.06 | 134.44 | AE1-071 | AP_P2-3_PE-500-015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 203981 | AD2-062_POI | 235188 | 01GREENE | 1 | 138 | 226/201 | 317 | 145.55 | 133.8 | AE1-071 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200532 | 26ROXBURY | 203981 | AD2-062_POI | 1 | 138 | 226 | 317 | 137.29 | 133.28 | AE1-071 | AP_P2-3_PE-500-016_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200532 | 26ROXBURY | 203981 | AD2-062_POI | 1 | 138 | 226 | 317 | 137.49 | 133.14 | AE1-071 | AP_P2-3_PE-500-015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200532 | 26ROXBURY | 203981 | AD2-062_POI | 1 | 138 | 226 | 317 | 144.99 | 132.49 | AE1-071 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200532 | 26ROXBURY | 200520 | 26ROXBURY | 2 | 138/115 | 226 | 435 | 114.93 | 129.03 | AE1-071 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200532 | 26ROXBURY | 200520 | 26ROXBURY | 2 | 138/115 | 226 | 435 | 114.93 | 129.03 | AE1-071 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200532 | 26ROXBURY | 200520 | 26ROXBURY | 2 | 138/115 | 226 | 435 | 114.78 | 128.85 | AE1-071 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 129.99 | 128.25 | AE1-071 | DVP_P4-2: 514T595_SRT-SW |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204538 | 27STRABAN | 204544 | 27LINCOLN | 1 | 115 | 227 | 371 | 125.26 | 127.11 | AE1-071 | PN_P1-3_PN-115-118_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204538 | 27STRABAN | 204544 | 27LINCOLN | 1 | 115 | 227 | 371 | 125.26 | 127.1 | AE1-071 | AP_P1-2_WP-138-340BT_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 128.27 | 126.56 | AE1-071 | DVP_P4-2: 51482_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 128.27 | 126.47 | AE1-071 | AP_P1-2_PE-500-407T_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 128.27 | 126.47 | AE1-071 | DVP_P1-2: LN 514_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 2 | 230 | 233 | 793 | 127.94 | 126.19 | AE1-071 | DVP_P4-2: 514T595_SRT-SW |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 793 | 127.94 | 126.19 | AE1-071 | DVP_P4-2: 514T595_SRT-SW |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200532 | 26ROXBURY | 200520 | 26ROXBURY | 2 | 138/115 | 226 | 435 | 110.8 | 125.03 | AE1-071 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200532 | 26ROXBURY | 200520 | 26ROXBURY | 2 | 138/115 | 226 | 435 | 110.8 | 125.03 | AE1-071 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200532 | 26ROXBURY | 200520 | 26ROXBURY | 2 | 138/115 | 226 | 435 | 110.8 | 125.03 | AE1-071 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 2 | 230 | 233 | 793 | 126.71 | 125 | AE1-071 | DVP_P4-2: 51482_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 793 | 126.71 | 125 | AE1-071 | DVP_P4-2: 51482_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 793 | 126.71 | 124.92 | AE1-071 | AP_P1-2_PE-500-407T_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 793 | 126.71 | 124.92 | AE1-071 | DVP_P1-2: LN 514_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 2 | 230 | 233 | 793 | 126.71 | 124.92 | AE1-071 | DVP_P1-2: LN 514_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 2 | 230 | 233 | 793 | 126.71 | 124.92 | AE1-071 | AP_P1-2_PE-500-407T_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200532 | 26ROXBURY | 200520 | 26ROXBURY | 2 | 138/115 | 226 | 435 | 110.63 | 124.86 | AE1-071 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200512 | 26LEWISTWN | 200519 | 26REED TAP | 1 | 115 | 226 | 271 | 115.62 | 123.65 | AE1-071 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200512 | 26LEWISTWN | 200519 | 26REED TAP | 1 | 115 | 226 | 271 | 115.69 | 123.6 | AE1-071 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200512 | 26LEWISTWN | 200519 | 26REED TAP | 1 | 115 | 226 | 271 | 115.69 | 123.6 | AE1-071 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200512 | 26LEWISTWN | 200519 | 26REED TAP | 1 | 115 | 226 | 271 | 115.69 | 123.6 | AE1-071 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204529 | 27GERMANTN | 204538 | 27STRABAN | 1 | 115 | 227 | 371 | 119.47 | 122.67 | AE1-071 | PN_P1-3_PN-115-118_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204529 | 27GERMANTN | 204538 | 27STRABAN | 1 | 115 | 227 | 371 | 119.47 | 122.65 | AE1-071 | AP_P1-2_WP-138-340BT_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200519 | 26REED TAP | 200522 | 26SHADE GP | 1 | 115 | 226 | 271 | 108.59 | 118.58 | AE1-071 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200519 | 26REED TAP | 200522 | 26SHADE GP | 1 | 115 | 226 | 271 | 108.66 | 118.54 | AE1-071 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200519 | 26REED TAP | 200522 | 26SHADE GP | 1 | 115 | 226 | 271 | 108.66 | 118.54 | AE1-071 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200519 | 26REED TAP | 200522 | 26SHADE GP | 1 | 115 | 226 | 271 | 108.66 | 118.54 | AE1-071 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200532 | 26ROXBURY | 200520 | 26ROXBURY | 2 | 138/115 | 226 | 435 | 105.66 | 117.85 | AE1-071 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200512 | 26LEWISTWN | 200519 | 26REED TAP | 1 | 115 | 226 | 271 | 112.86 | 117.54 | AE1-071 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 793 | 120.15 | 117.41 | AE1-071 | PEPCO_P1_PP2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 2 | 230 | 233 | 793 | 120.15 | 117.41 | AE1-071 | PEPCO_P1_PP1_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 118.49 | 116.57 | AE1-071 | AP_P2-3_PE-500-019C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200504 | 26CARLISLE | 204528 | 27GARDNERS | 1 | 115 | 226/227 | 190 | 111.09 | 116.22 | AE1-071 | PN_P2-3_PN-115-58B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200504 | 26CARLISLE | 204528 | 27GARDNERS | 1 | 115 | 226/227 | 190 | 111.57 | 116.17 | AE1-071 | PN_P2-2_PN-115-030_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200504 | 26CARLISLE | 204528 | 27GARDNERS | 1 | 115 | 226/227 | 190 | 111.57 | 116.17 | AE1-071 | PN_P1-3_PN-115-040_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200504 | 26CARLISLE | 204528 | 27GARDNERS | 1 | 115 | 226/227 | 190 | 110.92 | 116.14 | AE1-071 | PN_P1-2_PN-115-094_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200504 | 26CARLISLE | 204528 | 27GARDNERS | 1 | 115 | 226/227 | 190 | 105.96 | 113.32 | AE1-071 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200504 | 26CARLISLE | 204528 | 27GARDNERS | 1 | 115 | 226/227 | 190 | 105.96 | 113.32 | AE1-071 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200504 | 26CARLISLE | 204528 | 27GARDNERS | 1 | 115 | 226/227 | 190 | 105.71 | 113.04 | AE1-071 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200504 | 26CARLISLE | 204528 | 27GARDNERS | 1 | 115 | 226/227 | 190 | 108.85 | 112.68 | AE1-071 | PN_P2-3_PN-230-0014-12_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200519 | 26REED TAP | 200522 | 26SHADE GP | 1 | 115 | 226 | 271 | 105.83 | 112.56 | AE1-071 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200504 | 26CARLISLE | 204528 | 27GARDNERS | 1 | 115 | 226/227 | 190 | 108.84 | 112.3 | AE1-071 | PN_P1-3_PN-230-020A_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200504 | 26CARLISLE | 204528 | 27GARDNERS | 1 | 115 | 226/227 | 190 | 108.84 | 112.3 | AE1-071 | PN_P2-3_PN-230-0014-11_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200532 | 26ROXBURY | 200520 | 26ROXBURY | 2 | 138/115 | 226 | 435 | 100.05 | 112.05 | AE1-071 | AP_P2-3_PE-500-016_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200532 | 26ROXBURY | 200520 | 26ROXBURY | 2 | 138/115 | 226 | 435 | 100.19 | 111.91 | AE1-071 | AP_P2-3_PE-500-015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 793 | 114.36 | 111.73 | AE1-071 | PEPCO_P4_PP19_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200512 | 26LEWISTWN | 200519 | 26REED TAP | 1 | 115 | 226 | 271 | 109.25 | 111.51 | AE1-071 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200512 | 26LEWISTWN | 200519 | 26REED TAP | 1 | 115 | 226 | 271 | 109.25 | 111.51 | AE1-071 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200512 | 26LEWISTWN | 200519 | 26REED TAP | 1 | 115 | 226 | 271 | 109.2 | 111.43 | AE1-071 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3464 | 168.12 | 162.11 | AB2-070 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 2 | 230 | 233 | 793 | 110.95 | 109.07 | AE1-071 | AP_P2-3_PE-500-019C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 793 | 110.95 | 109.07 | AE1-071 | AP_P2-3_PE-500-019C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200520 | 26ROXBURY | 203971 | AE1-071-POI | 1 | 115 | 226 | 395 | 98.85 | 107.32 | AE1-071 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200520 | 26ROXBURY | 203971 | AE1-071-POI | 1 | 115 | 226 | 395 | 98.9 | 107.3 | AE1-071 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200520 | 26ROXBURY | 203971 | AE1-071-POI | 1 | 115 | 226 | 395 | 98.9 | 107.3 | AE1-071 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200520 | 26ROXBURY | 203971 | AE1-071-POI | 1 | 115 | 226 | 395 | 98.9 | 107.3 | AE1-071 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200519 | 26REED TAP | 200522 | 26SHADE GP | 1 | 115 | 226 | 271 | 102.22 | 106.63 | AE1-071 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200519 | 26REED TAP | 200522 | 26SHADE GP | 1 | 115 | 226 | 271 | 102.22 | 106.63 | AE1-071 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200519 | 26REED TAP | 200522 | 26SHADE GP | 1 | 115 | 226 | 271 | 102.17 | 106.55 | AE1-071 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200009 | JUNI | 208004 | JUNI | 2 | 500/230 | 225/229 | 1040 | 107.02 | 106.44 | AE1-071 | PL_10_P42_000140_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200512 | 26LEWISTWN | 200519 | 26REED TAP | 1 | 115 | 226 | 271 | 106.62 | 104.96 | AE1-071 | ME_P2-3_ME-115-003DT_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200512 | 26LEWISTWN | 200519 | 26REED TAP | 1 | 115 | 226 | 271 | 106.55 | 104.89 | AE1-071 | ME_P2-3_ME-115-003AT_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3464 | 168.23 | 162.22 | AB2-085 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3464 | 168.05 | 162.04 | AB2-100 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200520 | 26ROXBURY | 203971 | AE1-071-POI | 1 | 115 | 226 | 395 | 96.75 | 102.53 | AE1-071 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204520 | 27ALLEN | 208142 | WIGR-115 | 1 | 115 | 227/229 | 351.4 | 93.5 | 101 | AE1-071 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204520 | 27ALLEN | 208142 | WIGR-115 | 1 | 115 | 227/229 | 351.4 | 93.5 | 101 | AE1-071 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204520 | 27ALLEN | 208142 | WIGR-115 | 1 | 115 | 227/229 | 351.4 | 93.49 | 101 | AE1-071 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204520 | 27ALLEN | 208142 | WIGR-115 | 1 | 115 | 227/229 | 351.4 | 93.26 | 100.83 | AE1-071 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200519 | 26REED TAP | 200522 | 26SHADE GP | 1 | 115 | 226 | 271 | 99.59 | 100.16 | AE1-071 | ME_P2-3_ME-115-003DT_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200519 | 26REED TAP | 200522 | 26SHADE GP | 1 | 115 | 226 | 271 | 99.52 | 100.1 | AE1-071 | ME_P2-3_ME-115-003AT_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3464 | 169 | 162.97 | AB2-133 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.33 | 157.45 | AE1-079 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.33 | 157.45 | AE1-079 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 155.9 | 150.74 | AE1-079 | PN_P1-2_PN-500-010T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.23 | 148.5 | AE1-079 | AP_P2-3_PE-500-016_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.3 | 148.47 | AE1-079 | AP_P2-3_PE-500-015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.52 | 148.08 | AE1-079 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.21 | 148.08 | AE1-079 | PJM_500_BG_P4_5_CNSTN_L_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.32 | 147.89 | AE1-079 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.34 | 147.88 | AE1-079 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.07 | 147.68 | AE1-079 | PECO_P4_NOTTI85_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.01 | 147.67 | AE1-079 | PECO_P1-2_220-08_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.41 | 147.62 | AE1-079 | AP_P1-2_WP-500-DRT17_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.41 | 147.62 | AE1-079 | AP_P1-2_PE-500-001_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.94 | 147.6 | AE1-079 | PECO_P4_COOPR125_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.36 | 147.55 | AE1-079 | AP_P2-3_PE-500-018C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.36 | 147.55 | AE1-079 | AP_P2-3_PE-500-018D_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 142.88 | 146.99 | AE1-079 | AP_P1-2_PE-500-004_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 142.88 | 146.99 | AE1-079 | AP_P1-2_WP-500-006_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 142.88 | 146.99 | AE1-079 | AP_P2-3_WP-500-DRT19_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 142.88 | 146.99 | AE1-079 | AP_P2-3_WP-500-466_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3464 | 167.86 | 161.85 | AB2-134 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 153.69 | 158.17 | AE1-084 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.18 | 157.3 | AE1-084 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.18 | 157.3 | AE1-084 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 152 | 156.85 | AE1-084 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 161.67 | 154.45 | AE1-084 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 148.64 | 153.2 | AE1-084 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 155.75 | 150.6 | AE1-084 | PN_P1-2_PN-500-010T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.48 | 149.58 | AE1-084 | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.41 | 149.51 | AE1-084 | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.1 | 148.33 | AE1-084 | AP_P2-3_PE-500-016_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.16 | 148.31 | AE1-084 | AP_P2-3_PE-500-015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.07 | 147.93 | AE1-084 | PJM_500_BG_P4_5_CNSTN_L_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.35 | 147.92 | AE1-084 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.15 | 147.73 | AE1-084 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.18 | 147.71 | AE1-084 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.91 | 147.52 | AE1-084 | PECO_P4_NOTTI85_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.85 | 147.5 | AE1-084 | PECO_P1-2_220-08_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.28 | 147.45 | AE1-084 | AP_P1-2_WP-500-DRT17_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.28 | 147.45 | AE1-084 | AP_P1-2_PE-500-001_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.78 | 147.44 | AE1-084 | PECO_P4_COOPR125_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.23 | 147.39 | AE1-084 | AP_P2-3_PE-500-018C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3464 | 169.06 | 163.03 | AB2-135 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.89 | 144.18 | AE1-084 | PECO_P4_PEACH025_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.75 | 144.08 | AE1-084 | PECO_P1-2_PBTIE1_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 139.13 | 133.19 | AE1-084 | PECO_P4_PEACH205_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 139.02 | 132.87 | AE1-084 | PECO_P1-2_PBTIE2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 138.08 | 131.99 | AE1-084 | PECO_P4_PEACH055_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 133.4 | 127.57 | AE1-084 | PECO_P4_PEACH015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 128.91 | 127.19 | AE1-084 | DVP_P4-2: 514T595_SRT-SW |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 132.07 | 126.25 | AE1-084 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 127.17 | 125.47 | AE1-084 | DVP_P4-2: 51482_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 127.17 | 125.38 | AE1-084 | DVP_P1-2: LN 514_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 127.17 | 125.38 | AE1-084 | AP_P1-2_PE-500-407T_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 122.98 | 117.6 | AE1-084 | PECO_P4_PEACH225_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 117.36 | 115.45 | AE1-084 | AP_P2-3_PE-500-019C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3464 | 168.97 | 162.95 | AB2-136 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 153.79 | 158.3 | AE1-100 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.27 | 157.4 | AE1-100 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.27 | 157.4 | AE1-100 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 152.1 | 156.97 | AE1-100 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 161.77 | 154.55 | AE1-100 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 148.74 | 153.32 | AE1-100 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 155.85 | 150.69 | AE1-100 | PN_P1-2_PN-500-010T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.58 | 149.7 | AE1-100 | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.51 | 149.62 | AE1-100 | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.2 | 148.47 | AE1-100 | AP_P2-3_PE-500-016_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.27 | 148.44 | AE1-100 | AP_P2-3_PE-500-015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.16 | 148.03 | AE1-100 | PJM_500_BG_P4_5_CNSTN_L_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.44 | 148 | AE1-100 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.24 | 147.82 | AE1-100 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.27 | 147.8 | AE1-100 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.99 | 147.61 | AE1-100 | PECO_P4_NOTTI85_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.93 | 147.59 | AE1-100 | PECO_P1-2_220-08_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.38 | 147.59 | AE1-100 | AP_P1-2_PE-500-001_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.38 | 147.59 | AE1-100 | AP_P1-2_WP-500-DRT17_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.87 | 147.53 | AE1-100 | PECO_P4_COOPR125_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.33 | 147.52 | AE1-100 | AP_P2-3_PE-500-018C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3464 | 168.64 | 162.62 | AB2-153 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.99 | 144.27 | AE1-100 | PECO_P4_PEACH025_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.86 | 144.18 | AE1-100 | PECO_P1-2_PBTIE1_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 139.23 | 133.29 | AE1-100 | PECO_P4_PEACH205_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 139.12 | 132.96 | AE1-100 | PECO_P1-2_PBTIE2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 138.17 | 132.08 | AE1-100 | PECO_P4_PEACH055_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 133.5 | 127.68 | AE1-100 | PECO_P4_PEACH015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 132.17 | 126.34 | AE1-100 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 123.07 | 117.7 | AE1-100 | PECO_P4_PEACH225_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 223.51 | 236.61 | AE1-101 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 225.51 | 236.61 | AE1-101 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 225.44 | 236.54 | AE1-101 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 223.44 | 236.54 | AE1-101 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 225.44 | 236.54 | AE1-101 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 223.44 | 236.54 | AE1-101 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 213.46 | 226.46 | AE1-101 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 213.4 | 226.4 | AE1-101 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 213.4 | 226.4 | AE1-101 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 209.2 | 223.25 | AE1-101 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 209.14 | 223.19 | AE1-101 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 209.14 | 223.19 | AE1-101 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 210.61 | 217.52 | AE1-101 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 208.61 | 217.52 | AE1-101 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 199.07 | 207.96 | AE1-101 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 194.81 | 204.61 | AE1-101 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 172.89 | 167.89 | AE1-101 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 163.79 | 164.96 | AE1-101 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3464 | 168.02 | 162.01 | AB2-158 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 161.94 | 161.88 | AE1-101 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 161.94 | 161.88 | AE1-101 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 161.92 | 161.88 | AE1-101 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 153.5 | 157.94 | AE1-101 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 161.98 | 157.1 | AE1-101 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 161.98 | 157.1 | AE1-101 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 151.82 | 156.62 | AE1-101 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 161.46 | 154.22 | AE1-101 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 148.46 | 152.97 | AE1-101 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 155.53 | 150.37 | AE1-101 | PN_P1-2_PN-500-010T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 903 | 143.03 | 149.6 | AE1-101 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 903 | 143.03 | 149.6 | AE1-101 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 903 | 143.01 | 149.59 | AE1-101 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.29 | 149.35 | AE1-101 | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.22 | 149.28 | AE1-101 | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204539 | 27HUNTRSTN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 334 | 149.77 | 148.62 | AE1-101 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204539 | 27HUNTRSTN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 334 | 149.77 | 148.62 | AE1-101 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204539 | 27HUNTRSTN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 334 | 149.76 | 148.61 | AE1-101 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 334 | 150.2 | 148.52 | AE1-101 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 334 | 150.2 | 148.52 | AE1-101 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 334 | 150.19 | 148.52 | AE1-101 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204539 | 27HUNTRSTN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 334 | 149.58 | 148.42 | AE1-101 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 334 | 150.02 | 148.3 | AE1-101 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.84 | 148 | AE1-101 | AP_P2-3_PE-500-016_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.91 | 147.97 | AE1-101 | AP_P2-3_PE-500-015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.87 | 147.74 | AE1-101 | PJM_500_BG_P4_5_CNSTN_L_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.16 | 147.72 | AE1-101 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.96 | 147.54 | AE1-101 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.99 | 147.52 | AE1-101 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.72 | 147.33 | AE1-101 | PECO_P4_NOTTI85_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.66 | 147.31 | AE1-101 | PECO_P1-2_220-08_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.59 | 147.25 | AE1-101 | PECO_P4_COOPR125_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.03 | 147.13 | AE1-101 | AP_P1-2_PE-500-001_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.03 | 147.13 | AE1-101 | AP_P1-2_WP-500-DRT17_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143 | 147.07 | AE1-101 | AP_P2-3_PE-500-018C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3464 | 168.12 | 162.11 | AB2-160 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.66 | 143.96 | AE1-101 | PECO_P4_PEACH025_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.53 | 143.87 | AE1-101 | PECO_P1-2_PBTIE1_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 911 | 149.12 | 143.25 | AE1-101 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204502 | 27JACKSON | 204514 | 27TMI | 1 | 230 | 227 | 781 | 132.51 | 141.1 | AE1-101 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204502 | 27JACKSON | 204514 | 27TMI | 1 | 230 | 227 | 781 | 132.7 | 141.09 | AE1-101 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204502 | 27JACKSON | 204514 | 27TMI | 1 | 230 | 227 | 781 | 132.7 | 141.08 | AE1-101 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204502 | 27JACKSON | 204514 | 27TMI | 1 | 230 | 227 | 781 | 132.69 | 141.08 | AE1-101 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204539 | 27HUNTRSTN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 334 | 142.71 | 139.48 | AE1-101 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204538 | 27STRABAN | 204544 | 27LINCOLN | 1 | 115 | 227 | 371 | 139.18 | 139.34 | AE1-101 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204538 | 27STRABAN | 204544 | 27LINCOLN | 1 | 115 | 227 | 371 | 139.18 | 139.34 | AE1-101 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204538 | 27STRABAN | 204544 | 27LINCOLN | 1 | 115 | 227 | 371 | 139.17 | 139.33 | AE1-101 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204538 | 27STRABAN | 204544 | 27LINCOLN | 1 | 115 | 227 | 371 | 138.99 | 139.11 | AE1-101 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 1031 | 130.75 | 138.91 | AE1-101 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 1031 | 130.26 | 137.85 | AE1-101 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 1031 | 130.26 | 137.85 | AE1-101 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 1031 | 130.25 | 137.84 | AE1-101 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204529 | 27GERMANTN | 204538 | 27STRABAN | 1 | 115 | 227 | 371 | 133.42 | 135.04 | AE1-101 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204529 | 27GERMANTN | 204538 | 27STRABAN | 1 | 115 | 227 | 371 | 133.42 | 135.04 | AE1-101 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204529 | 27GERMANTN | 204538 | 27STRABAN | 1 | 115 | 227 | 371 | 133.41 | 135.03 | AE1-101 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204529 | 27GERMANTN | 204538 | 27STRABAN | 1 | 115 | 227 | 371 | 133.23 | 134.82 | AE1-101 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200512 | 26LEWISTWN | 200519 | 26REED TAP | 1 | 115 | 226 | 271 | 124.56 | 133.17 | AE1-101 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200512 | 26LEWISTWN | 200519 | 26REED TAP | 1 | 115 | 226 | 271 | 124.63 | 133.12 | AE1-101 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200512 | 26LEWISTWN | 200519 | 26REED TAP | 1 | 115 | 226 | 271 | 124.63 | 133.12 | AE1-101 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200512 | 26LEWISTWN | 200519 | 26REED TAP | 1 | 115 | 226 | 271 | 124.63 | 133.12 | AE1-101 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 334 | 133.41 | 133.02 | AE1-101 | PN_P1-3_PN-115-118_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 334 | 133.41 | 133.01 | AE1-101 | AP_P1-2_WP-138-340BT_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 334 | 133.26 | 133.01 | AE1-101 | AP_P1-2_WP-138-340AT_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 138.94 | 133 | AE1-101 | PECO_P4_PEACH205_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 138.82 | 132.67 | AE1-101 | PECO_P1-2_PBTIE2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 334 | 132.73 | 132.44 | AE1-101 | AP_P2-3_WP-138-272T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208078 | SAKR | 1 | 230 | 229 | 903 | 124.49 | 132.32 | AE1-101 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208078 | SAKR | 1 | 230 | 229 | 903 | 124.48 | 132.32 | AE1-101 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208078 | SAKR | 1 | 230 | 229 | 903 | 124.48 | 132.32 | AE1-101 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 334 | 132.51 | 132.02 | AE1-101 | PN_P2-3_PN-115-0331-D_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 203981 | AD2-062_POI | 235188 | 01GREENE | 1 | 138 | 226/201 | 317 | 139.81 | 131.82 | AE1-101 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 203981 | AD2-062_POI | 235188 | 01GREENE | 1 | 138 | 226/201 | 317 | 139.81 | 131.82 | AE1-101 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 137.89 | 131.81 | AE1-101 | PECO_P4_PEACH055_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 203981 | AD2-062_POI | 235188 | 01GREENE | 1 | 138 | 226/201 | 317 | 139.61 | 131.69 | AE1-101 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204539 | 27HUNTRSTN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 334 | 132.97 | 131.54 | AE1-101 | PN_P1-3_PN-115-118_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204539 | 27HUNTRSTN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 334 | 132.97 | 131.53 | AE1-101 | AP_P1-2_WP-138-340BT_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204539 | 27HUNTRSTN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 334 | 132.83 | 131.53 | AE1-101 | AP_P1-2_WP-138-340AT_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200504 | 26CARLISLE | 204528 | 27GARDNERS | 1 | 115 | 226/227 | 190 | 123.13 | 131.14 | AE1-101 | PN_P2-3_PN-115-0331-B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204539 | 27HUNTRSTN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 334 | 132.3 | 130.97 | AE1-101 | AP_P2-3_WP-138-272T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 334 | 131.43 | 130.92 | AE1-101 | PN_P2-3_PN-115-0331-A_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204538 | 27STRABAN | 204544 | 27LINCOLN | 1 | 115 | 227 | 371 | 132.03 | 130.91 | AE1-101 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204502 | 27JACKSON | 204514 | 27TMI | 1 | 230 | 227 | 781 | 125.06 | 130.54 | AE1-101 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204539 | 27HUNTRSTN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 334 | 132.08 | 130.54 | AE1-101 | PN_P2-3_PN-115-0331-D_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200532 | 26ROXBURY | 203981 | AD2-062_POI | 1 | 138 | 226 | 317 | 139.03 | 130.5 | AE1-101 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200532 | 26ROXBURY | 203981 | AD2-062_POI | 1 | 138 | 226 | 317 | 139.03 | 130.5 | AE1-101 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200532 | 26ROXBURY | 203981 | AD2-062_POI | 1 | 138 | 226 | 317 | 138.82 | 130.37 | AE1-101 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200504 | 26CARLISLE | 204528 | 27GARDNERS | 1 | 115 | 226/227 | 190 | 121.52 | 129.25 | AE1-101 | PN_P1-2_PN-115-094_A_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 1031 | 124.66 | 129.07 | AE1-101 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 130.68 | 128.92 | AE1-101 | DVP_P4-2: 514T595_SRT-SW |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 235463 | 01TANEY | 1 | 138 | 227/201 | 317 | 129.59 | 128.63 | AE1-101 | AP_P1-2_WP-138-340AT_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 235463 | 01TANEY | 1 | 138 | 227/201 | 317 | 129.76 | 128.58 | AE1-101 | PN_P1-3_PN-115-118_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 235463 | 01TANEY | 1 | 138 | 227/201 | 317 | 129.76 | 128.57 | AE1-101 | AP_P1-2_WP-138-340BT_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200504 | 26CARLISLE | 204528 | 27GARDNERS | 1 | 115 | 226/227 | 190 | 121.31 | 128.32 | AE1-101 | PN_P2-3_PN-115-58B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200504 | 26CARLISLE | 204528 | 27GARDNERS | 1 | 115 | 226/227 | 190 | 121.92 | 128.27 | AE1-101 | PN_P1-3_PN-115-040_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200504 | 26CARLISLE | 204528 | 27GARDNERS | 1 | 115 | 226/227 | 190 | 121.92 | 128.27 | AE1-101 | PN_P2-2_PN-115-030_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200504 | 26CARLISLE | 204528 | 27GARDNERS | 1 | 115 | 226/227 | 190 | 121.12 | 128.25 | AE1-101 | PN_P1-2_PN-115-094_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200519 | 26REED TAP | 200522 | 26SHADE GP | 1 | 115 | 226 | 271 | 117.04 | 128.06 | AE1-101 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 235463 | 01TANEY | 1 | 138 | 227/201 | 317 | 128.96 | 128.05 | AE1-101 | AP_P2-3_WP-138-272T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200519 | 26REED TAP | 200522 | 26SHADE GP | 1 | 115 | 226 | 271 | 117.11 | 128.02 | AE1-101 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200519 | 26REED TAP | 200522 | 26SHADE GP | 1 | 115 | 226 | 271 | 117.11 | 128.02 | AE1-101 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200519 | 26REED TAP | 200522 | 26SHADE GP | 1 | 115 | 226 | 271 | 117.11 | 128.02 | AE1-101 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 235463 | 01TANEY | 1 | 138 | 227/201 | 317 | 128.7 | 127.52 | AE1-101 | PN_P2-3_PN-115-0331-D_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 133.18 | 127.35 | AE1-101 | PECO_P4_PEACH015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 128.98 | 127.24 | AE1-101 | DVP_P4-2: 51482_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 128.98 | 127.15 | AE1-101 | AP_P1-2_PE-500-407T_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 128.98 | 127.15 | AE1-101 | DVP_P1-2: LN 514_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 2 | 230 | 233 | 793 | 128.91 | 127.13 | AE1-101 | DVP_P4-2: 514T595_SRT-SW |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 793 | 128.91 | 127.13 | AE1-101 | DVP_P4-2: 514T595_SRT-SW |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200512 | 26LEWISTWN | 200519 | 26REED TAP | 1 | 115 | 226 | 271 | 121.8 | 126.9 | AE1-101 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204529 | 27GERMANTN | 204538 | 27STRABAN | 1 | 115 | 227 | 371 | 126.28 | 126.55 | AE1-101 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 235463 | 01TANEY | 1 | 138 | 227/201 | 317 | 127.42 | 126.14 | AE1-101 | PN_P2-3_PN-115-0331-A_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 131.87 | 126.05 | AE1-101 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208020 | MANO TR3 | 1 | 230 | 229 | 793 | 112.28 | 126.01 | AE1-101 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 793 | 127.69 | 125.95 | AE1-101 | DVP_P4-2: 51482_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 2 | 230 | 233 | 793 | 127.69 | 125.95 | AE1-101 | DVP_P4-2: 51482_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 793 | 127.69 | 125.87 | AE1-101 | AP_P1-2_PE-500-407T_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 793 | 127.69 | 125.87 | AE1-101 | DVP_P1-2: LN 514_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 2 | 230 | 233 | 793 | 127.69 | 125.87 | AE1-101 | AP_P1-2_PE-500-407T_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 2 | 230 | 233 | 793 | 127.69 | 125.87 | AE1-101 | DVP_P1-2: LN 514_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208020 | MANO TR3 | 1 | 230 | 229 | 793 | 111.46 | 124.48 | AE1-101 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208020 | MANO TR3 | 1 | 230 | 229 | 793 | 111.46 | 124.48 | AE1-101 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208020 | MANO TR3 | 1 | 230 | 229 | 793 | 111.46 | 124.48 | AE1-101 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200504 | 26CARLISLE | 204528 | 27GARDNERS | 1 | 115 | 226/227 | 190 | 118.82 | 124.02 | AE1-101 | PN_P2-3_PN-230-0014-12_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204538 | 27STRABAN | 204544 | 27LINCOLN | 1 | 115 | 227 | 371 | 122.15 | 123.95 | AE1-101 | PN_P1-3_PN-115-118_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204538 | 27STRABAN | 204544 | 27LINCOLN | 1 | 115 | 227 | 371 | 122.15 | 123.94 | AE1-101 | AP_P1-2_WP-138-340BT_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204538 | 27STRABAN | 204544 | 27LINCOLN | 1 | 115 | 227 | 371 | 122 | 123.94 | AE1-101 | AP_P1-2_WP-138-340AT_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 235463 | 01TANEY | 1 | 138 | 227/201 | 317 | 124.52 | 123.65 | AE1-101 | ME_P1-2_ME-115-058T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 235463 | 01TANEY | 1 | 138 | 227/201 | 317 | 125.47 | 123.63 | AE1-101 | AP_P2-3_PE-230-033_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 235463 | 01TANEY | 1 | 138 | 227/201 | 317 | 125.47 | 123.63 | AE1-101 | AP_P7-1_PE-230-001_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200504 | 26CARLISLE | 204528 | 27GARDNERS | 1 | 115 | 226/227 | 190 | 118.81 | 123.6 | AE1-101 | PN_P1-3_PN-230-020A_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200504 | 26CARLISLE | 204528 | 27GARDNERS | 1 | 115 | 226/227 | 190 | 118.81 | 123.6 | AE1-101 | PN_P2-3_PN-230-0014-11_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200504 | 26CARLISLE | 204528 | 27GARDNERS | 1 | 115 | 226/227 | 190 | 118.74 | 123.59 | AE1-101 | PN_P2-2_PN-115-031_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 235463 | 01TANEY | 1 | 138 | 227/201 | 317 | 124.33 | 123.49 | AE1-101 | PN_P2-3_PN-115-10T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204538 | 27STRABAN | 204544 | 27LINCOLN | 1 | 115 | 227 | 371 | 121.46 | 123.37 | AE1-101 | AP_P2-3_WP-138-272T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3464 | 168.25 | 162.23 | AB2-161 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204538 | 27STRABAN | 204544 | 27LINCOLN | 1 | 115 | 227 | 371 | 121.24 | 122.94 | AE1-101 | PN_P2-3_PN-115-0331-D_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208078 | SAKR | 1 | 230 | 229 | 903 | 117.22 | 122.44 | AE1-101 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204512 | 27S.RDG | 204693 | 27BOONETOWN | 1 | 230 | 227 | 607 | 107.35 | 122.05 | AE1-101 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204512 | 27S.RDG | 204693 | 27BOONETOWN | 1 | 230 | 227 | 607 | 107.33 | 122.02 | AE1-101 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204512 | 27S.RDG | 204693 | 27BOONETOWN | 1 | 230 | 227 | 607 | 107.32 | 122.02 | AE1-101 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200519 | 26REED TAP | 200522 | 26SHADE GP | 1 | 115 | 226 | 271 | 114.29 | 121.9 | AE1-101 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3464 | 168.16 | 162.15 | AB2-169 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208031 | MLWD TR2 | 1 | 230 | 229 | 911 | 111.77 | 121.07 | AE1-101 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208031 | MLWD TR2 | 1 | 230 | 229 | 911 | 111.77 | 121.07 | AE1-101 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208031 | MLWD TR2 | 1 | 230 | 229 | 911 | 111.77 | 121.07 | AE1-101 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200512 | 26LEWISTWN | 200519 | 26REED TAP | 1 | 115 | 226 | 271 | 118.2 | 120.92 | AE1-101 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200512 | 26LEWISTWN | 200519 | 26REED TAP | 1 | 115 | 226 | 271 | 118.2 | 120.92 | AE1-101 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200512 | 26LEWISTWN | 200519 | 26REED TAP | 1 | 115 | 226 | 271 | 118.14 | 120.86 | AE1-101 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204529 | 27GERMANTN | 204538 | 27STRABAN | 1 | 115 | 227 | 371 | 116.39 | 119.51 | AE1-101 | PN_P1-3_PN-115-118_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204529 | 27GERMANTN | 204538 | 27STRABAN | 1 | 115 | 227 | 371 | 116.39 | 119.5 | AE1-101 | AP_P1-2_WP-138-340BT_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204529 | 27GERMANTN | 204538 | 27STRABAN | 1 | 115 | 227 | 371 | 116.24 | 119.5 | AE1-101 | AP_P1-2_WP-138-340AT_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204529 | 27GERMANTN | 204538 | 27STRABAN | 1 | 115 | 227 | 371 | 115.7 | 118.93 | AE1-101 | AP_P2-3_WP-138-272T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 2 | 230 | 233 | 793 | 121.53 | 118.77 | AE1-101 | PEPCO_P1_PP1_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 793 | 121.53 | 118.77 | AE1-101 | PEPCO_P1_PP2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204529 | 27GERMANTN | 204538 | 27STRABAN | 1 | 115 | 227 | 371 | 115.49 | 118.5 | AE1-101 | PN_P2-3_PN-115-0331-D_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 122.78 | 117.4 | AE1-101 | PECO_P4_PEACH225_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 203981 | AD2-062_POI | 235188 | 01GREENE | 1 | 138 | 226/201 | 317 | 134.2 | 117.31 | AE1-101 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 203981 | AD2-062_POI | 235188 | 01GREENE | 1 | 138 | 226/201 | 317 | 134.2 | 117.31 | AE1-101 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 203981 | AD2-062_POI | 235188 | 01GREENE | 1 | 138 | 226/201 | 317 | 134.2 | 117.31 | AE1-101 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 119.25 | 117.3 | AE1-101 | AP_P2-3_PE-500-019C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 203981 | AD2-062_POI | 235188 | 01GREENE | 1 | 138 | 226/201 | 317 | 133.97 | 116.96 | AE1-101 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200532 | 26ROXBURY | 203981 | AD2-062_POI | 1 | 138 | 226 | 317 | 133.42 | 116.01 | AE1-101 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200532 | 26ROXBURY | 203981 | AD2-062_POI | 1 | 138 | 226 | 317 | 133.42 | 116.01 | AE1-101 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200532 | 26ROXBURY | 203981 | AD2-062_POI | 1 | 138 | 226 | 317 | 133.41 | 116.01 | AE1-101 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200519 | 26REED TAP | 200522 | 26SHADE GP | 1 | 115 | 226 | 271 | 110.69 | 116.01 | AE1-101 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200519 | 26REED TAP | 200522 | 26SHADE GP | 1 | 115 | 226 | 271 | 110.69 | 116.01 | AE1-101 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200519 | 26REED TAP | 200522 | 26SHADE GP | 1 | 115 | 226 | 271 | 110.63 | 115.95 | AE1-101 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 203981 | AD2-062_POI | 235188 | 01GREENE | 1 | 138 | 226/201 | 317 | 119.44 | 115.69 | AE1-101 | AP_P2-3_PE-500-016_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200532 | 26ROXBURY | 203981 | AD2-062_POI | 1 | 138 | 226 | 317 | 133.18 | 115.66 | AE1-101 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200512 | 26LEWISTWN | 200519 | 26REED TAP | 1 | 115 | 226 | 271 | 117 | 115.61 | AE1-101 | ME_P2-3_ME-115-003DT_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200512 | 26LEWISTWN | 200519 | 26REED TAP | 1 | 115 | 226 | 271 | 116.94 | 115.54 | AE1-101 | ME_P2-3_ME-115-003AT_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 203981 | AD2-062_POI | 235188 | 01GREENE | 1 | 138 | 226/201 | 317 | 119.63 | 115.54 | AE1-101 | AP_P2-3_PE-500-015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 2 | 500/230 | 225/232 | 2168 | 109.63 | 114.91 | AE1-101 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 203981 | AD2-062_POI | 235188 | 01GREENE | 1 | 138 | 226/201 | 317 | 127.14 | 114.9 | AE1-101 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 2 | 500/230 | 225/232 | 2168 | 109.46 | 114.69 | AE1-101 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 2 | 500/230 | 225/232 | 2168 | 109.46 | 114.69 | AE1-101 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 1 | 500/230 | 225/232 | 2168 | 109.4 | 114.67 | AE1-101 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3464 | 168.96 | 162.93 | AB2-172 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200532 | 26ROXBURY | 200520 | 26ROXBURY | 2 | 138/115 | 226 | 435 | 101.32 | 114.55 | AE1-101 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200532 | 26ROXBURY | 200520 | 26ROXBURY | 2 | 138/115 | 226 | 435 | 101.32 | 114.55 | AE1-101 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 1 | 500/230 | 225/232 | 2168 | 109.23 | 114.45 | AE1-101 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 1 | 500/230 | 225/232 | 2168 | 109.22 | 114.45 | AE1-101 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200532 | 26ROXBURY | 200520 | 26ROXBURY | 2 | 138/115 | 226 | 435 | 101.17 | 114.4 | AE1-101 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200532 | 26ROXBURY | 203981 | AD2-062_POI | 1 | 138 | 226 | 317 | 118.66 | 114.4 | AE1-101 | AP_P2-3_PE-500-016_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200532 | 26ROXBURY | 203981 | AD2-062_POI | 1 | 138 | 226 | 317 | 118.85 | 114.25 | AE1-101 | AP_P2-3_PE-500-015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204512 | 27S.RDG | 204693 | 27BOONETOWN | 1 | 230 | 227 | 607 | 105.57 | 113.85 | AE1-101 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208020 | MANO TR3 | 208031 | MLWD TR2 | 1 | 230 | 229 | 903 | 102.58 | 113.61 | AE1-101 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200532 | 26ROXBURY | 203981 | AD2-062_POI | 1 | 138 | 226 | 317 | 126.36 | 113.61 | AE1-101 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 793 | 115.54 | 112.89 | AE1-101 | PEPCO_P4_PP19_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208020 | MANO TR3 | 208031 | MLWD TR2 | 1 | 230 | 229 | 903 | 101.88 | 112.43 | AE1-101 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208020 | MANO TR3 | 208031 | MLWD TR2 | 1 | 230 | 229 | 903 | 101.87 | 112.43 | AE1-101 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208020 | MANO TR3 | 208031 | MLWD TR2 | 1 | 230 | 229 | 903 | 101.88 | 112.43 | AE1-101 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208031 | MLWD TR2 | 1 | 230 | 229 | 911 | 105.02 | 111.67 | AE1-101 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3464 | 168.13 | 162.12 | AB2-174 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200519 | 26REED TAP | 200522 | 26SHADE GP | 1 | 115 | 226 | 271 | 109.49 | 110.78 | AE1-101 | ME_P2-3_ME-115-003DT_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200519 | 26REED TAP | 200522 | 26SHADE GP | 1 | 115 | 226 | 271 | 109.42 | 110.71 | AE1-101 | ME_P2-3_ME-115-003AT_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200532 | 26ROXBURY | 200520 | 26ROXBURY | 2 | 138/115 | 226 | 435 | 97.23 | 110.6 | AE1-101 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200532 | 26ROXBURY | 200520 | 26ROXBURY | 2 | 138/115 | 226 | 435 | 97.23 | 110.6 | AE1-101 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200532 | 26ROXBURY | 200520 | 26ROXBURY | 2 | 138/115 | 226 | 435 | 97.22 | 110.6 | AE1-101 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200532 | 26ROXBURY | 200520 | 26ROXBURY | 2 | 138/115 | 226 | 435 | 97.06 | 110.43 | AE1-101 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 2 | 230 | 233 | 793 | 112.01 | 110.09 | AE1-101 | AP_P2-3_PE-500-019C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 793 | 112.01 | 110.09 | AE1-101 | AP_P2-3_PE-500-019C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200009 | JUNI | 208004 | JUNI | 2 | 500/230 | 225/229 | 1040 | 107.81 | 107.24 | AE1-101 | PL_10_P42_000140_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 204529 | 27GERMANTN | 1 | 138/115 | 227 | 453 | 104.75 | 106.7 | AE1-101 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 204529 | 27GERMANTN | 1 | 138/115 | 227 | 453 | 104.75 | 106.7 | AE1-101 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 204529 | 27GERMANTN | 1 | 138/115 | 227 | 453 | 104.75 | 106.69 | AE1-101 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 204529 | 27GERMANTN | 1 | 138/115 | 227 | 453 | 104.6 | 106.52 | AE1-101 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200504 | 26CARLISLE | 200520 | 26ROXBURY | 1 | 115 | 226 | 190 | 95.46 | 105.13 | AE1-101 | PN_P1-2_PN-115-094_A_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200504 | 26CARLISLE | 200520 | 26ROXBURY | 1 | 115 | 226 | 190 | 95.27 | 104.29 | AE1-101 | PN_P2-3_PN-115-58B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200504 | 26CARLISLE | 200520 | 26ROXBURY | 1 | 115 | 226 | 190 | 95.86 | 104.24 | AE1-101 | PN_P1-3_PN-115-040_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200504 | 26CARLISLE | 200520 | 26ROXBURY | 1 | 115 | 226 | 190 | 95.86 | 104.24 | AE1-101 | PN_P2-2_PN-115-030_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200504 | 26CARLISLE | 200520 | 26ROXBURY | 1 | 115 | 226 | 190 | 95.08 | 104.22 | AE1-101 | PN_P1-2_PN-115-094_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200532 | 26ROXBURY | 200520 | 26ROXBURY | 2 | 138/115 | 226 | 435 | 92.08 | 103.35 | AE1-101 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 99.48 | 103.33 | AE1-101 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 99.47 | 103.33 | AE1-101 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 99.48 | 103.33 | AE1-101 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208020 | MANO TR3 | 208031 | MLWD TR2 | 1 | 230 | 229 | 903 | 95.51 | 103.29 | AE1-101 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 98.55 | 102 | AE1-101 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204520 | 27ALLEN | 208142 | WIGR-115 | 1 | 115 | 227/229 | 351.4 | 94.32 | 101.83 | AE1-101 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204520 | 27ALLEN | 208142 | WIGR-115 | 1 | 115 | 227/229 | 351.4 | 94.32 | 101.83 | AE1-101 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204520 | 27ALLEN | 208142 | WIGR-115 | 1 | 115 | 227/229 | 351.4 | 94.32 | 101.83 | AE1-101 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204520 | 27ALLEN | 208142 | WIGR-115 | 1 | 115 | 227/229 | 351.4 | 94.08 | 101.65 | AE1-101 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 98.65 | 100.66 | AE1-101 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200504 | 26CARLISLE | 200520 | 26ROXBURY | 1 | 115 | 226 | 190 | 86.13 | 100.64 | AE1-101 | PN_P2-3_PN-115-0331-B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 223960 | BRG 1T 230 | 1 | 500/230 | 225/233 | 1498 | 100.21 | 100.58 | AE1-101 | PEPCO_P4_PP41_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200504 | 26CARLISLE | 200520 | 26ROXBURY | 1 | 115 | 226 | 190 | 92.83 | 100.27 | AE1-101 | PN_P2-3_PN-230-0014-12_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 229.52 | 242.55 | AE1-104 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 227.45 | 242.54 | AE1-104 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 228.61 | 240.43 | AE1-104 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 226.55 | 240.43 | AE1-104 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 226.48 | 240.35 | AE1-104 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 228.55 | 240.35 | AE1-104 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 226.48 | 240.35 | AE1-104 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 228.55 | 240.35 | AE1-104 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 217.27 | 232.22 | AE1-104 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 216.39 | 230.17 | AE1-104 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 216.33 | 230.1 | AE1-104 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 216.33 | 230.1 | AE1-104 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 213 | 229.06 | AE1-104 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 212.13 | 226.98 | AE1-104 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 212.06 | 226.91 | AE1-104 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 212.06 | 226.91 | AE1-104 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 213.72 | 221.76 | AE1-104 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 211.65 | 221.76 | AE1-104 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 202.01 | 212.07 | AE1-104 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 197.74 | 208.75 | AE1-104 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 174.26 | 169.53 | AE1-104 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 173.34 | 168.14 | AE1-104 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 173.34 | 168.14 | AE1-104 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 173.32 | 168.14 | AE1-104 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 165.26 | 167.15 | AE1-104 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 163.46 | 164.09 | AE1-104 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 163.47 | 164.09 | AE1-104 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 163.47 | 164.09 | AE1-104 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3464 | 168.91 | 162.88 | AB2-179 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 165.39 | 160.44 | AE1-104 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 154.97 | 159.7 | AE1-104 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 163.63 | 158.75 | AE1-104 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 163.63 | 158.74 | AE1-104 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 153.27 | 158.37 | AE1-104 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 163.69 | 156.38 | AE1-104 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 149.91 | 154.72 | AE1-104 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 903 | 145.51 | 154.08 | AE1-104 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 154.53 | 153.27 | AE1-104 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 157.23 | 152.06 | AE1-104 | PN_P1-2_PN-500-010T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 903 | 144.05 | 151.41 | AE1-104 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 903 | 144.05 | 151.41 | AE1-104 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 903 | 144.03 | 151.41 | AE1-104 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 147.7 | 151.03 | AE1-104 | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 147.63 | 150.96 | AE1-104 | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 145.23 | 149.68 | AE1-104 | AP_P2-3_PE-500-016_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 145.3 | 149.66 | AE1-104 | AP_P2-3_PE-500-015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 155.07 | 149.6 | AE1-104 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 154.87 | 149.41 | AE1-104 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 154.89 | 149.4 | AE1-104 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 154.46 | 149.31 | AE1-104 | PJM_500_BG_P4_5_CNSTN_L_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 154.62 | 149.2 | AE1-104 | PECO_P4_NOTTI85_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 154.56 | 149.18 | AE1-104 | PECO_P1-2_220-08_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 154.49 | 149.12 | AE1-104 | PECO_P4_COOPR125_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.41 | 148.8 | AE1-104 | AP_P1-2_WP-500-DRT17_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.41 | 148.8 | AE1-104 | AP_P1-2_PE-500-001_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.36 | 148.73 | AE1-104 | AP_P2-3_PE-500-018C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3464 | 167.79 | 161.78 | AB2-190 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 153.23 | 146.42 | AE1-104 | PECO_P4_PEACH025_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 152.96 | 146.2 | AE1-104 | PECO_P1-2_PBTIE1_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 911 | 150.47 | 144.74 | AE1-104 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204502 | 27JACKSON | 204514 | 27TMI | 1 | 230 | 227 | 781 | 134.19 | 143.5 | AE1-104 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 911 | 149.57 | 143.48 | AE1-104 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 911 | 149.57 | 143.48 | AE1-104 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 911 | 149.55 | 143.47 | AE1-104 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204502 | 27JACKSON | 204514 | 27TMI | 1 | 230 | 227 | 781 | 134.38 | 143.42 | AE1-104 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204502 | 27JACKSON | 204514 | 27TMI | 1 | 230 | 227 | 781 | 134.38 | 143.42 | AE1-104 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204502 | 27JACKSON | 204514 | 27TMI | 1 | 230 | 227 | 781 | 134.36 | 143.42 | AE1-104 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 903 | 136.97 | 141.47 | AE1-104 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 1031 | 131.89 | 140.84 | AE1-104 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 1031 | 131.4 | 139.72 | AE1-104 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 1031 | 131.41 | 139.72 | AE1-104 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 1031 | 131.41 | 139.72 | AE1-104 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 911 | 141.7 | 136.49 | AE1-104 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 207922 | BRIS | 207923 | BRISREAC | RX | 230 | 229 | 676 | 126 | 135.93 | AE1-104 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 207923 | BRISREAC | 208132 | WHEM TR1 | 1 | 230 | 229 | 676 | 126 | 135.93 | AE1-104 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208078 | SAKR | 1 | 230 | 229 | 903 | 126.68 | 135.87 | AE1-104 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 140.89 | 134.88 | AE1-104 | PECO_P4_PEACH205_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 141.05 | 134.82 | AE1-104 | PECO_P1-2_PBTIE2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208078 | SAKR | 1 | 230 | 229 | 903 | 125.97 | 134.41 | AE1-104 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 207922 | BRIS | 207923 | BRISREAC | RX | 230 | 229 | 676 | 125.28 | 134.41 | AE1-104 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 207922 | BRIS | 207923 | BRISREAC | RX | 230 | 229 | 676 | 125.27 | 134.41 | AE1-104 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 207923 | BRISREAC | 208132 | WHEM TR1 | 1 | 230 | 229 | 676 | 125.27 | 134.41 | AE1-104 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 207923 | BRISREAC | 208132 | WHEM TR1 | 1 | 230 | 229 | 676 | 125.28 | 134.41 | AE1-104 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 207922 | BRIS | 207923 | BRISREAC | RX | 230 | 229 | 676 | 125.28 | 134.41 | AE1-104 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 207923 | BRISREAC | 208132 | WHEM TR1 | 1 | 230 | 229 | 676 | 125.28 | 134.41 | AE1-104 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208078 | SAKR | 1 | 230 | 229 | 903 | 125.97 | 134.4 | AE1-104 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208078 | SAKR | 1 | 230 | 229 | 903 | 125.97 | 134.4 | AE1-104 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 139.99 | 133.83 | AE1-104 | PECO_P4_PEACH055_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204502 | 27JACKSON | 204514 | 27TMI | 1 | 230 | 227 | 781 | 126.73 | 132.95 | AE1-104 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220972 | GRANITE1 | 1 | 230 | 232 | 829 | 136.29 | 132.29 | AE1-104 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220972 | GRANITE1 | 1 | 230 | 232 | 829 | 135.67 | 131.64 | AE1-104 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220972 | GRANITE1 | 1 | 230 | 232 | 829 | 135.67 | 131.64 | AE1-104 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 1031 | 125.81 | 130.94 | AE1-104 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220973 | GRANITE6 | 1 | 230 | 232 | 829 | 134.19 | 130.37 | AE1-104 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220973 | GRANITE6 | 1 | 230 | 232 | 829 | 133.6 | 129.76 | AE1-104 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220973 | GRANITE6 | 1 | 230 | 232 | 829 | 133.6 | 129.76 | AE1-104 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 135.61 | 129.71 | AE1-104 | PECO_P4_PEACH015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 128.78 | 129.15 | AE1-104 | BG_P7_GRCTN_CNSTN_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 126.72 | 129.15 | AE1-104 | BG_P7_GRCTN_CNSTN_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 130.09 | 128.35 | AE1-104 | DVP_P4-2: 514T595_SRT-SW |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208020 | MANO TR3 | 1 | 230 | 229 | 793 | 113.74 | 128.17 | AE1-104 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 134.08 | 128.17 | AE1-104 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220953 | HOWARD12 | 220972 | GRANITE1 | 1 | 230 | 232 | 772 | 131.3 | 127.28 | AE1-104 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 128.38 | 126.66 | AE1-104 | DVP_P4-2: 51482_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208020 | MANO TR3 | 1 | 230 | 229 | 793 | 112.94 | 126.57 | AE1-104 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 128.38 | 126.57 | AE1-104 | AP_P1-2_PE-500-407T_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 128.38 | 126.57 | AE1-104 | DVP_P1-2: LN 514_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208020 | MANO TR3 | 1 | 230 | 229 | 793 | 112.95 | 126.56 | AE1-104 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208020 | MANO TR3 | 1 | 230 | 229 | 793 | 112.95 | 126.56 | AE1-104 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220954 | HOWARD32 | 220973 | GRANITE6 | 1 | 230 | 232 | 772 | 130.06 | 126.5 | AE1-104 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220953 | HOWARD12 | 220972 | GRANITE1 | 1 | 230 | 232 | 772 | 130.4 | 126.31 | AE1-104 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220953 | HOWARD12 | 220972 | GRANITE1 | 1 | 230 | 232 | 772 | 130.39 | 126.31 | AE1-104 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 207922 | BRIS | 207923 | BRISREAC | RX | 230 | 229 | 676 | 120.18 | 126.26 | AE1-104 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 207923 | BRISREAC | 208132 | WHEM TR1 | 1 | 230 | 229 | 676 | 120.18 | 126.26 | AE1-104 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220954 | HOWARD32 | 220973 | GRANITE6 | 1 | 230 | 232 | 772 | 129.27 | 125.67 | AE1-104 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220954 | HOWARD32 | 220973 | GRANITE6 | 1 | 230 | 232 | 772 | 129.27 | 125.67 | AE1-104 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 119.64 | 124.6 | AE1-104 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 121.71 | 124.6 | AE1-104 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208078 | SAKR | 1 | 230 | 229 | 903 | 118.71 | 124.58 | AE1-104 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208031 | MLWD TR2 | 1 | 230 | 229 | 911 | 113.84 | 124.43 | AE1-104 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 119.46 | 124.39 | AE1-104 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 121.52 | 124.39 | AE1-104 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 121.52 | 124.39 | AE1-104 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 119.46 | 124.39 | AE1-104 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204512 | 27S.RDG | 204693 | 27BOONETOWN | 1 | 230 | 227 | 607 | 108.42 | 124.13 | AE1-104 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200025 | W CHAPEL | 1 | 500 | 225 | 1732 | 124.92 | 123.18 | AE1-104 | PEPCO_P4_PP41_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208031 | MLWD TR2 | 1 | 230 | 229 | 911 | 113.15 | 122.96 | AE1-104 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208031 | MLWD TR2 | 1 | 230 | 229 | 911 | 113.15 | 122.95 | AE1-104 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208031 | MLWD TR2 | 1 | 230 | 229 | 911 | 113.15 | 122.95 | AE1-104 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 120 | 122.43 | AE1-104 | BG_P7_GRCTN_CNSTN_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 120.73 | 121.38 | AE1-104 | PJM_500_BG_P4_5_CNSTN_15_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 118.67 | 121.38 | AE1-104 | PJM_500_BG_P4_5_CNSTN_15_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208131 | WHEM | 208132 | WHEM TR1 | 1 | 230 | 229 | 691 | 110.18 | 120.57 | AE1-104 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220965 | NEAST339 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 120.79 | 120.16 | AE1-104 | BG_P1_2315_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 911 | 119 | 120.06 | AE1-104 | PJM_500_BG_P4_5_CNSTN_15_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220965 | NEAST339 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 120.35 | 119.94 | AE1-104 | BG_P4_5_NEAST_17_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220965 | NEAST339 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 120.51 | 119.94 | AE1-104 | BG_P4_5_NEAST_15_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 125.02 | 119.56 | AE1-104 | PECO_P4_PEACH225_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 115.65 | 119.46 | AE1-104 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3464 | 168.29 | 162.27 | AC1-033 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3464 | 168.17 | 162.15 | AC1-034 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220979 | NEAST317 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 119.85 | 119.27 | AE1-104 | BG_P1_2337_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208131 | WHEM | 208132 | WHEM TR1 | 1 | 230 | 229 | 691 | 109.5 | 119.12 | AE1-104 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208131 | WHEM | 208132 | WHEM TR1 | 1 | 230 | 229 | 691 | 109.49 | 119.12 | AE1-104 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208131 | WHEM | 208132 | WHEM TR1 | 1 | 230 | 229 | 691 | 109.5 | 119.12 | AE1-104 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 115.3 | 119.12 | AE1-104 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 115.3 | 119.06 | AE1-104 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 115.3 | 119.06 | AE1-104 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220979 | NEAST317 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 119.51 | 118.99 | AE1-104 | BG_P4_5_NEAST_39_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220979 | NEAST317 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 119.51 | 118.99 | AE1-104 | BG_P4_5_NEAST_37_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 114.96 | 118.73 | AE1-104 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 114.96 | 118.72 | AE1-104 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 115.73 | 118.59 | AE1-104 | BG_P7_GRCTN_CNSTN_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 113.17 | 118.04 | AE1-104 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 112.99 | 117.84 | AE1-104 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 112.99 | 117.84 | AE1-104 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 118.56 | 116.64 | AE1-104 | AP_P2-3_PE-500-019C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3464 | 168.01 | 162 | AC1-043 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204512 | 27S.RDG | 204693 | 27BOONETOWN | 1 | 230 | 227 | 607 | 106.49 | 116.25 | AE1-104 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208020 | MANO TR3 | 1 | 230 | 229 | 793 | 105.76 | 116.13 | AE1-104 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 2 | 500/230 | 225/232 | 2168 | 110.47 | 115.89 | AE1-104 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 2 | 500/230 | 225/232 | 2168 | 110.29 | 115.68 | AE1-104 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 2 | 500/230 | 225/232 | 2168 | 110.29 | 115.68 | AE1-104 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208020 | MANO TR3 | 208031 | MLWD TR2 | 1 | 230 | 229 | 903 | 103.87 | 115.66 | AE1-104 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 1 | 500/230 | 225/232 | 2168 | 110.23 | 115.65 | AE1-104 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 1 | 500/230 | 225/232 | 2168 | 110.06 | 115.43 | AE1-104 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 1 | 500/230 | 225/232 | 2168 | 110.06 | 115.43 | AE1-104 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220964 | GRACETON | 220999 | BAGLEY2 | 13 | 230 | 232 | 1795 | 114.23 | 115.33 | AE1-104 | BG_P4_5_GRCTN_3T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 112.23 | 114.99 | AE1-104 | PJM_500_BG_P4_5_CNSTN_15_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 108.9 | 114.22 | AE1-104 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208020 | MANO TR3 | 208031 | MLWD TR2 | 1 | 230 | 229 | 903 | 103.19 | 114.14 | AE1-104 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208020 | MANO TR3 | 208031 | MLWD TR2 | 1 | 230 | 229 | 903 | 103.19 | 114.13 | AE1-104 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208020 | MANO TR3 | 208031 | MLWD TR2 | 1 | 230 | 229 | 903 | 103.19 | 114.13 | AE1-104 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 108.72 | 114.02 | AE1-104 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 108.72 | 114.02 | AE1-104 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208031 | MLWD TR2 | 1 | 230 | 229 | 911 | 106.4 | 113.67 | AE1-104 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 2 | 500/230 | 225/232 | 2168 | 109.15 | 112.52 | AE1-104 | PJM_500_BG_P4_5_CNSTN_15_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 107.26 | 112.24 | AE1-104 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 107.14 | 112.1 | AE1-104 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220980 | RAPHAEL | 220999 | BAGLEY2 | 13 | 230 | 232 | 1795 | 109.79 | 112.09 | AE1-104 | BG_P4_5_GRCTN_3T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3464 | 168.12 | 162.11 | AC1-053 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208131 | WHEM | 208133 | WHEM TR2 | 1 | 230 | 229 | 691 | 102.66 | 111.94 | AE1-104 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208131 | WHEM | 208132 | WHEM TR1 | 1 | 230 | 229 | 691 | 104.71 | 111.64 | AE1-104 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 107.96 | 111.29 | AE1-104 | PJM_500_BG_P4_5_CNSTN_15_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208131 | WHEM | 208133 | WHEM TR2 | 1 | 230 | 229 | 691 | 101.98 | 110.51 | AE1-104 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208131 | WHEM | 208133 | WHEM TR2 | 1 | 230 | 229 | 691 | 101.97 | 110.51 | AE1-104 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208131 | WHEM | 208133 | WHEM TR2 | 1 | 230 | 229 | 691 | 101.98 | 110.51 | AE1-104 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220973 | GRANITE6 | 1 | 230 | 232 | 829 | 109.92 | 108.72 | AE1-104 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220965 | NEAST339 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 109.3 | 107.87 | AE1-104 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220965 | NEAST339 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 109.2 | 107.76 | AE1-104 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220965 | NEAST339 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 109.2 | 107.76 | AE1-104 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220972 | GRANITE1 | 1 | 230 | 232 | 829 | 109.07 | 107.63 | AE1-104 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208021 | MANO TR4 | 208133 | WHEM TR2 | 2 | 230 | 229 | 593 | 97.3 | 106.81 | AE1-104 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 102.38 | 106.67 | AE1-104 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 102.29 | 106.59 | AE1-104 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200099 | LAUS | 208045 | LAUS | 3 | 500/230 | 225/229 | 1200 | 104.27 | 106.07 | AE1-104 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220972 | GRANITE1 | 1 | 230 | 232 | 829 | 107.03 | 105.69 | AE1-104 | BG_P4_5_NW230-4_2326_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200099 | LAUS | 208045 | LAUS | 3 | 500/230 | 225/229 | 1200 | 103.97 | 105.58 | AE1-104 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200099 | LAUS | 208045 | LAUS | 3 | 500/230 | 225/229 | 1200 | 103.97 | 105.58 | AE1-104 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 103.47 | 105.56 | AE1-104 | BG_P1_2322_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200099 | LAUS | 208045 | LAUS | 3 | 500/230 | 225/229 | 1200 | 103.96 | 105.56 | AE1-104 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 103.4 | 105.48 | AE1-104 | BG_P1_2310_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 103.41 | 105.45 | AE1-104 | BG_P4_5_NW2322_230-4_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 103.33 | 105.41 | AE1-104 | BG_P4_5_NW2310_230-5_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208021 | MANO TR4 | 208133 | WHEM TR2 | 2 | 230 | 229 | 593 | 96.53 | 105.21 | AE1-104 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208021 | MANO TR4 | 208133 | WHEM TR2 | 2 | 230 | 229 | 593 | 96.53 | 105.21 | AE1-104 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208021 | MANO TR4 | 208133 | WHEM TR2 | 2 | 230 | 229 | 593 | 96.51 | 105.21 | AE1-104 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208020 | MANO TR3 | 208031 | MLWD TR2 | 1 | 230 | 229 | 903 | 96.82 | 105.19 | AE1-104 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220973 | GRANITE6 | 1 | 230 | 232 | 829 | 106.7 | 105.16 | AE1-104 | BG_P4_5_NW230-5_2311_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220979 | NEAST317 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 106.15 | 104.78 | AE1-104 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220979 | NEAST317 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 106.05 | 104.67 | AE1-104 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220979 | NEAST317 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 106.05 | 104.66 | AE1-104 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 102.04 | 104.17 | AE1-104 | BG_P4_5_NW230-2_2322_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 99.83 | 104.12 | AE1-104 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 99.84 | 104.12 | AE1-104 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 99.83 | 104.11 | AE1-104 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 101.94 | 104.05 | AE1-104 | BG_P4_5_NW2371_2310_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 101.94 | 104.05 | AE1-104 | BG_P4_5_NW230-3_2310_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220973 | GRANITE6 | 1 | 230 | 232 | 829 | 104.62 | 103.57 | AE1-104 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208131 | WHEM | 208133 | WHEM TR2 | 1 | 230 | 229 | 691 | 97.2 | 103.33 | AE1-104 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 101.07 | 103.11 | AE1-104 | BG_P4_5_CNSTN_14_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220965 | NEAST339 | 220977 | RIV2339 | 1 | 230 | 232 | 991 | 104.56 | 103.11 | AE1-104 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220966 | RIV2317 | 220979 | NEAST317 | 1 | 230 | 232 | 940 | 104.13 | 103.07 | AE1-104 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220965 | NEAST339 | 220977 | RIV2339 | 1 | 230 | 232 | 991 | 104.52 | 103.05 | AE1-104 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220965 | NEAST339 | 220977 | RIV2339 | 1 | 230 | 232 | 991 | 104.52 | 103.05 | AE1-104 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220964 | GRACETON | 221000 | BAGLEY | 5 | 230 | 232 | 1795 | 102.22 | 103.02 | AE1-104 | BG_P1_2313_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220964 | GRACETON | 220999 | BAGLEY2 | 13 | 230 | 232 | 1795 | 102.22 | 103.02 | AE1-104 | BG_P1_2305_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220966 | RIV2317 | 220979 | NEAST317 | 1 | 230 | 232 | 940 | 104.08 | 103.01 | AE1-104 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220966 | RIV2317 | 220979 | NEAST317 | 1 | 230 | 232 | 940 | 104.08 | 103.01 | AE1-104 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220965 | NEAST339 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 103.59 | 102.99 | AE1-104 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 98.94 | 102.82 | AE1-104 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220972 | GRANITE1 | 1 | 230 | 232 | 829 | 104.03 | 102.8 | AE1-104 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 2 | 500/230 | 225/232 | 2168 | 99.59 | 102.39 | AE1-104 | BG_P1_CNSTN_500-2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 2 | 500/230 | 225/232 | 2168 | 99.59 | 102.39 | AE1-104 | PJM_500_BG_P2_CNSTN_230-N_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 1 | 500/230 | 225/232 | 2168 | 99.48 | 102.28 | AE1-104 | BG_P1_CNSTN_500-4_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 1 | 500/230 | 225/232 | 2168 | 99.48 | 102.28 | AE1-104 | PJM_500_BG_P2_CNSTN_230-S_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 223960 | BRG 1T 230 | 1 | 500/230 | 225/233 | 1498 | 101.06 | 101.49 | AE1-104 | PEPCO_P4_PP41_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 99.01 | 101.41 | AE1-104 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208021 | MANO TR4 | 1 | 230 | 229 | 600 | 90.36 | 100.93 | AE1-104 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220979 | NEAST317 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 101.45 | 100.85 | AE1-104 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220972 | GRANITE1 | 1 | 230 | 232 | 829 | 101.7 | 100.61 | AE1-104 | BG_P4_5_GRNITE26_32_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220973 | GRANITE6 | 1 | 230 | 232 | 829 | 101.53 | 100.17 | AE1-104 | BBG_P1_2311_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220972 | GRANITE1 | 1 | 230 | 232 | 829 | 101.22 | 100.12 | AE1-104 | BG_P1_2326_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220973 | GRANITE6 | 1 | 230 | 232 | 829 | 100.95 | 100.09 | AE1-104 | BG_P1_2312_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220973 | GRANITE6 | 1 | 230 | 232 | 829 | 101.09 | 100.08 | AE1-104 | BG_P4_5_GRNITE11_12_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 174.05 | 169.45 | AE1-129 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 173.11 | 167.81 | AE1-129 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 173.11 | 167.8 | AE1-129 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 173.09 | 167.8 | AE1-129 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 165.13 | 166.78 | AE1-129 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 163.31 | 163.77 | AE1-129 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 163.31 | 163.77 | AE1-129 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 163.3 | 163.77 | AE1-129 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 165.16 | 160.31 | AE1-129 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 154.3 | 158.9 | AE1-129 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 152.61 | 157.58 | AE1-129 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 903 | 146.16 | 154.31 | AE1-129 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 149.24 | 153.93 | AE1-129 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 154.37 | 153 | AE1-129 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 903 | 144.67 | 151.86 | AE1-129 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 903 | 144.67 | 151.86 | AE1-129 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 903 | 144.66 | 151.85 | AE1-129 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 147.03 | 150.23 | AE1-129 | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.96 | 150.16 | AE1-129 | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.63 | 148.97 | AE1-129 | AP_P2-3_PE-500-016_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.7 | 148.95 | AE1-129 | AP_P2-3_PE-500-015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.47 | 148.34 | AE1-129 | PJM_500_BG_P4_5_CNSTN_L_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.81 | 148.09 | AE1-129 | AP_P1-2_WP-500-DRT17_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.81 | 148.09 | AE1-129 | AP_P1-2_PE-500-001_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.76 | 148.02 | AE1-129 | AP_P2-3_PE-500-018C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 147.27 | 147.75 | AE1-129 | BG_P7_GRCTN_CNSTN_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3464 | 168.2 | 162.19 | AC1-054 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 151.09 | 146.12 | AE1-129 | PL_05_P71_000906_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 150.43 | 145.3 | AE1-129 | PL_04_P42_000557_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 150.02 | 144.83 | AE1-129 | PL_04_P42_000570_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 911 | 150.26 | 144.75 | AE1-129 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 149.82 | 144.69 | AE1-129 | PL_04_P42_000561_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 149.38 | 144.25 | AE1-129 | PL_04_P12_000257_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 149.38 | 144.25 | AE1-129 | PL_05_P22_000674_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 149.34 | 144.25 | AE1-129 | BG_P4_5_GRCTN_2T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 148.9 | 143.71 | AE1-129 | ME_P2-3_ME-230-019CT_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 148.6 | 143.44 | AE1-129 | PL_04_P42_000564_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 911 | 149.34 | 143.17 | AE1-129 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 911 | 149.34 | 143.17 | AE1-129 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 911 | 149.32 | 143.16 | AE1-129 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 142.68 | 142.32 | AE1-129 | PJM_500_BG_P4_5_CNSTN_15_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 903 | 137.59 | 141.85 | AE1-129 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204502 | 27JACKSON | 204514 | 27TMI | 1 | 230 | 227 | 781 | 132.58 | 141.32 | AE1-129 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204502 | 27JACKSON | 204514 | 27TMI | 1 | 230 | 227 | 781 | 132.58 | 141.31 | AE1-129 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204502 | 27JACKSON | 204514 | 27TMI | 1 | 230 | 227 | 781 | 132.57 | 141.31 | AE1-129 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204502 | 27JACKSON | 204514 | 27TMI | 1 | 230 | 227 | 781 | 132.39 | 141.01 | AE1-129 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 911 | 141.46 | 136.42 | AE1-129 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 139.62 | 133.67 | AE1-129 | PECO_P4_PEACH205_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204502 | 27JACKSON | 204514 | 27TMI | 1 | 230 | 227 | 781 | 124.93 | 130.65 | AE1-129 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 129.66 | 127.93 | AE1-129 | DVP_P4-2: 514T595_SRT-SW |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 911 | 124.12 | 126.62 | AE1-129 | BG_P7_GRCTN_CNSTN_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 127.94 | 126.24 | AE1-129 | DVP_P4-2: 51482_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 127.94 | 126.15 | AE1-129 | AP_P1-2_PE-500-407T_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 127.94 | 126.15 | AE1-129 | DVP_P1-2: LN 514_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 911 | 119.64 | 120.67 | AE1-129 | PJM_500_BG_P4_5_CNSTN_15_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 119.7 | 118.4 | AE1-129 | PL_04_P42_000564_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 119.7 | 118.4 | AE1-129 | PL_04_P12_000260_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 118.13 | 116.22 | AE1-129 | AP_P2-3_PE-500-019C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204538 | 27STRABAN | 204544 | 27LINCOLN | 1 | 115 | 227 | 371 | 113.32 | 114.15 | AE1-129 | ME_P2-3_ME-230-DTR059_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 115.14 | 113.99 | AE1-129 | BG_P4_5_CNSTN_14_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3464 | 167.82 | 161.81 | AC1-065 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204529 | 27GERMANTN | 204538 | 27STRABAN | 1 | 115 | 227 | 371 | 107.52 | 109.72 | AE1-129 | ME_P2-3_ME-230-DTR059_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200009 | JUNI | 208004 | JUNI | 2 | 500/230 | 225/229 | 1040 | 107.59 | 107.04 | AE1-129 | PL_10_P42_000140_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 235463 | 01TANEY | 1 | 138 | 227/201 | 317 | 106.28 | 105.02 | AE1-129 | ME_P1-3_ME-500-003_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 235463 | 01TANEY | 1 | 138 | 227/201 | 317 | 106.28 | 105.02 | AE1-129 | ME_P2-3_ME-500-002IT_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 235463 | 01TANEY | 1 | 138 | 227/201 | 317 | 106.29 | 105.02 | AE1-129 | ME_P1-2_ME-230-019_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204538 | 27STRABAN | 204544 | 27LINCOLN | 1 | 115 | 227 | 371 | 102.14 | 102.49 | AE1-129 | ME_P1-2_ME-230-019_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204538 | 27STRABAN | 204544 | 27LINCOLN | 1 | 115 | 227 | 371 | 102.14 | 102.49 | AE1-129 | ME_P2-3_ME-500-002IT_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204538 | 27STRABAN | 204544 | 27LINCOLN | 1 | 115 | 227 | 371 | 102.14 | 102.49 | AE1-129 | ME_P1-3_ME-500-003_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204520 | 27ALLEN | 208142 | WIGR-115 | 1 | 115 | 227/229 | 351.4 | 94.03 | 101.56 | AE1-129 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204520 | 27ALLEN | 208142 | WIGR-115 | 1 | 115 | 227/229 | 351.4 | 94.03 | 101.56 | AE1-129 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204520 | 27ALLEN | 208142 | WIGR-115 | 1 | 115 | 227/229 | 351.4 | 94.03 | 101.55 | AE1-129 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204520 | 27ALLEN | 208142 | WIGR-115 | 1 | 115 | 227/229 | 351.4 | 93.8 | 101.23 | AE1-129 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3464 | 168.2 | 162.19 | AC1-074 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 162.17 | 154.93 | AE1-142 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.78 | 148.34 | AE1-142 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.58 | 148.15 | AE1-142 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.61 | 148.14 | AE1-142 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.34 | 147.94 | AE1-142 | PECO_P4_NOTTI85_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.28 | 147.93 | AE1-142 | PECO_P1-2_220-08_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.21 | 147.86 | AE1-142 | PECO_P4_COOPR125_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.05 | 147.71 | AE1-142 | AP_P2-3_PE-500-016_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.08 | 147.7 | AE1-142 | AP_P2-3_PE-500-015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.87 | 147.67 | AE1-142 | PECO_P1-2_220-93_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 151.56 | 147.24 | AE1-142 | AP_P1-2_WP-500-DRT17_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 151.41 | 144.68 | AE1-142 | PECO_P4_PEACH025_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 151.28 | 144.59 | AE1-142 | PECO_P1-2_PBTIE1_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 139.51 | 133.34 | AE1-142 | PECO_P1-2_PBTIE2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 133.91 | 128.08 | AE1-142 | PECO_P4_PEACH015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 123.45 | 118.06 | AE1-142 | PECO_P4_PEACH225_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 225.34 | 236.56 | AE1-153 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 223.34 | 236.56 | AE1-153 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 225.28 | 236.51 | AE1-153 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 223.28 | 236.51 | AE1-153 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 225.27 | 236.51 | AE1-153 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 223.28 | 236.51 | AE1-153 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 213.3 | 226.42 | AE1-153 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 213.24 | 226.37 | AE1-153 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 213.24 | 226.36 | AE1-153 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 209.04 | 223.2 | AE1-153 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 208.98 | 223.15 | AE1-153 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 208.98 | 223.15 | AE1-153 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 210.44 | 217.45 | AE1-153 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 208.44 | 217.44 | AE1-153 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 198.91 | 207.89 | AE1-153 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 194.65 | 204.54 | AE1-153 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 172.55 | 167.56 | AE1-153 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 171.59 | 166.13 | AE1-153 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 171.59 | 166.13 | AE1-153 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 171.57 | 166.12 | AE1-153 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 163.42 | 164.63 | AE1-153 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3464 | 168.16 | 162.15 | AC1-075 and AC1-080 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 161.56 | 161.55 | AE1-153 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 161.55 | 161.55 | AE1-153 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 161.54 | 161.54 | AE1-153 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 163.64 | 158.68 | AE1-153 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 153.33 | 157.74 | AE1-153 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 161.85 | 156.97 | AE1-153 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 161.85 | 156.97 | AE1-153 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 151.65 | 156.42 | AE1-153 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 161.31 | 154.1 | AE1-153 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 148.28 | 152.77 | AE1-153 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 903 | 144.08 | 151.86 | AE1-153 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 152.62 | 150.95 | AE1-153 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 155.43 | 150.28 | AE1-153 | PN_P1-2_PN-500-010T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 903 | 142.55 | 149.24 | AE1-153 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 903 | 142.55 | 149.24 | AE1-153 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 903 | 142.54 | 149.22 | AE1-153 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.13 | 149.17 | AE1-153 | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.06 | 149.1 | AE1-153 | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.74 | 147.89 | AE1-153 | AP_P2-3_PE-500-016_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.81 | 147.87 | AE1-153 | AP_P2-3_PE-500-015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.74 | 147.61 | AE1-153 | PJM_500_BG_P4_5_CNSTN_L_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.03 | 147.61 | AE1-153 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.83 | 147.42 | AE1-153 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.86 | 147.4 | AE1-153 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.59 | 147.21 | AE1-153 | PECO_P4_NOTTI85_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.53 | 147.19 | AE1-153 | PECO_P1-2_220-08_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.46 | 147.13 | AE1-153 | PECO_P4_COOPR125_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 142.92 | 147.02 | AE1-153 | AP_P1-2_PE-500-001_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 142.92 | 147.02 | AE1-153 | AP_P1-2_WP-500-DRT17_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 142.87 | 146.96 | AE1-153 | AP_P2-3_PE-500-018C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3464 | 168.17 | 162.16 | AC1-076 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.55 | 143.85 | AE1-153 | PECO_P4_PEACH025_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.37 | 143.71 | AE1-153 | PECO_P1-2_PBTIE1_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 911 | 148.8 | 142.93 | AE1-153 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 911 | 147.86 | 141.62 | AE1-153 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 911 | 147.86 | 141.62 | AE1-153 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 911 | 147.84 | 141.61 | AE1-153 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204502 | 27JACKSON | 204514 | 27TMI | 1 | 230 | 227 | 781 | 132.92 | 141.38 | AE1-153 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204502 | 27JACKSON | 204514 | 27TMI | 1 | 230 | 227 | 781 | 132.92 | 141.38 | AE1-153 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204502 | 27JACKSON | 204514 | 27TMI | 1 | 230 | 227 | 781 | 132.91 | 141.37 | AE1-153 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 140.91 | 140.52 | AE1-153 | PJM_500_BG_P4_5_CNSTN_15_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 903 | 135.48 | 139.38 | AE1-153 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 1031 | 130.7 | 138.95 | AE1-153 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 1031 | 130.21 | 137.88 | AE1-153 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 1031 | 130.21 | 137.87 | AE1-153 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 1031 | 130.2 | 137.86 | AE1-153 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 911 | 139.99 | 134.9 | AE1-153 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 138.78 | 132.86 | AE1-153 | PECO_P4_PEACH205_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 207923 | BRISREAC | 208132 | WHEM TR1 | 1 | 230 | 229 | 676 | 124.18 | 132.7 | AE1-153 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 207922 | BRIS | 207923 | BRISREAC | RX | 230 | 229 | 676 | 124.18 | 132.7 | AE1-153 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 207923 | BRISREAC | 208132 | WHEM TR1 | 1 | 230 | 229 | 676 | 124.18 | 132.7 | AE1-153 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 207922 | BRIS | 207923 | BRISREAC | RX | 230 | 229 | 676 | 124.18 | 132.7 | AE1-153 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 207923 | BRISREAC | 208132 | WHEM TR1 | 1 | 230 | 229 | 676 | 124.17 | 132.69 | AE1-153 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 207922 | BRIS | 207923 | BRISREAC | RX | 230 | 229 | 676 | 124.17 | 132.69 | AE1-153 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 138.67 | 132.53 | AE1-153 | PECO_P1-2_PBTIE2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208078 | SAKR | 1 | 230 | 229 | 903 | 124.36 | 132.28 | AE1-153 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208078 | SAKR | 1 | 230 | 229 | 903 | 124.36 | 132.28 | AE1-153 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208078 | SAKR | 1 | 230 | 229 | 903 | 124.36 | 132.27 | AE1-153 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 137.75 | 131.68 | AE1-153 | PECO_P4_PEACH055_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204502 | 27JACKSON | 204514 | 27TMI | 1 | 230 | 227 | 781 | 125.28 | 130.83 | AE1-153 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220972 | GRANITE1 | 1 | 230 | 232 | 829 | 134.72 | 130.76 | AE1-153 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220972 | GRANITE1 | 1 | 230 | 232 | 829 | 134.09 | 130.11 | AE1-153 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220972 | GRANITE1 | 1 | 230 | 232 | 829 | 134.09 | 130.11 | AE1-153 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 1031 | 124.61 | 129.08 | AE1-153 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220973 | GRANITE6 | 1 | 230 | 232 | 829 | 132.65 | 128.87 | AE1-153 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220973 | GRANITE6 | 1 | 230 | 232 | 829 | 132.06 | 128.26 | AE1-153 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220973 | GRANITE6 | 1 | 230 | 232 | 829 | 132.06 | 128.25 | AE1-153 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 133.02 | 127.21 | AE1-153 | PECO_P4_PEACH015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 127.89 | 126.12 | AE1-153 | DVP_P4-2: 514T595_SRT-SW |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208020 | MANO TR3 | 1 | 230 | 229 | 793 | 112.18 | 125.99 | AE1-153 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 131.72 | 125.92 | AE1-153 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220953 | HOWARD12 | 220972 | GRANITE1 | 1 | 230 | 232 | 772 | 129.46 | 125.48 | AE1-153 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220954 | HOWARD32 | 220973 | GRANITE6 | 1 | 230 | 232 | 772 | 128.32 | 124.79 | AE1-153 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220953 | HOWARD12 | 220972 | GRANITE1 | 1 | 230 | 232 | 772 | 128.55 | 124.51 | AE1-153 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220953 | HOWARD12 | 220972 | GRANITE1 | 1 | 230 | 232 | 772 | 128.54 | 124.51 | AE1-153 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208020 | MANO TR3 | 1 | 230 | 229 | 793 | 111.35 | 124.46 | AE1-153 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208020 | MANO TR3 | 1 | 230 | 229 | 793 | 111.35 | 124.46 | AE1-153 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208020 | MANO TR3 | 1 | 230 | 229 | 793 | 111.35 | 124.45 | AE1-153 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 793 | 126.18 | 124.38 | AE1-153 | DVP_P4-2: 514T595_SRT-SW |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 2 | 230 | 233 | 793 | 126.18 | 124.38 | AE1-153 | DVP_P4-2: 514T595_SRT-SW |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 126.12 | 124.38 | AE1-153 | DVP_P4-2: 51482_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 126.12 | 124.29 | AE1-153 | DVP_P1-2: LN 514_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 126.12 | 124.29 | AE1-153 | AP_P1-2_PE-500-407T_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220954 | HOWARD32 | 220973 | GRANITE6 | 1 | 230 | 232 | 772 | 127.53 | 123.95 | AE1-153 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220954 | HOWARD32 | 220973 | GRANITE6 | 1 | 230 | 232 | 772 | 127.53 | 123.95 | AE1-153 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 793 | 124.92 | 123.16 | AE1-153 | DVP_P4-2: 51482_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 2 | 230 | 233 | 793 | 124.92 | 123.16 | AE1-153 | DVP_P4-2: 51482_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 793 | 124.92 | 123.08 | AE1-153 | DVP_P1-2: LN 514_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 793 | 124.92 | 123.08 | AE1-153 | AP_P1-2_PE-500-407T_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 2 | 230 | 233 | 793 | 124.92 | 123.08 | AE1-153 | DVP_P1-2: LN 514_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 2 | 230 | 233 | 793 | 124.92 | 123.08 | AE1-153 | AP_P1-2_PE-500-407T_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208031 | MLWD TR2 | 1 | 230 | 229 | 911 | 112.38 | 122.35 | AE1-153 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208078 | SAKR | 1 | 230 | 229 | 903 | 117.09 | 122.3 | AE1-153 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200025 | W CHAPEL | 1 | 500 | 225 | 1732 | 123.51 | 121.72 | AE1-153 | PEPCO_P4_PP41_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208031 | MLWD TR2 | 1 | 230 | 229 | 911 | 111.66 | 121.03 | AE1-153 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208031 | MLWD TR2 | 1 | 230 | 229 | 911 | 111.66 | 121.03 | AE1-153 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208031 | MLWD TR2 | 1 | 230 | 229 | 911 | 111.66 | 121.03 | AE1-153 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220965 | NEAST339 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 119.65 | 119 | AE1-153 | BG_P1_2315_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 911 | 117.92 | 118.91 | AE1-153 | PJM_500_BG_P4_5_CNSTN_15_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220965 | NEAST339 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 119.23 | 118.79 | AE1-153 | BG_P4_5_NEAST_17_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220965 | NEAST339 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 119.39 | 118.79 | AE1-153 | BG_P4_5_NEAST_15_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 114.6 | 118.28 | AE1-153 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220979 | NEAST317 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 118.74 | 118.13 | AE1-153 | BG_P1_2337_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 114.26 | 117.94 | AE1-153 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 114.25 | 117.88 | AE1-153 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 114.25 | 117.88 | AE1-153 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220979 | NEAST317 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 118.41 | 117.87 | AE1-153 | BG_P4_5_NEAST_39_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220979 | NEAST317 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 118.41 | 117.87 | AE1-153 | BG_P4_5_NEAST_37_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 113.92 | 117.55 | AE1-153 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 113.92 | 117.55 | AE1-153 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208131 | WHEM | 208132 | WHEM TR1 | 1 | 230 | 229 | 691 | 108.46 | 117.54 | AE1-153 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 122.63 | 117.27 | AE1-153 | PECO_P4_PEACH225_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 793 | 118.32 | 115.55 | AE1-153 | PEPCO_P1_PP2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 2 | 230 | 233 | 793 | 118.32 | 115.55 | AE1-153 | PEPCO_P1_PP1_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 2 | 500/230 | 225/232 | 2168 | 109.57 | 114.86 | AE1-153 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 2 | 500/230 | 225/232 | 2168 | 109.39 | 114.65 | AE1-153 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 2 | 500/230 | 225/232 | 2168 | 109.39 | 114.65 | AE1-153 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 1 | 500/230 | 225/232 | 2168 | 109.34 | 114.62 | AE1-153 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 1 | 500/230 | 225/232 | 2168 | 109.16 | 114.41 | AE1-153 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 1 | 500/230 | 225/232 | 2168 | 109.16 | 114.4 | AE1-153 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 116.35 | 114.39 | AE1-153 | AP_P2-3_PE-500-019C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220964 | GRACETON | 220999 | BAGLEY2 | 13 | 230 | 232 | 1795 | 113.34 | 114.38 | AE1-153 | BG_P4_5_GRCTN_3T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208020 | MANO TR3 | 1 | 230 | 229 | 793 | 104.17 | 113.94 | AE1-153 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208020 | MANO TR3 | 208031 | MLWD TR2 | 1 | 230 | 229 | 903 | 102.48 | 113.59 | AE1-153 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208020 | MANO TR3 | 208031 | MLWD TR2 | 1 | 230 | 229 | 903 | 101.78 | 112.4 | AE1-153 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208020 | MANO TR3 | 208031 | MLWD TR2 | 1 | 230 | 229 | 903 | 101.78 | 112.4 | AE1-153 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208020 | MANO TR3 | 208031 | MLWD TR2 | 1 | 230 | 229 | 903 | 101.78 | 112.4 | AE1-153 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 2 | 500/230 | 225/232 | 2168 | 108.44 | 111.73 | AE1-153 | PJM_500_BG_P4_5_CNSTN_15_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208031 | MLWD TR2 | 1 | 230 | 229 | 911 | 104.91 | 111.54 | AE1-153 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 106.39 | 111.15 | AE1-153 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220980 | RAPHAEL | 220999 | BAGLEY2 | 13 | 230 | 232 | 1795 | 108.93 | 111.13 | AE1-153 | BG_P4_5_GRCTN_3T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 106.27 | 111.01 | AE1-153 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 793 | 112.42 | 109.76 | AE1-153 | PEPCO_P4_PP19_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 2 | 230 | 233 | 793 | 109.17 | 107.24 | AE1-153 | AP_P2-3_PE-500-019C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 793 | 109.17 | 107.24 | AE1-153 | AP_P2-3_PE-500-019C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220965 | NEAST339 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 108.21 | 106.78 | AE1-153 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220965 | NEAST339 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 108.11 | 106.67 | AE1-153 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220965 | NEAST339 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 108.11 | 106.67 | AE1-153 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 101.51 | 105.67 | AE1-153 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 101.43 | 105.58 | AE1-153 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220979 | NEAST317 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 105.11 | 103.74 | AE1-153 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220979 | NEAST317 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 105.01 | 103.62 | AE1-153 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220979 | NEAST317 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 105.01 | 103.62 | AE1-153 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 99.4 | 103.26 | AE1-153 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 99.4 | 103.26 | AE1-153 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 99.4 | 103.25 | AE1-153 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208020 | MANO TR3 | 208031 | MLWD TR2 | 1 | 230 | 229 | 903 | 95.41 | 103.17 | AE1-153 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220964 | GRACETON | 220999 | BAGLEY2 | 13 | 230 | 232 | 1795 | 101.41 | 102.15 | AE1-153 | BG_P1_2305_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220964 | GRACETON | 221000 | BAGLEY | 5 | 230 | 232 | 1795 | 101.41 | 102.15 | AE1-153 | BG_P1_2313_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220965 | NEAST339 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 102.65 | 101.96 | AE1-153 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 98.48 | 101.93 | AE1-153 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220965 | NEAST339 | 220977 | RIV2339 | 1 | 230 | 232 | 991 | 103.28 | 101.84 | AE1-153 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220965 | NEAST339 | 220977 | RIV2339 | 1 | 230 | 232 | 991 | 103.24 | 101.78 | AE1-153 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220965 | NEAST339 | 220977 | RIV2339 | 1 | 230 | 232 | 991 | 103.24 | 101.78 | AE1-153 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 2 | 500/230 | 225/232 | 2168 | 98.96 | 101.7 | AE1-153 | PJM_500_BG_P2_CNSTN_230-N_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 2 | 500/230 | 225/232 | 2168 | 98.96 | 101.7 | AE1-153 | BG_P1_CNSTN_500-2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 1 | 500/230 | 225/232 | 2168 | 98.85 | 101.59 | AE1-153 | PJM_500_BG_P2_CNSTN_230-S_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 1 | 500/230 | 225/232 | 2168 | 98.85 | 101.59 | AE1-153 | BG_P1_CNSTN_500-4_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 223960 | BRG 1T 230 | 1 | 500/230 | 225/233 | 1498 | 100.25 | 100.63 | AE1-153 | PEPCO_P4_PP41_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 98.57 | 100.58 | AE1-153 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 225.5 | 236.82 | AE1-155 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 223.5 | 236.82 | AE1-155 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 225.44 | 236.76 | AE1-155 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 225.43 | 236.76 | AE1-155 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 223.43 | 236.76 | AE1-155 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 223.43 | 236.76 | AE1-155 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 213.45 | 226.67 | AE1-155 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 213.39 | 226.61 | AE1-155 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 213.39 | 226.61 | AE1-155 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 209.19 | 223.46 | AE1-155 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 209.13 | 223.4 | AE1-155 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 209.13 | 223.4 | AE1-155 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 210.6 | 217.67 | AE1-155 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 208.6 | 217.67 | AE1-155 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 199.06 | 208.11 | AE1-155 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 194.8 | 204.76 | AE1-155 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 172.68 | 167.7 | AE1-155 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 171.71 | 166.26 | AE1-155 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 171.71 | 166.26 | AE1-155 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 171.69 | 166.25 | AE1-155 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 163.54 | 164.8 | AE1-155 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3464 | 167.94 | 161.93 | AC1-078 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 161.68 | 161.73 | AE1-155 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 161.68 | 161.72 | AE1-155 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 161.67 | 161.72 | AE1-155 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 163.76 | 158.79 | AE1-155 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 153.45 | 157.89 | AE1-155 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 161.96 | 157.08 | AE1-155 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 161.96 | 157.08 | AE1-155 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 151.77 | 156.57 | AE1-155 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 161.43 | 154.21 | AE1-155 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 148.4 | 152.91 | AE1-155 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 903 | 144.19 | 152.01 | AE1-155 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 152.74 | 151.1 | AE1-155 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 155.53 | 150.39 | AE1-155 | PN_P1-2_PN-500-010T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 903 | 142.66 | 149.4 | AE1-155 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 903 | 142.66 | 149.4 | AE1-155 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 903 | 142.64 | 149.39 | AE1-155 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.25 | 149.31 | AE1-155 | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.18 | 149.24 | AE1-155 | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.86 | 148.05 | AE1-155 | AP_P2-3_PE-500-016_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.93 | 148.02 | AE1-155 | AP_P2-3_PE-500-015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.85 | 147.72 | AE1-155 | PJM_500_BG_P4_5_CNSTN_L_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.14 | 147.71 | AE1-155 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.94 | 147.52 | AE1-155 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.97 | 147.51 | AE1-155 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.69 | 147.31 | AE1-155 | PECO_P4_NOTTI85_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.63 | 147.3 | AE1-155 | PECO_P1-2_220-08_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.57 | 147.23 | AE1-155 | PECO_P4_COOPR125_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.04 | 147.17 | AE1-155 | AP_P1-2_WP-500-DRT17_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.04 | 147.17 | AE1-155 | AP_P1-2_PE-500-001_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 142.99 | 147.11 | AE1-155 | AP_P2-3_PE-500-018C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3464 | 168.05 | 162.04 | AC1-083 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.66 | 143.96 | AE1-155 | PECO_P4_PEACH025_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.5 | 143.84 | AE1-155 | PECO_P1-2_PBTIE1_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 911 | 148.92 | 143.05 | AE1-155 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204502 | 27JACKSON | 204514 | 27TMI | 1 | 230 | 227 | 781 | 133.01 | 141.52 | AE1-155 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204502 | 27JACKSON | 204514 | 27TMI | 1 | 230 | 227 | 781 | 133.01 | 141.52 | AE1-155 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204502 | 27JACKSON | 204514 | 27TMI | 1 | 230 | 227 | 781 | 133 | 141.51 | AE1-155 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 903 | 135.58 | 139.54 | AE1-155 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 1031 | 130.29 | 138.01 | AE1-155 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 1031 | 130.29 | 138.01 | AE1-155 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 1031 | 130.28 | 138 | AE1-155 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 138.9 | 132.97 | AE1-155 | PECO_P4_PEACH205_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 138.78 | 132.64 | AE1-155 | PECO_P1-2_PBTIE2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208078 | SAKR | 1 | 230 | 229 | 903 | 124.46 | 132.43 | AE1-155 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208078 | SAKR | 1 | 230 | 229 | 903 | 124.46 | 132.43 | AE1-155 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208078 | SAKR | 1 | 230 | 229 | 903 | 124.45 | 132.43 | AE1-155 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 137.86 | 131.78 | AE1-155 | PECO_P4_PEACH055_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 1031 | 124.69 | 129.21 | AE1-155 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 133.14 | 127.33 | AE1-155 | PECO_P4_PEACH015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 128.3 | 126.59 | AE1-155 | DVP_P4-2: 514T595_SRT-SW |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 131.84 | 126.03 | AE1-155 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 126.54 | 124.8 | AE1-155 | DVP_P4-2: 51482_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 793 | 126.49 | 124.73 | AE1-155 | DVP_P4-2: 514T595_SRT-SW |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 2 | 230 | 233 | 793 | 126.49 | 124.73 | AE1-155 | DVP_P4-2: 514T595_SRT-SW |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 126.54 | 124.71 | AE1-155 | AP_P1-2_PE-500-407T_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 126.54 | 124.71 | AE1-155 | DVP_P1-2: LN 514_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208020 | MANO TR3 | 1 | 230 | 229 | 793 | 111.45 | 124.6 | AE1-155 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208020 | MANO TR3 | 1 | 230 | 229 | 793 | 111.45 | 124.6 | AE1-155 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208020 | MANO TR3 | 1 | 230 | 229 | 793 | 111.45 | 124.6 | AE1-155 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 2 | 230 | 233 | 793 | 125.23 | 123.48 | AE1-155 | DVP_P4-2: 51482_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 793 | 125.23 | 123.48 | AE1-155 | DVP_P4-2: 51482_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 2 | 230 | 233 | 793 | 125.23 | 123.4 | AE1-155 | DVP_P1-2: LN 514_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 2 | 230 | 233 | 793 | 125.23 | 123.4 | AE1-155 | AP_P1-2_PE-500-407T_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 793 | 125.23 | 123.4 | AE1-155 | DVP_P1-2: LN 514_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 793 | 125.23 | 123.4 | AE1-155 | AP_P1-2_PE-500-407T_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208078 | SAKR | 1 | 230 | 229 | 903 | 117.19 | 122.44 | AE1-155 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200025 | W CHAPEL | 1 | 500 | 225 | 1732 | 123.58 | 121.8 | AE1-155 | PEPCO_P4_PP41_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208031 | MLWD TR2 | 1 | 230 | 229 | 911 | 111.75 | 121.17 | AE1-155 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208031 | MLWD TR2 | 1 | 230 | 229 | 911 | 111.75 | 121.17 | AE1-155 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208031 | MLWD TR2 | 1 | 230 | 229 | 911 | 111.75 | 121.17 | AE1-155 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 114.68 | 118.37 | AE1-155 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 114.34 | 118.03 | AE1-155 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 114.33 | 117.97 | AE1-155 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 114.33 | 117.97 | AE1-155 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 113.99 | 117.64 | AE1-155 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 113.99 | 117.64 | AE1-155 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 122.74 | 117.38 | AE1-155 | PECO_P4_PEACH225_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 2 | 230 | 233 | 793 | 118.56 | 115.78 | AE1-155 | PEPCO_P1_PP1_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 793 | 118.56 | 115.78 | AE1-155 | PEPCO_P1_PP2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 2 | 500/230 | 225/232 | 2168 | 109.63 | 114.94 | AE1-155 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 116.76 | 114.8 | AE1-155 | AP_P2-3_PE-500-019C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 2 | 500/230 | 225/232 | 2168 | 109.45 | 114.72 | AE1-155 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 2 | 500/230 | 225/232 | 2168 | 109.45 | 114.72 | AE1-155 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 1 | 500/230 | 225/232 | 2168 | 109.4 | 114.7 | AE1-155 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 1 | 500/230 | 225/232 | 2168 | 109.22 | 114.48 | AE1-155 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 1 | 500/230 | 225/232 | 2168 | 109.22 | 114.48 | AE1-155 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220964 | GRACETON | 220999 | BAGLEY2 | 13 | 230 | 232 | 1795 | 113.4 | 114.44 | AE1-155 | BG_P4_5_GRCTN_3T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208020 | MANO TR3 | 1 | 230 | 229 | 793 | 104.27 | 114.03 | AE1-155 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208020 | MANO TR3 | 208031 | MLWD TR2 | 1 | 230 | 229 | 903 | 101.86 | 112.53 | AE1-155 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 2 | 500/230 | 225/232 | 2168 | 108.49 | 111.79 | AE1-155 | PJM_500_BG_P4_5_CNSTN_15_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208031 | MLWD TR2 | 1 | 230 | 229 | 911 | 105 | 111.68 | AE1-155 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220980 | RAPHAEL | 220999 | BAGLEY2 | 13 | 230 | 232 | 1795 | 108.99 | 111.2 | AE1-155 | BG_P4_5_GRCTN_3T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 793 | 112.71 | 110.04 | AE1-155 | PEPCO_P4_PP19_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 793 | 109.46 | 107.53 | AE1-155 | AP_P2-3_PE-500-019C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 2 | 230 | 233 | 793 | 109.46 | 107.53 | AE1-155 | AP_P2-3_PE-500-019C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 99.47 | 103.36 | AE1-155 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 99.47 | 103.36 | AE1-155 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 99.47 | 103.36 | AE1-155 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208020 | MANO TR3 | 208031 | MLWD TR2 | 1 | 230 | 229 | 903 | 95.49 | 103.3 | AE1-155 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 98.54 | 102.03 | AE1-155 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 98.64 | 100.67 | AE1-155 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 144.58 | 139.43 | AE1-156 | PL_10_P42_100570_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 144.58 | 139.43 | AE1-156 | PL_10_P42_100570_A_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 143.77 | 138.63 | AE1-156 | PL_10_P12_000085_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 143.67 | 138.54 | AE1-156 | PN_P2-3_PN-500-004-DRT-008_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 143.67 | 138.54 | AE1-156 | PN_P2-3_PN-500-DRT31_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 143.3 | 138.18 | AE1-156 | PL_30_P42_000131_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 138.66 | 133.72 | AE1-156 | PL_10_P42_100572_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 225.52 | 236.86 | AE1-157 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 223.52 | 236.85 | AE1-157 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 225.46 | 236.8 | AE1-157 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 225.46 | 236.79 | AE1-157 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 223.45 | 236.79 | AE1-157 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 223.45 | 236.79 | AE1-157 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 213.47 | 226.7 | AE1-157 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 213.41 | 226.64 | AE1-157 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 213.41 | 226.64 | AE1-157 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 209.21 | 223.49 | AE1-157 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 209.15 | 223.43 | AE1-157 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 209.15 | 223.43 | AE1-157 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 210.62 | 217.7 | AE1-157 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 208.62 | 217.7 | AE1-157 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 199.08 | 208.14 | AE1-157 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 194.82 | 204.79 | AE1-157 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 172.69 | 167.71 | AE1-157 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 171.72 | 166.27 | AE1-157 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 171.72 | 166.27 | AE1-157 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 171.7 | 166.26 | AE1-157 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 163.56 | 164.83 | AE1-157 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3464 | 167.38 | 161.38 | AC1-085 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 161.7 | 161.74 | AE1-157 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 161.7 | 161.74 | AE1-157 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 161.68 | 161.74 | AE1-157 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 163.77 | 158.8 | AE1-157 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 153.46 | 157.9 | AE1-157 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 161.97 | 157.09 | AE1-157 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 161.97 | 157.09 | AE1-157 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 151.78 | 156.58 | AE1-157 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 161.45 | 154.23 | AE1-157 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 148.41 | 152.93 | AE1-157 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 903 | 144.19 | 152.05 | AE1-157 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 152.75 | 151.12 | AE1-157 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 155.55 | 150.4 | AE1-157 | PN_P1-2_PN-500-010T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 903 | 142.67 | 149.42 | AE1-157 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 903 | 142.67 | 149.42 | AE1-157 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 903 | 142.65 | 149.41 | AE1-157 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.26 | 149.32 | AE1-157 | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.19 | 149.25 | AE1-157 | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.87 | 148.06 | AE1-157 | AP_P2-3_PE-500-016_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.94 | 148.03 | AE1-157 | AP_P2-3_PE-500-015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.86 | 147.73 | AE1-157 | PJM_500_BG_P4_5_CNSTN_L_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.16 | 147.72 | AE1-157 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.95 | 147.54 | AE1-157 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.98 | 147.52 | AE1-157 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.71 | 147.33 | AE1-157 | PECO_P4_NOTTI85_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.65 | 147.31 | AE1-157 | PECO_P1-2_220-08_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.58 | 147.25 | AE1-157 | PECO_P4_COOPR125_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.05 | 147.18 | AE1-157 | AP_P1-2_WP-500-DRT17_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.05 | 147.18 | AE1-157 | AP_P1-2_PE-500-001_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143 | 147.12 | AE1-157 | AP_P2-3_PE-500-018C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3464 | 167.74 | 161.74 | AC1-086 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.68 | 143.98 | AE1-157 | PECO_P4_PEACH025_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.51 | 143.85 | AE1-157 | PECO_P1-2_PBTIE1_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 911 | 148.93 | 143.06 | AE1-157 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204502 | 27JACKSON | 204514 | 27TMI | 1 | 230 | 227 | 781 | 133.02 | 141.54 | AE1-157 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204502 | 27JACKSON | 204514 | 27TMI | 1 | 230 | 227 | 781 | 133.02 | 141.54 | AE1-157 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204502 | 27JACKSON | 204514 | 27TMI | 1 | 230 | 227 | 781 | 133.01 | 141.53 | AE1-157 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 903 | 135.59 | 139.55 | AE1-157 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 1031 | 130.3 | 138.03 | AE1-157 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 1031 | 130.3 | 138.03 | AE1-157 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 1031 | 130.29 | 138.02 | AE1-157 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 138.91 | 132.98 | AE1-157 | PECO_P4_PEACH205_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 138.8 | 132.66 | AE1-157 | PECO_P1-2_PBTIE2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208078 | SAKR | 1 | 230 | 229 | 903 | 124.47 | 132.45 | AE1-157 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208078 | SAKR | 1 | 230 | 229 | 903 | 124.47 | 132.45 | AE1-157 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208078 | SAKR | 1 | 230 | 229 | 903 | 124.47 | 132.45 | AE1-157 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 137.87 | 131.8 | AE1-157 | PECO_P4_PEACH055_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 1031 | 124.7 | 129.22 | AE1-157 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 133.16 | 127.35 | AE1-157 | PECO_P4_PEACH015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 128.29 | 126.58 | AE1-157 | DVP_P4-2: 514T595_SRT-SW |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 131.85 | 126.04 | AE1-157 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 126.53 | 124.79 | AE1-157 | DVP_P4-2: 51482_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 2 | 230 | 233 | 793 | 126.47 | 124.72 | AE1-157 | DVP_P4-2: 514T595_SRT-SW |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 793 | 126.47 | 124.72 | AE1-157 | DVP_P4-2: 514T595_SRT-SW |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 126.53 | 124.71 | AE1-157 | DVP_P1-2: LN 514_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 126.53 | 124.71 | AE1-157 | AP_P1-2_PE-500-407T_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208020 | MANO TR3 | 1 | 230 | 229 | 793 | 111.46 | 124.62 | AE1-157 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208020 | MANO TR3 | 1 | 230 | 229 | 793 | 111.46 | 124.62 | AE1-157 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208020 | MANO TR3 | 1 | 230 | 229 | 793 | 111.46 | 124.62 | AE1-157 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 793 | 125.21 | 123.46 | AE1-157 | DVP_P4-2: 51482_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 2 | 230 | 233 | 793 | 125.21 | 123.46 | AE1-157 | DVP_P4-2: 51482_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 793 | 125.21 | 123.38 | AE1-157 | DVP_P1-2: LN 514_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 2 | 230 | 233 | 793 | 125.21 | 123.38 | AE1-157 | DVP_P1-2: LN 514_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 793 | 125.21 | 123.38 | AE1-157 | AP_P1-2_PE-500-407T_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 2 | 230 | 233 | 793 | 125.21 | 123.38 | AE1-157 | AP_P1-2_PE-500-407T_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208078 | SAKR | 1 | 230 | 229 | 903 | 117.2 | 122.46 | AE1-157 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200025 | W CHAPEL | 1 | 500 | 225 | 1732 | 123.58 | 121.8 | AE1-157 | PEPCO_P4_PP41_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208031 | MLWD TR2 | 1 | 230 | 229 | 911 | 111.77 | 121.19 | AE1-157 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208031 | MLWD TR2 | 1 | 230 | 229 | 911 | 111.76 | 121.19 | AE1-157 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208031 | MLWD TR2 | 1 | 230 | 229 | 911 | 111.76 | 121.19 | AE1-157 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 114.68 | 118.38 | AE1-157 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 114.35 | 118.04 | AE1-157 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 114.33 | 117.98 | AE1-157 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 114.33 | 117.98 | AE1-157 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 114 | 117.65 | AE1-157 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 114 | 117.65 | AE1-157 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 122.76 | 117.39 | AE1-157 | PECO_P4_PEACH225_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 793 | 118.54 | 115.77 | AE1-157 | PEPCO_P1_PP2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 2 | 230 | 233 | 793 | 118.54 | 115.77 | AE1-157 | PEPCO_P1_PP1_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 2 | 500/230 | 225/232 | 2168 | 109.64 | 114.94 | AE1-157 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 116.75 | 114.8 | AE1-157 | AP_P2-3_PE-500-019C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 2 | 500/230 | 225/232 | 2168 | 109.46 | 114.73 | AE1-157 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 2 | 500/230 | 225/232 | 2168 | 109.46 | 114.73 | AE1-157 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 1 | 500/230 | 225/232 | 2168 | 109.4 | 114.7 | AE1-157 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 1 | 500/230 | 225/232 | 2168 | 109.23 | 114.49 | AE1-157 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 1 | 500/230 | 225/232 | 2168 | 109.23 | 114.49 | AE1-157 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220964 | GRACETON | 220999 | BAGLEY2 | 13 | 230 | 232 | 1795 | 113.41 | 114.45 | AE1-157 | BG_P4_5_GRCTN_3T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208020 | MANO TR3 | 1 | 230 | 229 | 793 | 104.28 | 114.05 | AE1-157 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 2 | 500/230 | 225/232 | 2168 | 108.49 | 111.79 | AE1-157 | PJM_500_BG_P4_5_CNSTN_15_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208031 | MLWD TR2 | 1 | 230 | 229 | 911 | 105.01 | 111.69 | AE1-157 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220980 | RAPHAEL | 220999 | BAGLEY2 | 13 | 230 | 232 | 1795 | 109 | 111.2 | AE1-157 | BG_P4_5_GRCTN_3T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 793 | 112.7 | 110.03 | AE1-157 | PEPCO_P4_PP19_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 2 | 230 | 233 | 793 | 109.44 | 107.52 | AE1-157 | AP_P2-3_PE-500-019C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 793 | 109.44 | 107.52 | AE1-157 | AP_P2-3_PE-500-019C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 99.47 | 103.36 | AE1-157 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 99.47 | 103.36 | AE1-157 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 99.47 | 103.36 | AE1-157 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208020 | MANO TR3 | 208031 | MLWD TR2 | 1 | 230 | 229 | 903 | 95.5 | 103.31 | AE1-157 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 98.54 | 102.04 | AE1-157 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 98.64 | 100.68 | AE1-157 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200504 | 26CARLISLE | 200520 | 26ROXBURY | 1 | 115 | 226 | 190 | 91.54 | 106.66 | AE1-188 | PN_P2-3_PN-115-0331-B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 172.89 | 167.92 | AE1-191 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3464 | 168.05 | 162.04 | AC1-089 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 153.65 | 158.12 | AE1-191 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.15 | 157.27 | AE1-191 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.15 | 157.27 | AE1-191 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 151.96 | 156.8 | AE1-191 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 161.65 | 154.42 | AE1-191 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 148.6 | 153.15 | AE1-191 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 155.72 | 150.57 | AE1-191 | PN_P1-2_PN-500-010T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.44 | 149.53 | AE1-191 | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.37 | 149.46 | AE1-191 | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.06 | 148.28 | AE1-191 | AP_P2-3_PE-500-016_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.12 | 148.25 | AE1-191 | AP_P2-3_PE-500-015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.04 | 147.9 | AE1-191 | PJM_500_BG_P4_5_CNSTN_L_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.33 | 147.89 | AE1-191 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.13 | 147.71 | AE1-191 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.15 | 147.69 | AE1-191 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.88 | 147.5 | AE1-191 | PECO_P4_NOTTI85_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.82 | 147.48 | AE1-191 | PECO_P1-2_220-08_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.76 | 147.42 | AE1-191 | PECO_P4_COOPR125_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.24 | 147.4 | AE1-191 | AP_P1-2_PE-500-001_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.24 | 147.4 | AE1-191 | AP_P1-2_WP-500-DRT17_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.19 | 147.33 | AE1-191 | AP_P2-3_PE-500-018C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3464 | 168.64 | 162.62 | AC1-091 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.87 | 144.16 | AE1-191 | PECO_P4_PEACH025_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.72 | 144.05 | AE1-191 | PECO_P1-2_PBTIE1_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 911 | 149.12 | 143.24 | AE1-191 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 139.1 | 133.16 | AE1-191 | PECO_P4_PEACH205_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 138.99 | 132.84 | AE1-191 | PECO_P1-2_PBTIE2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 138.06 | 131.97 | AE1-191 | PECO_P4_PEACH055_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 133.37 | 127.55 | AE1-191 | PECO_P4_PEACH015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 128.69 | 127 | AE1-191 | DVP_P4-2: 514T595_SRT-SW |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 132.04 | 126.22 | AE1-191 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 126.94 | 125.22 | AE1-191 | DVP_P4-2: 51482_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 126.94 | 125.13 | AE1-191 | DVP_P1-2: LN 514_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 126.94 | 125.13 | AE1-191 | AP_P1-2_PE-500-407T_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200025 | W CHAPEL | 1 | 500 | 225 | 1732 | 123.77 | 121.99 | AE1-191 | PEPCO_P4_PP41_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 122.95 | 117.57 | AE1-191 | PECO_P4_PEACH225_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 117.14 | 115.22 | AE1-191 | AP_P2-3_PE-500-019C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 98.65 | 102.2 | AE1-191 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3464 | 168.64 | 162.62 | AC1-092 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 153.77 | 158.27 | AE1-212 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.25 | 157.37 | AE1-212 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.24 | 157.37 | AE1-212 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 152.08 | 156.95 | AE1-212 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 161.73 | 154.5 | AE1-212 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 148.72 | 153.3 | AE1-212 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 155.82 | 150.67 | AE1-212 | PN_P1-2_PN-500-010T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.56 | 149.67 | AE1-212 | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.49 | 149.6 | AE1-212 | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.19 | 148.46 | AE1-212 | AP_P2-3_PE-500-016_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.25 | 148.43 | AE1-212 | AP_P2-3_PE-500-015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.13 | 148 | AE1-212 | PJM_500_BG_P4_5_CNSTN_L_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.4 | 147.96 | AE1-212 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.2 | 147.78 | AE1-212 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.22 | 147.76 | AE1-212 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.37 | 147.58 | AE1-212 | AP_P1-2_PE-500-001_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.37 | 147.58 | AE1-212 | AP_P1-2_WP-500-DRT17_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.95 | 147.57 | AE1-212 | PECO_P4_NOTTI85_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.89 | 147.55 | AE1-212 | PECO_P1-2_220-08_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.32 | 147.51 | AE1-212 | AP_P2-3_PE-500-018C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.83 | 147.49 | AE1-212 | PECO_P4_COOPR125_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3464 | 168.63 | 162.61 | AC1-093 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.94 | 144.22 | AE1-212 | PECO_P4_PEACH025_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.81 | 144.14 | AE1-212 | PECO_P1-2_PBTIE1_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 139.19 | 133.25 | AE1-212 | PECO_P4_PEACH205_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 139.08 | 132.92 | AE1-212 | PECO_P1-2_PBTIE2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 138.13 | 132.04 | AE1-212 | PECO_P4_PEACH055_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 133.46 | 127.64 | AE1-212 | PECO_P4_PEACH015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 132.13 | 126.3 | AE1-212 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 123.03 | 117.66 | AE1-212 | PECO_P4_PEACH225_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208394 | PPL-BGE TIE | 221092 | FIVE.FOR | 1 | 115 | 229/232 | 247 | 124.63 | 127.88 | AE1-226 | PL_05_P71_000906_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208393 | FARO DC TIE | 208395 | FARO FF | 1 | 115/69 | 229 | 120 | 130.86 | 127.22 | AE1-226 | PL_05_P71_000906_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208393 | FARO DC TIE | 208395 | FARO FF | 2 | 115/69 | 229 | 120 | 130.86 | 127.22 | AE1-226 | PL_05_P71_000906_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208394 | PPL-BGE TIE | 221092 | FIVE.FOR | 1 | 115 | 229/232 | 247 | 121.06 | 122.93 | AE1-226 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208394 | PPL-BGE TIE | 221092 | FIVE.FOR | 1 | 115 | 229/232 | 247 | 120.99 | 122.84 | AE1-226 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208394 | PPL-BGE TIE | 221092 | FIVE.FOR | 1 | 115 | 229/232 | 247 | 120.99 | 122.84 | AE1-226 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208394 | PPL-BGE TIE | 221092 | FIVE.FOR | 1 | 115 | 229/232 | 247 | 120.99 | 122.83 | AE1-226 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208393 | FARO DC TIE | 208395 | FARO FF | 1 | 115/69 | 229 | 120 | 127.18 | 121.92 | AE1-226 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208393 | FARO DC TIE | 208395 | FARO FF | 2 | 115/69 | 229 | 120 | 127.19 | 121.91 | AE1-226 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208393 | FARO DC TIE | 208395 | FARO FF | 1 | 115/69 | 229 | 120 | 127.11 | 121.88 | AE1-226 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208393 | FARO DC TIE | 208395 | FARO FF | 1 | 115/69 | 229 | 120 | 127.11 | 121.88 | AE1-226 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208393 | FARO DC TIE | 208395 | FARO FF | 2 | 115/69 | 229 | 120 | 127.12 | 121.88 | AE1-226 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208393 | FARO DC TIE | 208395 | FARO FF | 2 | 115/69 | 229 | 120 | 127.12 | 121.88 | AE1-226 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208393 | FARO DC TIE | 208395 | FARO FF | 1 | 115/69 | 229 | 120 | 127.11 | 121.87 | AE1-226 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208393 | FARO DC TIE | 208395 | FARO FF | 2 | 115/69 | 229 | 120 | 127.11 | 121.87 | AE1-226 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208394 | PPL-BGE TIE | 221092 | FIVE.FOR | 1 | 115 | 229/232 | 247 | 115.23 | 121.32 | AE1-226 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208393 | FARO DC TIE | 208395 | FARO FF | 1 | 115/69 | 229 | 120 | 121.19 | 119.39 | AE1-226 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208393 | FARO DC TIE | 208395 | FARO FF | 2 | 115/69 | 229 | 120 | 121.19 | 119.38 | AE1-226 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208395 | FARO FF | 208396 | FARO | 1 | 69 | 229 | 270 | 116.34 | 119.07 | AE1-226 | PL_05_P71_000906_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208394 | PPL-BGE TIE | 221092 | FIVE.FOR | 1 | 115 | 229/232 | 247 | 116.57 | 118.54 | AE1-226 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208393 | FARO DC TIE | 208395 | FARO FF | 1 | 115/69 | 229 | 120 | 122.56 | 118.01 | AE1-226 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208393 | FARO DC TIE | 208395 | FARO FF | 2 | 115/69 | 229 | 120 | 122.56 | 118.01 | AE1-226 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208394 | PPL-BGE TIE | 221092 | FIVE.FOR | 1 | 115 | 229/232 | 247 | 111.09 | 116.62 | AE1-226 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208393 | FARO DC TIE | 208395 | FARO FF | 1 | 115/69 | 229 | 120 | 117.46 | 115.92 | AE1-226 | BG_P4_5_GRCTN_2T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208393 | FARO DC TIE | 208395 | FARO FF | 2 | 115/69 | 229 | 120 | 117.46 | 115.92 | AE1-226 | BG_P4_5_GRCTN_2T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3464 | 168.22 | 162.21 | AC1-098 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208394 | PPL-BGE TIE | 221092 | FIVE.FOR | 1 | 115 | 229/232 | 247 | 111.61 | 115.68 | AE1-226 | BG_P4_5_GRCTN_2T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208393 | FARO DC TIE | 208395 | FARO FF | 1 | 115/69 | 229 | 120 | 116.92 | 115.53 | AE1-226 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208393 | FARO DC TIE | 208395 | FARO FF | 2 | 115/69 | 229 | 120 | 116.93 | 115.53 | AE1-226 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208394 | PPL-BGE TIE | 221092 | FIVE.FOR | 1 | 115 | 229/232 | 247 | 108.29 | 115.05 | AE1-226 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208393 | FARO DC TIE | 208395 | FARO FF | 1 | 115/69 | 229 | 120 | 114.04 | 114.66 | AE1-226 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208393 | FARO DC TIE | 208395 | FARO FF | 2 | 115/69 | 229 | 120 | 114.04 | 114.66 | AE1-226 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208395 | FARO FF | 208396 | FARO | 1 | 69 | 229 | 270 | 113.08 | 114.45 | AE1-226 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208395 | FARO FF | 208396 | FARO | 1 | 69 | 229 | 270 | 113.01 | 114.36 | AE1-226 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208395 | FARO FF | 208396 | FARO | 1 | 69 | 229 | 270 | 113.01 | 114.35 | AE1-226 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208395 | FARO FF | 208396 | FARO | 1 | 69 | 229 | 270 | 113.01 | 114.35 | AE1-226 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208395 | FARO FF | 208396 | FARO | 1 | 69 | 229 | 270 | 107.74 | 112.92 | AE1-226 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208395 | FARO FF | 208396 | FARO | 1 | 69 | 229 | 270 | 108.96 | 110.36 | AE1-226 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3464 | 168.26 | 162.25 | AC1-105 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208395 | FARO FF | 208396 | FARO | 1 | 69 | 229 | 270 | 103.95 | 108.56 | AE1-226 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208395 | FARO FF | 208396 | FARO | 1 | 69 | 229 | 270 | 104.43 | 107.69 | AE1-226 | BG_P4_5_GRCTN_2T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208395 | FARO FF | 208396 | FARO | 1 | 69 | 229 | 270 | 101.39 | 107.09 | AE1-226 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208393 | FARO DC TIE | 208394 | PPL-BGE TIE | 1 | 115 | 229 | 302 | 103.72 | 104.62 | AE1-226 | PL_05_P71_000906_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3464 | 168.19 | 162.17 | AC1-120 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 104.28 | 102.81 | AE1-226 | PL_04_P13_001758_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 104.24 | 102.81 | AE1-226 | PL_05_P12_101717_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 104.27 | 102.81 | AE1-226 | PL_04_P43_102445_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 104.14 | 102.81 | AE1-226 | BG_P1_110901_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 103.25 | 101.66 | AE1-226 | PL_04_P42_000570_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 102.65 | 101.21 | AE1-226 | PL_04_P42_102534_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208393 | FARO DC TIE | 208394 | PPL-BGE TIE | 1 | 115 | 229 | 302 | 100.8 | 100.56 | AE1-226 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208393 | FARO DC TIE | 208394 | PPL-BGE TIE | 1 | 115 | 229 | 302 | 100.74 | 100.49 | AE1-226 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208393 | FARO DC TIE | 208394 | PPL-BGE TIE | 1 | 115 | 229 | 302 | 100.74 | 100.49 | AE1-226 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208393 | FARO DC TIE | 208394 | PPL-BGE TIE | 1 | 115 | 229 | 302 | 100.74 | 100.49 | AE1-226 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 101.11 | 100.04 | AE1-226 | BG_P4_5_FFORKS_512_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 101.08 | 100.03 | AE1-226 | BG_P4_5_FFORKS_511_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 101.3 | 100.03 | AE1-226 | BG_P1_110510_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 229.09 | 241.87 | AE1-229 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 227.03 | 241.87 | AE1-229 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 226.12 | 239.81 | AE1-229 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 228.18 | 239.81 | AE1-229 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 228.11 | 239.76 | AE1-229 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 226.05 | 239.76 | AE1-229 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 228.11 | 239.76 | AE1-229 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 226.05 | 239.76 | AE1-229 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 216.86 | 231.57 | AE1-229 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 215.98 | 229.56 | AE1-229 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 215.92 | 229.51 | AE1-229 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 215.92 | 229.51 | AE1-229 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 212.6 | 228.4 | AE1-229 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 211.72 | 226.37 | AE1-229 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 211.65 | 226.32 | AE1-229 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 211.65 | 226.32 | AE1-229 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 213.28 | 221.17 | AE1-229 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 211.22 | 221.17 | AE1-229 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 201.59 | 211.5 | AE1-229 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 197.33 | 208.17 | AE1-229 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 174.05 | 169.34 | AE1-229 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 173.12 | 167.93 | AE1-229 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 173.12 | 167.93 | AE1-229 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 173.1 | 167.92 | AE1-229 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 165.03 | 166.83 | AE1-229 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 163.23 | 163.78 | AE1-229 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 163.22 | 163.78 | AE1-229 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 163.21 | 163.78 | AE1-229 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3464 | 168.2 | 162.19 | AC1-122 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 165.17 | 160.23 | AE1-229 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 154.77 | 159.46 | AE1-229 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 163.39 | 158.51 | AE1-229 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 163.39 | 158.51 | AE1-229 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 153.07 | 158.13 | AE1-229 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 163.34 | 156.05 | AE1-229 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 149.71 | 154.48 | AE1-229 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 903 | 145.34 | 153.75 | AE1-229 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 154.29 | 152.98 | AE1-229 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 156.98 | 151.82 | AE1-229 | PN_P1-2_PN-500-010T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 903 | 143.86 | 151.14 | AE1-229 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 903 | 143.86 | 151.13 | AE1-229 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 903 | 143.85 | 151.12 | AE1-229 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 147.51 | 150.8 | AE1-229 | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 147.44 | 150.73 | AE1-229 | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 145.06 | 149.48 | AE1-229 | AP_P2-3_PE-500-016_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 145.12 | 149.45 | AE1-229 | AP_P2-3_PE-500-015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 154.78 | 149.31 | AE1-229 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 154.58 | 149.13 | AE1-229 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 154.6 | 149.11 | AE1-229 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 154.23 | 149.08 | AE1-229 | PJM_500_BG_P4_5_CNSTN_L_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 154.33 | 148.92 | AE1-229 | PECO_P4_NOTTI85_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 154.27 | 148.9 | AE1-229 | PECO_P1-2_220-08_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 154.2 | 148.84 | AE1-229 | PECO_P4_COOPR125_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.24 | 148.6 | AE1-229 | AP_P1-2_WP-500-DRT17_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.24 | 148.6 | AE1-229 | AP_P1-2_PE-500-001_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.19 | 148.53 | AE1-229 | AP_P2-3_PE-500-018C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3464 | 168.19 | 162.17 | AC1-143 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 152.81 | 146.02 | AE1-229 | PECO_P4_PEACH025_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 152.57 | 145.83 | AE1-229 | PECO_P1-2_PBTIE1_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 911 | 150.26 | 144.58 | AE1-229 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 911 | 149.35 | 143.29 | AE1-229 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 911 | 149.35 | 143.29 | AE1-229 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 911 | 149.33 | 143.28 | AE1-229 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204502 | 27JACKSON | 204514 | 27TMI | 1 | 230 | 227 | 781 | 133.99 | 143.15 | AE1-229 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204502 | 27JACKSON | 204514 | 27TMI | 1 | 230 | 227 | 781 | 134.18 | 143.13 | AE1-229 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204502 | 27JACKSON | 204514 | 27TMI | 1 | 230 | 227 | 781 | 134.18 | 143.13 | AE1-229 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204502 | 27JACKSON | 204514 | 27TMI | 1 | 230 | 227 | 781 | 134.16 | 143.11 | AE1-229 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 903 | 136.79 | 141.2 | AE1-229 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 1031 | 131.74 | 140.54 | AE1-229 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 1031 | 131.26 | 139.47 | AE1-229 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 1031 | 131.26 | 139.47 | AE1-229 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 1031 | 131.25 | 139.45 | AE1-229 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 911 | 141.48 | 136.29 | AE1-229 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 207922 | BRIS | 207923 | BRISREAC | RX | 230 | 229 | 676 | 125.87 | 135.67 | AE1-229 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 207923 | BRISREAC | 208132 | WHEM TR1 | 1 | 230 | 229 | 676 | 125.87 | 135.67 | AE1-229 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208078 | SAKR | 1 | 230 | 229 | 903 | 126.47 | 135.5 | AE1-229 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 140.6 | 134.6 | AE1-229 | PECO_P4_PEACH205_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 140.7 | 134.48 | AE1-229 | PECO_P1-2_PBTIE2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208078 | SAKR | 1 | 230 | 229 | 903 | 125.75 | 134.09 | AE1-229 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208078 | SAKR | 1 | 230 | 229 | 903 | 125.75 | 134.09 | AE1-229 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208078 | SAKR | 1 | 230 | 229 | 903 | 125.75 | 134.08 | AE1-229 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 139.65 | 133.5 | AE1-229 | PECO_P4_PEACH055_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204502 | 27JACKSON | 204514 | 27TMI | 1 | 230 | 227 | 781 | 126.53 | 132.66 | AE1-229 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220972 | GRANITE1 | 1 | 230 | 232 | 829 | 136.1 | 132.11 | AE1-229 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220972 | GRANITE1 | 1 | 230 | 232 | 829 | 135.48 | 131.46 | AE1-229 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220972 | GRANITE1 | 1 | 230 | 232 | 829 | 135.48 | 131.46 | AE1-229 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 1031 | 125.66 | 130.69 | AE1-229 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220973 | GRANITE6 | 1 | 230 | 232 | 829 | 134.01 | 130.19 | AE1-229 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220973 | GRANITE6 | 1 | 230 | 232 | 829 | 133.42 | 129.58 | AE1-229 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220973 | GRANITE6 | 1 | 230 | 232 | 829 | 133.42 | 129.58 | AE1-229 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 135.22 | 129.33 | AE1-229 | PECO_P4_PEACH015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 128.57 | 128.93 | AE1-229 | BG_P7_GRCTN_CNSTN_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 126.51 | 128.93 | AE1-229 | BG_P7_GRCTN_CNSTN_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 129.94 | 128.2 | AE1-229 | DVP_P4-2: 514T595_SRT-SW |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208020 | MANO TR3 | 1 | 230 | 229 | 793 | 113.53 | 127.88 | AE1-229 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 133.72 | 127.82 | AE1-229 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220953 | HOWARD12 | 220972 | GRANITE1 | 1 | 230 | 232 | 772 | 131.08 | 127.06 | AE1-229 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 128.22 | 126.51 | AE1-229 | DVP_P4-2: 51482_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 128.22 | 126.42 | AE1-229 | AP_P1-2_PE-500-407T_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 128.22 | 126.42 | AE1-229 | DVP_P1-2: LN 514_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220954 | HOWARD32 | 220973 | GRANITE6 | 1 | 230 | 232 | 772 | 129.85 | 126.29 | AE1-229 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208020 | MANO TR3 | 1 | 230 | 229 | 793 | 112.73 | 126.26 | AE1-229 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208020 | MANO TR3 | 1 | 230 | 229 | 793 | 112.73 | 126.26 | AE1-229 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208020 | MANO TR3 | 1 | 230 | 229 | 793 | 112.73 | 126.25 | AE1-229 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220953 | HOWARD12 | 220972 | GRANITE1 | 1 | 230 | 232 | 772 | 130.17 | 126.1 | AE1-229 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220953 | HOWARD12 | 220972 | GRANITE1 | 1 | 230 | 232 | 772 | 130.17 | 126.1 | AE1-229 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 207922 | BRIS | 207923 | BRISREAC | RX | 230 | 229 | 676 | 120.04 | 126.04 | AE1-229 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 207923 | BRISREAC | 208132 | WHEM TR1 | 1 | 230 | 229 | 676 | 120.04 | 126.04 | AE1-229 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220954 | HOWARD32 | 220973 | GRANITE6 | 1 | 230 | 232 | 772 | 129.06 | 125.46 | AE1-229 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220954 | HOWARD32 | 220973 | GRANITE6 | 1 | 230 | 232 | 772 | 129.06 | 125.46 | AE1-229 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 119.42 | 124.36 | AE1-229 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 121.48 | 124.36 | AE1-229 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208078 | SAKR | 1 | 230 | 229 | 903 | 118.49 | 124.28 | AE1-229 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 119.24 | 124.15 | AE1-229 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 121.3 | 124.15 | AE1-229 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 119.24 | 124.15 | AE1-229 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 121.3 | 124.15 | AE1-229 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208031 | MLWD TR2 | 1 | 230 | 229 | 911 | 113.64 | 124.09 | AE1-229 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204512 | 27S.RDG | 204693 | 27BOONETOWN | 1 | 230 | 227 | 607 | 108.31 | 123.78 | AE1-229 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200025 | W CHAPEL | 1 | 500 | 225 | 1732 | 124.75 | 123 | AE1-229 | PEPCO_P4_PP41_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208031 | MLWD TR2 | 1 | 230 | 229 | 911 | 112.95 | 122.66 | AE1-229 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208031 | MLWD TR2 | 1 | 230 | 229 | 911 | 112.95 | 122.66 | AE1-229 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208031 | MLWD TR2 | 1 | 230 | 229 | 911 | 112.95 | 122.65 | AE1-229 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 119.8 | 122.21 | AE1-229 | BG_P7_GRCTN_CNSTN_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 120.52 | 121.16 | AE1-229 | PJM_500_BG_P4_5_CNSTN_15_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 118.46 | 121.16 | AE1-229 | PJM_500_BG_P4_5_CNSTN_15_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208131 | WHEM | 208132 | WHEM TR1 | 1 | 230 | 229 | 691 | 110.06 | 120.29 | AE1-229 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220965 | NEAST339 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 120.65 | 120.02 | AE1-229 | BG_P1_2315_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220965 | NEAST339 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 120.21 | 119.8 | AE1-229 | BG_P4_5_NEAST_17_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220965 | NEAST339 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 120.38 | 119.8 | AE1-229 | BG_P4_5_NEAST_15_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 115.52 | 119.32 | AE1-229 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 124.66 | 119.21 | AE1-229 | PECO_P4_PEACH225_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220979 | NEAST317 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 119.72 | 119.14 | AE1-229 | BG_P1_2337_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3464 | 168.28 | 162.27 | AC1-145 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3464 | 165.4 | 159.44 | AC1-158 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 115.18 | 118.98 | AE1-229 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 115.17 | 118.92 | AE1-229 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 115.17 | 118.92 | AE1-229 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220979 | NEAST317 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 119.38 | 118.86 | AE1-229 | BG_P4_5_NEAST_39_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220979 | NEAST317 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 119.38 | 118.86 | AE1-229 | BG_P4_5_NEAST_37_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 114.84 | 118.58 | AE1-229 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 114.84 | 118.58 | AE1-229 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 115.54 | 118.37 | AE1-229 | BG_P7_GRCTN_CNSTN_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 112.96 | 117.81 | AE1-229 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 112.78 | 117.61 | AE1-229 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 112.78 | 117.61 | AE1-229 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 118.4 | 116.49 | AE1-229 | AP_P2-3_PE-500-019C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3464 | 167.45 | 161.45 | AC1-161 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208020 | MANO TR3 | 1 | 230 | 229 | 793 | 105.55 | 115.83 | AE1-229 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 2 | 500/230 | 225/232 | 2168 | 110.35 | 115.76 | AE1-229 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 2 | 500/230 | 225/232 | 2168 | 110.18 | 115.55 | AE1-229 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 2 | 500/230 | 225/232 | 2168 | 110.18 | 115.55 | AE1-229 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 1 | 500/230 | 225/232 | 2168 | 110.12 | 115.52 | AE1-229 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208020 | MANO TR3 | 208031 | MLWD TR2 | 1 | 230 | 229 | 903 | 103.68 | 115.34 | AE1-229 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 1 | 500/230 | 225/232 | 2168 | 109.95 | 115.3 | AE1-229 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 1 | 500/230 | 225/232 | 2168 | 109.94 | 115.3 | AE1-229 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220964 | GRACETON | 220999 | BAGLEY2 | 13 | 230 | 232 | 1795 | 114.12 | 115.22 | AE1-229 | BG_P4_5_GRCTN_3T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 112.03 | 114.77 | AE1-229 | PJM_500_BG_P4_5_CNSTN_15_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 108.69 | 113.99 | AE1-229 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208020 | MANO TR3 | 208031 | MLWD TR2 | 1 | 230 | 229 | 903 | 103 | 113.85 | AE1-229 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208020 | MANO TR3 | 208031 | MLWD TR2 | 1 | 230 | 229 | 903 | 103 | 113.85 | AE1-229 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208020 | MANO TR3 | 208031 | MLWD TR2 | 1 | 230 | 229 | 903 | 103 | 113.85 | AE1-229 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 108.52 | 113.78 | AE1-229 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 108.52 | 113.78 | AE1-229 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208031 | MLWD TR2 | 1 | 230 | 229 | 911 | 106.19 | 113.39 | AE1-229 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 2 | 500/230 | 225/232 | 2168 | 109.06 | 112.42 | AE1-229 | PJM_500_BG_P4_5_CNSTN_15_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 107.16 | 112.11 | AE1-229 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 107.03 | 111.97 | AE1-229 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220980 | RAPHAEL | 220999 | BAGLEY2 | 13 | 230 | 232 | 1795 | 109.69 | 111.97 | AE1-229 | BG_P4_5_GRCTN_3T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3464 | 167.67 | 161.66 | AC1-164 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208131 | WHEM | 208133 | WHEM TR2 | 1 | 230 | 229 | 691 | 102.53 | 111.66 | AE1-229 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208131 | WHEM | 208132 | WHEM TR1 | 1 | 230 | 229 | 691 | 104.58 | 111.44 | AE1-229 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 107.76 | 111.07 | AE1-229 | PJM_500_BG_P4_5_CNSTN_15_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220973 | GRANITE6 | 1 | 230 | 232 | 829 | 109.78 | 108.57 | AE1-229 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220965 | NEAST339 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 109.17 | 107.74 | AE1-229 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220965 | NEAST339 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 109.07 | 107.63 | AE1-229 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220965 | NEAST339 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 109.07 | 107.63 | AE1-229 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220972 | GRANITE1 | 1 | 230 | 232 | 829 | 108.93 | 107.48 | AE1-229 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 102.27 | 106.55 | AE1-229 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 102.19 | 106.47 | AE1-229 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208021 | MANO TR4 | 208133 | WHEM TR2 | 2 | 230 | 229 | 593 | 97.16 | 106.45 | AE1-229 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200099 | LAUS | 208045 | LAUS | 3 | 500/230 | 225/229 | 1200 | 104.1 | 105.89 | AE1-229 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 103.37 | 105.45 | AE1-229 | BG_P1_2322_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200099 | LAUS | 208045 | LAUS | 3 | 500/230 | 225/229 | 1200 | 103.81 | 105.4 | AE1-229 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200099 | LAUS | 208045 | LAUS | 3 | 500/230 | 225/229 | 1200 | 103.81 | 105.4 | AE1-229 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200099 | LAUS | 208045 | LAUS | 3 | 500/230 | 225/229 | 1200 | 103.8 | 105.39 | AE1-229 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 103.3 | 105.37 | AE1-229 | BG_P1_2310_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 103.31 | 105.34 | AE1-229 | BG_P4_5_NW2322_230-4_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 103.23 | 105.3 | AE1-229 | BG_P4_5_NW2310_230-5_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208020 | MANO TR3 | 208031 | MLWD TR2 | 1 | 230 | 229 | 903 | 96.63 | 104.92 | AE1-229 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220979 | NEAST317 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 106.02 | 104.65 | AE1-229 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220979 | NEAST317 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 105.92 | 104.54 | AE1-229 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220979 | NEAST317 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 105.92 | 104.54 | AE1-229 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 101.95 | 104.06 | AE1-229 | BG_P4_5_NW230-2_2322_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 99.82 | 104.03 | AE1-229 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 99.81 | 104.03 | AE1-229 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 99.81 | 104.03 | AE1-229 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 101.84 | 103.95 | AE1-229 | BG_P4_5_NW2371_2310_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 101.84 | 103.94 | AE1-229 | BG_P4_5_NW230-3_2310_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 100.97 | 103 | AE1-229 | BG_P4_5_CNSTN_14_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220965 | NEAST339 | 220977 | RIV2339 | 1 | 230 | 232 | 991 | 104.41 | 102.96 | AE1-229 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220966 | RIV2317 | 220979 | NEAST317 | 1 | 230 | 232 | 940 | 103.98 | 102.92 | AE1-229 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220964 | GRACETON | 221000 | BAGLEY | 5 | 230 | 232 | 1795 | 102.12 | 102.92 | AE1-229 | BG_P1_2313_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220964 | GRACETON | 220999 | BAGLEY2 | 13 | 230 | 232 | 1795 | 102.12 | 102.92 | AE1-229 | BG_P1_2305_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220965 | NEAST339 | 220977 | RIV2339 | 1 | 230 | 232 | 991 | 104.36 | 102.9 | AE1-229 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220965 | NEAST339 | 220977 | RIV2339 | 1 | 230 | 232 | 991 | 104.36 | 102.9 | AE1-229 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220965 | NEAST339 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 103.48 | 102.87 | AE1-229 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220966 | RIV2317 | 220979 | NEAST317 | 1 | 230 | 232 | 940 | 103.93 | 102.86 | AE1-229 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220966 | RIV2317 | 220979 | NEAST317 | 1 | 230 | 232 | 940 | 103.93 | 102.86 | AE1-229 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 98.92 | 102.72 | AE1-229 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 2 | 500/230 | 225/232 | 2168 | 99.5 | 102.3 | AE1-229 | PJM_500_BG_P2_CNSTN_230-N_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 2 | 500/230 | 225/232 | 2168 | 99.5 | 102.3 | AE1-229 | BG_P1_CNSTN_500-2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 1 | 500/230 | 225/232 | 2168 | 99.4 | 102.19 | AE1-229 | PJM_500_BG_P2_CNSTN_230-S_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 1 | 500/230 | 225/232 | 2168 | 99.4 | 102.19 | AE1-229 | BG_P1_CNSTN_500-4_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 223960 | BRG 1T 230 | 1 | 500/230 | 225/233 | 1498 | 100.96 | 101.39 | AE1-229 | PEPCO_P4_PP41_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 98.99 | 101.34 | AE1-229 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220979 | NEAST317 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 101.34 | 100.74 | AE1-229 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208021 | MANO TR4 | 1 | 230 | 229 | 600 | 90.23 | 100.64 | AE1-229 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.32 | 157.45 | AE1-237 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.32 | 157.44 | AE1-237 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 155.89 | 150.74 | AE1-237 | PN_P1-2_PN-500-010T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.22 | 148.49 | AE1-237 | AP_P2-3_PE-500-016_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.29 | 148.47 | AE1-237 | AP_P2-3_PE-500-015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.51 | 148.07 | AE1-237 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.2 | 148.07 | AE1-237 | PJM_500_BG_P4_5_CNSTN_L_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.31 | 147.89 | AE1-237 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.34 | 147.87 | AE1-237 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.07 | 147.68 | AE1-237 | PECO_P4_NOTTI85_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.01 | 147.66 | AE1-237 | PECO_P1-2_220-08_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.4 | 147.61 | AE1-237 | AP_P1-2_WP-500-DRT17_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.4 | 147.61 | AE1-237 | AP_P1-2_PE-500-001_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.94 | 147.6 | AE1-237 | PECO_P4_COOPR125_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.35 | 147.54 | AE1-237 | AP_P2-3_PE-500-018C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.35 | 147.54 | AE1-237 | AP_P2-3_PE-500-018D_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3464 | 168.19 | 162.17 | AC1-174 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 142.87 | 146.98 | AE1-237 | AP_P2-3_WP-500-DRT19_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 142.87 | 146.98 | AE1-237 | AP_P2-3_WP-500-466_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 142.87 | 146.98 | AE1-237 | AP_P1-2_WP-500-006_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 142.87 | 146.98 | AE1-237 | AP_P1-2_PE-500-004_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 225.81 | 240.19 | AE1-240 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 227.84 | 240.18 | AE1-240 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 215.68 | 229.92 | AE1-240 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 211.42 | 226.73 | AE1-240 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 196.12 | 206.62 | AE1-240 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3464 | 168.19 | 162.17 | AC1-175 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 154.25 | 158.84 | AE1-240 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.78 | 157.9 | AE1-240 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.78 | 157.9 | AE1-240 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 152.55 | 157.51 | AE1-240 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 162.46 | 155.2 | AE1-240 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 149.19 | 153.86 | AE1-240 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 156.35 | 151.2 | AE1-240 | PN_P1-2_PN-500-010T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 147.01 | 150.21 | AE1-240 | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.94 | 150.14 | AE1-240 | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.6 | 148.94 | AE1-240 | AP_P2-3_PE-500-016_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.67 | 148.92 | AE1-240 | AP_P2-3_PE-500-015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 154.03 | 148.58 | AE1-240 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.64 | 148.5 | AE1-240 | PJM_500_BG_P4_5_CNSTN_L_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.83 | 148.39 | AE1-240 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.85 | 148.38 | AE1-240 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.58 | 148.18 | AE1-240 | PECO_P4_NOTTI85_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.52 | 148.17 | AE1-240 | PECO_P1-2_220-08_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.46 | 148.1 | AE1-240 | PECO_P4_COOPR125_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.78 | 148.06 | AE1-240 | AP_P1-2_PE-500-001_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.78 | 148.06 | AE1-240 | AP_P1-2_WP-500-DRT17_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.73 | 147.99 | AE1-240 | AP_P2-3_PE-500-018C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3464 | 168.13 | 162.11 | AC1-189 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 151.77 | 145.02 | AE1-240 | PECO_P4_PEACH025_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 151.6 | 144.89 | AE1-240 | PECO_P1-2_PBTIE1_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 139.83 | 133.87 | AE1-240 | PECO_P4_PEACH205_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 139.8 | 133.62 | AE1-240 | PECO_P1-2_PBTIE2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 138.81 | 132.7 | AE1-240 | PECO_P4_PEACH055_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 134.24 | 128.39 | AE1-240 | PECO_P4_PEACH015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 132.84 | 126.97 | AE1-240 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 123.75 | 118.35 | AE1-240 | PECO_P4_PEACH225_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 231.19 | 245.16 | AE2-000 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 229.09 | 245.16 | AE2-000 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 230.31 | 243.04 | AE2-000 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 228.21 | 243.04 | AE2-000 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 230.25 | 242.98 | AE2-000 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 228.14 | 242.98 | AE2-000 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 230.25 | 242.98 | AE2-000 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 228.14 | 242.98 | AE2-000 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 218.85 | 234.76 | AE2-000 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 218 | 232.7 | AE2-000 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 217.94 | 232.64 | AE2-000 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 217.94 | 232.64 | AE2-000 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 214.58 | 231.62 | AE2-000 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 213.73 | 229.54 | AE2-000 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 213.67 | 229.47 | AE2-000 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 213.67 | 229.47 | AE2-000 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 215.44 | 224.12 | AE2-000 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 213.33 | 224.12 | AE2-000 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 203.64 | 214.36 | AE2-000 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 199.37 | 211.05 | AE2-000 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 334 | 176.46 | 179.15 | AE2-000 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 334 | 176.46 | 179.15 | AE2-000 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 334 | 176.33 | 179 | AE2-000 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204539 | 27HUNTRSTN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 334 | 176.07 | 177.45 | AE2-000 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204539 | 27HUNTRSTN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 334 | 176.07 | 177.45 | AE2-000 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204539 | 27HUNTRSTN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 334 | 175.94 | 177.3 | AE2-000 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 235463 | 01TANEY | 1 | 138 | 227/201 | 317 | 180.67 | 174.57 | AE2-000 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 235463 | 01TANEY | 1 | 138 | 227/201 | 317 | 180.67 | 174.57 | AE2-000 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 235463 | 01TANEY | 1 | 138 | 227/201 | 317 | 180.52 | 174.4 | AE2-000 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204538 | 27STRABAN | 204544 | 27LINCOLN | 1 | 115 | 227 | 371 | 165.71 | 170.6 | AE2-000 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204538 | 27STRABAN | 204544 | 27LINCOLN | 1 | 115 | 227 | 371 | 165.71 | 170.6 | AE2-000 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 175.24 | 170.52 | AE2-000 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204538 | 27STRABAN | 204544 | 27LINCOLN | 1 | 115 | 227 | 371 | 165.58 | 170.45 | AE2-000 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 174.34 | 169.08 | AE2-000 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 174.34 | 169.08 | AE2-000 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 174.32 | 169.07 | AE2-000 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 166.31 | 168.61 | AE2-000 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204529 | 27GERMANTN | 204538 | 27STRABAN | 1 | 115 | 227 | 371 | 159.89 | 166.05 | AE2-000 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204529 | 27GERMANTN | 204538 | 27STRABAN | 1 | 115 | 227 | 371 | 159.89 | 166.05 | AE2-000 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204529 | 27GERMANTN | 204538 | 27STRABAN | 1 | 115 | 227 | 371 | 159.76 | 165.9 | AE2-000 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 164.56 | 165.52 | AE2-000 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 164.56 | 165.52 | AE2-000 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 164.55 | 165.51 | AE2-000 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3464 | 168.09 | 162.08 | AC1-191 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 166.4 | 161.36 | AE2-000 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 155.79 | 160.68 | AE2-000 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 164.54 | 159.64 | AE2-000 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 164.54 | 159.64 | AE2-000 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 154.08 | 159.35 | AE2-000 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 164.97 | 157.61 | AE2-000 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 150.71 | 155.69 | AE2-000 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 903 | 146.29 | 155.39 | AE2-000 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 155.64 | 154.57 | AE2-000 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 158.14 | 152.96 | AE2-000 | PN_P1-2_PN-500-010T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 903 | 144.87 | 152.77 | AE2-000 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 903 | 144.87 | 152.77 | AE2-000 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 903 | 144.85 | 152.76 | AE2-000 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204539 | 27HUNTRSTN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 334 | 152.84 | 152.75 | AE2-000 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204539 | 27HUNTRSTN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 334 | 152.84 | 152.75 | AE2-000 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204539 | 27HUNTRSTN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 334 | 152.83 | 152.74 | AE2-000 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204539 | 27HUNTRSTN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 334 | 152.67 | 152.59 | AE2-000 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 334 | 153.23 | 152.48 | AE2-000 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 334 | 153.23 | 152.48 | AE2-000 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 334 | 153.22 | 152.48 | AE2-000 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 334 | 153.05 | 152.29 | AE2-000 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 148.48 | 151.95 | AE2-000 | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 148.41 | 151.87 | AE2-000 | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 156.14 | 150.65 | AE2-000 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 145.94 | 150.52 | AE2-000 | AP_P2-3_PE-500-016_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.01 | 150.49 | AE2-000 | AP_P2-3_PE-500-015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 155.94 | 150.47 | AE2-000 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 155.97 | 150.45 | AE2-000 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 155.69 | 150.26 | AE2-000 | PECO_P4_NOTTI85_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 155.63 | 150.24 | AE2-000 | PECO_P1-2_220-08_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 155.57 | 150.17 | AE2-000 | PECO_P4_COOPR125_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 155.33 | 150.16 | AE2-000 | PJM_500_BG_P4_5_CNSTN_L_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 145.12 | 149.63 | AE2-000 | AP_P1-2_WP-500-DRT17_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 145.12 | 149.63 | AE2-000 | AP_P1-2_PE-500-001_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 145.07 | 149.57 | AE2-000 | AP_P2-3_PE-500-018C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3464 | 168.12 | 162.11 | AC1-194 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3464 | 168.14 | 162.13 | AC1-208 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 147.49 | 148.08 | AE2-000 | BG_P7_GRCTN_CNSTN_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 154.6 | 147.74 | AE2-000 | PECO_P4_PEACH025_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 154.38 | 147.56 | AE2-000 | PECO_P1-2_PBTIE1_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 911 | 151.44 | 145.61 | AE2-000 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204502 | 27JACKSON | 204514 | 27TMI | 1 | 230 | 227 | 781 | 135.05 | 144.91 | AE2-000 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204502 | 27JACKSON | 204514 | 27TMI | 1 | 230 | 227 | 781 | 135.23 | 144.84 | AE2-000 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204502 | 27JACKSON | 204514 | 27TMI | 1 | 230 | 227 | 781 | 135.23 | 144.84 | AE2-000 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204502 | 27JACKSON | 204514 | 27TMI | 1 | 230 | 227 | 781 | 135.22 | 144.83 | AE2-000 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 911 | 150.56 | 144.31 | AE2-000 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 911 | 150.56 | 144.31 | AE2-000 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 911 | 150.54 | 144.3 | AE2-000 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 334 | 146.19 | 143.63 | AE2-000 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204539 | 27HUNTRSTN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 334 | 145.79 | 143.41 | AE2-000 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204538 | 27STRABAN | 204544 | 27LINCOLN | 1 | 115 | 227 | 371 | 142.15 | 143.3 | AE2-000 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204538 | 27STRABAN | 204544 | 27LINCOLN | 1 | 115 | 227 | 371 | 142.15 | 143.3 | AE2-000 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204538 | 27STRABAN | 204544 | 27LINCOLN | 1 | 115 | 227 | 371 | 142.14 | 143.29 | AE2-000 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204538 | 27STRABAN | 204544 | 27LINCOLN | 1 | 115 | 227 | 371 | 141.98 | 143.11 | AE2-000 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3464 | 168.04 | 162.04 | AC1-216 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 334 | 143.96 | 143.03 | AE2-000 | ME_P2-3_ME-115-019-B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 903 | 137.8 | 142.66 | AE2-000 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 142.69 | 142.38 | AE2-000 | PJM_500_BG_P4_5_CNSTN_15_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 1031 | 132.56 | 142.07 | AE2-000 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 334 | 140.36 | 141.7 | AE2-000 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204539 | 27HUNTRSTN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 334 | 143.57 | 141.56 | AE2-000 | ME_P2-3_ME-115-019-B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 1031 | 132.09 | 140.96 | AE2-000 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 1031 | 132.09 | 140.96 | AE2-000 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 1031 | 132.08 | 140.96 | AE2-000 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204539 | 27HUNTRSTN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 334 | 139.98 | 140.19 | AE2-000 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200512 | 26LEWISTWN | 200519 | 26REED TAP | 1 | 115 | 226 | 271 | 129.3 | 139.59 | AE2-000 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204529 | 27GERMANTN | 204538 | 27STRABAN | 1 | 115 | 227 | 371 | 136.34 | 139.01 | AE2-000 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204529 | 27GERMANTN | 204538 | 27STRABAN | 1 | 115 | 227 | 371 | 136.34 | 139.01 | AE2-000 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204529 | 27GERMANTN | 204538 | 27STRABAN | 1 | 115 | 227 | 371 | 136.33 | 139.01 | AE2-000 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204529 | 27GERMANTN | 204538 | 27STRABAN | 1 | 115 | 227 | 371 | 136.16 | 138.83 | AE2-000 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 235463 | 01TANEY | 1 | 138 | 227/201 | 317 | 137.83 | 137.55 | AE2-000 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208078 | SAKR | 1 | 230 | 229 | 903 | 127.66 | 137.35 | AE2-000 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 911 | 142.7 | 137.32 | AE2-000 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 207923 | BRISREAC | 208132 | WHEM TR1 | 1 | 230 | 229 | 676 | 126.59 | 137.06 | AE2-000 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 207922 | BRIS | 207923 | BRISREAC | RX | 230 | 229 | 676 | 126.59 | 137.06 | AE2-000 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 235463 | 01TANEY | 1 | 138 | 227/201 | 317 | 137.43 | 136.93 | AE2-000 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 142.17 | 136.11 | AE2-000 | PECO_P4_PEACH205_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 142.36 | 136.08 | AE2-000 | PECO_P1-2_PBTIE2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208078 | SAKR | 1 | 230 | 229 | 903 | 126.97 | 135.89 | AE2-000 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208078 | SAKR | 1 | 230 | 229 | 903 | 126.96 | 135.89 | AE2-000 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208078 | SAKR | 1 | 230 | 229 | 903 | 126.97 | 135.89 | AE2-000 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 207923 | BRISREAC | 208132 | WHEM TR1 | 1 | 230 | 229 | 676 | 125.89 | 135.53 | AE2-000 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 207922 | BRIS | 207923 | BRISREAC | RX | 230 | 229 | 676 | 125.89 | 135.53 | AE2-000 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 207923 | BRISREAC | 208132 | WHEM TR1 | 1 | 230 | 229 | 676 | 125.89 | 135.53 | AE2-000 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 207922 | BRIS | 207923 | BRISREAC | RX | 230 | 229 | 676 | 125.89 | 135.53 | AE2-000 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 207923 | BRISREAC | 208132 | WHEM TR1 | 1 | 230 | 229 | 676 | 125.88 | 135.52 | AE2-000 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 207922 | BRIS | 207923 | BRISREAC | RX | 230 | 229 | 676 | 125.88 | 135.52 | AE2-000 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 141.12 | 134.92 | AE2-000 | PECO_P4_PEACH055_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 235463 | 01TANEY | 1 | 138 | 227/201 | 317 | 135.16 | 134.8 | AE2-000 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204538 | 27STRABAN | 204544 | 27LINCOLN | 1 | 115 | 227 | 371 | 135.02 | 134.45 | AE2-000 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200519 | 26REED TAP | 200522 | 26SHADE GP | 1 | 115 | 226 | 271 | 121.53 | 134.41 | AE2-000 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204502 | 27JACKSON | 204514 | 27TMI | 1 | 230 | 227 | 781 | 127.6 | 134.22 | AE2-000 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204538 | 27STRABAN | 204544 | 27LINCOLN | 1 | 115 | 227 | 371 | 130.29 | 133.23 | AE2-000 | AP_P2-3_PE-500-016_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204538 | 27STRABAN | 204544 | 27LINCOLN | 1 | 115 | 227 | 371 | 130.39 | 133.16 | AE2-000 | AP_P2-3_PE-500-015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220972 | GRANITE1 | 1 | 230 | 232 | 829 | 137.08 | 133.05 | AE2-000 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 235463 | 01TANEY | 1 | 138 | 227/201 | 317 | 135.32 | 132.72 | AE2-000 | PEPCO_P4_PP41_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 204529 | 27GERMANTN | 1 | 138/115 | 227 | 453 | 126.43 | 132.44 | AE2-000 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 204529 | 27GERMANTN | 1 | 138/115 | 227 | 453 | 126.43 | 132.44 | AE2-000 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220972 | GRANITE1 | 1 | 230 | 232 | 829 | 136.47 | 132.4 | AE2-000 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220972 | GRANITE1 | 1 | 230 | 232 | 829 | 136.46 | 132.4 | AE2-000 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 204529 | 27GERMANTN | 1 | 138/115 | 227 | 453 | 126.32 | 132.32 | AE2-000 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 1031 | 126.5 | 132.01 | AE2-000 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 235463 | 01TANEY | 1 | 138 | 227/201 | 317 | 132.54 | 131.23 | AE2-000 | AP_P2-3_PE-500-019B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220973 | GRANITE6 | 1 | 230 | 232 | 829 | 134.96 | 131.11 | AE2-000 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 137.05 | 131.09 | AE2-000 | PECO_P4_PEACH015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220973 | GRANITE6 | 1 | 230 | 232 | 829 | 134.38 | 130.5 | AE2-000 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220973 | GRANITE6 | 1 | 230 | 232 | 829 | 134.38 | 130.5 | AE2-000 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 235463 | 01TANEY | 1 | 138 | 227/201 | 317 | 132.73 | 130.42 | AE2-000 | AP_P2-3_PE-500-019F_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204529 | 27GERMANTN | 204538 | 27STRABAN | 1 | 115 | 227 | 371 | 129.2 | 130.12 | AE2-000 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 129.64 | 130.06 | AE2-000 | BG_P7_GRCTN_CNSTN_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 127.54 | 130.06 | AE2-000 | BG_P7_GRCTN_CNSTN_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208020 | MANO TR3 | 1 | 230 | 229 | 793 | 114.7 | 129.75 | AE2-000 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 135.37 | 129.41 | AE2-000 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 130.77 | 129.01 | AE2-000 | DVP_P4-2: 514T595_SRT-SW |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 235463 | 01TANEY | 1 | 138 | 227/201 | 317 | 130.91 | 128.79 | AE2-000 | PEPCO_P1_5055_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204529 | 27GERMANTN | 204538 | 27STRABAN | 1 | 115 | 227 | 371 | 124.47 | 128.78 | AE2-000 | AP_P2-3_PE-500-016_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204529 | 27GERMANTN | 204538 | 27STRABAN | 1 | 115 | 227 | 371 | 124.57 | 128.7 | AE2-000 | AP_P2-3_PE-500-015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220953 | HOWARD12 | 220972 | GRANITE1 | 1 | 230 | 232 | 772 | 132.22 | 128.17 | AE2-000 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208020 | MANO TR3 | 1 | 230 | 229 | 793 | 113.92 | 128.13 | AE2-000 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208020 | MANO TR3 | 1 | 230 | 229 | 793 | 113.93 | 128.13 | AE2-000 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208020 | MANO TR3 | 1 | 230 | 229 | 793 | 113.93 | 128.13 | AE2-000 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220954 | HOWARD32 | 220973 | GRANITE6 | 1 | 230 | 232 | 772 | 130.93 | 127.34 | AE2-000 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 129.07 | 127.33 | AE2-000 | DVP_P4-2: 51482_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 129.07 | 127.24 | AE2-000 | DVP_P1-2: LN 514_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 129.07 | 127.24 | AE2-000 | AP_P1-2_PE-500-407T_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 207922 | BRIS | 207923 | BRISREAC | RX | 230 | 229 | 676 | 120.79 | 127.23 | AE2-000 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 207923 | BRISREAC | 208132 | WHEM TR1 | 1 | 230 | 229 | 676 | 120.79 | 127.23 | AE2-000 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220953 | HOWARD12 | 220972 | GRANITE1 | 1 | 230 | 232 | 772 | 131.32 | 127.21 | AE2-000 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220953 | HOWARD12 | 220972 | GRANITE1 | 1 | 230 | 232 | 772 | 131.32 | 127.21 | AE2-000 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 911 | 124.36 | 126.98 | AE2-000 | BG_P7_GRCTN_CNSTN_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220954 | HOWARD32 | 220973 | GRANITE6 | 1 | 230 | 232 | 772 | 130.15 | 126.51 | AE2-000 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220954 | HOWARD32 | 220973 | GRANITE6 | 1 | 230 | 232 | 772 | 130.15 | 126.51 | AE2-000 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 793 | 128.07 | 126.31 | AE2-000 | DVP_P4-2: 514T595_SRT-SW |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 2 | 230 | 233 | 793 | 128.07 | 126.31 | AE2-000 | DVP_P4-2: 514T595_SRT-SW |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208078 | SAKR | 1 | 230 | 229 | 903 | 119.71 | 125.92 | AE2-000 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208031 | MLWD TR2 | 1 | 230 | 229 | 911 | 114.74 | 125.76 | AE2-000 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 122.64 | 125.61 | AE2-000 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 120.53 | 125.61 | AE2-000 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204512 | 27S.RDG | 204693 | 27BOONETOWN | 1 | 230 | 227 | 607 | 109.07 | 125.6 | AE2-000 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 122.46 | 125.4 | AE2-000 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 120.35 | 125.4 | AE2-000 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 120.35 | 125.4 | AE2-000 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 122.46 | 125.4 | AE2-000 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 793 | 126.85 | 125.13 | AE2-000 | DVP_P4-2: 51482_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 2 | 230 | 233 | 793 | 126.85 | 125.13 | AE2-000 | DVP_P4-2: 51482_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 2 | 230 | 233 | 793 | 126.85 | 125.05 | AE2-000 | AP_P1-2_PE-500-407T_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 793 | 126.85 | 125.05 | AE2-000 | DVP_P1-2: LN 514_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 2 | 230 | 233 | 793 | 126.85 | 125.05 | AE2-000 | DVP_P1-2: LN 514_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 793 | 126.85 | 125.05 | AE2-000 | AP_P1-2_PE-500-407T_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204512 | 27S.RDG | 204693 | 27BOONETOWN | 1 | 230 | 227 | 607 | 108.92 | 124.77 | AE2-000 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204512 | 27S.RDG | 204693 | 27BOONETOWN | 1 | 230 | 227 | 607 | 108.9 | 124.74 | AE2-000 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204512 | 27S.RDG | 204693 | 27BOONETOWN | 1 | 230 | 227 | 607 | 108.9 | 124.74 | AE2-000 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208031 | MLWD TR2 | 1 | 230 | 229 | 911 | 114.07 | 124.43 | AE2-000 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208031 | MLWD TR2 | 1 | 230 | 229 | 911 | 114.06 | 124.43 | AE2-000 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208031 | MLWD TR2 | 1 | 230 | 229 | 911 | 114.07 | 124.43 | AE2-000 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200025 | W CHAPEL | 1 | 500 | 225 | 1732 | 125.62 | 123.9 | AE2-000 | PEPCO_P4_PP41_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 120.8 | 123.3 | AE2-000 | BG_P7_GRCTN_CNSTN_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 121.62 | 122.31 | AE2-000 | PJM_500_BG_P4_5_CNSTN_15_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 119.52 | 122.31 | AE2-000 | PJM_500_BG_P4_5_CNSTN_15_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200532 | 26ROXBURY | 200520 | 26ROXBURY | 2 | 138/115 | 226 | 435 | 106.68 | 121.76 | AE2-000 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200532 | 26ROXBURY | 200520 | 26ROXBURY | 2 | 138/115 | 226 | 435 | 106.68 | 121.76 | AE2-000 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200532 | 26ROXBURY | 200520 | 26ROXBURY | 2 | 138/115 | 226 | 435 | 106.53 | 121.58 | AE2-000 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208131 | WHEM | 208132 | WHEM TR1 | 1 | 230 | 229 | 691 | 110.72 | 121.56 | AE2-000 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 126.35 | 120.83 | AE2-000 | PECO_P4_PEACH225_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 911 | 119.68 | 120.77 | AE2-000 | PJM_500_BG_P4_5_CNSTN_15_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220965 | NEAST339 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 121.37 | 120.75 | AE2-000 | BG_P1_2315_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220965 | NEAST339 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 120.92 | 120.53 | AE2-000 | BG_P4_5_NEAST_17_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220965 | NEAST339 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 121.09 | 120.53 | AE2-000 | BG_P4_5_NEAST_15_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3464 | 168.21 | 162.2 | AC1-221 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3464 | 168.21 | 162.2 | AC1-222 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208131 | WHEM | 208132 | WHEM TR1 | 1 | 230 | 229 | 691 | 110.06 | 120.18 | AE2-000 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208131 | WHEM | 208132 | WHEM TR1 | 1 | 230 | 229 | 691 | 110.06 | 120.18 | AE2-000 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208131 | WHEM | 208132 | WHEM TR1 | 1 | 230 | 229 | 691 | 110.05 | 120.18 | AE2-000 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 116.17 | 120.05 | AE2-000 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220979 | NEAST317 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 120.43 | 119.87 | AE2-000 | BG_P1_2337_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 115.83 | 119.7 | AE2-000 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 115.83 | 119.65 | AE2-000 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 115.83 | 119.65 | AE2-000 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220979 | NEAST317 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 120.08 | 119.58 | AE2-000 | BG_P4_5_NEAST_39_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220979 | NEAST317 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 120.08 | 119.58 | AE2-000 | BG_P4_5_NEAST_37_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 116.53 | 119.46 | AE2-000 | BG_P7_GRCTN_CNSTN_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 115.49 | 119.31 | AE2-000 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 115.49 | 119.31 | AE2-000 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 114.03 | 119.02 | AE2-000 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 113.86 | 118.82 | AE2-000 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 113.86 | 118.82 | AE2-000 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200532 | 26ROXBURY | 200520 | 26ROXBURY | 2 | 138/115 | 226 | 435 | 102.63 | 118.69 | AE2-000 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200532 | 26ROXBURY | 200520 | 26ROXBURY | 2 | 138/115 | 226 | 435 | 102.63 | 118.69 | AE2-000 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200532 | 26ROXBURY | 200520 | 26ROXBURY | 2 | 138/115 | 226 | 435 | 102.62 | 118.68 | AE2-000 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200532 | 26ROXBURY | 200520 | 26ROXBURY | 2 | 138/115 | 226 | 435 | 102.47 | 118.54 | AE2-000 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 119.54 | 118.27 | AE2-000 | PL_04_P42_000564_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 119.54 | 118.27 | AE2-000 | PL_04_P12_000260_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3464 | 167.83 | 161.82 | AC2-012 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208020 | MANO TR3 | 1 | 230 | 229 | 793 | 106.75 | 117.55 | AE2-000 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204512 | 27S.RDG | 204693 | 27BOONETOWN | 1 | 230 | 227 | 607 | 107.14 | 117.48 | AE2-000 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 119.25 | 117.31 | AE2-000 | AP_P2-3_PE-500-019C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 2 | 230 | 233 | 793 | 119.96 | 117.22 | AE2-000 | PEPCO_P1_PP1_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 793 | 119.96 | 117.22 | AE2-000 | PEPCO_P1_PP2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208020 | MANO TR3 | 208031 | MLWD TR2 | 1 | 230 | 229 | 903 | 104.72 | 116.85 | AE2-000 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 2 | 500/230 | 225/232 | 2168 | 110.89 | 116.38 | AE2-000 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 2 | 500/230 | 225/232 | 2168 | 110.71 | 116.17 | AE2-000 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 2 | 500/230 | 225/232 | 2168 | 110.71 | 116.17 | AE2-000 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 1 | 500/230 | 225/232 | 2168 | 110.65 | 116.13 | AE2-000 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 1 | 500/230 | 225/232 | 2168 | 110.48 | 115.92 | AE2-000 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 1 | 500/230 | 225/232 | 2168 | 110.48 | 115.92 | AE2-000 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 113.05 | 115.89 | AE2-000 | PJM_500_BG_P4_5_CNSTN_15_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220964 | GRACETON | 220999 | BAGLEY2 | 13 | 230 | 232 | 1795 | 114.69 | 115.82 | AE2-000 | BG_P4_5_GRCTN_3T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208020 | MANO TR3 | 208031 | MLWD TR2 | 1 | 230 | 229 | 903 | 104.06 | 115.64 | AE2-000 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208020 | MANO TR3 | 208031 | MLWD TR2 | 1 | 230 | 229 | 903 | 104.06 | 115.64 | AE2-000 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208020 | MANO TR3 | 208031 | MLWD TR2 | 1 | 230 | 229 | 903 | 104.06 | 115.64 | AE2-000 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3464 | 168.91 | 162.89 | AC2-023 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 109.76 | 115.2 | AE2-000 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208031 | MLWD TR2 | 1 | 230 | 229 | 911 | 107.32 | 115.01 | AE2-000 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 109.59 | 115 | AE2-000 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 109.59 | 115 | AE2-000 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 114.95 | 113.84 | AE2-000 | BG_P4_5_CNSTN_14_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3464 | 168.07 | 162.06 | AC2-059 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208131 | WHEM | 208133 | WHEM TR2 | 1 | 230 | 229 | 691 | 103.2 | 112.89 | AE2-000 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 2 | 500/230 | 225/232 | 2168 | 109.48 | 112.87 | AE2-000 | PJM_500_BG_P4_5_CNSTN_15_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 107.71 | 112.8 | AE2-000 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 107.58 | 112.66 | AE2-000 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220980 | RAPHAEL | 220999 | BAGLEY2 | 13 | 230 | 232 | 1795 | 110.24 | 112.58 | AE2-000 | BG_P4_5_GRCTN_3T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208131 | WHEM | 208132 | WHEM TR1 | 1 | 230 | 229 | 691 | 105.28 | 112.57 | AE2-000 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 108.78 | 112.19 | AE2-000 | PJM_500_BG_P4_5_CNSTN_15_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 793 | 114.54 | 111.9 | AE2-000 | PEPCO_P4_PP19_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208131 | WHEM | 208133 | WHEM TR2 | 1 | 230 | 229 | 691 | 102.54 | 111.55 | AE2-000 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208131 | WHEM | 208133 | WHEM TR2 | 1 | 230 | 229 | 691 | 102.54 | 111.55 | AE2-000 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208131 | WHEM | 208133 | WHEM TR2 | 1 | 230 | 229 | 691 | 102.53 | 111.54 | AE2-000 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200532 | 26ROXBURY | 200520 | 26ROXBURY | 2 | 138/115 | 226 | 435 | 97.49 | 111.21 | AE2-000 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204512 | 27S.RDG | 204693 | 27BOONETOWN | 1 | 230 | 227 | 607 | 111.39 | 110.71 | AE2-000 | PL_04_P42_101307_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204512 | 27S.RDG | 204693 | 27BOONETOWN | 1 | 230 | 227 | 607 | 111.4 | 110.65 | AE2-000 | PL_24_P42_102306_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3464 | 168.12 | 162.11 | AC2-060 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 204529 | 27GERMANTN | 1 | 138/115 | 227 | 453 | 107.13 | 109.97 | AE2-000 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 204529 | 27GERMANTN | 1 | 138/115 | 227 | 453 | 107.13 | 109.97 | AE2-000 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 204529 | 27GERMANTN | 1 | 138/115 | 227 | 453 | 107.13 | 109.97 | AE2-000 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 204529 | 27GERMANTN | 1 | 138/115 | 227 | 453 | 106.99 | 109.82 | AE2-000 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220973 | GRANITE6 | 1 | 230 | 232 | 829 | 110.52 | 109.37 | AE2-000 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 2 | 230 | 233 | 793 | 111.03 | 109.14 | AE2-000 | AP_P2-3_PE-500-019C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 793 | 111.03 | 109.14 | AE2-000 | AP_P2-3_PE-500-019C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204512 | 27S.RDG | 204693 | 27BOONETOWN | 1 | 230 | 227 | 607 | 109.45 | 108.84 | AE2-000 | PL_04_P43_102301_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204512 | 27S.RDG | 204693 | 27BOONETOWN | 1 | 230 | 227 | 607 | 109.45 | 108.84 | AE2-000 | PL_04_P22_102291_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204512 | 27S.RDG | 204693 | 27BOONETOWN | 1 | 230 | 227 | 607 | 109.45 | 108.82 | AE2-000 | PL_04_P43_102300_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220965 | NEAST339 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 109.86 | 108.42 | AE2-000 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220965 | NEAST339 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 109.76 | 108.31 | AE2-000 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220965 | NEAST339 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 109.76 | 108.31 | AE2-000 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220972 | GRANITE1 | 1 | 230 | 232 | 829 | 109.68 | 108.29 | AE2-000 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208021 | MANO TR4 | 208133 | WHEM TR2 | 2 | 230 | 229 | 593 | 97.91 | 107.76 | AE2-000 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 102.82 | 107.22 | AE2-000 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 102.73 | 107.13 | AE2-000 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200099 | LAUS | 208045 | LAUS | 3 | 500/230 | 225/229 | 1200 | 104.95 | 106.82 | AE2-000 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208020 | MANO TR3 | 208031 | MLWD TR2 | 1 | 230 | 229 | 903 | 97.7 | 106.56 | AE2-000 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208021 | MANO TR4 | 208133 | WHEM TR2 | 2 | 230 | 229 | 593 | 97.15 | 106.37 | AE2-000 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208021 | MANO TR4 | 208133 | WHEM TR2 | 2 | 230 | 229 | 593 | 97.15 | 106.37 | AE2-000 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208021 | MANO TR4 | 208133 | WHEM TR2 | 2 | 230 | 229 | 593 | 97.14 | 106.36 | AE2-000 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220972 | GRANITE1 | 1 | 230 | 232 | 829 | 107.66 | 106.32 | AE2-000 | BG_P4_5_NW230-4_2326_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200099 | LAUS | 208045 | LAUS | 3 | 500/230 | 225/229 | 1200 | 104.66 | 106.3 | AE2-000 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200099 | LAUS | 208045 | LAUS | 3 | 500/230 | 225/229 | 1200 | 104.66 | 106.3 | AE2-000 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200099 | LAUS | 208045 | LAUS | 3 | 500/230 | 225/229 | 1200 | 104.65 | 106.29 | AE2-000 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 103.9 | 106.03 | AE2-000 | BG_P1_2322_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 103.82 | 105.95 | AE2-000 | BG_P1_2310_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 103.83 | 105.91 | AE2-000 | BG_P4_5_NW2322_230-4_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 103.76 | 105.87 | AE2-000 | BG_P4_5_NW2310_230-5_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220973 | GRANITE6 | 1 | 230 | 232 | 829 | 107.34 | 105.8 | AE2-000 | BG_P4_5_NW230-5_2311_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220979 | NEAST317 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 106.68 | 105.3 | AE2-000 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204520 | 27ALLEN | 208142 | WIGR-115 | 1 | 115 | 227/229 | 351.4 | 96.8 | 105.23 | AE2-000 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204520 | 27ALLEN | 208142 | WIGR-115 | 1 | 115 | 227/229 | 351.4 | 96.8 | 105.23 | AE2-000 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204520 | 27ALLEN | 208142 | WIGR-115 | 1 | 115 | 227/229 | 351.4 | 96.8 | 105.23 | AE2-000 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220979 | NEAST317 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 106.58 | 105.19 | AE2-000 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220979 | NEAST317 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 106.58 | 105.19 | AE2-000 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204520 | 27ALLEN | 208142 | WIGR-115 | 1 | 115 | 227/229 | 351.4 | 96.58 | 105.09 | AE2-000 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 102.46 | 104.62 | AE2-000 | BG_P4_5_NW230-2_2322_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 99.95 | 104.53 | AE2-000 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 99.95 | 104.53 | AE2-000 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 99.95 | 104.53 | AE2-000 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 102.35 | 104.51 | AE2-000 | BG_P4_5_NW2371_2310_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 102.35 | 104.5 | AE2-000 | BG_P4_5_NW230-3_2310_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220973 | GRANITE6 | 1 | 230 | 232 | 829 | 105.22 | 104.22 | AE2-000 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208131 | WHEM | 208133 | WHEM TR2 | 1 | 230 | 229 | 691 | 97.77 | 104.21 | AE2-000 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220965 | NEAST339 | 220977 | RIV2339 | 1 | 230 | 232 | 991 | 105.21 | 103.75 | AE2-000 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220966 | RIV2317 | 220979 | NEAST317 | 1 | 230 | 232 | 940 | 104.77 | 103.7 | AE2-000 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220965 | NEAST339 | 220977 | RIV2339 | 1 | 230 | 232 | 991 | 105.17 | 103.69 | AE2-000 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220965 | NEAST339 | 220977 | RIV2339 | 1 | 230 | 232 | 991 | 105.17 | 103.69 | AE2-000 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220966 | RIV2317 | 220979 | NEAST317 | 1 | 230 | 232 | 940 | 104.72 | 103.64 | AE2-000 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220966 | RIV2317 | 220979 | NEAST317 | 1 | 230 | 232 | 940 | 104.72 | 103.64 | AE2-000 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 101.48 | 103.56 | AE2-000 | BG_P4_5_CNSTN_14_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220965 | NEAST339 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 104.07 | 103.52 | AE2-000 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220964 | GRACETON | 220999 | BAGLEY2 | 13 | 230 | 232 | 1795 | 102.64 | 103.47 | AE2-000 | BG_P1_2305_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220964 | GRACETON | 221000 | BAGLEY | 5 | 230 | 232 | 1795 | 102.64 | 103.47 | AE2-000 | BG_P1_2313_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220972 | GRANITE1 | 1 | 230 | 232 | 829 | 104.63 | 103.45 | AE2-000 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 99.08 | 103.24 | AE2-000 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 2 | 500/230 | 225/232 | 2168 | 99.86 | 102.69 | AE2-000 | PJM_500_BG_P2_CNSTN_230-N_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 2 | 500/230 | 225/232 | 2168 | 99.86 | 102.69 | AE2-000 | BG_P1_CNSTN_500-2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 204529 | 27GERMANTN | 1 | 138/115 | 227 | 453 | 101.29 | 102.63 | AE2-000 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 1 | 500/230 | 225/232 | 2168 | 99.75 | 102.58 | AE2-000 | BG_P1_CNSTN_500-4_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 1 | 500/230 | 225/232 | 2168 | 99.75 | 102.58 | AE2-000 | PJM_500_BG_P2_CNSTN_230-S_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208021 | MANO TR4 | 1 | 230 | 229 | 600 | 90.95 | 102.17 | AE2-000 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 204529 | 27GERMANTN | 1 | 138/115 | 227 | 453 | 97.42 | 101.92 | AE2-000 | AP_P2-3_PE-500-016_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 223960 | BRG 1T 230 | 1 | 500/230 | 225/233 | 1498 | 101.45 | 101.91 | AE2-000 | PEPCO_P4_PP41_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 204529 | 27GERMANTN | 1 | 138/115 | 227 | 453 | 97.5 | 101.86 | AE2-000 | AP_P2-3_PE-500-015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 99.12 | 101.75 | AE2-000 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220979 | NEAST317 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 101.91 | 101.36 | AE2-000 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220972 | GRANITE1 | 1 | 230 | 232 | 829 | 102.32 | 101.23 | AE2-000 | BG_P4_5_GRNITE26_32_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220973 | GRANITE6 | 1 | 230 | 232 | 829 | 102.14 | 100.78 | AE2-000 | BBG_P1_2311_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220972 | GRANITE1 | 1 | 230 | 232 | 829 | 101.83 | 100.73 | AE2-000 | BG_P1_2326_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220973 | GRANITE6 | 1 | 230 | 232 | 829 | 101.55 | 100.69 | AE2-000 | BG_P1_2312_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220973 | GRANITE6 | 1 | 230 | 232 | 829 | 101.7 | 100.68 | AE2-000 | BG_P4_5_GRNITE11_12_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208021 | MANO TR4 | 1 | 230 | 229 | 600 | 90.18 | 100.47 | AE2-000 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208021 | MANO TR4 | 1 | 230 | 229 | 600 | 90.18 | 100.47 | AE2-000 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208021 | MANO TR4 | 1 | 230 | 229 | 600 | 90.17 | 100.46 | AE2-000 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200099 | LAUS | 208045 | LAUS | 3 | 500/230 | 225/229 | 1200 | 98.71 | 100.35 | AE2-000 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220941 | H.RDGE16 | 221010 | COLUMB12 | 1 | 230 | 232 | 876 | 103.55 | 100.27 | AE2-000 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220980 | RAPHAEL | 220999 | BAGLEY2 | 13 | 230 | 232 | 1795 | 98.2 | 100.23 | AE2-000 | BG_P1_2305_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220980 | RAPHAEL | 221000 | BAGLEY | 5 | 230 | 232 | 1795 | 98.19 | 100.23 | AE2-000 | BG_P1_2313_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 2 | 500/230 | 225/232 | 2168 | 97.2 | 100.04 | AE2-000 | PJM_500_BG_P4_5_CNSTN_10_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 2 | 500/230 | 225/232 | 2168 | 97.2 | 100.04 | AE2-000 | PJM_500_BG_P4_5_CNSTN_9_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 228.51 | 244.07 | AE2-020 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 230.6 | 244.07 | AE2-020 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 229.71 | 242.07 | AE2-020 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 227.62 | 242.07 | AE2-020 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 229.65 | 242.02 | AE2-020 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 227.56 | 242.02 | AE2-020 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 229.65 | 242.02 | AE2-020 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 227.55 | 242.02 | AE2-020 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 218.29 | 233.7 | AE2-020 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 217.43 | 231.76 | AE2-020 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 217.37 | 231.71 | AE2-020 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 217.37 | 231.71 | AE2-020 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 214.02 | 230.55 | AE2-020 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 213.16 | 228.59 | AE2-020 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 213.1 | 228.54 | AE2-020 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 213.1 | 228.53 | AE2-020 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 214.83 | 223.22 | AE2-020 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 212.73 | 223.22 | AE2-020 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 203.06 | 213.49 | AE2-020 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 198.79 | 210.17 | AE2-020 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 235463 | 01TANEY | 1 | 138 | 227/201 | 317 | 180.2 | 174.12 | AE2-020 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 235463 | 01TANEY | 1 | 138 | 227/201 | 317 | 180.2 | 174.12 | AE2-020 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 235463 | 01TANEY | 1 | 138 | 227/201 | 317 | 180.05 | 174.03 | AE2-020 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204538 | 27STRABAN | 204544 | 27LINCOLN | 1 | 115 | 227 | 371 | 165.3 | 170.11 | AE2-020 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204538 | 27STRABAN | 204544 | 27LINCOLN | 1 | 115 | 227 | 371 | 165.3 | 170.11 | AE2-020 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 174.78 | 170.08 | AE2-020 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204538 | 27STRABAN | 204544 | 27LINCOLN | 1 | 115 | 227 | 371 | 165.17 | 169.98 | AE2-020 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 173.87 | 168.62 | AE2-020 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 173.86 | 168.62 | AE2-020 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 173.85 | 168.62 | AE2-020 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 165.83 | 167.95 | AE2-020 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204529 | 27GERMANTN | 204538 | 27STRABAN | 1 | 115 | 227 | 371 | 159.49 | 165.56 | AE2-020 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204529 | 27GERMANTN | 204538 | 27STRABAN | 1 | 115 | 227 | 371 | 159.49 | 165.56 | AE2-020 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204529 | 27GERMANTN | 204538 | 27STRABAN | 1 | 115 | 227 | 371 | 159.36 | 165.43 | AE2-020 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 164.07 | 164.88 | AE2-020 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 164.06 | 164.88 | AE2-020 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 164.05 | 164.87 | AE2-020 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3464 | 168.13 | 162.12 | AC2-061 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 165.92 | 160.89 | AE2-020 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 155.45 | 160.28 | AE2-020 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 164.2 | 159.3 | AE2-020 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 164.2 | 159.3 | AE2-020 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 153.75 | 158.95 | AE2-020 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 164.49 | 157.15 | AE2-020 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 150.38 | 155.29 | AE2-020 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 903 | 145.94 | 154.77 | AE2-020 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 155.13 | 153.97 | AE2-020 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 157.8 | 152.62 | AE2-020 | PN_P1-2_PN-500-010T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204539 | 27HUNTRSTN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 334 | 152.46 | 152.2 | AE2-020 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204539 | 27HUNTRSTN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 334 | 152.46 | 152.2 | AE2-020 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204539 | 27HUNTRSTN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 334 | 152.46 | 152.18 | AE2-020 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 903 | 144.49 | 152.17 | AE2-020 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 903 | 144.49 | 152.17 | AE2-020 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 903 | 144.48 | 152.16 | AE2-020 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204539 | 27HUNTRSTN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 334 | 152.29 | 151.99 | AE2-020 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 334 | 152.86 | 151.96 | AE2-020 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 334 | 152.86 | 151.96 | AE2-020 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 334 | 152.85 | 151.95 | AE2-020 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 334 | 152.68 | 151.73 | AE2-020 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 148.16 | 151.58 | AE2-020 | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 148.09 | 151.5 | AE2-020 | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 155.75 | 150.26 | AE2-020 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 145.65 | 150.18 | AE2-020 | AP_P2-3_PE-500-016_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 145.72 | 150.15 | AE2-020 | AP_P2-3_PE-500-015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 155.54 | 150.08 | AE2-020 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 155.57 | 150.06 | AE2-020 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 155.3 | 149.86 | AE2-020 | PECO_P4_NOTTI85_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 155.24 | 149.85 | AE2-020 | PECO_P1-2_220-08_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 155 | 149.83 | AE2-020 | PJM_500_BG_P4_5_CNSTN_L_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 155.17 | 149.78 | AE2-020 | PECO_P4_COOPR125_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.83 | 149.29 | AE2-020 | AP_P1-2_PE-500-001_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.83 | 149.29 | AE2-020 | AP_P1-2_WP-500-DRT17_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.78 | 149.22 | AE2-020 | AP_P2-3_PE-500-018C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3464 | 168.3 | 162.29 | AC2-067 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 147.2 | 147.77 | AE2-020 | BG_P7_GRCTN_CNSTN_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 154.16 | 147.31 | AE2-020 | PECO_P4_PEACH025_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 153.84 | 147.04 | AE2-020 | PECO_P1-2_PBTIE1_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 911 | 150.98 | 145.23 | AE2-020 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204502 | 27JACKSON | 204514 | 27TMI | 1 | 230 | 227 | 781 | 134.85 | 144.24 | AE2-020 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204502 | 27JACKSON | 204514 | 27TMI | 1 | 230 | 227 | 781 | 134.85 | 144.24 | AE2-020 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204502 | 27JACKSON | 204514 | 27TMI | 1 | 230 | 227 | 781 | 134.66 | 144.24 | AE2-020 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204502 | 27JACKSON | 204514 | 27TMI | 1 | 230 | 227 | 781 | 134.84 | 144.22 | AE2-020 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 911 | 150.09 | 143.89 | AE2-020 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 911 | 150.09 | 143.89 | AE2-020 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 911 | 150.07 | 143.89 | AE2-020 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 334 | 145.82 | 143.18 | AE2-020 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204539 | 27HUNTRSTN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 334 | 145.41 | 142.89 | AE2-020 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204538 | 27STRABAN | 204544 | 27LINCOLN | 1 | 115 | 227 | 371 | 141.79 | 142.78 | AE2-020 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204538 | 27STRABAN | 204544 | 27LINCOLN | 1 | 115 | 227 | 371 | 141.79 | 142.78 | AE2-020 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204538 | 27STRABAN | 204544 | 27LINCOLN | 1 | 115 | 227 | 371 | 141.78 | 142.77 | AE2-020 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204538 | 27STRABAN | 204544 | 27LINCOLN | 1 | 115 | 227 | 371 | 141.61 | 142.56 | AE2-020 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 903 | 137.42 | 142.15 | AE2-020 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 142.3 | 141.98 | AE2-020 | PJM_500_BG_P4_5_CNSTN_15_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 1031 | 132.25 | 141.49 | AE2-020 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 1031 | 131.78 | 140.43 | AE2-020 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 1031 | 131.78 | 140.43 | AE2-020 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 1031 | 131.77 | 140.42 | AE2-020 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204529 | 27GERMANTN | 204538 | 27STRABAN | 1 | 115 | 227 | 371 | 135.98 | 138.49 | AE2-020 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204529 | 27GERMANTN | 204538 | 27STRABAN | 1 | 115 | 227 | 371 | 135.98 | 138.49 | AE2-020 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204529 | 27GERMANTN | 204538 | 27STRABAN | 1 | 115 | 227 | 371 | 135.97 | 138.48 | AE2-020 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204529 | 27GERMANTN | 204538 | 27STRABAN | 1 | 115 | 227 | 371 | 135.8 | 138.27 | AE2-020 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 911 | 142.23 | 136.89 | AE2-020 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208078 | SAKR | 1 | 230 | 229 | 903 | 127.19 | 136.63 | AE2-020 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 207922 | BRIS | 207923 | BRISREAC | RX | 230 | 229 | 676 | 126.31 | 136.52 | AE2-020 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 207923 | BRISREAC | 208132 | WHEM TR1 | 1 | 230 | 229 | 676 | 126.31 | 136.52 | AE2-020 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 141.87 | 135.6 | AE2-020 | PECO_P1-2_PBTIE2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 141.59 | 135.56 | AE2-020 | PECO_P4_PEACH205_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208078 | SAKR | 1 | 230 | 229 | 903 | 126.49 | 135.22 | AE2-020 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208078 | SAKR | 1 | 230 | 229 | 903 | 126.49 | 135.22 | AE2-020 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208078 | SAKR | 1 | 230 | 229 | 903 | 126.49 | 135.21 | AE2-020 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 207922 | BRIS | 207923 | BRISREAC | RX | 230 | 229 | 676 | 125.61 | 135.06 | AE2-020 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 207923 | BRISREAC | 208132 | WHEM TR1 | 1 | 230 | 229 | 676 | 125.61 | 135.06 | AE2-020 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 207922 | BRIS | 207923 | BRISREAC | RX | 230 | 229 | 676 | 125.61 | 135.06 | AE2-020 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 207923 | BRISREAC | 208132 | WHEM TR1 | 1 | 230 | 229 | 676 | 125.61 | 135.06 | AE2-020 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 207922 | BRIS | 207923 | BRISREAC | RX | 230 | 229 | 676 | 125.6 | 135.05 | AE2-020 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 207923 | BRISREAC | 208132 | WHEM TR1 | 1 | 230 | 229 | 676 | 125.6 | 135.05 | AE2-020 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 140.74 | 134.55 | AE2-020 | PECO_P4_PEACH055_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204538 | 27STRABAN | 204544 | 27LINCOLN | 1 | 115 | 227 | 371 | 134.65 | 134 | AE2-020 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204502 | 27JACKSON | 204514 | 27TMI | 1 | 230 | 227 | 781 | 127.21 | 133.67 | AE2-020 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220972 | GRANITE1 | 1 | 230 | 232 | 829 | 136.75 | 132.73 | AE2-020 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204538 | 27STRABAN | 204544 | 27LINCOLN | 1 | 115 | 227 | 371 | 128.79 | 132.37 | AE2-020 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220972 | GRANITE1 | 1 | 230 | 232 | 829 | 136.13 | 132.08 | AE2-020 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220972 | GRANITE1 | 1 | 230 | 232 | 829 | 136.13 | 132.08 | AE2-020 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 204529 | 27GERMANTN | 1 | 138/115 | 227 | 453 | 126.1 | 132.05 | AE2-020 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 204529 | 27GERMANTN | 1 | 138/115 | 227 | 453 | 126.1 | 132.05 | AE2-020 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 204529 | 27GERMANTN | 1 | 138/115 | 227 | 453 | 126 | 131.94 | AE2-020 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204538 | 27STRABAN | 204544 | 27LINCOLN | 1 | 115 | 227 | 371 | 128.45 | 131.76 | AE2-020 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 1031 | 126.19 | 131.54 | AE2-020 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220973 | GRANITE6 | 1 | 230 | 232 | 829 | 134.64 | 130.8 | AE2-020 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 136.5 | 130.56 | AE2-020 | PECO_P4_PEACH015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220973 | GRANITE6 | 1 | 230 | 232 | 829 | 134.06 | 130.19 | AE2-020 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220973 | GRANITE6 | 1 | 230 | 232 | 829 | 134.05 | 130.19 | AE2-020 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 129.36 | 129.76 | AE2-020 | BG_P7_GRCTN_CNSTN_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 127.27 | 129.76 | AE2-020 | BG_P7_GRCTN_CNSTN_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204529 | 27GERMANTN | 204538 | 27STRABAN | 1 | 115 | 227 | 371 | 128.84 | 129.66 | AE2-020 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208020 | MANO TR3 | 1 | 230 | 229 | 793 | 114.24 | 129.04 | AE2-020 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 134.88 | 128.94 | AE2-020 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 130.49 | 128.73 | AE2-020 | DVP_P4-2: 514T595_SRT-SW |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204529 | 27GERMANTN | 204538 | 27STRABAN | 1 | 115 | 227 | 371 | 122.98 | 127.91 | AE2-020 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220953 | HOWARD12 | 220972 | GRANITE1 | 1 | 230 | 232 | 772 | 131.83 | 127.79 | AE2-020 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208020 | MANO TR3 | 1 | 230 | 229 | 793 | 113.46 | 127.55 | AE2-020 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208020 | MANO TR3 | 1 | 230 | 229 | 793 | 113.46 | 127.55 | AE2-020 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208020 | MANO TR3 | 1 | 230 | 229 | 793 | 113.46 | 127.54 | AE2-020 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204529 | 27GERMANTN | 204538 | 27STRABAN | 1 | 115 | 227 | 371 | 122.64 | 127.31 | AE2-020 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 128.78 | 127.05 | AE2-020 | DVP_P4-2: 51482_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220954 | HOWARD32 | 220973 | GRANITE6 | 1 | 230 | 232 | 772 | 130.56 | 126.98 | AE2-020 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 128.78 | 126.96 | AE2-020 | AP_P1-2_PE-500-407T_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 128.78 | 126.96 | AE2-020 | DVP_P1-2: LN 514_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220953 | HOWARD12 | 220972 | GRANITE1 | 1 | 230 | 232 | 772 | 130.93 | 126.83 | AE2-020 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220953 | HOWARD12 | 220972 | GRANITE1 | 1 | 230 | 232 | 772 | 130.93 | 126.83 | AE2-020 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 207922 | BRIS | 207923 | BRISREAC | RX | 230 | 229 | 676 | 120.51 | 126.81 | AE2-020 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 207923 | BRISREAC | 208132 | WHEM TR1 | 1 | 230 | 229 | 676 | 120.51 | 126.81 | AE2-020 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 911 | 124.07 | 126.66 | AE2-020 | BG_P7_GRCTN_CNSTN_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220954 | HOWARD32 | 220973 | GRANITE6 | 1 | 230 | 232 | 772 | 129.78 | 126.15 | AE2-020 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220954 | HOWARD32 | 220973 | GRANITE6 | 1 | 230 | 232 | 772 | 129.78 | 126.15 | AE2-020 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 793 | 127.91 | 126.15 | AE2-020 | DVP_P4-2: 514T595_SRT-SW |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 2 | 230 | 233 | 793 | 127.91 | 126.15 | AE2-020 | DVP_P4-2: 514T595_SRT-SW |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 120.23 | 125.26 | AE2-020 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 122.32 | 125.26 | AE2-020 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208078 | SAKR | 1 | 230 | 229 | 903 | 119.23 | 125.26 | AE2-020 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208031 | MLWD TR2 | 1 | 230 | 229 | 911 | 114.31 | 125.09 | AE2-020 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 122.14 | 125.05 | AE2-020 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 120.05 | 125.05 | AE2-020 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 122.14 | 125.05 | AE2-020 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 120.05 | 125.05 | AE2-020 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 2 | 230 | 233 | 793 | 126.69 | 124.97 | AE2-020 | DVP_P4-2: 51482_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 793 | 126.69 | 124.97 | AE2-020 | DVP_P4-2: 51482_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 793 | 126.69 | 124.89 | AE2-020 | DVP_P1-2: LN 514_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 2 | 230 | 233 | 793 | 126.69 | 124.89 | AE2-020 | DVP_P1-2: LN 514_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 2 | 230 | 233 | 793 | 126.69 | 124.89 | AE2-020 | AP_P1-2_PE-500-407T_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 793 | 126.69 | 124.89 | AE2-020 | AP_P1-2_PE-500-407T_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204512 | 27S.RDG | 204693 | 27BOONETOWN | 1 | 230 | 227 | 607 | 108.73 | 124.85 | AE2-020 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204512 | 27S.RDG | 204693 | 27BOONETOWN | 1 | 230 | 227 | 607 | 108.59 | 124.11 | AE2-020 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204512 | 27S.RDG | 204693 | 27BOONETOWN | 1 | 230 | 227 | 607 | 108.56 | 124.09 | AE2-020 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204512 | 27S.RDG | 204693 | 27BOONETOWN | 1 | 230 | 227 | 607 | 108.56 | 124.09 | AE2-020 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208031 | MLWD TR2 | 1 | 230 | 229 | 911 | 113.63 | 123.81 | AE2-020 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208031 | MLWD TR2 | 1 | 230 | 229 | 911 | 113.63 | 123.81 | AE2-020 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208031 | MLWD TR2 | 1 | 230 | 229 | 911 | 113.63 | 123.8 | AE2-020 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200025 | W CHAPEL | 1 | 500 | 225 | 1732 | 125.33 | 123.6 | AE2-020 | PEPCO_P4_PP41_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 120.53 | 123.01 | AE2-020 | BG_P7_GRCTN_CNSTN_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 121.32 | 122 | AE2-020 | PJM_500_BG_P4_5_CNSTN_15_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 119.23 | 122 | AE2-020 | PJM_500_BG_P4_5_CNSTN_15_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208131 | WHEM | 208132 | WHEM TR1 | 1 | 230 | 229 | 691 | 110.47 | 121.06 | AE2-020 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220965 | NEAST339 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 121.12 | 120.5 | AE2-020 | BG_P1_2315_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 911 | 119.29 | 120.36 | AE2-020 | PJM_500_BG_P4_5_CNSTN_15_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 125.84 | 120.34 | AE2-020 | PECO_P4_PEACH225_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220965 | NEAST339 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 120.68 | 120.27 | AE2-020 | BG_P4_5_NEAST_17_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220965 | NEAST339 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 120.84 | 120.27 | AE2-020 | BG_P4_5_NEAST_15_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3464 | 168.1 | 162.09 | AC2-079 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3464 | 168.21 | 162.2 | AC2-084 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 115.95 | 119.8 | AE2-020 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208131 | WHEM | 208132 | WHEM TR1 | 1 | 230 | 229 | 691 | 109.8 | 119.71 | AE2-020 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208131 | WHEM | 208132 | WHEM TR1 | 1 | 230 | 229 | 691 | 109.8 | 119.71 | AE2-020 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208131 | WHEM | 208132 | WHEM TR1 | 1 | 230 | 229 | 691 | 109.79 | 119.7 | AE2-020 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220979 | NEAST317 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 120.18 | 119.61 | AE2-020 | BG_P1_2337_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 115.61 | 119.45 | AE2-020 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 115.61 | 119.4 | AE2-020 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 115.61 | 119.4 | AE2-020 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220979 | NEAST317 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 119.83 | 119.33 | AE2-020 | BG_P4_5_NEAST_37_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220979 | NEAST317 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 119.83 | 119.33 | AE2-020 | BG_P4_5_NEAST_39_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 116.26 | 119.17 | AE2-020 | BG_P7_GRCTN_CNSTN_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 115.27 | 119.06 | AE2-020 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 115.27 | 119.06 | AE2-020 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 113.74 | 118.68 | AE2-020 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 113.56 | 118.48 | AE2-020 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 113.56 | 118.48 | AE2-020 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200532 | 26ROXBURY | 200520 | 26ROXBURY | 2 | 138/115 | 226 | 435 | 102.37 | 118.23 | AE2-020 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200532 | 26ROXBURY | 200520 | 26ROXBURY | 2 | 138/115 | 226 | 435 | 102.37 | 118.22 | AE2-020 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200532 | 26ROXBURY | 200520 | 26ROXBURY | 2 | 138/115 | 226 | 435 | 102.37 | 118.22 | AE2-020 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200532 | 26ROXBURY | 200520 | 26ROXBURY | 2 | 138/115 | 226 | 435 | 102.21 | 118.05 | AE2-020 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 119.17 | 117.9 | AE2-020 | PL_04_P12_000260_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 119.17 | 117.9 | AE2-020 | PL_04_P42_000564_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3464 | 168.24 | 162.22 | AC2-088 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204512 | 27S.RDG | 204693 | 27BOONETOWN | 1 | 230 | 227 | 607 | 106.8 | 117.11 | AE2-020 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 118.96 | 117.03 | AE2-020 | AP_P2-3_PE-500-019C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208020 | MANO TR3 | 1 | 230 | 229 | 793 | 106.28 | 116.9 | AE2-020 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208020 | MANO TR3 | 208031 | MLWD TR2 | 1 | 230 | 229 | 903 | 104.31 | 116.22 | AE2-020 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 2 | 500/230 | 225/232 | 2168 | 110.73 | 116.2 | AE2-020 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 2 | 500/230 | 225/232 | 2168 | 110.56 | 115.99 | AE2-020 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 2 | 500/230 | 225/232 | 2168 | 110.56 | 115.99 | AE2-020 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 1 | 500/230 | 225/232 | 2168 | 110.5 | 115.95 | AE2-020 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 1 | 500/230 | 225/232 | 2168 | 110.32 | 115.74 | AE2-020 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 1 | 500/230 | 225/232 | 2168 | 110.32 | 115.74 | AE2-020 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220964 | GRACETON | 220999 | BAGLEY2 | 13 | 230 | 232 | 1795 | 114.49 | 115.61 | AE2-020 | BG_P4_5_GRCTN_3T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 112.77 | 115.58 | AE2-020 | PJM_500_BG_P4_5_CNSTN_15_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208020 | MANO TR3 | 208031 | MLWD TR2 | 1 | 230 | 229 | 903 | 103.65 | 115.06 | AE2-020 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208020 | MANO TR3 | 208031 | MLWD TR2 | 1 | 230 | 229 | 903 | 103.65 | 115.06 | AE2-020 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208020 | MANO TR3 | 208031 | MLWD TR2 | 1 | 230 | 229 | 903 | 103.64 | 115.06 | AE2-020 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 109.47 | 114.86 | AE2-020 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 109.29 | 114.66 | AE2-020 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 109.29 | 114.66 | AE2-020 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208031 | MLWD TR2 | 1 | 230 | 229 | 911 | 106.88 | 114.39 | AE2-020 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 114.59 | 113.47 | AE2-020 | BG_P4_5_CNSTN_14_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 2 | 500/230 | 225/232 | 2168 | 109.36 | 112.74 | AE2-020 | PJM_500_BG_P4_5_CNSTN_15_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3464 | 168.23 | 162.22 | AC2-100 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 107.52 | 112.56 | AE2-020 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 107.39 | 112.42 | AE2-020 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208131 | WHEM | 208133 | WHEM TR2 | 1 | 230 | 229 | 691 | 102.95 | 112.42 | AE2-020 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220980 | RAPHAEL | 220999 | BAGLEY2 | 13 | 230 | 232 | 1795 | 110.05 | 112.37 | AE2-020 | BG_P4_5_GRCTN_3T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208131 | WHEM | 208132 | WHEM TR1 | 1 | 230 | 229 | 691 | 105.02 | 112.19 | AE2-020 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 108.5 | 111.88 | AE2-020 | PJM_500_BG_P4_5_CNSTN_15_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 793 | 114.33 | 111.69 | AE2-020 | PEPCO_P4_PP19_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208131 | WHEM | 208133 | WHEM TR2 | 1 | 230 | 229 | 691 | 102.28 | 111.09 | AE2-020 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208131 | WHEM | 208133 | WHEM TR2 | 1 | 230 | 229 | 691 | 102.28 | 111.09 | AE2-020 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208131 | WHEM | 208133 | WHEM TR2 | 1 | 230 | 229 | 691 | 102.27 | 111.08 | AE2-020 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200532 | 26ROXBURY | 200520 | 26ROXBURY | 2 | 138/115 | 226 | 435 | 97.23 | 110.69 | AE2-020 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204512 | 27S.RDG | 204693 | 27BOONETOWN | 1 | 230 | 227 | 607 | 110.95 | 110.27 | AE2-020 | PL_04_P42_101307_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204512 | 27S.RDG | 204693 | 27BOONETOWN | 1 | 230 | 227 | 607 | 110.96 | 110.22 | AE2-020 | PL_24_P42_102306_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 204529 | 27GERMANTN | 1 | 138/115 | 227 | 453 | 106.84 | 109.54 | AE2-020 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 204529 | 27GERMANTN | 1 | 138/115 | 227 | 453 | 106.84 | 109.54 | AE2-020 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 204529 | 27GERMANTN | 1 | 138/115 | 227 | 453 | 106.84 | 109.53 | AE2-020 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 204529 | 27GERMANTN | 1 | 138/115 | 227 | 453 | 106.7 | 109.36 | AE2-020 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220973 | GRANITE6 | 1 | 230 | 232 | 829 | 110.27 | 109.09 | AE2-020 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 793 | 110.86 | 108.98 | AE2-020 | AP_P2-3_PE-500-019C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 2 | 230 | 233 | 793 | 110.86 | 108.98 | AE2-020 | AP_P2-3_PE-500-019C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220965 | NEAST339 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 109.62 | 108.18 | AE2-020 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220965 | NEAST339 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 109.53 | 108.07 | AE2-020 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220965 | NEAST339 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 109.52 | 108.07 | AE2-020 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220972 | GRANITE1 | 1 | 230 | 232 | 829 | 109.42 | 108.01 | AE2-020 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208021 | MANO TR4 | 208133 | WHEM TR2 | 2 | 230 | 229 | 593 | 97.63 | 107.25 | AE2-020 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 102.63 | 106.98 | AE2-020 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 102.54 | 106.9 | AE2-020 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200099 | LAUS | 208045 | LAUS | 3 | 500/230 | 225/229 | 1200 | 104.63 | 106.45 | AE2-020 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220972 | GRANITE1 | 1 | 230 | 232 | 829 | 107.39 | 106.05 | AE2-020 | BG_P4_5_NW230-4_2326_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208020 | MANO TR3 | 208031 | MLWD TR2 | 1 | 230 | 229 | 903 | 97.28 | 105.98 | AE2-020 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200099 | LAUS | 208045 | LAUS | 3 | 500/230 | 225/229 | 1200 | 104.34 | 105.97 | AE2-020 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200099 | LAUS | 208045 | LAUS | 3 | 500/230 | 225/229 | 1200 | 104.34 | 105.97 | AE2-020 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200099 | LAUS | 208045 | LAUS | 3 | 500/230 | 225/229 | 1200 | 104.33 | 105.95 | AE2-020 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 103.72 | 105.83 | AE2-020 | BG_P1_2322_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208021 | MANO TR4 | 208133 | WHEM TR2 | 2 | 230 | 229 | 593 | 96.87 | 105.81 | AE2-020 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208021 | MANO TR4 | 208133 | WHEM TR2 | 2 | 230 | 229 | 593 | 96.87 | 105.81 | AE2-020 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208021 | MANO TR4 | 208133 | WHEM TR2 | 2 | 230 | 229 | 593 | 96.85 | 105.79 | AE2-020 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 103.64 | 105.75 | AE2-020 | BG_P1_2310_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 103.65 | 105.71 | AE2-020 | BG_P4_5_NW2322_230-4_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 103.58 | 105.67 | AE2-020 | BG_P4_5_NW2310_230-5_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220973 | GRANITE6 | 1 | 230 | 232 | 829 | 107.07 | 105.53 | AE2-020 | BG_P4_5_NW230-5_2311_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220979 | NEAST317 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 106.45 | 105.08 | AE2-020 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220979 | NEAST317 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 106.36 | 104.96 | AE2-020 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220979 | NEAST317 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 106.36 | 104.96 | AE2-020 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204520 | 27ALLEN | 208142 | WIGR-115 | 1 | 115 | 227/229 | 351.4 | 96.35 | 104.66 | AE2-020 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 102.28 | 104.43 | AE2-020 | BG_P4_5_NW230-2_2322_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 99.89 | 104.36 | AE2-020 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 99.89 | 104.36 | AE2-020 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 99.89 | 104.36 | AE2-020 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 102.18 | 104.31 | AE2-020 | BG_P4_5_NW2371_2310_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 102.18 | 104.31 | AE2-020 | BG_P4_5_NW230-3_2310_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220973 | GRANITE6 | 1 | 230 | 232 | 829 | 104.96 | 103.94 | AE2-020 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208131 | WHEM | 208133 | WHEM TR2 | 1 | 230 | 229 | 691 | 97.5 | 103.84 | AE2-020 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220965 | NEAST339 | 220977 | RIV2339 | 1 | 230 | 232 | 991 | 104.94 | 103.47 | AE2-020 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220966 | RIV2317 | 220979 | NEAST317 | 1 | 230 | 232 | 940 | 104.5 | 103.43 | AE2-020 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220965 | NEAST339 | 220977 | RIV2339 | 1 | 230 | 232 | 991 | 104.89 | 103.42 | AE2-020 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220965 | NEAST339 | 220977 | RIV2339 | 1 | 230 | 232 | 991 | 104.89 | 103.42 | AE2-020 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 101.31 | 103.38 | AE2-020 | BG_P4_5_CNSTN_14_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220966 | RIV2317 | 220979 | NEAST317 | 1 | 230 | 232 | 940 | 104.45 | 103.37 | AE2-020 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220966 | RIV2317 | 220979 | NEAST317 | 1 | 230 | 232 | 940 | 104.45 | 103.37 | AE2-020 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220965 | NEAST339 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 103.87 | 103.29 | AE2-020 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220964 | GRACETON | 220999 | BAGLEY2 | 13 | 230 | 232 | 1795 | 102.46 | 103.28 | AE2-020 | BG_P1_2305_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220964 | GRACETON | 221000 | BAGLEY | 5 | 230 | 232 | 1795 | 102.46 | 103.28 | AE2-020 | BG_P1_2313_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220972 | GRANITE1 | 1 | 230 | 232 | 829 | 104.38 | 103.17 | AE2-020 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 99.01 | 103.04 | AE2-020 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 2 | 500/230 | 225/232 | 2168 | 99.77 | 102.59 | AE2-020 | BG_P1_CNSTN_500-2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 2 | 500/230 | 225/232 | 2168 | 99.77 | 102.59 | AE2-020 | PJM_500_BG_P2_CNSTN_230-N_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 1 | 500/230 | 225/232 | 2168 | 99.66 | 102.48 | AE2-020 | BG_P1_CNSTN_500-4_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 1 | 500/230 | 225/232 | 2168 | 99.66 | 102.48 | AE2-020 | PJM_500_BG_P2_CNSTN_230-S_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 204529 | 27GERMANTN | 1 | 138/115 | 227 | 453 | 101 | 102.27 | AE2-020 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 223960 | BRG 1T 230 | 1 | 500/230 | 225/233 | 1498 | 101.29 | 101.74 | AE2-020 | PEPCO_P4_PP41_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208021 | MANO TR4 | 1 | 230 | 229 | 600 | 90.68 | 101.68 | AE2-020 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 99.06 | 101.6 | AE2-020 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 204529 | 27GERMANTN | 1 | 138/115 | 227 | 453 | 96.2 | 101.22 | AE2-020 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220979 | NEAST317 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 101.71 | 101.14 | AE2-020 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220972 | GRANITE1 | 1 | 230 | 232 | 829 | 102.06 | 100.97 | AE2-020 | BG_P4_5_GRNITE26_32_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 204529 | 27GERMANTN | 1 | 138/115 | 227 | 453 | 95.92 | 100.73 | AE2-020 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220973 | GRANITE6 | 1 | 230 | 232 | 829 | 101.88 | 100.52 | AE2-020 | BBG_P1_2311_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220972 | GRANITE1 | 1 | 230 | 232 | 829 | 101.58 | 100.47 | AE2-020 | BG_P1_2326_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220973 | GRANITE6 | 1 | 230 | 232 | 829 | 101.29 | 100.44 | AE2-020 | BG_P1_2312_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220973 | GRANITE6 | 1 | 230 | 232 | 829 | 101.44 | 100.42 | AE2-020 | BG_P4_5_GRNITE11_12_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220980 | RAPHAEL | 220999 | BAGLEY2 | 13 | 230 | 232 | 1795 | 98.02 | 100.04 | AE2-020 | BG_P1_2305_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220980 | RAPHAEL | 221000 | BAGLEY | 5 | 230 | 232 | 1795 | 98.02 | 100.04 | AE2-020 | BG_P1_2313_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200099 | LAUS | 208045 | LAUS | 3 | 500/230 | 225/229 | 1200 | 98.38 | 100.04 | AE2-020 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 228.51 | 244.07 | AE2-021 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 230.6 | 244.07 | AE2-021 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 229.71 | 242.07 | AE2-021 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 227.62 | 242.07 | AE2-021 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 229.65 | 242.02 | AE2-021 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 227.56 | 242.02 | AE2-021 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 229.65 | 242.02 | AE2-021 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 227.55 | 242.02 | AE2-021 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 218.29 | 233.7 | AE2-021 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 217.43 | 231.76 | AE2-021 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 217.37 | 231.71 | AE2-021 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 217.37 | 231.71 | AE2-021 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 214.02 | 230.55 | AE2-021 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 213.16 | 228.59 | AE2-021 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 213.1 | 228.54 | AE2-021 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 213.1 | 228.53 | AE2-021 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 214.83 | 223.22 | AE2-021 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 212.73 | 223.22 | AE2-021 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 203.06 | 213.49 | AE2-021 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 198.79 | 210.17 | AE2-021 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 235463 | 01TANEY | 1 | 138 | 227/201 | 317 | 180.2 | 174.12 | AE2-021 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 235463 | 01TANEY | 1 | 138 | 227/201 | 317 | 180.2 | 174.12 | AE2-021 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 235463 | 01TANEY | 1 | 138 | 227/201 | 317 | 180.05 | 174.03 | AE2-021 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204538 | 27STRABAN | 204544 | 27LINCOLN | 1 | 115 | 227 | 371 | 165.3 | 170.11 | AE2-021 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204538 | 27STRABAN | 204544 | 27LINCOLN | 1 | 115 | 227 | 371 | 165.3 | 170.11 | AE2-021 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 174.78 | 170.08 | AE2-021 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204538 | 27STRABAN | 204544 | 27LINCOLN | 1 | 115 | 227 | 371 | 165.17 | 169.98 | AE2-021 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 173.87 | 168.62 | AE2-021 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 173.86 | 168.62 | AE2-021 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 173.85 | 168.62 | AE2-021 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 165.83 | 167.95 | AE2-021 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204529 | 27GERMANTN | 204538 | 27STRABAN | 1 | 115 | 227 | 371 | 159.49 | 165.56 | AE2-021 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204529 | 27GERMANTN | 204538 | 27STRABAN | 1 | 115 | 227 | 371 | 159.49 | 165.56 | AE2-021 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204529 | 27GERMANTN | 204538 | 27STRABAN | 1 | 115 | 227 | 371 | 159.36 | 165.43 | AE2-021 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 164.07 | 164.88 | AE2-021 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 164.06 | 164.88 | AE2-021 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 164.05 | 164.87 | AE2-021 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3464 | 168.05 | 162.04 | AC2-103 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 165.92 | 160.89 | AE2-021 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 155.45 | 160.28 | AE2-021 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 164.2 | 159.3 | AE2-021 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 164.2 | 159.3 | AE2-021 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 153.75 | 158.95 | AE2-021 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 164.49 | 157.15 | AE2-021 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 150.38 | 155.29 | AE2-021 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 903 | 145.94 | 154.77 | AE2-021 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 155.13 | 153.97 | AE2-021 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 157.8 | 152.62 | AE2-021 | PN_P1-2_PN-500-010T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204539 | 27HUNTRSTN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 334 | 152.46 | 152.2 | AE2-021 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204539 | 27HUNTRSTN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 334 | 152.46 | 152.2 | AE2-021 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204539 | 27HUNTRSTN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 334 | 152.46 | 152.18 | AE2-021 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 903 | 144.49 | 152.17 | AE2-021 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 903 | 144.49 | 152.17 | AE2-021 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 903 | 144.48 | 152.16 | AE2-021 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204539 | 27HUNTRSTN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 334 | 152.29 | 151.99 | AE2-021 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 334 | 152.86 | 151.96 | AE2-021 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 334 | 152.86 | 151.96 | AE2-021 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 334 | 152.85 | 151.95 | AE2-021 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 334 | 152.68 | 151.73 | AE2-021 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 148.16 | 151.58 | AE2-021 | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 148.09 | 151.5 | AE2-021 | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 155.75 | 150.26 | AE2-021 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 145.65 | 150.18 | AE2-021 | AP_P2-3_PE-500-016_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 145.72 | 150.15 | AE2-021 | AP_P2-3_PE-500-015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 155.54 | 150.08 | AE2-021 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 155.57 | 150.06 | AE2-021 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 155.3 | 149.86 | AE2-021 | PECO_P4_NOTTI85_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 155.24 | 149.85 | AE2-021 | PECO_P1-2_220-08_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 155 | 149.83 | AE2-021 | PJM_500_BG_P4_5_CNSTN_L_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 155.17 | 149.78 | AE2-021 | PECO_P4_COOPR125_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.83 | 149.29 | AE2-021 | AP_P1-2_PE-500-001_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.83 | 149.29 | AE2-021 | AP_P1-2_WP-500-DRT17_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.78 | 149.22 | AE2-021 | AP_P2-3_PE-500-018C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3464 | 168.24 | 162.22 | AC2-111 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 147.2 | 147.77 | AE2-021 | BG_P7_GRCTN_CNSTN_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 154.16 | 147.31 | AE2-021 | PECO_P4_PEACH025_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 153.84 | 147.04 | AE2-021 | PECO_P1-2_PBTIE1_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 911 | 150.98 | 145.23 | AE2-021 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204502 | 27JACKSON | 204514 | 27TMI | 1 | 230 | 227 | 781 | 134.85 | 144.24 | AE2-021 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204502 | 27JACKSON | 204514 | 27TMI | 1 | 230 | 227 | 781 | 134.85 | 144.24 | AE2-021 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204502 | 27JACKSON | 204514 | 27TMI | 1 | 230 | 227 | 781 | 134.66 | 144.24 | AE2-021 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204502 | 27JACKSON | 204514 | 27TMI | 1 | 230 | 227 | 781 | 134.84 | 144.22 | AE2-021 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 911 | 150.09 | 143.89 | AE2-021 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 911 | 150.09 | 143.89 | AE2-021 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 911 | 150.07 | 143.89 | AE2-021 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 334 | 145.82 | 143.18 | AE2-021 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204539 | 27HUNTRSTN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 334 | 145.41 | 142.89 | AE2-021 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204538 | 27STRABAN | 204544 | 27LINCOLN | 1 | 115 | 227 | 371 | 141.79 | 142.78 | AE2-021 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204538 | 27STRABAN | 204544 | 27LINCOLN | 1 | 115 | 227 | 371 | 141.79 | 142.78 | AE2-021 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204538 | 27STRABAN | 204544 | 27LINCOLN | 1 | 115 | 227 | 371 | 141.78 | 142.77 | AE2-021 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204538 | 27STRABAN | 204544 | 27LINCOLN | 1 | 115 | 227 | 371 | 141.61 | 142.56 | AE2-021 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 903 | 137.42 | 142.15 | AE2-021 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 142.3 | 141.98 | AE2-021 | PJM_500_BG_P4_5_CNSTN_15_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 1031 | 132.25 | 141.49 | AE2-021 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 1031 | 131.78 | 140.43 | AE2-021 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 1031 | 131.78 | 140.43 | AE2-021 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 1031 | 131.77 | 140.42 | AE2-021 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204529 | 27GERMANTN | 204538 | 27STRABAN | 1 | 115 | 227 | 371 | 135.98 | 138.49 | AE2-021 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204529 | 27GERMANTN | 204538 | 27STRABAN | 1 | 115 | 227 | 371 | 135.98 | 138.49 | AE2-021 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204529 | 27GERMANTN | 204538 | 27STRABAN | 1 | 115 | 227 | 371 | 135.97 | 138.48 | AE2-021 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204529 | 27GERMANTN | 204538 | 27STRABAN | 1 | 115 | 227 | 371 | 135.8 | 138.27 | AE2-021 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 911 | 142.23 | 136.89 | AE2-021 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208078 | SAKR | 1 | 230 | 229 | 903 | 127.19 | 136.63 | AE2-021 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 207922 | BRIS | 207923 | BRISREAC | RX | 230 | 229 | 676 | 126.31 | 136.52 | AE2-021 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 207923 | BRISREAC | 208132 | WHEM TR1 | 1 | 230 | 229 | 676 | 126.31 | 136.52 | AE2-021 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 141.87 | 135.6 | AE2-021 | PECO_P1-2_PBTIE2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 141.59 | 135.56 | AE2-021 | PECO_P4_PEACH205_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208078 | SAKR | 1 | 230 | 229 | 903 | 126.49 | 135.22 | AE2-021 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208078 | SAKR | 1 | 230 | 229 | 903 | 126.49 | 135.22 | AE2-021 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208078 | SAKR | 1 | 230 | 229 | 903 | 126.49 | 135.21 | AE2-021 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 207922 | BRIS | 207923 | BRISREAC | RX | 230 | 229 | 676 | 125.61 | 135.06 | AE2-021 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 207923 | BRISREAC | 208132 | WHEM TR1 | 1 | 230 | 229 | 676 | 125.61 | 135.06 | AE2-021 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 207922 | BRIS | 207923 | BRISREAC | RX | 230 | 229 | 676 | 125.61 | 135.06 | AE2-021 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 207923 | BRISREAC | 208132 | WHEM TR1 | 1 | 230 | 229 | 676 | 125.61 | 135.06 | AE2-021 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 207922 | BRIS | 207923 | BRISREAC | RX | 230 | 229 | 676 | 125.6 | 135.05 | AE2-021 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 207923 | BRISREAC | 208132 | WHEM TR1 | 1 | 230 | 229 | 676 | 125.6 | 135.05 | AE2-021 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 140.74 | 134.55 | AE2-021 | PECO_P4_PEACH055_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204538 | 27STRABAN | 204544 | 27LINCOLN | 1 | 115 | 227 | 371 | 134.65 | 134 | AE2-021 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204502 | 27JACKSON | 204514 | 27TMI | 1 | 230 | 227 | 781 | 127.21 | 133.67 | AE2-021 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220972 | GRANITE1 | 1 | 230 | 232 | 829 | 136.75 | 132.73 | AE2-021 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204538 | 27STRABAN | 204544 | 27LINCOLN | 1 | 115 | 227 | 371 | 128.79 | 132.37 | AE2-021 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220972 | GRANITE1 | 1 | 230 | 232 | 829 | 136.13 | 132.08 | AE2-021 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220972 | GRANITE1 | 1 | 230 | 232 | 829 | 136.13 | 132.08 | AE2-021 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 204529 | 27GERMANTN | 1 | 138/115 | 227 | 453 | 126.1 | 132.05 | AE2-021 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 204529 | 27GERMANTN | 1 | 138/115 | 227 | 453 | 126.1 | 132.05 | AE2-021 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 204529 | 27GERMANTN | 1 | 138/115 | 227 | 453 | 126 | 131.94 | AE2-021 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204538 | 27STRABAN | 204544 | 27LINCOLN | 1 | 115 | 227 | 371 | 128.45 | 131.76 | AE2-021 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 1031 | 126.19 | 131.54 | AE2-021 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220973 | GRANITE6 | 1 | 230 | 232 | 829 | 134.64 | 130.8 | AE2-021 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 136.5 | 130.56 | AE2-021 | PECO_P4_PEACH015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220973 | GRANITE6 | 1 | 230 | 232 | 829 | 134.06 | 130.19 | AE2-021 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220973 | GRANITE6 | 1 | 230 | 232 | 829 | 134.05 | 130.19 | AE2-021 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 129.36 | 129.76 | AE2-021 | BG_P7_GRCTN_CNSTN_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 127.27 | 129.76 | AE2-021 | BG_P7_GRCTN_CNSTN_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204529 | 27GERMANTN | 204538 | 27STRABAN | 1 | 115 | 227 | 371 | 128.84 | 129.66 | AE2-021 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208020 | MANO TR3 | 1 | 230 | 229 | 793 | 114.24 | 129.04 | AE2-021 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 134.88 | 128.94 | AE2-021 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 130.49 | 128.73 | AE2-021 | DVP_P4-2: 514T595_SRT-SW |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204529 | 27GERMANTN | 204538 | 27STRABAN | 1 | 115 | 227 | 371 | 122.98 | 127.91 | AE2-021 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220953 | HOWARD12 | 220972 | GRANITE1 | 1 | 230 | 232 | 772 | 131.83 | 127.79 | AE2-021 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208020 | MANO TR3 | 1 | 230 | 229 | 793 | 113.46 | 127.55 | AE2-021 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208020 | MANO TR3 | 1 | 230 | 229 | 793 | 113.46 | 127.55 | AE2-021 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208020 | MANO TR3 | 1 | 230 | 229 | 793 | 113.46 | 127.54 | AE2-021 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204529 | 27GERMANTN | 204538 | 27STRABAN | 1 | 115 | 227 | 371 | 122.64 | 127.31 | AE2-021 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 128.78 | 127.05 | AE2-021 | DVP_P4-2: 51482_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220954 | HOWARD32 | 220973 | GRANITE6 | 1 | 230 | 232 | 772 | 130.56 | 126.98 | AE2-021 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 128.78 | 126.96 | AE2-021 | AP_P1-2_PE-500-407T_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 128.78 | 126.96 | AE2-021 | DVP_P1-2: LN 514_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220953 | HOWARD12 | 220972 | GRANITE1 | 1 | 230 | 232 | 772 | 130.93 | 126.83 | AE2-021 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220953 | HOWARD12 | 220972 | GRANITE1 | 1 | 230 | 232 | 772 | 130.93 | 126.83 | AE2-021 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 207922 | BRIS | 207923 | BRISREAC | RX | 230 | 229 | 676 | 120.51 | 126.81 | AE2-021 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 207923 | BRISREAC | 208132 | WHEM TR1 | 1 | 230 | 229 | 676 | 120.51 | 126.81 | AE2-021 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 911 | 124.07 | 126.66 | AE2-021 | BG_P7_GRCTN_CNSTN_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220954 | HOWARD32 | 220973 | GRANITE6 | 1 | 230 | 232 | 772 | 129.78 | 126.15 | AE2-021 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220954 | HOWARD32 | 220973 | GRANITE6 | 1 | 230 | 232 | 772 | 129.78 | 126.15 | AE2-021 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 793 | 127.91 | 126.15 | AE2-021 | DVP_P4-2: 514T595_SRT-SW |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 2 | 230 | 233 | 793 | 127.91 | 126.15 | AE2-021 | DVP_P4-2: 514T595_SRT-SW |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 120.23 | 125.26 | AE2-021 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 122.32 | 125.26 | AE2-021 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208078 | SAKR | 1 | 230 | 229 | 903 | 119.23 | 125.26 | AE2-021 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208031 | MLWD TR2 | 1 | 230 | 229 | 911 | 114.31 | 125.09 | AE2-021 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 122.14 | 125.05 | AE2-021 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 120.05 | 125.05 | AE2-021 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 122.14 | 125.05 | AE2-021 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 120.05 | 125.05 | AE2-021 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 2 | 230 | 233 | 793 | 126.69 | 124.97 | AE2-021 | DVP_P4-2: 51482_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 793 | 126.69 | 124.97 | AE2-021 | DVP_P4-2: 51482_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 793 | 126.69 | 124.89 | AE2-021 | DVP_P1-2: LN 514_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 2 | 230 | 233 | 793 | 126.69 | 124.89 | AE2-021 | DVP_P1-2: LN 514_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 2 | 230 | 233 | 793 | 126.69 | 124.89 | AE2-021 | AP_P1-2_PE-500-407T_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 793 | 126.69 | 124.89 | AE2-021 | AP_P1-2_PE-500-407T_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204512 | 27S.RDG | 204693 | 27BOONETOWN | 1 | 230 | 227 | 607 | 108.73 | 124.85 | AE2-021 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204512 | 27S.RDG | 204693 | 27BOONETOWN | 1 | 230 | 227 | 607 | 108.59 | 124.11 | AE2-021 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204512 | 27S.RDG | 204693 | 27BOONETOWN | 1 | 230 | 227 | 607 | 108.56 | 124.09 | AE2-021 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204512 | 27S.RDG | 204693 | 27BOONETOWN | 1 | 230 | 227 | 607 | 108.56 | 124.09 | AE2-021 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208031 | MLWD TR2 | 1 | 230 | 229 | 911 | 113.63 | 123.81 | AE2-021 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208031 | MLWD TR2 | 1 | 230 | 229 | 911 | 113.63 | 123.81 | AE2-021 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208031 | MLWD TR2 | 1 | 230 | 229 | 911 | 113.63 | 123.8 | AE2-021 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200025 | W CHAPEL | 1 | 500 | 225 | 1732 | 125.33 | 123.6 | AE2-021 | PEPCO_P4_PP41_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 120.53 | 123.01 | AE2-021 | BG_P7_GRCTN_CNSTN_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 121.32 | 122 | AE2-021 | PJM_500_BG_P4_5_CNSTN_15_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 119.23 | 122 | AE2-021 | PJM_500_BG_P4_5_CNSTN_15_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208131 | WHEM | 208132 | WHEM TR1 | 1 | 230 | 229 | 691 | 110.47 | 121.06 | AE2-021 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220965 | NEAST339 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 121.12 | 120.5 | AE2-021 | BG_P1_2315_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 911 | 119.29 | 120.36 | AE2-021 | PJM_500_BG_P4_5_CNSTN_15_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 125.84 | 120.34 | AE2-021 | PECO_P4_PEACH225_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220965 | NEAST339 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 120.68 | 120.27 | AE2-021 | BG_P4_5_NEAST_17_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220965 | NEAST339 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 120.84 | 120.27 | AE2-021 | BG_P4_5_NEAST_15_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3464 | 167.88 | 161.88 | AC2-112 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3464 | 168.29 | 162.28 | AC2-120 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 115.95 | 119.8 | AE2-021 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208131 | WHEM | 208132 | WHEM TR1 | 1 | 230 | 229 | 691 | 109.8 | 119.71 | AE2-021 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208131 | WHEM | 208132 | WHEM TR1 | 1 | 230 | 229 | 691 | 109.8 | 119.71 | AE2-021 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208131 | WHEM | 208132 | WHEM TR1 | 1 | 230 | 229 | 691 | 109.79 | 119.7 | AE2-021 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220979 | NEAST317 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 120.18 | 119.61 | AE2-021 | BG_P1_2337_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 115.61 | 119.45 | AE2-021 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 115.61 | 119.4 | AE2-021 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 115.61 | 119.4 | AE2-021 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220979 | NEAST317 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 119.83 | 119.33 | AE2-021 | BG_P4_5_NEAST_37_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220979 | NEAST317 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 119.83 | 119.33 | AE2-021 | BG_P4_5_NEAST_39_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 116.26 | 119.17 | AE2-021 | BG_P7_GRCTN_CNSTN_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 115.27 | 119.06 | AE2-021 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 115.27 | 119.06 | AE2-021 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 113.74 | 118.68 | AE2-021 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 113.56 | 118.48 | AE2-021 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 113.56 | 118.48 | AE2-021 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200532 | 26ROXBURY | 200520 | 26ROXBURY | 2 | 138/115 | 226 | 435 | 102.37 | 118.23 | AE2-021 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200532 | 26ROXBURY | 200520 | 26ROXBURY | 2 | 138/115 | 226 | 435 | 102.37 | 118.22 | AE2-021 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200532 | 26ROXBURY | 200520 | 26ROXBURY | 2 | 138/115 | 226 | 435 | 102.37 | 118.22 | AE2-021 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200532 | 26ROXBURY | 200520 | 26ROXBURY | 2 | 138/115 | 226 | 435 | 102.21 | 118.05 | AE2-021 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 119.17 | 117.9 | AE2-021 | PL_04_P12_000260_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 119.17 | 117.9 | AE2-021 | PL_04_P42_000564_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3464 | 168.22 | 162.21 | AC2-123 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204512 | 27S.RDG | 204693 | 27BOONETOWN | 1 | 230 | 227 | 607 | 106.8 | 117.11 | AE2-021 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 118.96 | 117.03 | AE2-021 | AP_P2-3_PE-500-019C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208020 | MANO TR3 | 1 | 230 | 229 | 793 | 106.28 | 116.9 | AE2-021 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208020 | MANO TR3 | 208031 | MLWD TR2 | 1 | 230 | 229 | 903 | 104.31 | 116.22 | AE2-021 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 2 | 500/230 | 225/232 | 2168 | 110.73 | 116.2 | AE2-021 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 2 | 500/230 | 225/232 | 2168 | 110.56 | 115.99 | AE2-021 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 2 | 500/230 | 225/232 | 2168 | 110.56 | 115.99 | AE2-021 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 1 | 500/230 | 225/232 | 2168 | 110.5 | 115.95 | AE2-021 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 1 | 500/230 | 225/232 | 2168 | 110.32 | 115.74 | AE2-021 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 1 | 500/230 | 225/232 | 2168 | 110.32 | 115.74 | AE2-021 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220964 | GRACETON | 220999 | BAGLEY2 | 13 | 230 | 232 | 1795 | 114.49 | 115.61 | AE2-021 | BG_P4_5_GRCTN_3T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 112.77 | 115.58 | AE2-021 | PJM_500_BG_P4_5_CNSTN_15_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208020 | MANO TR3 | 208031 | MLWD TR2 | 1 | 230 | 229 | 903 | 103.65 | 115.06 | AE2-021 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208020 | MANO TR3 | 208031 | MLWD TR2 | 1 | 230 | 229 | 903 | 103.65 | 115.06 | AE2-021 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208020 | MANO TR3 | 208031 | MLWD TR2 | 1 | 230 | 229 | 903 | 103.64 | 115.06 | AE2-021 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 109.47 | 114.86 | AE2-021 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 109.29 | 114.66 | AE2-021 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 109.29 | 114.66 | AE2-021 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208031 | MLWD TR2 | 1 | 230 | 229 | 911 | 106.88 | 114.39 | AE2-021 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 114.59 | 113.47 | AE2-021 | BG_P4_5_CNSTN_14_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 2 | 500/230 | 225/232 | 2168 | 109.36 | 112.74 | AE2-021 | PJM_500_BG_P4_5_CNSTN_15_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3464 | 168.04 | 162.03 | AC2-165 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 107.52 | 112.56 | AE2-021 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 107.39 | 112.42 | AE2-021 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208131 | WHEM | 208133 | WHEM TR2 | 1 | 230 | 229 | 691 | 102.95 | 112.42 | AE2-021 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220980 | RAPHAEL | 220999 | BAGLEY2 | 13 | 230 | 232 | 1795 | 110.05 | 112.37 | AE2-021 | BG_P4_5_GRCTN_3T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208131 | WHEM | 208132 | WHEM TR1 | 1 | 230 | 229 | 691 | 105.02 | 112.19 | AE2-021 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 108.5 | 111.88 | AE2-021 | PJM_500_BG_P4_5_CNSTN_15_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 793 | 114.33 | 111.69 | AE2-021 | PEPCO_P4_PP19_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208131 | WHEM | 208133 | WHEM TR2 | 1 | 230 | 229 | 691 | 102.28 | 111.09 | AE2-021 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208131 | WHEM | 208133 | WHEM TR2 | 1 | 230 | 229 | 691 | 102.28 | 111.09 | AE2-021 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208131 | WHEM | 208133 | WHEM TR2 | 1 | 230 | 229 | 691 | 102.27 | 111.08 | AE2-021 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200532 | 26ROXBURY | 200520 | 26ROXBURY | 2 | 138/115 | 226 | 435 | 97.23 | 110.69 | AE2-021 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204512 | 27S.RDG | 204693 | 27BOONETOWN | 1 | 230 | 227 | 607 | 110.95 | 110.27 | AE2-021 | PL_04_P42_101307_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204512 | 27S.RDG | 204693 | 27BOONETOWN | 1 | 230 | 227 | 607 | 110.96 | 110.22 | AE2-021 | PL_24_P42_102306_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 204529 | 27GERMANTN | 1 | 138/115 | 227 | 453 | 106.84 | 109.54 | AE2-021 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 204529 | 27GERMANTN | 1 | 138/115 | 227 | 453 | 106.84 | 109.54 | AE2-021 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 204529 | 27GERMANTN | 1 | 138/115 | 227 | 453 | 106.84 | 109.53 | AE2-021 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 204529 | 27GERMANTN | 1 | 138/115 | 227 | 453 | 106.7 | 109.36 | AE2-021 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220973 | GRANITE6 | 1 | 230 | 232 | 829 | 110.27 | 109.09 | AE2-021 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 793 | 110.86 | 108.98 | AE2-021 | AP_P2-3_PE-500-019C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 2 | 230 | 233 | 793 | 110.86 | 108.98 | AE2-021 | AP_P2-3_PE-500-019C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220965 | NEAST339 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 109.62 | 108.18 | AE2-021 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220965 | NEAST339 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 109.53 | 108.07 | AE2-021 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220965 | NEAST339 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 109.52 | 108.07 | AE2-021 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220972 | GRANITE1 | 1 | 230 | 232 | 829 | 109.42 | 108.01 | AE2-021 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208021 | MANO TR4 | 208133 | WHEM TR2 | 2 | 230 | 229 | 593 | 97.63 | 107.25 | AE2-021 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 102.63 | 106.98 | AE2-021 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 102.54 | 106.9 | AE2-021 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200099 | LAUS | 208045 | LAUS | 3 | 500/230 | 225/229 | 1200 | 104.63 | 106.45 | AE2-021 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220972 | GRANITE1 | 1 | 230 | 232 | 829 | 107.39 | 106.05 | AE2-021 | BG_P4_5_NW230-4_2326_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208020 | MANO TR3 | 208031 | MLWD TR2 | 1 | 230 | 229 | 903 | 97.28 | 105.98 | AE2-021 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200099 | LAUS | 208045 | LAUS | 3 | 500/230 | 225/229 | 1200 | 104.34 | 105.97 | AE2-021 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200099 | LAUS | 208045 | LAUS | 3 | 500/230 | 225/229 | 1200 | 104.34 | 105.97 | AE2-021 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200099 | LAUS | 208045 | LAUS | 3 | 500/230 | 225/229 | 1200 | 104.33 | 105.95 | AE2-021 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 103.72 | 105.83 | AE2-021 | BG_P1_2322_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208021 | MANO TR4 | 208133 | WHEM TR2 | 2 | 230 | 229 | 593 | 96.87 | 105.81 | AE2-021 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208021 | MANO TR4 | 208133 | WHEM TR2 | 2 | 230 | 229 | 593 | 96.87 | 105.81 | AE2-021 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208021 | MANO TR4 | 208133 | WHEM TR2 | 2 | 230 | 229 | 593 | 96.85 | 105.79 | AE2-021 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 103.64 | 105.75 | AE2-021 | BG_P1_2310_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 103.65 | 105.71 | AE2-021 | BG_P4_5_NW2322_230-4_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 103.58 | 105.67 | AE2-021 | BG_P4_5_NW2310_230-5_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220973 | GRANITE6 | 1 | 230 | 232 | 829 | 107.07 | 105.53 | AE2-021 | BG_P4_5_NW230-5_2311_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220979 | NEAST317 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 106.45 | 105.08 | AE2-021 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220979 | NEAST317 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 106.36 | 104.96 | AE2-021 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220979 | NEAST317 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 106.36 | 104.96 | AE2-021 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204520 | 27ALLEN | 208142 | WIGR-115 | 1 | 115 | 227/229 | 351.4 | 96.35 | 104.66 | AE2-021 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 102.28 | 104.43 | AE2-021 | BG_P4_5_NW230-2_2322_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 99.89 | 104.36 | AE2-021 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 99.89 | 104.36 | AE2-021 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 99.89 | 104.36 | AE2-021 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 102.18 | 104.31 | AE2-021 | BG_P4_5_NW2371_2310_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 102.18 | 104.31 | AE2-021 | BG_P4_5_NW230-3_2310_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220973 | GRANITE6 | 1 | 230 | 232 | 829 | 104.96 | 103.94 | AE2-021 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208131 | WHEM | 208133 | WHEM TR2 | 1 | 230 | 229 | 691 | 97.5 | 103.84 | AE2-021 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220965 | NEAST339 | 220977 | RIV2339 | 1 | 230 | 232 | 991 | 104.94 | 103.47 | AE2-021 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220966 | RIV2317 | 220979 | NEAST317 | 1 | 230 | 232 | 940 | 104.5 | 103.43 | AE2-021 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220965 | NEAST339 | 220977 | RIV2339 | 1 | 230 | 232 | 991 | 104.89 | 103.42 | AE2-021 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220965 | NEAST339 | 220977 | RIV2339 | 1 | 230 | 232 | 991 | 104.89 | 103.42 | AE2-021 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 101.31 | 103.38 | AE2-021 | BG_P4_5_CNSTN_14_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220966 | RIV2317 | 220979 | NEAST317 | 1 | 230 | 232 | 940 | 104.45 | 103.37 | AE2-021 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220966 | RIV2317 | 220979 | NEAST317 | 1 | 230 | 232 | 940 | 104.45 | 103.37 | AE2-021 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220965 | NEAST339 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 103.87 | 103.29 | AE2-021 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220964 | GRACETON | 220999 | BAGLEY2 | 13 | 230 | 232 | 1795 | 102.46 | 103.28 | AE2-021 | BG_P1_2305_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220964 | GRACETON | 221000 | BAGLEY | 5 | 230 | 232 | 1795 | 102.46 | 103.28 | AE2-021 | BG_P1_2313_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220972 | GRANITE1 | 1 | 230 | 232 | 829 | 104.38 | 103.17 | AE2-021 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 99.01 | 103.04 | AE2-021 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 2 | 500/230 | 225/232 | 2168 | 99.77 | 102.59 | AE2-021 | BG_P1_CNSTN_500-2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 2 | 500/230 | 225/232 | 2168 | 99.77 | 102.59 | AE2-021 | PJM_500_BG_P2_CNSTN_230-N_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 1 | 500/230 | 225/232 | 2168 | 99.66 | 102.48 | AE2-021 | BG_P1_CNSTN_500-4_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 1 | 500/230 | 225/232 | 2168 | 99.66 | 102.48 | AE2-021 | PJM_500_BG_P2_CNSTN_230-S_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 204529 | 27GERMANTN | 1 | 138/115 | 227 | 453 | 101 | 102.27 | AE2-021 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 223960 | BRG 1T 230 | 1 | 500/230 | 225/233 | 1498 | 101.29 | 101.74 | AE2-021 | PEPCO_P4_PP41_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208021 | MANO TR4 | 1 | 230 | 229 | 600 | 90.68 | 101.68 | AE2-021 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 99.06 | 101.6 | AE2-021 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 204529 | 27GERMANTN | 1 | 138/115 | 227 | 453 | 96.2 | 101.22 | AE2-021 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220979 | NEAST317 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 101.71 | 101.14 | AE2-021 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220972 | GRANITE1 | 1 | 230 | 232 | 829 | 102.06 | 100.97 | AE2-021 | BG_P4_5_GRNITE26_32_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 204529 | 27GERMANTN | 1 | 138/115 | 227 | 453 | 95.92 | 100.73 | AE2-021 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220973 | GRANITE6 | 1 | 230 | 232 | 829 | 101.88 | 100.52 | AE2-021 | BBG_P1_2311_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220972 | GRANITE1 | 1 | 230 | 232 | 829 | 101.58 | 100.47 | AE2-021 | BG_P1_2326_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220973 | GRANITE6 | 1 | 230 | 232 | 829 | 101.29 | 100.44 | AE2-021 | BG_P1_2312_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220973 | GRANITE6 | 1 | 230 | 232 | 829 | 101.44 | 100.42 | AE2-021 | BG_P4_5_GRNITE11_12_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220980 | RAPHAEL | 220999 | BAGLEY2 | 13 | 230 | 232 | 1795 | 98.02 | 100.04 | AE2-021 | BG_P1_2305_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220980 | RAPHAEL | 221000 | BAGLEY | 5 | 230 | 232 | 1795 | 98.02 | 100.04 | AE2-021 | BG_P1_2313_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200099 | LAUS | 208045 | LAUS | 3 | 500/230 | 225/229 | 1200 | 98.38 | 100.04 | AE2-021 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 228.9 | 241.69 | AE2-022 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 226.85 | 241.68 | AE2-022 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 227.98 | 239.59 | AE2-022 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 225.93 | 239.59 | AE2-022 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 227.92 | 239.52 | AE2-022 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 227.92 | 239.52 | AE2-022 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 225.87 | 239.51 | AE2-022 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 225.86 | 239.51 | AE2-022 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 216.68 | 231.38 | AE2-022 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 215.8 | 229.35 | AE2-022 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 215.74 | 229.27 | AE2-022 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 215.74 | 229.27 | AE2-022 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 212.42 | 228.21 | AE2-022 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 211.54 | 226.16 | AE2-022 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 211.47 | 226.08 | AE2-022 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 211.47 | 226.08 | AE2-022 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 213.08 | 220.94 | AE2-022 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 211.03 | 220.94 | AE2-022 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 201.41 | 211.28 | AE2-022 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 197.15 | 207.95 | AE2-022 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 174.01 | 169.28 | AE2-022 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 173.07 | 167.88 | AE2-022 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 173.07 | 167.88 | AE2-022 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 173.05 | 167.87 | AE2-022 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 164.97 | 166.76 | AE2-022 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 163.15 | 163.7 | AE2-022 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 163.17 | 163.7 | AE2-022 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 163.17 | 163.7 | AE2-022 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3464 | 168.25 | 162.23 | AC2-176 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 165.12 | 160.18 | AE2-022 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 154.71 | 159.39 | AE2-022 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 163.33 | 158.44 | AE2-022 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 163.32 | 158.44 | AE2-022 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 153.02 | 158.06 | AE2-022 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 163.24 | 155.95 | AE2-022 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 149.65 | 154.42 | AE2-022 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 903 | 145.3 | 153.71 | AE2-022 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 154.23 | 152.9 | AE2-022 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 156.91 | 151.75 | AE2-022 | PN_P1-2_PN-500-010T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 903 | 143.82 | 151.06 | AE2-022 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 903 | 143.82 | 151.06 | AE2-022 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 903 | 143.8 | 151.05 | AE2-022 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 147.46 | 150.74 | AE2-022 | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 147.39 | 150.66 | AE2-022 | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 145.01 | 149.42 | AE2-022 | AP_P2-3_PE-500-016_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 145.07 | 149.39 | AE2-022 | AP_P2-3_PE-500-015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 154.69 | 149.23 | AE2-022 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 154.49 | 149.04 | AE2-022 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 154.51 | 149.03 | AE2-022 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 154.16 | 149.02 | AE2-022 | PJM_500_BG_P4_5_CNSTN_L_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 154.24 | 148.83 | AE2-022 | PECO_P4_NOTTI85_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 154.18 | 148.81 | AE2-022 | PECO_P1-2_220-08_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 154.12 | 148.75 | AE2-022 | PECO_P4_COOPR125_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.19 | 148.54 | AE2-022 | AP_P1-2_PE-500-001_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.19 | 148.54 | AE2-022 | AP_P1-2_WP-500-DRT17_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.14 | 148.47 | AE2-022 | AP_P2-3_PE-500-018C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3464 | 168.82 | 162.8 | AC2-185 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 152.69 | 145.9 | AE2-022 | PECO_P4_PEACH025_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 152.46 | 145.72 | AE2-022 | PECO_P1-2_PBTIE1_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 911 | 150.22 | 144.52 | AE2-022 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 911 | 149.3 | 143.24 | AE2-022 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 911 | 149.3 | 143.24 | AE2-022 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 911 | 149.29 | 143.23 | AE2-022 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204502 | 27JACKSON | 204514 | 27TMI | 1 | 230 | 227 | 781 | 133.94 | 143.09 | AE2-022 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204502 | 27JACKSON | 204514 | 27TMI | 1 | 230 | 227 | 781 | 134.13 | 143.04 | AE2-022 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204502 | 27JACKSON | 204514 | 27TMI | 1 | 230 | 227 | 781 | 134.13 | 143.04 | AE2-022 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204502 | 27JACKSON | 204514 | 27TMI | 1 | 230 | 227 | 781 | 134.11 | 143.04 | AE2-022 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 903 | 136.74 | 141.14 | AE2-022 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 1031 | 131.7 | 140.49 | AE2-022 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 1031 | 131.22 | 139.4 | AE2-022 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 1031 | 131.22 | 139.4 | AE2-022 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 1031 | 131.21 | 139.39 | AE2-022 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 911 | 141.43 | 136.25 | AE2-022 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 207923 | BRISREAC | 208132 | WHEM TR1 | 1 | 230 | 229 | 676 | 125.84 | 135.65 | AE2-022 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 207922 | BRIS | 207923 | BRISREAC | RX | 230 | 229 | 676 | 125.84 | 135.64 | AE2-022 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208078 | SAKR | 1 | 230 | 229 | 903 | 126.42 | 135.45 | AE2-022 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 140.51 | 134.52 | AE2-022 | PECO_P4_PEACH205_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 140.6 | 134.38 | AE2-022 | PECO_P1-2_PBTIE2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208078 | SAKR | 1 | 230 | 229 | 903 | 125.7 | 134 | AE2-022 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208078 | SAKR | 1 | 230 | 229 | 903 | 125.7 | 134 | AE2-022 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208078 | SAKR | 1 | 230 | 229 | 903 | 125.7 | 134 | AE2-022 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 139.55 | 133.41 | AE2-022 | PECO_P4_PEACH055_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204502 | 27JACKSON | 204514 | 27TMI | 1 | 230 | 227 | 781 | 126.48 | 132.58 | AE2-022 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220972 | GRANITE1 | 1 | 230 | 232 | 829 | 136.05 | 132.06 | AE2-022 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220972 | GRANITE1 | 1 | 230 | 232 | 829 | 135.43 | 131.4 | AE2-022 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220972 | GRANITE1 | 1 | 230 | 232 | 829 | 135.43 | 131.4 | AE2-022 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 1031 | 125.62 | 130.63 | AE2-022 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220973 | GRANITE6 | 1 | 230 | 232 | 829 | 133.95 | 130.14 | AE2-022 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220973 | GRANITE6 | 1 | 230 | 232 | 829 | 133.36 | 129.53 | AE2-022 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220973 | GRANITE6 | 1 | 230 | 232 | 829 | 133.36 | 129.53 | AE2-022 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 135.11 | 129.22 | AE2-022 | PECO_P4_PEACH015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 128.45 | 128.8 | AE2-022 | BG_P7_GRCTN_CNSTN_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 126.39 | 128.8 | AE2-022 | BG_P7_GRCTN_CNSTN_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 129.89 | 128.16 | AE2-022 | DVP_P4-2: 514T595_SRT-SW |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208020 | MANO TR3 | 1 | 230 | 229 | 793 | 113.48 | 127.83 | AE2-022 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 133.63 | 127.73 | AE2-022 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220953 | HOWARD12 | 220972 | GRANITE1 | 1 | 230 | 232 | 772 | 131.01 | 127 | AE2-022 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 128.17 | 126.46 | AE2-022 | DVP_P4-2: 51482_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 128.17 | 126.37 | AE2-022 | DVP_P1-2: LN 514_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 128.17 | 126.37 | AE2-022 | AP_P1-2_PE-500-407T_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220954 | HOWARD32 | 220973 | GRANITE6 | 1 | 230 | 232 | 772 | 129.79 | 126.24 | AE2-022 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208020 | MANO TR3 | 1 | 230 | 229 | 793 | 112.68 | 126.17 | AE2-022 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208020 | MANO TR3 | 1 | 230 | 229 | 793 | 112.68 | 126.17 | AE2-022 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208020 | MANO TR3 | 1 | 230 | 229 | 793 | 112.68 | 126.17 | AE2-022 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220953 | HOWARD12 | 220972 | GRANITE1 | 1 | 230 | 232 | 772 | 130.11 | 126.04 | AE2-022 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220953 | HOWARD12 | 220972 | GRANITE1 | 1 | 230 | 232 | 772 | 130.11 | 126.04 | AE2-022 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 207922 | BRIS | 207923 | BRISREAC | RX | 230 | 229 | 676 | 120.01 | 125.98 | AE2-022 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 207923 | BRISREAC | 208132 | WHEM TR1 | 1 | 230 | 229 | 676 | 120.01 | 125.98 | AE2-022 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220954 | HOWARD32 | 220973 | GRANITE6 | 1 | 230 | 232 | 772 | 129 | 125.4 | AE2-022 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220954 | HOWARD32 | 220973 | GRANITE6 | 1 | 230 | 232 | 772 | 129 | 125.4 | AE2-022 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 119.3 | 124.22 | AE2-022 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 121.35 | 124.22 | AE2-022 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208078 | SAKR | 1 | 230 | 229 | 903 | 118.44 | 124.2 | AE2-022 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208031 | MLWD TR2 | 1 | 230 | 229 | 911 | 113.6 | 124.03 | AE2-022 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 119.11 | 124.01 | AE2-022 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 121.17 | 124.01 | AE2-022 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 121.17 | 124.01 | AE2-022 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 119.11 | 124.01 | AE2-022 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204512 | 27S.RDG | 204693 | 27BOONETOWN | 1 | 230 | 227 | 607 | 108.27 | 123.74 | AE2-022 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200025 | W CHAPEL | 1 | 500 | 225 | 1732 | 124.7 | 122.95 | AE2-022 | PEPCO_P4_PP41_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208031 | MLWD TR2 | 1 | 230 | 229 | 911 | 112.9 | 122.58 | AE2-022 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208031 | MLWD TR2 | 1 | 230 | 229 | 911 | 112.9 | 122.58 | AE2-022 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208031 | MLWD TR2 | 1 | 230 | 229 | 911 | 112.9 | 122.58 | AE2-022 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 119.69 | 122.09 | AE2-022 | BG_P7_GRCTN_CNSTN_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 120.39 | 121.02 | AE2-022 | PJM_500_BG_P4_5_CNSTN_15_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 118.34 | 121.02 | AE2-022 | PJM_500_BG_P4_5_CNSTN_15_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208131 | WHEM | 208132 | WHEM TR1 | 1 | 230 | 229 | 691 | 110.03 | 120.26 | AE2-022 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220965 | NEAST339 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 120.61 | 119.97 | AE2-022 | BG_P1_2315_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220965 | NEAST339 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 120.17 | 119.76 | AE2-022 | BG_P4_5_NEAST_17_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220965 | NEAST339 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 120.34 | 119.76 | AE2-022 | BG_P4_5_NEAST_15_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 115.49 | 119.28 | AE2-022 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 124.56 | 119.12 | AE2-022 | PECO_P4_PEACH225_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220979 | NEAST317 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 119.68 | 119.1 | AE2-022 | BG_P1_2337_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3464 | 168.65 | 162.63 | AC2-187 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3464 | 168.65 | 162.63 | AC2-188 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 115.14 | 118.94 | AE2-022 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 115.14 | 118.88 | AE2-022 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 115.14 | 118.88 | AE2-022 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220979 | NEAST317 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 119.34 | 118.82 | AE2-022 | BG_P4_5_NEAST_39_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220979 | NEAST317 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 119.34 | 118.82 | AE2-022 | BG_P4_5_NEAST_37_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 114.8 | 118.54 | AE2-022 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 114.8 | 118.54 | AE2-022 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 115.42 | 118.25 | AE2-022 | BG_P7_GRCTN_CNSTN_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 112.84 | 117.68 | AE2-022 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 112.66 | 117.47 | AE2-022 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 112.66 | 117.47 | AE2-022 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 118.36 | 116.44 | AE2-022 | AP_P2-3_PE-500-019C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3464 | 168.2 | 162.19 | AC2-195 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208020 | MANO TR3 | 1 | 230 | 229 | 793 | 105.5 | 115.76 | AE2-022 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 2 | 500/230 | 225/232 | 2168 | 110.32 | 115.73 | AE2-022 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 2 | 500/230 | 225/232 | 2168 | 110.15 | 115.51 | AE2-022 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 2 | 500/230 | 225/232 | 2168 | 110.15 | 115.51 | AE2-022 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 1 | 500/230 | 225/232 | 2168 | 110.09 | 115.48 | AE2-022 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208020 | MANO TR3 | 208031 | MLWD TR2 | 1 | 230 | 229 | 903 | 103.64 | 115.29 | AE2-022 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 1 | 500/230 | 225/232 | 2168 | 109.91 | 115.27 | AE2-022 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 1 | 500/230 | 225/232 | 2168 | 109.91 | 115.27 | AE2-022 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220964 | GRACETON | 220999 | BAGLEY2 | 13 | 230 | 232 | 1795 | 114.09 | 115.18 | AE2-022 | BG_P4_5_GRCTN_3T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 111.91 | 114.64 | AE2-022 | PJM_500_BG_P4_5_CNSTN_15_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 108.57 | 113.86 | AE2-022 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208020 | MANO TR3 | 208031 | MLWD TR2 | 1 | 230 | 229 | 903 | 102.95 | 113.78 | AE2-022 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208020 | MANO TR3 | 208031 | MLWD TR2 | 1 | 230 | 229 | 903 | 102.96 | 113.78 | AE2-022 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208020 | MANO TR3 | 208031 | MLWD TR2 | 1 | 230 | 229 | 903 | 102.96 | 113.77 | AE2-022 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 108.39 | 113.65 | AE2-022 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 108.39 | 113.65 | AE2-022 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208031 | MLWD TR2 | 1 | 230 | 229 | 911 | 106.15 | 113.32 | AE2-022 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 2 | 500/230 | 225/232 | 2168 | 109.04 | 112.39 | AE2-022 | PJM_500_BG_P4_5_CNSTN_15_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 107.13 | 112.07 | AE2-022 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220980 | RAPHAEL | 220999 | BAGLEY2 | 13 | 230 | 232 | 1795 | 109.66 | 111.94 | AE2-022 | BG_P4_5_GRCTN_3T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 107 | 111.93 | AE2-022 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208131 | WHEM | 208133 | WHEM TR2 | 1 | 230 | 229 | 691 | 102.51 | 111.63 | AE2-022 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3464 | 168.13 | 162.12 | AD1-022 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 107.65 | 110.94 | AE2-022 | PJM_500_BG_P4_5_CNSTN_15_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220965 | NEAST339 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 109.13 | 107.7 | AE2-022 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220965 | NEAST339 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 109.03 | 107.59 | AE2-022 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220965 | NEAST339 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 109.03 | 107.59 | AE2-022 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 102.24 | 106.52 | AE2-022 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 102.16 | 106.43 | AE2-022 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208021 | MANO TR4 | 208133 | WHEM TR2 | 2 | 230 | 229 | 593 | 97.13 | 106.42 | AE2-022 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200099 | LAUS | 208045 | LAUS | 3 | 500/230 | 225/229 | 1200 | 104.07 | 105.87 | AE2-022 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 103.34 | 105.42 | AE2-022 | BG_P1_2322_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200099 | LAUS | 208045 | LAUS | 3 | 500/230 | 225/229 | 1200 | 103.77 | 105.36 | AE2-022 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200099 | LAUS | 208045 | LAUS | 3 | 500/230 | 225/229 | 1200 | 103.77 | 105.36 | AE2-022 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200099 | LAUS | 208045 | LAUS | 3 | 500/230 | 225/229 | 1200 | 103.76 | 105.36 | AE2-022 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 103.27 | 105.34 | AE2-022 | BG_P1_2310_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 103.28 | 105.3 | AE2-022 | BG_P4_5_NW2322_230-4_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 103.2 | 105.26 | AE2-022 | BG_P4_5_NW2310_230-5_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208020 | MANO TR3 | 208031 | MLWD TR2 | 1 | 230 | 229 | 903 | 96.58 | 104.85 | AE2-022 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220979 | NEAST317 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 105.98 | 104.62 | AE2-022 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220979 | NEAST317 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 105.89 | 104.5 | AE2-022 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220979 | NEAST317 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 105.89 | 104.5 | AE2-022 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 99.81 | 104.01 | AE2-022 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 99.81 | 104.01 | AE2-022 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 99.81 | 104.01 | AE2-022 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 100.94 | 102.97 | AE2-022 | BG_P4_5_CNSTN_14_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220965 | NEAST339 | 220977 | RIV2339 | 1 | 230 | 232 | 991 | 104.36 | 102.91 | AE2-022 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220964 | GRACETON | 221000 | BAGLEY | 5 | 230 | 232 | 1795 | 102.09 | 102.89 | AE2-022 | BG_P1_2313_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220964 | GRACETON | 220999 | BAGLEY2 | 13 | 230 | 232 | 1795 | 102.09 | 102.89 | AE2-022 | BG_P1_2305_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220966 | RIV2317 | 220979 | NEAST317 | 1 | 230 | 232 | 940 | 103.93 | 102.88 | AE2-022 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220965 | NEAST339 | 220977 | RIV2339 | 1 | 230 | 232 | 991 | 104.32 | 102.86 | AE2-022 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220965 | NEAST339 | 220977 | RIV2339 | 1 | 230 | 232 | 991 | 104.32 | 102.86 | AE2-022 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220965 | NEAST339 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 103.44 | 102.83 | AE2-022 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220966 | RIV2317 | 220979 | NEAST317 | 1 | 230 | 232 | 940 | 103.89 | 102.82 | AE2-022 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220966 | RIV2317 | 220979 | NEAST317 | 1 | 230 | 232 | 940 | 103.89 | 102.82 | AE2-022 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 98.91 | 102.71 | AE2-022 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 2 | 500/230 | 225/232 | 2168 | 99.48 | 102.28 | AE2-022 | BG_P1_CNSTN_500-2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 2 | 500/230 | 225/232 | 2168 | 99.48 | 102.28 | AE2-022 | PJM_500_BG_P2_CNSTN_230-N_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 1 | 500/230 | 225/232 | 2168 | 99.37 | 102.16 | AE2-022 | PJM_500_BG_P2_CNSTN_230-S_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 1 | 500/230 | 225/232 | 2168 | 99.37 | 102.16 | AE2-022 | BG_P1_CNSTN_500-4_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 223960 | BRG 1T 230 | 1 | 500/230 | 225/233 | 1498 | 100.93 | 101.36 | AE2-022 | PEPCO_P4_PP41_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 98.98 | 101.32 | AE2-022 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220979 | NEAST317 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 101.31 | 100.7 | AE2-022 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208021 | MANO TR4 | 1 | 230 | 229 | 600 | 90.2 | 100.61 | AE2-022 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 225.55 | 236.93 | AE2-027 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 223.55 | 236.93 | AE2-027 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 225.49 | 236.84 | AE2-027 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 223.48 | 236.84 | AE2-027 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 225.48 | 236.84 | AE2-027 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 223.48 | 236.84 | AE2-027 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 213.5 | 226.77 | AE2-027 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 213.44 | 226.69 | AE2-027 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 213.43 | 226.69 | AE2-027 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 209.24 | 223.56 | AE2-027 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 209.18 | 223.48 | AE2-027 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 209.18 | 223.48 | AE2-027 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 210.65 | 217.74 | AE2-027 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 208.65 | 217.74 | AE2-027 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 199.11 | 208.18 | AE2-027 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 194.85 | 204.83 | AE2-027 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 172.72 | 167.73 | AE2-027 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 163.59 | 164.85 | AE2-027 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3464 | 167.81 | 161.81 | AD1-025 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 161.72 | 161.78 | AE2-027 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 161.72 | 161.78 | AE2-027 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 161.71 | 161.77 | AE2-027 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 153.49 | 157.93 | AE2-027 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 161.99 | 157.11 | AE2-027 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 161.99 | 157.11 | AE2-027 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 151.8 | 156.61 | AE2-027 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 161.47 | 154.25 | AE2-027 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 148.44 | 152.96 | AE2-027 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 903 | 144.22 | 152.07 | AE2-027 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 152.78 | 151.15 | AE2-027 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 155.57 | 150.42 | AE2-027 | PN_P1-2_PN-500-010T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 903 | 142.68 | 149.45 | AE2-027 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 903 | 142.7 | 149.45 | AE2-027 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 903 | 142.7 | 149.45 | AE2-027 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.29 | 149.35 | AE2-027 | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.22 | 149.28 | AE2-027 | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.9 | 148.09 | AE2-027 | AP_P2-3_PE-500-016_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.97 | 148.06 | AE2-027 | AP_P2-3_PE-500-015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.89 | 147.75 | AE2-027 | PJM_500_BG_P4_5_CNSTN_L_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.17 | 147.74 | AE2-027 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.97 | 147.55 | AE2-027 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153 | 147.54 | AE2-027 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.73 | 147.34 | AE2-027 | PECO_P4_NOTTI85_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.67 | 147.33 | AE2-027 | PECO_P1-2_220-08_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.6 | 147.26 | AE2-027 | PECO_P4_COOPR125_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.08 | 147.21 | AE2-027 | AP_P1-2_PE-500-001_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.08 | 147.21 | AE2-027 | AP_P1-2_WP-500-DRT17_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.03 | 147.15 | AE2-027 | AP_P2-3_PE-500-018C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3464 | 168.16 | 162.15 | AD1-033 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.7 | 143.99 | AE2-027 | PECO_P4_PEACH025_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.53 | 143.87 | AE2-027 | PECO_P1-2_PBTIE1_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 911 | 148.96 | 143.08 | AE2-027 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204502 | 27JACKSON | 204514 | 27TMI | 1 | 230 | 227 | 781 | 133.02 | 141.58 | AE2-027 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204502 | 27JACKSON | 204514 | 27TMI | 1 | 230 | 227 | 781 | 133.04 | 141.57 | AE2-027 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204502 | 27JACKSON | 204514 | 27TMI | 1 | 230 | 227 | 781 | 133.04 | 141.57 | AE2-027 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 903 | 135.62 | 139.58 | AE2-027 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 1031 | 130.31 | 138.07 | AE2-027 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 1031 | 130.32 | 138.06 | AE2-027 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 1031 | 130.32 | 138.06 | AE2-027 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 138.93 | 133 | AE2-027 | PECO_P4_PEACH205_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 138.82 | 132.68 | AE2-027 | PECO_P1-2_PBTIE2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208078 | SAKR | 1 | 230 | 229 | 903 | 124.49 | 132.49 | AE2-027 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208078 | SAKR | 1 | 230 | 229 | 903 | 124.49 | 132.48 | AE2-027 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208078 | SAKR | 1 | 230 | 229 | 903 | 124.49 | 132.48 | AE2-027 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 137.89 | 131.81 | AE2-027 | PECO_P4_PEACH055_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 1031 | 124.72 | 129.25 | AE2-027 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 133.18 | 127.37 | AE2-027 | PECO_P4_PEACH015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 128.41 | 126.7 | AE2-027 | DVP_P4-2: 514T595_SRT-SW |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 131.88 | 126.06 | AE2-027 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 126.65 | 124.92 | AE2-027 | DVP_P4-2: 51482_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 793 | 126.57 | 124.84 | AE2-027 | DVP_P4-2: 514T595_SRT-SW |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 2 | 230 | 233 | 793 | 126.57 | 124.84 | AE2-027 | DVP_P4-2: 514T595_SRT-SW |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 126.65 | 124.83 | AE2-027 | AP_P1-2_PE-500-407T_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 126.65 | 124.83 | AE2-027 | DVP_P1-2: LN 514_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208020 | MANO TR3 | 1 | 230 | 229 | 793 | 111.48 | 124.67 | AE2-027 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208020 | MANO TR3 | 1 | 230 | 229 | 793 | 111.48 | 124.65 | AE2-027 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208020 | MANO TR3 | 1 | 230 | 229 | 793 | 111.48 | 124.65 | AE2-027 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 2 | 230 | 233 | 793 | 125.32 | 123.58 | AE2-027 | DVP_P4-2: 51482_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 793 | 125.32 | 123.58 | AE2-027 | DVP_P4-2: 51482_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 793 | 125.32 | 123.51 | AE2-027 | DVP_P1-2: LN 514_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 2 | 230 | 233 | 793 | 125.32 | 123.51 | AE2-027 | AP_P1-2_PE-500-407T_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 793 | 125.32 | 123.51 | AE2-027 | AP_P1-2_PE-500-407T_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 2 | 230 | 233 | 793 | 125.32 | 123.51 | AE2-027 | DVP_P1-2: LN 514_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208078 | SAKR | 1 | 230 | 229 | 903 | 117.22 | 122.49 | AE2-027 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200025 | W CHAPEL | 1 | 500 | 225 | 1732 | 123.63 | 121.84 | AE2-027 | PEPCO_P4_PP41_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208031 | MLWD TR2 | 1 | 230 | 229 | 911 | 111.78 | 121.23 | AE2-027 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208031 | MLWD TR2 | 1 | 230 | 229 | 911 | 111.78 | 121.22 | AE2-027 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208031 | MLWD TR2 | 1 | 230 | 229 | 911 | 111.78 | 121.22 | AE2-027 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 114.71 | 118.4 | AE2-027 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 114.37 | 118.06 | AE2-027 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 122.78 | 117.41 | AE2-027 | PECO_P4_PEACH225_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 2 | 500/230 | 225/232 | 2168 | 109.65 | 114.96 | AE2-027 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 116.86 | 114.92 | AE2-027 | AP_P2-3_PE-500-019C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 2 | 500/230 | 225/232 | 2168 | 109.48 | 114.75 | AE2-027 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 2 | 500/230 | 225/232 | 2168 | 109.48 | 114.75 | AE2-027 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 1 | 500/230 | 225/232 | 2168 | 109.42 | 114.72 | AE2-027 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 1 | 500/230 | 225/232 | 2168 | 109.25 | 114.51 | AE2-027 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 1 | 500/230 | 225/232 | 2168 | 109.25 | 114.51 | AE2-027 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208031 | MLWD TR2 | 1 | 230 | 229 | 911 | 105.03 | 111.72 | AE2-027 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 793 | 112.79 | 110.17 | AE2-027 | PEPCO_P4_PP19_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 793 | 109.54 | 107.64 | AE2-027 | AP_P2-3_PE-500-019C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 2 | 230 | 233 | 793 | 109.54 | 107.64 | AE2-027 | AP_P2-3_PE-500-019C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 99.49 | 103.4 | AE2-027 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 99.5 | 103.4 | AE2-027 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 99.5 | 103.39 | AE2-027 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208020 | MANO TR3 | 208031 | MLWD TR2 | 1 | 230 | 229 | 903 | 95.52 | 103.34 | AE2-027 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 98.57 | 102.07 | AE2-027 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 98.67 | 100.7 | AE2-027 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3464 | 168.24 | 162.23 | AD1-041 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 153.8 | 158.31 | AE2-029 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.29 | 157.41 | AE2-029 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.29 | 157.41 | AE2-029 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 152.11 | 156.98 | AE2-029 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 161.8 | 154.57 | AE2-029 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 148.75 | 153.33 | AE2-029 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 155.86 | 150.71 | AE2-029 | PN_P1-2_PN-500-010T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.58 | 149.71 | AE2-029 | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.51 | 149.63 | AE2-029 | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.2 | 148.47 | AE2-029 | AP_P2-3_PE-500-016_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.27 | 148.44 | AE2-029 | AP_P2-3_PE-500-015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.17 | 148.04 | AE2-029 | PJM_500_BG_P4_5_CNSTN_L_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.47 | 148.03 | AE2-029 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.27 | 147.84 | AE2-029 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.29 | 147.83 | AE2-029 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.02 | 147.63 | AE2-029 | PECO_P4_NOTTI85_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.96 | 147.62 | AE2-029 | PECO_P1-2_220-08_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.38 | 147.59 | AE2-029 | AP_P1-2_PE-500-001_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.38 | 147.59 | AE2-029 | AP_P1-2_WP-500-DRT17_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.89 | 147.55 | AE2-029 | PECO_P4_COOPR125_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.33 | 147.52 | AE2-029 | AP_P2-3_PE-500-018C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3464 | 167.95 | 161.95 | AD1-070 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 151.02 | 144.31 | AE2-029 | PECO_P4_PEACH025_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.89 | 144.21 | AE2-029 | PECO_P1-2_PBTIE1_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 139.25 | 133.31 | AE2-029 | PECO_P4_PEACH205_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 139.15 | 132.99 | AE2-029 | PECO_P1-2_PBTIE2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 138.2 | 132.11 | AE2-029 | PECO_P4_PEACH055_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 133.53 | 127.7 | AE2-029 | PECO_P4_PEACH015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 132.19 | 126.37 | AE2-029 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 123.1 | 117.72 | AE2-029 | PECO_P4_PEACH225_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 144.31 | 139.17 | AE2-035 | PL_10_P42_100570_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 144.31 | 139.17 | AE2-035 | PL_10_P42_100570_A_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 143.41 | 138.28 | AE2-035 | PN_P2-3_PN-500-004-DRT-008_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 143.41 | 138.28 | AE2-035 | PN_P2-3_PN-500-DRT31_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3464 | 168.17 | 162.16 | AD1-082 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 154.26 | 158.85 | AE2-042 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.75 | 157.87 | AE2-042 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.74 | 157.87 | AE2-042 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 152.57 | 157.53 | AE2-042 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 162.39 | 155.14 | AE2-042 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 149.2 | 153.88 | AE2-042 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 156.31 | 151.16 | AE2-042 | PN_P1-2_PN-500-010T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 147.02 | 150.22 | AE2-042 | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.95 | 150.15 | AE2-042 | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.61 | 148.96 | AE2-042 | AP_P2-3_PE-500-016_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.68 | 148.93 | AE2-042 | AP_P2-3_PE-500-015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.96 | 148.51 | AE2-042 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.61 | 148.48 | AE2-042 | PJM_500_BG_P4_5_CNSTN_L_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.76 | 148.33 | AE2-042 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.78 | 148.31 | AE2-042 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.51 | 148.12 | AE2-042 | PECO_P4_NOTTI85_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.45 | 148.1 | AE2-042 | PECO_P1-2_220-08_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.79 | 148.07 | AE2-042 | AP_P1-2_PE-500-001_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.79 | 148.07 | AE2-042 | AP_P1-2_WP-500-DRT17_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.39 | 148.04 | AE2-042 | PECO_P4_COOPR125_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.74 | 148 | AE2-042 | AP_P2-3_PE-500-018C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3464 | 168.03 | 162.02 | AD1-083 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 151.53 | 144.82 | AE2-042 | PECO_P1-2_PBTIE1_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 151.56 | 144.82 | AE2-042 | PECO_P4_PEACH025_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 139.85 | 133.89 | AE2-042 | PECO_P4_PEACH205_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 139.73 | 133.55 | AE2-042 | PECO_P1-2_PBTIE2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 138.74 | 132.62 | AE2-042 | PECO_P4_PEACH055_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 134.17 | 128.32 | AE2-042 | PECO_P4_PEACH015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 132.78 | 126.92 | AE2-042 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 123.69 | 118.28 | AE2-042 | PECO_P4_PEACH225_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3464 | 168.2 | 162.19 | AD1-087 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 154.21 | 158.79 | AE2-046 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.7 | 157.82 | AE2-046 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.7 | 157.82 | AE2-046 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 152.51 | 157.47 | AE2-046 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 162.33 | 155.08 | AE2-046 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 149.15 | 153.81 | AE2-046 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 156.27 | 151.11 | AE2-046 | PN_P1-2_PN-500-010T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.97 | 150.16 | AE2-046 | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.9 | 150.09 | AE2-046 | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.57 | 148.9 | AE2-046 | AP_P2-3_PE-500-016_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.63 | 148.87 | AE2-046 | AP_P2-3_PE-500-015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.91 | 148.47 | AE2-046 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.57 | 148.43 | AE2-046 | PJM_500_BG_P4_5_CNSTN_L_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.71 | 148.28 | AE2-046 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.74 | 148.26 | AE2-046 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.47 | 148.07 | AE2-046 | PECO_P4_NOTTI85_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.41 | 148.05 | AE2-046 | PECO_P1-2_220-08_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.75 | 148.02 | AE2-046 | AP_P1-2_PE-500-001_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.75 | 148.02 | AE2-046 | AP_P1-2_WP-500-DRT17_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.34 | 147.99 | AE2-046 | PECO_P4_COOPR125_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.7 | 147.95 | AE2-046 | AP_P2-3_PE-500-018C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3464 | 168.01 | 162 | AD1-088 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 151.53 | 144.79 | AE2-046 | PECO_P4_PEACH025_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 151.46 | 144.76 | AE2-046 | PECO_P1-2_PBTIE1_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 139.78 | 133.82 | AE2-046 | PECO_P4_PEACH205_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 139.67 | 133.49 | AE2-046 | PECO_P1-2_PBTIE2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 138.68 | 132.57 | AE2-046 | PECO_P4_PEACH055_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 134.1 | 128.25 | AE2-046 | PECO_P4_PEACH015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 132.71 | 126.86 | AE2-046 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 123.62 | 118.22 | AE2-046 | PECO_P4_PEACH225_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200009 | JUNI | 208004 | JUNI | 2 | 500/230 | 225/229 | 1040 | 107.59 | 107 | AE2-060 | PL_10_P42_000140_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 225.89 | 240.26 | AE2-093 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 227.92 | 240.25 | AE2-093 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 215.76 | 229.99 | AE2-093 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 211.5 | 226.8 | AE2-093 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 212.08 | 219.65 | AE2-093 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 210.05 | 219.65 | AE2-093 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 200.46 | 210.03 | AE2-093 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 196.2 | 206.69 | AE2-093 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3464 | 168.12 | 162.11 | AD1-105 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 154.25 | 158.84 | AE2-093 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.79 | 157.91 | AE2-093 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.79 | 157.91 | AE2-093 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 152.56 | 157.52 | AE2-093 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 162.48 | 155.23 | AE2-093 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 149.19 | 153.86 | AE2-093 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 156.37 | 151.21 | AE2-093 | PN_P1-2_PN-500-010T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 147.01 | 150.21 | AE2-093 | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.94 | 150.14 | AE2-093 | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.61 | 148.95 | AE2-093 | AP_P2-3_PE-500-016_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.67 | 148.92 | AE2-093 | AP_P2-3_PE-500-015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 154.05 | 148.6 | AE2-093 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.65 | 148.51 | AE2-093 | PJM_500_BG_P4_5_CNSTN_L_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.85 | 148.41 | AE2-093 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.88 | 148.4 | AE2-093 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.61 | 148.2 | AE2-093 | PECO_P4_NOTTI85_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.54 | 148.19 | AE2-093 | PECO_P1-2_220-08_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.48 | 148.12 | AE2-093 | PECO_P4_COOPR125_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.78 | 148.06 | AE2-093 | AP_P1-2_WP-500-DRT17_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.78 | 148.06 | AE2-093 | AP_P1-2_PE-500-001_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.73 | 147.99 | AE2-093 | AP_P2-3_PE-500-018C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3464 | 168.3 | 162.29 | AD1-106 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 151.82 | 145.07 | AE2-093 | PECO_P4_PEACH025_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 151.62 | 144.91 | AE2-093 | PECO_P1-2_PBTIE1_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 139.8 | 133.84 | AE2-093 | PECO_P4_PEACH205_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 139.82 | 133.64 | AE2-093 | PECO_P1-2_PBTIE2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 138.86 | 132.74 | AE2-093 | PECO_P4_PEACH055_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 134.26 | 128.41 | AE2-093 | PECO_P4_PEACH015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 132.86 | 127 | AE2-093 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 123.77 | 118.37 | AE2-093 | PECO_P4_PEACH225_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3464 | 168.22 | 162.21 | AD1-115 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 153.78 | 158.28 | AE2-104 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.27 | 157.4 | AE2-104 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.27 | 157.4 | AE2-104 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 152.09 | 156.96 | AE2-104 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 161.79 | 154.56 | AE2-104 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 148.73 | 153.31 | AE2-104 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 155.85 | 150.69 | AE2-104 | PN_P1-2_PN-500-010T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.57 | 149.68 | AE2-104 | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.5 | 149.61 | AE2-104 | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.18 | 148.44 | AE2-104 | AP_P2-3_PE-500-016_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.25 | 148.41 | AE2-104 | AP_P2-3_PE-500-015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.16 | 148.02 | AE2-104 | PJM_500_BG_P4_5_CNSTN_L_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.45 | 148.01 | AE2-104 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.25 | 147.83 | AE2-104 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.28 | 147.81 | AE2-104 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.01 | 147.62 | AE2-104 | PECO_P4_NOTTI85_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.95 | 147.6 | AE2-104 | PECO_P1-2_220-08_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.36 | 147.56 | AE2-104 | AP_P1-2_PE-500-001_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.36 | 147.56 | AE2-104 | AP_P1-2_WP-500-DRT17_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.88 | 147.54 | AE2-104 | PECO_P4_COOPR125_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.31 | 147.49 | AE2-104 | AP_P2-3_PE-500-018C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3464 | 168.3 | 162.29 | AD1-125 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 151.01 | 144.3 | AE2-104 | PECO_P4_PEACH025_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.87 | 144.19 | AE2-104 | PECO_P1-2_PBTIE1_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 139.24 | 133.3 | AE2-104 | PECO_P4_PEACH205_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 139.13 | 132.97 | AE2-104 | PECO_P1-2_PBTIE2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 138.18 | 132.09 | AE2-104 | PECO_P4_PEACH055_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 133.51 | 127.69 | AE2-104 | PECO_P4_PEACH015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 128.95 | 127.21 | AE2-104 | DVP_P4-2: 514T595_SRT-SW |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 132.18 | 126.35 | AE2-104 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 127.21 | 125.5 | AE2-104 | DVP_P4-2: 51482_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 127.21 | 125.41 | AE2-104 | AP_P1-2_PE-500-407T_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 127.21 | 125.41 | AE2-104 | DVP_P1-2: LN 514_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 123.08 | 117.7 | AE2-104 | PECO_P4_PEACH225_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 117.4 | 115.49 | AE2-104 | AP_P2-3_PE-500-019C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3464 | 168.05 | 162.04 | AD1-128 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 162.18 | 154.94 | AE2-112 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.8 | 148.35 | AE2-112 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.6 | 148.17 | AE2-112 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.62 | 148.15 | AE2-112 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.35 | 147.95 | AE2-112 | PECO_P4_NOTTI85_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.29 | 147.94 | AE2-112 | PECO_P1-2_220-08_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.22 | 147.87 | AE2-112 | PECO_P4_COOPR125_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.06 | 147.72 | AE2-112 | AP_P2-3_PE-500-016_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.09 | 147.71 | AE2-112 | AP_P2-3_PE-500-015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.88 | 147.68 | AE2-112 | PECO_P1-2_220-93_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 151.57 | 147.25 | AE2-112 | AP_P1-2_WP-500-DRT17_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 151.45 | 144.71 | AE2-112 | PECO_P4_PEACH025_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 151.29 | 144.6 | AE2-112 | PECO_P1-2_PBTIE1_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 139.52 | 133.35 | AE2-112 | PECO_P1-2_PBTIE2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 138.56 | 132.45 | AE2-112 | PECO_P4_PEACH055_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 133.93 | 128.09 | AE2-112 | PECO_P4_PEACH015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 132.56 | 126.71 | AE2-112 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204512 | 27S.RDG | 204693 | 27BOONETOWN | 1 | 230 | 227 | 607 | 107.71 | 122.15 | AE2-112 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 123.47 | 118.07 | AE2-112 | PECO_P4_PEACH225_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3464 | 167.99 | 161.98 | AD1-140 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 153.71 | 158.21 | AE2-206 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.17 | 157.3 | AE2-206 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.17 | 157.3 | AE2-206 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 152.03 | 156.88 | AE2-206 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 161.61 | 154.39 | AE2-206 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 148.66 | 153.23 | AE2-206 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 155.75 | 150.6 | AE2-206 | PN_P1-2_PN-500-010T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.5 | 149.61 | AE2-206 | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.43 | 149.54 | AE2-206 | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.15 | 148.42 | AE2-206 | AP_P2-3_PE-500-016_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.22 | 148.39 | AE2-206 | AP_P2-3_PE-500-015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.06 | 147.93 | AE2-206 | PJM_500_BG_P4_5_CNSTN_L_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.29 | 147.86 | AE2-206 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.09 | 147.67 | AE2-206 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.12 | 147.66 | AE2-206 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.33 | 147.54 | AE2-206 | AP_P1-2_WP-500-DRT17_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.33 | 147.54 | AE2-206 | AP_P1-2_PE-500-001_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.28 | 147.47 | AE2-206 | AP_P2-3_PE-500-018C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.85 | 147.46 | AE2-206 | PECO_P4_NOTTI85_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.79 | 147.45 | AE2-206 | PECO_P1-2_220-08_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.72 | 147.38 | AE2-206 | PECO_P4_COOPR125_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3464 | 168.99 | 162.96 | AD1-143 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.8 | 144.09 | AE2-206 | PECO_P4_PEACH025_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.7 | 144.02 | AE2-206 | PECO_P1-2_PBTIE1_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 139.09 | 133.16 | AE2-206 | PECO_P4_PEACH205_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 138.97 | 132.82 | AE2-206 | PECO_P1-2_PBTIE2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 138.03 | 131.95 | AE2-206 | PECO_P4_PEACH055_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 133.35 | 127.53 | AE2-206 | PECO_P4_PEACH015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 132.02 | 126.21 | AE2-206 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 122.93 | 117.56 | AE2-206 | PECO_P4_PEACH225_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 225.59 | 237.1 | AE2-217 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 223.58 | 237.1 | AE2-217 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 225.52 | 237.04 | AE2-217 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 223.52 | 237.04 | AE2-217 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 225.52 | 237.04 | AE2-217 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 223.52 | 237.04 | AE2-217 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 213.53 | 226.94 | AE2-217 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 213.47 | 226.88 | AE2-217 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 213.47 | 226.88 | AE2-217 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 209.27 | 223.73 | AE2-217 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 209.21 | 223.67 | AE2-217 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 209.21 | 223.67 | AE2-217 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 208.69 | 217.91 | AE2-217 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 210.69 | 217.91 | AE2-217 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 199.15 | 208.34 | AE2-217 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 194.89 | 205 | AE2-217 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 172.84 | 167.91 | AE2-217 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 161.82 | 161.97 | AE2-217 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 161.82 | 161.97 | AE2-217 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 161.81 | 161.97 | AE2-217 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3464 | 168.14 | 162.13 | AD1-152 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 153.63 | 158.11 | AE2-217 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.08 | 157.21 | AE2-217 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.08 | 157.21 | AE2-217 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 151.95 | 156.79 | AE2-217 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 161.49 | 154.28 | AE2-217 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 148.58 | 153.14 | AE2-217 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 155.66 | 150.51 | AE2-217 | PN_P1-2_PN-500-010T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.42 | 149.52 | AE2-217 | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.35 | 149.45 | AE2-217 | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.08 | 148.35 | AE2-217 | AP_P2-3_PE-500-016_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.15 | 148.32 | AE2-217 | AP_P2-3_PE-500-015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.97 | 147.85 | AE2-217 | PJM_500_BG_P4_5_CNSTN_L_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.19 | 147.76 | AE2-217 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.99 | 147.57 | AE2-217 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.01 | 147.56 | AE2-217 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.26 | 147.47 | AE2-217 | AP_P1-2_PE-500-001_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.26 | 147.47 | AE2-217 | AP_P1-2_WP-500-DRT17_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.21 | 147.4 | AE2-217 | AP_P2-3_PE-500-018C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.74 | 147.36 | AE2-217 | PECO_P4_NOTTI85_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.68 | 147.34 | AE2-217 | PECO_P1-2_220-08_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.62 | 147.28 | AE2-217 | PECO_P4_COOPR125_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3464 | 168.15 | 162.14 | AD1-155 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.67 | 143.97 | AE2-217 | PECO_P4_PEACH025_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.57 | 143.91 | AE2-217 | PECO_P1-2_PBTIE1_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 911 | 149.08 | 143.25 | AE2-217 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 1031 | 130.36 | 138.21 | AE2-217 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 138.99 | 133.05 | AE2-217 | PECO_P4_PEACH205_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 138.86 | 132.71 | AE2-217 | PECO_P1-2_PBTIE2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 137.92 | 131.84 | AE2-217 | PECO_P4_PEACH055_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 133.23 | 127.42 | AE2-217 | PECO_P4_PEACH015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 131.91 | 126.1 | AE2-217 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208020 | MANO TR3 | 1 | 230 | 229 | 793 | 111.54 | 124.75 | AE2-217 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208020 | MANO TR3 | 1 | 230 | 229 | 793 | 111.53 | 124.75 | AE2-217 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208020 | MANO TR3 | 1 | 230 | 229 | 793 | 111.54 | 124.75 | AE2-217 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 122.82 | 117.46 | AE2-217 | PECO_P4_PEACH225_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 225.58 | 237.09 | AE2-218 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 223.58 | 237.09 | AE2-218 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 225.52 | 237.03 | AE2-218 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 223.51 | 237.03 | AE2-218 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 225.52 | 237.03 | AE2-218 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 223.51 | 237.03 | AE2-218 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 213.53 | 226.93 | AE2-218 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 213.46 | 226.87 | AE2-218 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 213.46 | 226.87 | AE2-218 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 209.27 | 223.72 | AE2-218 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 209.21 | 223.66 | AE2-218 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 209.2 | 223.66 | AE2-218 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 208.68 | 217.9 | AE2-218 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 210.69 | 217.9 | AE2-218 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 199.15 | 208.33 | AE2-218 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 194.89 | 204.98 | AE2-218 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 172.83 | 167.9 | AE2-218 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 161.82 | 161.96 | AE2-218 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 161.82 | 161.96 | AE2-218 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 161.8 | 161.95 | AE2-218 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3464 | 168.2 | 162.19 | AD2-009 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 153.62 | 158.1 | AE2-218 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.07 | 157.2 | AE2-218 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.07 | 157.2 | AE2-218 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 151.94 | 156.78 | AE2-218 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 161.49 | 154.27 | AE2-218 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 148.57 | 153.13 | AE2-218 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 155.65 | 150.5 | AE2-218 | PN_P1-2_PN-500-010T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.41 | 149.51 | AE2-218 | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.34 | 149.44 | AE2-218 | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.07 | 148.33 | AE2-218 | AP_P2-3_PE-500-016_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.14 | 148.3 | AE2-218 | AP_P2-3_PE-500-015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.96 | 147.84 | AE2-218 | PJM_500_BG_P4_5_CNSTN_L_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.18 | 147.75 | AE2-218 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.98 | 147.57 | AE2-218 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.01 | 147.55 | AE2-218 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.25 | 147.45 | AE2-218 | AP_P1-2_PE-500-001_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.25 | 147.45 | AE2-218 | AP_P1-2_WP-500-DRT17_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.2 | 147.38 | AE2-218 | AP_P2-3_PE-500-018C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.74 | 147.36 | AE2-218 | PECO_P4_NOTTI85_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.68 | 147.34 | AE2-218 | PECO_P1-2_220-08_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.61 | 147.28 | AE2-218 | PECO_P4_COOPR125_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3464 | 167.72 | 161.72 | AD2-016 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.67 | 143.97 | AE2-218 | PECO_P4_PEACH025_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.57 | 143.9 | AE2-218 | PECO_P1-2_PBTIE1_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 911 | 149.08 | 143.24 | AE2-218 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 1031 | 130.36 | 138.2 | AE2-218 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 138.98 | 133.05 | AE2-218 | PECO_P4_PEACH205_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 138.85 | 132.7 | AE2-218 | PECO_P1-2_PBTIE2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208078 | SAKR | 1 | 230 | 229 | 903 | 124.55 | 132.65 | AE2-218 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 137.92 | 131.84 | AE2-218 | PECO_P4_PEACH055_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 133.22 | 127.41 | AE2-218 | PECO_P4_PEACH015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 131.91 | 126.1 | AE2-218 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208020 | MANO TR3 | 1 | 230 | 229 | 793 | 111.53 | 124.74 | AE2-218 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208020 | MANO TR3 | 1 | 230 | 229 | 793 | 111.53 | 124.74 | AE2-218 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208020 | MANO TR3 | 1 | 230 | 229 | 793 | 111.53 | 124.74 | AE2-218 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 122.82 | 117.45 | AE2-218 | PECO_P4_PEACH225_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 223.17 | 236.49 | AE2-221 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 225.16 | 236.48 | AE2-221 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 223.1 | 236.39 | AE2-221 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 225.1 | 236.39 | AE2-221 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 223.1 | 236.39 | AE2-221 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 225.1 | 236.39 | AE2-221 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 213.13 | 226.34 | AE2-221 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 213.07 | 226.26 | AE2-221 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 213.07 | 226.26 | AE2-221 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 208.87 | 223.13 | AE2-221 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 208.81 | 223.04 | AE2-221 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 208.81 | 223.04 | AE2-221 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 210.28 | 217.39 | AE2-221 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 208.29 | 217.38 | AE2-221 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 198.76 | 207.83 | AE2-221 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 194.5 | 204.48 | AE2-221 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 172.59 | 167.66 | AE2-221 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 171.61 | 166.22 | AE2-221 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 171.61 | 166.22 | AE2-221 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 171.59 | 166.21 | AE2-221 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 163.42 | 164.72 | AE2-221 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3464 | 168.26 | 162.25 | AD2-048 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 161.54 | 161.63 | AE2-221 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 161.54 | 161.62 | AE2-221 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 161.53 | 161.62 | AE2-221 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 163.67 | 158.76 | AE2-221 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 153.41 | 157.85 | AE2-221 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 161.84 | 156.97 | AE2-221 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 161.84 | 156.97 | AE2-221 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 151.72 | 156.52 | AE2-221 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 161.17 | 153.97 | AE2-221 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 148.36 | 152.87 | AE2-221 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 903 | 144.15 | 151.99 | AE2-221 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 152.61 | 151.03 | AE2-221 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 155.42 | 150.28 | AE2-221 | PN_P1-2_PN-500-010T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 903 | 142.59 | 149.35 | AE2-221 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 903 | 142.6 | 149.35 | AE2-221 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 903 | 142.6 | 149.35 | AE2-221 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.21 | 149.27 | AE2-221 | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.14 | 149.2 | AE2-221 | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.89 | 148.13 | AE2-221 | AP_P2-3_PE-500-016_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.96 | 148.1 | AE2-221 | AP_P2-3_PE-500-015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.74 | 147.62 | AE2-221 | PJM_500_BG_P4_5_CNSTN_L_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.91 | 147.48 | AE2-221 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.71 | 147.29 | AE2-221 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.73 | 147.28 | AE2-221 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.07 | 147.24 | AE2-221 | AP_P1-2_WP-500-DRT17_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.07 | 147.24 | AE2-221 | AP_P1-2_PE-500-001_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.02 | 147.17 | AE2-221 | AP_P2-3_PE-500-018C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.46 | 147.08 | AE2-221 | PECO_P4_NOTTI85_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.4 | 147.07 | AE2-221 | PECO_P1-2_220-08_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.34 | 147 | AE2-221 | PECO_P4_COOPR125_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3464 | 168.19 | 162.18 | AD2-072 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.34 | 143.65 | AE2-221 | PECO_P4_PEACH025_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.25 | 143.59 | AE2-221 | PECO_P1-2_PBTIE1_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 911 | 148.84 | 143.04 | AE2-221 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204502 | 27JACKSON | 204514 | 27TMI | 1 | 230 | 227 | 781 | 132.83 | 141.35 | AE2-221 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204502 | 27JACKSON | 204514 | 27TMI | 1 | 230 | 227 | 781 | 132.84 | 141.34 | AE2-221 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204502 | 27JACKSON | 204514 | 27TMI | 1 | 230 | 227 | 781 | 132.84 | 141.34 | AE2-221 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 903 | 135.53 | 139.52 | AE2-221 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 1031 | 130.69 | 138.98 | AE2-221 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 1031 | 130.18 | 137.91 | AE2-221 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 1031 | 130.19 | 137.89 | AE2-221 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 1031 | 130.19 | 137.89 | AE2-221 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 138.7 | 132.78 | AE2-221 | PECO_P4_PEACH205_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 138.56 | 132.42 | AE2-221 | PECO_P1-2_PBTIE2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208078 | SAKR | 1 | 230 | 229 | 903 | 124.32 | 132.31 | AE2-221 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208078 | SAKR | 1 | 230 | 229 | 903 | 124.33 | 132.29 | AE2-221 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208078 | SAKR | 1 | 230 | 229 | 903 | 124.33 | 132.29 | AE2-221 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 137.64 | 131.57 | AE2-221 | PECO_P4_PEACH055_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204502 | 27JACKSON | 204514 | 27TMI | 1 | 230 | 227 | 781 | 125.2 | 130.82 | AE2-221 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 1031 | 124.6 | 129.13 | AE2-221 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 128.91 | 127.23 | AE2-221 | DVP_P4-2: 514T595_SRT-SW |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 132.92 | 127.12 | AE2-221 | PECO_P4_PEACH015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208020 | MANO TR3 | 1 | 230 | 229 | 793 | 112.14 | 126.01 | AE2-221 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 131.62 | 125.82 | AE2-221 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 127.16 | 125.51 | AE2-221 | DVP_P4-2: 51482_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 127.16 | 125.42 | AE2-221 | DVP_P1-2: LN 514_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 127.16 | 125.42 | AE2-221 | AP_P1-2_PE-500-407T_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208020 | MANO TR3 | 1 | 230 | 229 | 793 | 111.3 | 124.47 | AE2-221 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208020 | MANO TR3 | 1 | 230 | 229 | 793 | 111.31 | 124.45 | AE2-221 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208020 | MANO TR3 | 1 | 230 | 229 | 793 | 111.3 | 124.45 | AE2-221 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208078 | SAKR | 1 | 230 | 229 | 903 | 117.07 | 122.35 | AE2-221 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204512 | 27S.RDG | 204693 | 27BOONETOWN | 1 | 230 | 227 | 607 | 107.24 | 122.06 | AE2-221 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204512 | 27S.RDG | 204693 | 27BOONETOWN | 1 | 230 | 227 | 607 | 107.21 | 122 | AE2-221 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204512 | 27S.RDG | 204693 | 27BOONETOWN | 1 | 230 | 227 | 607 | 107.21 | 122 | AE2-221 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200025 | W CHAPEL | 1 | 500 | 225 | 1732 | 123.68 | 121.88 | AE2-221 | PEPCO_P4_PP41_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208031 | MLWD TR2 | 1 | 230 | 229 | 911 | 111.62 | 121.05 | AE2-221 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208031 | MLWD TR2 | 1 | 230 | 229 | 911 | 111.63 | 121.04 | AE2-221 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208031 | MLWD TR2 | 1 | 230 | 229 | 911 | 111.63 | 121.04 | AE2-221 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 114.67 | 118.39 | AE2-221 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 114.33 | 118.05 | AE2-221 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 114.31 | 117.99 | AE2-221 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 114.31 | 117.99 | AE2-221 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 113.98 | 117.66 | AE2-221 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 113.98 | 117.66 | AE2-221 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 122.53 | 117.18 | AE2-221 | PECO_P4_PEACH225_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 117.34 | 115.48 | AE2-221 | AP_P2-3_PE-500-019C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 2 | 500/230 | 225/232 | 2168 | 109.63 | 114.96 | AE2-221 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 2 | 500/230 | 225/232 | 2168 | 109.45 | 114.75 | AE2-221 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 2 | 500/230 | 225/232 | 2168 | 109.45 | 114.74 | AE2-221 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 1 | 500/230 | 225/232 | 2168 | 109.4 | 114.72 | AE2-221 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 1 | 500/230 | 225/232 | 2168 | 109.22 | 114.5 | AE2-221 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 1 | 500/230 | 225/232 | 2168 | 109.22 | 114.5 | AE2-221 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220964 | GRACETON | 220999 | BAGLEY2 | 13 | 230 | 232 | 1795 | 113.4 | 114.44 | AE2-221 | BG_P4_5_GRCTN_3T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208020 | MANO TR3 | 1 | 230 | 229 | 793 | 104.13 | 113.92 | AE2-221 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208020 | MANO TR3 | 208031 | MLWD TR2 | 1 | 230 | 229 | 903 | 102.45 | 113.61 | AE2-221 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208020 | MANO TR3 | 208031 | MLWD TR2 | 1 | 230 | 229 | 903 | 101.74 | 112.41 | AE2-221 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208020 | MANO TR3 | 208031 | MLWD TR2 | 1 | 230 | 229 | 903 | 101.74 | 112.4 | AE2-221 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208020 | MANO TR3 | 208031 | MLWD TR2 | 1 | 230 | 229 | 903 | 101.74 | 112.4 | AE2-221 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208031 | MLWD TR2 | 1 | 230 | 229 | 911 | 104.88 | 111.58 | AE2-221 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220980 | RAPHAEL | 220999 | BAGLEY2 | 13 | 230 | 232 | 1795 | 108.99 | 111.2 | AE2-221 | BG_P4_5_GRCTN_3T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 99.65 | 103.56 | AE2-221 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 99.65 | 103.55 | AE2-221 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 99.65 | 103.55 | AE2-221 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208020 | MANO TR3 | 208031 | MLWD TR2 | 1 | 230 | 229 | 903 | 95.38 | 103.2 | AE2-221 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 98.82 | 100.87 | AE2-221 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 223960 | BRG 1T 230 | 1 | 500/230 | 225/233 | 1498 | 100.26 | 100.64 | AE2-221 | PEPCO_P4_PP41_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.51 | 148.84 | AE2-224 | AP_P2-3_PE-500-016_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.58 | 148.81 | AE2-224 | AP_P2-3_PE-500-015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.69 | 147.96 | AE2-224 | AP_P1-2_WP-500-DRT17_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.69 | 147.96 | AE2-224 | AP_P1-2_PE-500-001_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.64 | 147.89 | AE2-224 | AP_P2-3_PE-500-018C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.64 | 147.88 | AE2-224 | AP_P2-3_PE-500-018D_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.15 | 147.32 | AE2-224 | AP_P2-3_WP-500-466_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.15 | 147.32 | AE2-224 | AP_P2-3_WP-500-DRT19_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.15 | 147.32 | AE2-224 | AP_P1-2_WP-500-006_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.15 | 147.32 | AE2-224 | AP_P1-2_PE-500-004_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200009 | JUNI | 208004 | JUNI | 2 | 500/230 | 225/229 | 1040 | 107.89 | 107.31 | AE2-224 | PL_10_P42_000140_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 99.93 | 104.05 | AE2-224 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 99.93 | 104.05 | AE2-224 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 99.93 | 104.05 | AE2-224 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 99 | 102.6 | AE2-224 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 99.1 | 101.29 | AE2-224 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 225.54 | 236.91 | AE2-230 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 223.54 | 236.91 | AE2-230 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 225.48 | 236.84 | AE2-230 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 223.47 | 236.84 | AE2-230 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 225.48 | 236.84 | AE2-230 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 223.47 | 236.84 | AE2-230 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 213.49 | 226.75 | AE2-230 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 213.43 | 226.69 | AE2-230 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 213.43 | 226.69 | AE2-230 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 209.23 | 223.54 | AE2-230 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 209.17 | 223.48 | AE2-230 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 209.17 | 223.48 | AE2-230 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 210.64 | 217.73 | AE2-230 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 208.64 | 217.73 | AE2-230 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 199.1 | 208.16 | AE2-230 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 194.84 | 204.82 | AE2-230 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 172.73 | 167.74 | AE2-230 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 163.6 | 164.87 | AE2-230 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3464 | 168.08 | 162.07 | AD2-074 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 161.73 | 161.79 | AE2-230 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 161.73 | 161.78 | AE2-230 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 161.72 | 161.78 | AE2-230 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 153.48 | 157.92 | AE2-230 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 161.99 | 157.11 | AE2-230 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 161.99 | 157.11 | AE2-230 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 151.8 | 156.6 | AE2-230 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 161.46 | 154.24 | AE2-230 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 148.44 | 152.95 | AE2-230 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 152.79 | 151.16 | AE2-230 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 155.56 | 150.41 | AE2-230 | PN_P1-2_PN-500-010T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 903 | 142.71 | 149.47 | AE2-230 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 903 | 142.71 | 149.47 | AE2-230 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 903 | 142.7 | 149.46 | AE2-230 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.28 | 149.34 | AE2-230 | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.21 | 149.27 | AE2-230 | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.89 | 148.08 | AE2-230 | AP_P2-3_PE-500-016_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.96 | 148.05 | AE2-230 | AP_P2-3_PE-500-015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.88 | 147.75 | AE2-230 | PJM_500_BG_P4_5_CNSTN_L_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.16 | 147.73 | AE2-230 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.96 | 147.54 | AE2-230 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.99 | 147.53 | AE2-230 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.72 | 147.33 | AE2-230 | PECO_P4_NOTTI85_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.66 | 147.32 | AE2-230 | PECO_P1-2_220-08_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.59 | 147.25 | AE2-230 | PECO_P4_COOPR125_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.08 | 147.2 | AE2-230 | AP_P1-2_PE-500-001_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.08 | 147.2 | AE2-230 | AP_P1-2_WP-500-DRT17_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.03 | 147.14 | AE2-230 | AP_P2-3_PE-500-018C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3464 | 168.92 | 162.89 | AD2-076 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.68 | 143.98 | AE2-230 | PECO_P4_PEACH025_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.52 | 143.86 | AE2-230 | PECO_P1-2_PBTIE1_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 911 | 148.97 | 143.09 | AE2-230 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204502 | 27JACKSON | 204514 | 27TMI | 1 | 230 | 227 | 781 | 133.02 | 141.56 | AE2-230 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204502 | 27JACKSON | 204514 | 27TMI | 1 | 230 | 227 | 781 | 133.02 | 141.56 | AE2-230 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204502 | 27JACKSON | 204514 | 27TMI | 1 | 230 | 227 | 781 | 133 | 141.55 | AE2-230 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 903 | 135.64 | 139.6 | AE2-230 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 1031 | 130.31 | 138.06 | AE2-230 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 1031 | 130.31 | 138.06 | AE2-230 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 1031 | 130.3 | 138.06 | AE2-230 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 138.93 | 132.99 | AE2-230 | PECO_P4_PEACH205_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 138.81 | 132.67 | AE2-230 | PECO_P1-2_PBTIE2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208078 | SAKR | 1 | 230 | 229 | 903 | 124.49 | 132.49 | AE2-230 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208078 | SAKR | 1 | 230 | 229 | 903 | 124.49 | 132.49 | AE2-230 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208078 | SAKR | 1 | 230 | 229 | 903 | 124.49 | 132.48 | AE2-230 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 137.88 | 131.8 | AE2-230 | PECO_P4_PEACH055_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 1031 | 124.71 | 129.24 | AE2-230 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 133.17 | 127.36 | AE2-230 | PECO_P4_PEACH015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 128.94 | 127.22 | AE2-230 | DVP_P4-2: 514T595_SRT-SW |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 131.87 | 126.05 | AE2-230 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 127.2 | 125.5 | AE2-230 | DVP_P4-2: 51482_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 127.2 | 125.41 | AE2-230 | DVP_P1-2: LN 514_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 127.2 | 125.41 | AE2-230 | AP_P1-2_PE-500-407T_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208020 | MANO TR3 | 1 | 230 | 229 | 793 | 111.47 | 124.66 | AE2-230 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208020 | MANO TR3 | 1 | 230 | 229 | 793 | 111.48 | 124.66 | AE2-230 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208020 | MANO TR3 | 1 | 230 | 229 | 793 | 111.48 | 124.66 | AE2-230 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208078 | SAKR | 1 | 230 | 229 | 903 | 117.22 | 122.49 | AE2-230 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200025 | W CHAPEL | 1 | 500 | 225 | 1732 | 123.72 | 121.92 | AE2-230 | PEPCO_P4_PP41_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208031 | MLWD TR2 | 1 | 230 | 229 | 911 | 111.78 | 121.23 | AE2-230 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208031 | MLWD TR2 | 1 | 230 | 229 | 911 | 111.78 | 121.23 | AE2-230 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208031 | MLWD TR2 | 1 | 230 | 229 | 911 | 111.78 | 121.22 | AE2-230 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 114.71 | 118.41 | AE2-230 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 114.37 | 118.07 | AE2-230 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 122.77 | 117.4 | AE2-230 | PECO_P4_PEACH225_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 117.4 | 115.49 | AE2-230 | AP_P2-3_PE-500-019C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 2 | 500/230 | 225/232 | 2168 | 109.66 | 114.97 | AE2-230 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 2 | 500/230 | 225/232 | 2168 | 109.48 | 114.75 | AE2-230 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 2 | 500/230 | 225/232 | 2168 | 109.48 | 114.75 | AE2-230 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 1 | 500/230 | 225/232 | 2168 | 109.43 | 114.72 | AE2-230 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 1 | 500/230 | 225/232 | 2168 | 109.25 | 114.51 | AE2-230 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 1 | 500/230 | 225/232 | 2168 | 109.25 | 114.51 | AE2-230 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208031 | MLWD TR2 | 1 | 230 | 229 | 911 | 105.03 | 111.72 | AE2-230 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 99.5 | 103.41 | AE2-230 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 99.51 | 103.41 | AE2-230 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 99.51 | 103.41 | AE2-230 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208020 | MANO TR3 | 208031 | MLWD TR2 | 1 | 230 | 229 | 903 | 95.52 | 103.33 | AE2-230 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 98.58 | 102.08 | AE2-230 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 98.68 | 100.71 | AE2-230 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 225.69 | 237.14 | AE2-253 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 223.68 | 237.14 | AE2-253 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 223.62 | 237.09 | AE2-253 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 225.62 | 237.09 | AE2-253 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 225.62 | 237.08 | AE2-253 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 223.62 | 237.08 | AE2-253 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 213.63 | 226.98 | AE2-253 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 213.56 | 226.93 | AE2-253 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 213.56 | 226.92 | AE2-253 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 209.37 | 223.77 | AE2-253 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 209.31 | 223.72 | AE2-253 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 209.3 | 223.71 | AE2-253 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 210.78 | 217.93 | AE2-253 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 208.78 | 217.93 | AE2-253 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 199.24 | 208.36 | AE2-253 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 194.98 | 205.02 | AE2-253 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 172.82 | 167.84 | AE2-253 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 163.69 | 165.01 | AE2-253 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3464 | 168.24 | 162.23 | AD2-085 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 161.83 | 161.91 | AE2-253 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 161.83 | 161.91 | AE2-253 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 161.82 | 161.9 | AE2-253 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 153.58 | 158.04 | AE2-253 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.08 | 157.2 | AE2-253 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.08 | 157.2 | AE2-253 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 151.9 | 156.72 | AE2-253 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 161.57 | 154.35 | AE2-253 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 148.54 | 153.07 | AE2-253 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 152.89 | 151.28 | AE2-253 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 155.66 | 150.5 | AE2-253 | PN_P1-2_PN-500-010T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 903 | 142.79 | 149.61 | AE2-253 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 903 | 142.78 | 149.61 | AE2-253 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 903 | 142.77 | 149.6 | AE2-253 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.38 | 149.46 | AE2-253 | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.31 | 149.39 | AE2-253 | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.99 | 148.2 | AE2-253 | AP_P2-3_PE-500-016_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.06 | 148.17 | AE2-253 | AP_P2-3_PE-500-015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.97 | 147.84 | AE2-253 | PJM_500_BG_P4_5_CNSTN_L_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.26 | 147.83 | AE2-253 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.06 | 147.64 | AE2-253 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.09 | 147.62 | AE2-253 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.82 | 147.43 | AE2-253 | PECO_P4_NOTTI85_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.76 | 147.41 | AE2-253 | PECO_P1-2_220-08_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.69 | 147.35 | AE2-253 | PECO_P4_COOPR125_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.17 | 147.32 | AE2-253 | AP_P1-2_PE-500-001_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.17 | 147.32 | AE2-253 | AP_P1-2_WP-500-DRT17_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.12 | 147.25 | AE2-253 | AP_P2-3_PE-500-018C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3464 | 167.86 | 161.86 | AD2-093 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.79 | 144.09 | AE2-253 | PECO_P4_PEACH025_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.64 | 143.97 | AE2-253 | PECO_P1-2_PBTIE1_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 911 | 149.05 | 143.17 | AE2-253 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 1031 | 130.38 | 138.2 | AE2-253 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 1031 | 130.38 | 138.19 | AE2-253 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 1031 | 130.37 | 138.18 | AE2-253 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 139.03 | 133.09 | AE2-253 | PECO_P4_PEACH205_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 138.92 | 132.77 | AE2-253 | PECO_P1-2_PBTIE2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208078 | SAKR | 1 | 230 | 229 | 903 | 124.57 | 132.63 | AE2-253 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 137.98 | 131.9 | AE2-253 | PECO_P4_PEACH055_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 133.29 | 127.47 | AE2-253 | PECO_P4_PEACH015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 128.58 | 126.89 | AE2-253 | DVP_P4-2: 514T595_SRT-SW |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 131.97 | 126.15 | AE2-253 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 126.83 | 125.11 | AE2-253 | DVP_P4-2: 51482_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 126.83 | 125.02 | AE2-253 | DVP_P1-2: LN 514_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 126.83 | 125.02 | AE2-253 | AP_P1-2_PE-500-407T_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208020 | MANO TR3 | 1 | 230 | 229 | 793 | 111.56 | 124.74 | AE2-253 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208020 | MANO TR3 | 1 | 230 | 229 | 793 | 111.56 | 124.74 | AE2-253 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208020 | MANO TR3 | 1 | 230 | 229 | 793 | 111.56 | 124.74 | AE2-253 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200025 | W CHAPEL | 1 | 500 | 225 | 1732 | 123.72 | 121.93 | AE2-253 | PEPCO_P4_PP41_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 122.87 | 117.5 | AE2-253 | PECO_P4_PEACH225_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 117.04 | 115.11 | AE2-253 | AP_P2-3_PE-500-019C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 2 | 500/230 | 225/232 | 2168 | 109.7 | 115.02 | AE2-253 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 2 | 500/230 | 225/232 | 2168 | 109.53 | 114.81 | AE2-253 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 2 | 500/230 | 225/232 | 2168 | 109.53 | 114.81 | AE2-253 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 1 | 500/230 | 225/232 | 2168 | 109.47 | 114.78 | AE2-253 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 1 | 500/230 | 225/232 | 2168 | 109.3 | 114.57 | AE2-253 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 1 | 500/230 | 225/232 | 2168 | 109.3 | 114.57 | AE2-253 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 99.54 | 103.48 | AE2-253 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 99.54 | 103.48 | AE2-253 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 99.54 | 103.48 | AE2-253 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 98.62 | 102.15 | AE2-253 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 98.71 | 100.77 | AE2-253 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.52 | 148.08 | AE2-254 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.32 | 147.89 | AE2-254 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.34 | 147.88 | AE2-254 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.07 | 147.68 | AE2-254 | PECO_P4_NOTTI85_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.01 | 147.67 | AE2-254 | PECO_P1-2_220-08_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.94 | 147.6 | AE2-254 | PECO_P4_COOPR125_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.6 | 147.41 | AE2-254 | PECO_P1-2_220-93_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 148.34 | 142.99 | AE2-254 | AP_P2-3_WP-500-696_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 148.34 | 142.99 | AE2-254 | AP_P2-3_WP-500-707T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 148.34 | 142.97 | AE2-254 | AP_P2-3_WP-500-706T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3464 | 168.15 | 162.14 | AD2-134 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 161.83 | 154.61 | AE2-282 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.49 | 148.05 | AE2-282 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.29 | 147.87 | AE2-282 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.32 | 147.85 | AE2-282 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.05 | 147.66 | AE2-282 | PECO_P4_NOTTI85_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.99 | 147.64 | AE2-282 | PECO_P1-2_220-08_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.92 | 147.58 | AE2-282 | PECO_P4_COOPR125_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 151.78 | 147.46 | AE2-282 | AP_P2-3_PE-500-016_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 151.82 | 147.44 | AE2-282 | AP_P2-3_PE-500-015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.58 | 147.39 | AE2-282 | PECO_P1-2_220-93_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 151.3 | 146.98 | AE2-282 | AP_P1-2_WP-500-DRT17_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 151.04 | 144.32 | AE2-282 | PECO_P4_PEACH025_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.92 | 144.24 | AE2-282 | PECO_P1-2_PBTIE1_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 139.18 | 133.02 | AE2-282 | PECO_P1-2_PBTIE2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3464 | 168.1 | 162.09 | AD2-158 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.3 | 157.43 | AE2-290 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.3 | 157.43 | AE2-290 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 161.77 | 154.55 | AE2-290 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 155.88 | 150.73 | AE2-290 | PN_P1-2_PN-500-010T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.19 | 148.06 | AE2-290 | PJM_500_BG_P4_5_CNSTN_L_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.44 | 148 | AE2-290 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.24 | 147.81 | AE2-290 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.26 | 147.8 | AE2-290 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.99 | 147.6 | AE2-290 | PECO_P4_NOTTI85_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.93 | 147.59 | AE2-290 | PECO_P1-2_220-08_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.86 | 147.52 | AE2-290 | PECO_P4_COOPR125_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.97 | 144.25 | AE2-290 | PECO_P4_PEACH025_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.86 | 144.19 | AE2-290 | PECO_P1-2_PBTIE1_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 138.77 | 140.93 | AE2-290 | AP_P2-3_WP-500-DRT45_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 138.77 | 140.93 | AE2-290 | AP_P1-2_WP-500-008_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 137.18 | 139.15 | AE2-290 | AP_P2-3_WP-500-706T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 136.66 | 138.86 | AE2-290 | PN_P2-3_PN-500-DRT28_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 136.66 | 138.86 | AE2-290 | PN_P2-3_PN-500-004-DRT-002_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 136.66 | 138.86 | AE2-290 | PN_P2-3_PN-500-DRT32_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 136.59 | 138.77 | AE2-290 | AP_P1-2_WP-500-303T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 136.57 | 138.75 | AE2-290 | AP_P2-3_WP-500-461T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 136.57 | 138.75 | AE2-290 | AP_P2-3_WP-500-DRT40_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 136.57 | 138.75 | AE2-290 | AP_P2-3_WP-500-DRT41_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 139.24 | 133.3 | AE2-290 | PECO_P4_PEACH205_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 139.12 | 132.97 | AE2-290 | PECO_P1-2_PBTIE2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 138.18 | 132.09 | AE2-290 | PECO_P4_PEACH055_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 133.51 | 127.69 | AE2-290 | PECO_P4_PEACH015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 132.18 | 126.35 | AE2-290 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204512 | 27S.RDG | 204693 | 27BOONETOWN | 1 | 230 | 227 | 607 | 107.69 | 123.51 | AE2-290 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 123.08 | 117.7 | AE2-290 | PECO_P4_PEACH225_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 225.7 | 237.25 | AE2-297 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 223.69 | 237.25 | AE2-297 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 225.63 | 237.19 | AE2-297 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 223.63 | 237.19 | AE2-297 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 225.63 | 237.19 | AE2-297 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 223.62 | 237.19 | AE2-297 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 213.64 | 227.08 | AE2-297 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 213.57 | 227.03 | AE2-297 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 213.57 | 227.03 | AE2-297 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 209.38 | 223.88 | AE2-297 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 209.31 | 223.82 | AE2-297 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 209.31 | 223.82 | AE2-297 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3464 | 168.25 | 162.23 | AD2-160 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 153.68 | 158.17 | AE2-297 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.14 | 157.26 | AE2-297 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.14 | 157.26 | AE2-297 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 151.99 | 156.84 | AE2-297 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 161.57 | 154.36 | AE2-297 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 148.63 | 153.19 | AE2-297 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 155.71 | 150.56 | AE2-297 | PN_P1-2_PN-500-010T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.47 | 149.57 | AE2-297 | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.4 | 149.5 | AE2-297 | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.12 | 148.38 | AE2-297 | AP_P2-3_PE-500-016_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.18 | 148.35 | AE2-297 | AP_P2-3_PE-500-015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.02 | 147.9 | AE2-297 | PJM_500_BG_P4_5_CNSTN_L_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.26 | 147.83 | AE2-297 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.06 | 147.64 | AE2-297 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.09 | 147.63 | AE2-297 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.29 | 147.5 | AE2-297 | AP_P1-2_WP-500-DRT17_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.29 | 147.5 | AE2-297 | AP_P1-2_PE-500-001_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.82 | 147.43 | AE2-297 | PECO_P4_NOTTI85_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.24 | 147.43 | AE2-297 | AP_P2-3_PE-500-018C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.76 | 147.42 | AE2-297 | PECO_P1-2_220-08_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.69 | 147.35 | AE2-297 | PECO_P4_COOPR125_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3464 | 167.98 | 161.98 | AD2-163 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.76 | 144.06 | AE2-297 | PECO_P4_PEACH025_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.66 | 143.99 | AE2-297 | PECO_P1-2_PBTIE1_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 139.06 | 133.12 | AE2-297 | PECO_P4_PEACH205_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 138.93 | 132.78 | AE2-297 | PECO_P1-2_PBTIE2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 138 | 131.91 | AE2-297 | PECO_P4_PEACH055_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 133.31 | 127.49 | AE2-297 | PECO_P4_PEACH015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 131.99 | 126.17 | AE2-297 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 122.89 | 117.53 | AE2-297 | PECO_P4_PEACH225_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 144.32 | 139.17 | AE2-303 | PL_10_P42_100570_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 144.32 | 139.17 | AE2-303 | PL_10_P42_100570_A_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 143.51 | 138.38 | AE2-303 | PL_10_P12_000085_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 143.41 | 138.29 | AE2-303 | PN_P2-3_PN-500-004-DRT-008_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 143.41 | 138.29 | AE2-303 | PN_P2-3_PN-500-DRT31_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 143.04 | 137.92 | AE2-303 | PL_30_P42_000131_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3464 | 168.25 | 162.24 | AD2-180 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 153.79 | 158.29 | AE2-318 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.25 | 157.38 | AE2-318 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.25 | 157.38 | AE2-318 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 152.1 | 156.97 | AE2-318 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 161.73 | 154.5 | AE2-318 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 148.74 | 153.32 | AE2-318 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 155.83 | 150.68 | AE2-318 | PN_P1-2_PN-500-010T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.57 | 149.69 | AE2-318 | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.5 | 149.62 | AE2-318 | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.21 | 148.49 | AE2-318 | AP_P2-3_PE-500-016_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.27 | 148.46 | AE2-318 | AP_P2-3_PE-500-015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.14 | 148.01 | AE2-318 | PJM_500_BG_P4_5_CNSTN_L_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.4 | 147.96 | AE2-318 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.2 | 147.77 | AE2-318 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.22 | 147.76 | AE2-318 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.39 | 147.6 | AE2-318 | AP_P1-2_PE-500-001_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.39 | 147.6 | AE2-318 | AP_P1-2_WP-500-DRT17_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.95 | 147.56 | AE2-318 | PECO_P4_NOTTI85_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.89 | 147.55 | AE2-318 | PECO_P1-2_220-08_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.34 | 147.53 | AE2-318 | AP_P2-3_PE-500-018C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.82 | 147.48 | AE2-318 | PECO_P4_COOPR125_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3464 | 168.61 | 162.59 | AD2-213 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.93 | 144.22 | AE2-318 | PECO_P4_PEACH025_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.81 | 144.14 | AE2-318 | PECO_P1-2_PBTIE1_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 139.19 | 133.25 | AE2-318 | PECO_P4_PEACH205_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 139.08 | 132.92 | AE2-318 | PECO_P1-2_PBTIE2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 138.13 | 132.04 | AE2-318 | PECO_P4_PEACH055_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 133.46 | 127.64 | AE2-318 | PECO_P4_PEACH015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 132.13 | 126.31 | AE2-318 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204512 | 27S.RDG | 204693 | 27BOONETOWN | 1 | 230 | 227 | 607 | 107.68 | 123.45 | AE2-318 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 123.03 | 117.66 | AE2-318 | PECO_P4_PEACH225_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3464 | 167.51 | 161.51 | AE1-044 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 153.79 | 158.3 | AE2-319 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.26 | 157.39 | AE2-319 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.26 | 157.38 | AE2-319 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 152.1 | 156.98 | AE2-319 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 161.73 | 154.51 | AE2-319 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 148.74 | 153.33 | AE2-319 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 155.83 | 150.68 | AE2-319 | PN_P1-2_PN-500-010T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.58 | 149.7 | AE2-319 | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.51 | 149.63 | AE2-319 | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.22 | 148.5 | AE2-319 | AP_P2-3_PE-500-016_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.28 | 148.47 | AE2-319 | AP_P2-3_PE-500-015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.14 | 148.01 | AE2-319 | PJM_500_BG_P4_5_CNSTN_L_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.4 | 147.97 | AE2-319 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.2 | 147.78 | AE2-319 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.23 | 147.76 | AE2-319 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.39 | 147.61 | AE2-319 | AP_P1-2_WP-500-DRT17_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.39 | 147.61 | AE2-319 | AP_P1-2_PE-500-001_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.96 | 147.57 | AE2-319 | PECO_P4_NOTTI85_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.9 | 147.55 | AE2-319 | PECO_P1-2_220-08_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.34 | 147.54 | AE2-319 | AP_P2-3_PE-500-018C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.83 | 147.49 | AE2-319 | PECO_P4_COOPR125_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3464 | 168.2 | 162.19 | AE1-056 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.93 | 144.22 | AE2-319 | PECO_P4_PEACH025_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.82 | 144.14 | AE2-319 | PECO_P1-2_PBTIE1_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 139.2 | 133.26 | AE2-319 | PECO_P4_PEACH205_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 139.08 | 132.93 | AE2-319 | PECO_P1-2_PBTIE2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 138.14 | 132.05 | AE2-319 | PECO_P4_PEACH055_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 133.46 | 127.64 | AE2-319 | PECO_P4_PEACH015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 132.13 | 126.31 | AE2-319 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204512 | 27S.RDG | 204693 | 27BOONETOWN | 1 | 230 | 227 | 607 | 107.68 | 123.46 | AE2-319 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 123.04 | 117.66 | AE2-319 | PECO_P4_PEACH225_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 223.69 | 237.14 | AE2-333 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 225.7 | 237.14 | AE2-333 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 223.63 | 237.08 | AE2-333 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 223.63 | 237.08 | AE2-333 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 225.64 | 237.08 | AE2-333 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 225.63 | 237.08 | AE2-333 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 213.64 | 226.98 | AE2-333 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 213.58 | 226.92 | AE2-333 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 213.58 | 226.92 | AE2-333 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 209.38 | 223.77 | AE2-333 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 209.32 | 223.71 | AE2-333 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 209.32 | 223.71 | AE2-333 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 210.8 | 217.93 | AE2-333 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 208.79 | 217.93 | AE2-333 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 199.25 | 208.37 | AE2-333 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 194.99 | 205.02 | AE2-333 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 172.85 | 167.88 | AE2-333 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 163.73 | 165.04 | AE2-333 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3464 | 168.14 | 162.13 | AE1-084 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 161.86 | 161.94 | AE2-333 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 161.86 | 161.94 | AE2-333 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 161.85 | 161.94 | AE2-333 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 153.58 | 158.03 | AE2-333 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.08 | 157.21 | AE2-333 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.08 | 157.2 | AE2-333 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 151.89 | 156.71 | AE2-333 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 161.57 | 154.35 | AE2-333 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 148.53 | 153.06 | AE2-333 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 155.66 | 150.5 | AE2-333 | PN_P1-2_PN-500-010T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.37 | 149.45 | AE2-333 | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.3 | 149.37 | AE2-333 | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.93 | 148.11 | AE2-333 | AP_P2-3_PE-500-016_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.99 | 148.08 | AE2-333 | AP_P2-3_PE-500-015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.97 | 147.84 | AE2-333 | PJM_500_BG_P4_5_CNSTN_L_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.26 | 147.83 | AE2-333 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.06 | 147.64 | AE2-333 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.09 | 147.63 | AE2-333 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.82 | 147.43 | AE2-333 | PECO_P4_NOTTI85_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.76 | 147.42 | AE2-333 | PECO_P1-2_220-08_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.69 | 147.35 | AE2-333 | PECO_P4_COOPR125_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.11 | 147.24 | AE2-333 | AP_P1-2_WP-500-DRT17_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.11 | 147.24 | AE2-333 | AP_P1-2_PE-500-001_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.08 | 147.19 | AE2-333 | AP_P2-3_PE-500-018C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3464 | 168.23 | 162.22 | AE1-100 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.8 | 144.09 | AE2-333 | PECO_P4_PEACH025_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.64 | 143.98 | AE2-333 | PECO_P1-2_PBTIE1_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 911 | 149.09 | 143.22 | AE2-333 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 1031 | 130.38 | 138.18 | AE2-333 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 1031 | 130.38 | 138.18 | AE2-333 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 1031 | 130.37 | 138.17 | AE2-333 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 139.03 | 133.1 | AE2-333 | PECO_P4_PEACH205_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 138.92 | 132.77 | AE2-333 | PECO_P1-2_PBTIE2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208078 | SAKR | 1 | 230 | 229 | 903 | 124.58 | 132.63 | AE2-333 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 137.99 | 131.9 | AE2-333 | PECO_P4_PEACH055_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 129.95 | 128.2 | AE2-333 | DVP_P4-2: 514T595_SRT-SW |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 133.29 | 127.47 | AE2-333 | PECO_P4_PEACH015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 128.23 | 126.51 | AE2-333 | DVP_P4-2: 51482_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 128.23 | 126.42 | AE2-333 | DVP_P1-2: LN 514_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 128.23 | 126.42 | AE2-333 | AP_P1-2_PE-500-407T_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 2 | 230 | 233 | 793 | 128.03 | 126.26 | AE2-333 | DVP_P4-2: 514T595_SRT-SW |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 793 | 128.03 | 126.26 | AE2-333 | DVP_P4-2: 514T595_SRT-SW |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 131.97 | 126.15 | AE2-333 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 2 | 230 | 233 | 793 | 126.8 | 125.07 | AE2-333 | DVP_P4-2: 51482_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 793 | 126.8 | 125.07 | AE2-333 | DVP_P4-2: 51482_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 793 | 126.8 | 125 | AE2-333 | DVP_P1-2: LN 514_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 793 | 126.8 | 125 | AE2-333 | AP_P1-2_PE-500-407T_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 2 | 230 | 233 | 793 | 126.8 | 125 | AE2-333 | AP_P1-2_PE-500-407T_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 2 | 230 | 233 | 793 | 126.8 | 125 | AE2-333 | DVP_P1-2: LN 514_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208020 | MANO TR3 | 1 | 230 | 229 | 793 | 111.57 | 124.74 | AE2-333 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208020 | MANO TR3 | 1 | 230 | 229 | 793 | 111.56 | 124.74 | AE2-333 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208020 | MANO TR3 | 1 | 230 | 229 | 793 | 111.57 | 124.74 | AE2-333 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 122.88 | 117.5 | AE2-333 | PECO_P4_PEACH225_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 2 | 230 | 233 | 793 | 120.05 | 117.31 | AE2-333 | PEPCO_P1_PP1_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 793 | 120.05 | 117.31 | AE2-333 | PEPCO_P1_PP2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 118.4 | 116.47 | AE2-333 | AP_P2-3_PE-500-019C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 2 | 500/230 | 225/232 | 2168 | 109.71 | 115.03 | AE2-333 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 2 | 500/230 | 225/232 | 2168 | 109.53 | 114.81 | AE2-333 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 2 | 500/230 | 225/232 | 2168 | 109.53 | 114.81 | AE2-333 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 1 | 500/230 | 225/232 | 2168 | 109.48 | 114.79 | AE2-333 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 1 | 500/230 | 225/232 | 2168 | 109.3 | 114.57 | AE2-333 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 1 | 500/230 | 225/232 | 2168 | 109.3 | 114.57 | AE2-333 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 793 | 114.17 | 111.54 | AE2-333 | PEPCO_P4_PP19_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 2 | 230 | 233 | 793 | 110.97 | 109.06 | AE2-333 | AP_P2-3_PE-500-019C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 793 | 110.97 | 109.06 | AE2-333 | AP_P2-3_PE-500-019C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 99.54 | 103.48 | AE2-333 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 99.54 | 103.48 | AE2-333 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 99.54 | 103.48 | AE2-333 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 98.62 | 102.14 | AE2-333 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 98.71 | 100.77 | AE2-333 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 225.73 | 240.07 | AE2-334 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 215.61 | 229.81 | AE2-334 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 211.34 | 226.62 | AE2-334 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3464 | 167.93 | 161.92 | AE1-101 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 154.21 | 158.79 | AE2-334 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.73 | 157.86 | AE2-334 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.73 | 157.85 | AE2-334 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 152.52 | 157.47 | AE2-334 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 162.39 | 155.14 | AE2-334 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 149.15 | 153.82 | AE2-334 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 156.31 | 151.15 | AE2-334 | PN_P1-2_PN-500-010T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.97 | 150.17 | AE2-334 | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.9 | 150.1 | AE2-334 | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.57 | 148.91 | AE2-334 | AP_P2-3_PE-500-016_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.64 | 148.88 | AE2-334 | AP_P2-3_PE-500-015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.97 | 148.53 | AE2-334 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.6 | 148.46 | AE2-334 | PJM_500_BG_P4_5_CNSTN_L_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.77 | 148.34 | AE2-334 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.8 | 148.33 | AE2-334 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.53 | 148.13 | AE2-334 | PECO_P4_NOTTI85_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.47 | 148.11 | AE2-334 | PECO_P1-2_220-08_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.4 | 148.05 | AE2-334 | PECO_P4_COOPR125_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.75 | 148.02 | AE2-334 | AP_P1-2_WP-500-DRT17_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.75 | 148.02 | AE2-334 | AP_P1-2_PE-500-001_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.7 | 147.95 | AE2-334 | AP_P2-3_PE-500-018C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3464 | 169.99 | 163.95 | AE1-104 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 151.69 | 144.94 | AE2-334 | PECO_P4_PEACH025_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 151.53 | 144.82 | AE2-334 | PECO_P1-2_PBTIE1_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 139.78 | 133.82 | AE2-334 | PECO_P4_PEACH205_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 139.74 | 133.56 | AE2-334 | PECO_P1-2_PBTIE2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 138.75 | 132.64 | AE2-334 | PECO_P4_PEACH055_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 134.17 | 128.32 | AE2-334 | PECO_P4_PEACH015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 132.77 | 126.91 | AE2-334 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 123.69 | 118.28 | AE2-334 | PECO_P4_PEACH225_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.32 | 157.45 | AE2-343 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.32 | 157.45 | AE2-343 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 155.89 | 150.74 | AE2-343 | PN_P1-2_PN-500-010T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.22 | 148.5 | AE2-343 | AP_P2-3_PE-500-016_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.29 | 148.47 | AE2-343 | AP_P2-3_PE-500-015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.51 | 148.08 | AE2-343 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.2 | 148.07 | AE2-343 | PJM_500_BG_P4_5_CNSTN_L_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.31 | 147.89 | AE2-343 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.34 | 147.87 | AE2-343 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.07 | 147.68 | AE2-343 | PECO_P4_NOTTI85_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.01 | 147.66 | AE2-343 | PECO_P1-2_220-08_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.4 | 147.62 | AE2-343 | AP_P1-2_PE-500-001_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.4 | 147.62 | AE2-343 | AP_P1-2_WP-500-DRT17_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.94 | 147.6 | AE2-343 | PECO_P4_COOPR125_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.35 | 147.55 | AE2-343 | AP_P2-3_PE-500-018C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.35 | 147.54 | AE2-343 | AP_P2-3_PE-500-018D_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3464 | 168.61 | 162.59 | AE1-142 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 142.87 | 146.98 | AE2-343 | AP_P2-3_WP-500-466_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 142.87 | 146.98 | AE2-343 | AP_P1-2_WP-500-006_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 142.87 | 146.98 | AE2-343 | AP_P2-3_WP-500-DRT19_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 142.87 | 146.98 | AE2-343 | AP_P1-2_PE-500-004_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3464 | 167.79 | 161.79 | AE1-153 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 162.18 | 154.94 | AF1-015 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.79 | 148.35 | AF1-015 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.59 | 148.16 | AF1-015 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.62 | 148.15 | AF1-015 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.35 | 147.95 | AF1-015 | PECO_P4_NOTTI85_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.29 | 147.94 | AF1-015 | PECO_P1-2_220-08_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.22 | 147.87 | AF1-015 | PECO_P4_COOPR125_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.05 | 147.72 | AF1-015 | AP_P2-3_PE-500-016_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.09 | 147.7 | AF1-015 | AP_P2-3_PE-500-015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.88 | 147.68 | AF1-015 | PECO_P1-2_220-93_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 151.57 | 147.24 | AF1-015 | AP_P1-2_PE-500-001_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 151.44 | 144.71 | AF1-015 | PECO_P4_PEACH025_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 151.29 | 144.6 | AF1-015 | PECO_P1-2_PBTIE1_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 139.52 | 133.34 | AF1-015 | PECO_P1-2_PBTIE2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 138.55 | 132.45 | AF1-015 | PECO_P4_PEACH055_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 133.92 | 128.09 | AF1-015 | PECO_P4_PEACH015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 132.56 | 126.71 | AF1-015 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204512 | 27S.RDG | 204693 | 27BOONETOWN | 1 | 230 | 227 | 607 | 107.71 | 122.14 | AF1-015 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 123.46 | 118.07 | AF1-015 | PECO_P4_PEACH225_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3464 | 167.91 | 161.9 | AE1-155 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.61 | 157.73 | AF1-036 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.6 | 157.73 | AF1-036 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 162.21 | 154.97 | AF1-036 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 156.18 | 151.02 | AF1-036 | PN_P1-2_PN-500-010T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.82 | 148.38 | AF1-036 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.48 | 148.34 | AF1-036 | PJM_500_BG_P4_5_CNSTN_L_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.62 | 148.19 | AF1-036 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.65 | 148.18 | AF1-036 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.38 | 147.98 | AF1-036 | PECO_P4_NOTTI85_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.32 | 147.96 | AF1-036 | PECO_P1-2_220-08_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.25 | 147.9 | AF1-036 | PECO_P4_COOPR125_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 151.48 | 144.75 | AF1-036 | PECO_P4_PEACH025_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 151.33 | 144.63 | AF1-036 | PECO_P1-2_PBTIE1_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 139.55 | 133.38 | AF1-036 | PECO_P1-2_PBTIE2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 138.59 | 132.48 | AF1-036 | PECO_P4_PEACH055_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 133.96 | 128.12 | AF1-036 | PECO_P4_PEACH015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 132.59 | 126.74 | AF1-036 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 123.5 | 118.1 | AF1-036 | PECO_P4_PEACH225_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200762 | 26GARRETT | 235470 | 01GARRET | 1 | 115 | 226/201 | 190 | 98.9 | 100.93 | AF1-039 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200762 | 26GARRETT | 235470 | 01GARRET | 1 | 115 | 226/201 | 190 | 98.9 | 100.93 | AF1-039 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200762 | 26GARRETT | 235470 | 01GARRET | 1 | 115 | 226/201 | 190 | 98.74 | 100.76 | AF1-039 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3464 | 167.92 | 161.92 | AE1-157 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 153.78 | 158.28 | AF1-042 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.28 | 157.4 | AF1-042 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.27 | 157.4 | AF1-042 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 152.09 | 156.96 | AF1-042 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 161.79 | 154.56 | AF1-042 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 148.73 | 153.31 | AF1-042 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 155.85 | 150.69 | AF1-042 | PN_P1-2_PN-500-010T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.57 | 149.68 | AF1-042 | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.5 | 149.61 | AF1-042 | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.18 | 148.44 | AF1-042 | AP_P2-3_PE-500-016_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.25 | 148.41 | AF1-042 | AP_P2-3_PE-500-015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.16 | 148.03 | AF1-042 | PJM_500_BG_P4_5_CNSTN_L_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.46 | 148.02 | AF1-042 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.26 | 147.83 | AF1-042 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.28 | 147.82 | AF1-042 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.01 | 147.62 | AF1-042 | PECO_P4_NOTTI85_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.95 | 147.61 | AF1-042 | PECO_P1-2_220-08_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.36 | 147.56 | AF1-042 | AP_P1-2_WP-500-DRT17_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.36 | 147.56 | AF1-042 | AP_P1-2_PE-500-001_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.89 | 147.54 | AF1-042 | PECO_P4_COOPR125_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.31 | 147.49 | AF1-042 | AP_P2-3_PE-500-018C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3464 | 168.11 | 162.1 | AE1-191 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 151.02 | 144.3 | AF1-042 | PECO_P4_PEACH025_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.87 | 144.2 | AF1-042 | PECO_P1-2_PBTIE1_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 139.24 | 133.3 | AF1-042 | PECO_P4_PEACH205_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 139.13 | 132.98 | AF1-042 | PECO_P1-2_PBTIE2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 138.19 | 132.1 | AF1-042 | PECO_P4_PEACH055_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 133.51 | 127.69 | AF1-042 | PECO_P4_PEACH015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 128.93 | 127.19 | AF1-042 | DVP_P4-2: 514T595_SRT-SW |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 132.18 | 126.35 | AF1-042 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 127.19 | 125.48 | AF1-042 | DVP_P4-2: 51482_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 127.19 | 125.39 | AF1-042 | AP_P1-2_PE-500-407T_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 127.19 | 125.39 | AF1-042 | DVP_P1-2: LN 514_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 123.08 | 117.71 | AF1-042 | PECO_P4_PEACH225_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 117.38 | 115.47 | AF1-042 | AP_P2-3_PE-500-019C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 144.58 | 139.43 | AF1-133 | PL_10_P42_100570_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 144.58 | 139.43 | AF1-133 | PL_10_P42_100570_A_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 143.77 | 138.63 | AF1-133 | PL_10_P12_000085_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 143.67 | 138.54 | AF1-133 | PN_P2-3_PN-500-004-DRT-008_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 143.67 | 138.54 | AF1-133 | PN_P2-3_PN-500-DRT31_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 143.3 | 138.18 | AF1-133 | PL_30_P42_000131_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 225.58 | 236.95 | AF1-147 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 223.57 | 236.95 | AF1-147 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 225.51 | 236.87 | AF1-147 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 223.51 | 236.87 | AF1-147 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 225.51 | 236.87 | AF1-147 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 223.51 | 236.87 | AF1-147 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 213.52 | 226.79 | AF1-147 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 213.46 | 226.72 | AF1-147 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 213.46 | 226.72 | AF1-147 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 209.26 | 223.58 | AF1-147 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 209.2 | 223.51 | AF1-147 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 209.2 | 223.51 | AF1-147 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 210.67 | 217.77 | AF1-147 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 208.67 | 217.77 | AF1-147 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 199.13 | 208.2 | AF1-147 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 194.87 | 204.86 | AF1-147 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 172.72 | 167.75 | AF1-147 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 163.59 | 164.87 | AF1-147 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3464 | 168.19 | 162.18 | AE1-212 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 161.73 | 161.79 | AF1-147 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 161.73 | 161.79 | AF1-147 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 161.72 | 161.79 | AF1-147 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 153.48 | 157.92 | AF1-147 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 161.99 | 157.12 | AF1-147 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 161.99 | 157.12 | AF1-147 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 151.79 | 156.6 | AF1-147 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 161.48 | 154.26 | AF1-147 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 148.43 | 152.95 | AF1-147 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 903 | 144.22 | 152.08 | AF1-147 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 152.79 | 151.16 | AF1-147 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 155.57 | 150.42 | AF1-147 | PN_P1-2_PN-500-010T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 903 | 142.7 | 149.46 | AF1-147 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 903 | 142.7 | 149.46 | AF1-147 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 903 | 142.68 | 149.46 | AF1-147 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.28 | 149.34 | AF1-147 | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.21 | 149.27 | AF1-147 | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.88 | 148.07 | AF1-147 | AP_P2-3_PE-500-016_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.94 | 148.04 | AF1-147 | AP_P2-3_PE-500-015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.89 | 147.76 | AF1-147 | PJM_500_BG_P4_5_CNSTN_L_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.19 | 147.76 | AF1-147 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.99 | 147.57 | AF1-147 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.01 | 147.56 | AF1-147 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.74 | 147.36 | AF1-147 | PECO_P4_NOTTI85_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.68 | 147.34 | AF1-147 | PECO_P1-2_220-08_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.62 | 147.28 | AF1-147 | PECO_P4_COOPR125_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.06 | 147.19 | AF1-147 | AP_P1-2_WP-500-DRT17_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.06 | 147.19 | AF1-147 | AP_P1-2_PE-500-001_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.01 | 147.13 | AF1-147 | AP_P2-3_PE-500-018C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3464 | 169.68 | 163.64 | AE1-229 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.72 | 144.02 | AF1-147 | PECO_P4_PEACH025_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.55 | 143.89 | AF1-147 | PECO_P1-2_PBTIE1_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 911 | 148.96 | 143.09 | AF1-147 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204502 | 27JACKSON | 204514 | 27TMI | 1 | 230 | 227 | 781 | 133.04 | 141.58 | AF1-147 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204502 | 27JACKSON | 204514 | 27TMI | 1 | 230 | 227 | 781 | 133.03 | 141.58 | AF1-147 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204502 | 27JACKSON | 204514 | 27TMI | 1 | 230 | 227 | 781 | 133.04 | 141.58 | AF1-147 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 903 | 135.62 | 139.59 | AF1-147 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 1031 | 130.31 | 138.07 | AF1-147 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 1031 | 130.32 | 138.06 | AF1-147 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 1031 | 130.32 | 138.06 | AF1-147 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 138.94 | 133.01 | AF1-147 | PECO_P4_PEACH205_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 138.83 | 132.69 | AF1-147 | PECO_P1-2_PBTIE2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208078 | SAKR | 1 | 230 | 229 | 903 | 124.49 | 132.5 | AF1-147 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208078 | SAKR | 1 | 230 | 229 | 903 | 124.5 | 132.49 | AF1-147 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208078 | SAKR | 1 | 230 | 229 | 903 | 124.5 | 132.49 | AF1-147 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 137.91 | 131.83 | AF1-147 | PECO_P4_PEACH055_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 1031 | 124.72 | 129.25 | AF1-147 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 133.2 | 127.38 | AF1-147 | PECO_P4_PEACH015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 131.89 | 126.07 | AF1-147 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 127.7 | 125.97 | AF1-147 | DVP_P4-2: 514T595_SRT-SW |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208020 | MANO TR3 | 1 | 230 | 229 | 793 | 111.49 | 124.68 | AF1-147 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208020 | MANO TR3 | 1 | 230 | 229 | 793 | 111.49 | 124.67 | AF1-147 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208020 | MANO TR3 | 1 | 230 | 229 | 793 | 111.49 | 124.67 | AF1-147 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 793 | 126.04 | 124.28 | AF1-147 | DVP_P4-2: 514T595_SRT-SW |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 2 | 230 | 233 | 793 | 126.04 | 124.28 | AF1-147 | DVP_P4-2: 514T595_SRT-SW |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 125.96 | 124.2 | AF1-147 | DVP_P4-2: 51482_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 125.96 | 124.12 | AF1-147 | DVP_P1-2: LN 514_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 125.96 | 124.12 | AF1-147 | AP_P1-2_PE-500-407T_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 2 | 230 | 233 | 793 | 124.8 | 123.03 | AF1-147 | DVP_P4-2: 51482_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 793 | 124.8 | 123.03 | AF1-147 | DVP_P4-2: 51482_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 793 | 124.8 | 122.96 | AF1-147 | DVP_P1-2: LN 514_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 2 | 230 | 233 | 793 | 124.8 | 122.96 | AF1-147 | DVP_P1-2: LN 514_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 2 | 230 | 233 | 793 | 124.8 | 122.96 | AF1-147 | AP_P1-2_PE-500-407T_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 793 | 124.8 | 122.96 | AF1-147 | AP_P1-2_PE-500-407T_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208078 | SAKR | 1 | 230 | 229 | 903 | 117.23 | 122.5 | AF1-147 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200025 | W CHAPEL | 1 | 500 | 225 | 1732 | 123.69 | 121.9 | AF1-147 | PEPCO_P4_PP41_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208031 | MLWD TR2 | 1 | 230 | 229 | 911 | 111.79 | 121.24 | AF1-147 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208031 | MLWD TR2 | 1 | 230 | 229 | 911 | 111.79 | 121.23 | AF1-147 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208031 | MLWD TR2 | 1 | 230 | 229 | 911 | 111.79 | 121.23 | AF1-147 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 114.7 | 118.4 | AF1-147 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 114.36 | 118.06 | AF1-147 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 114.35 | 118 | AF1-147 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 114.35 | 118 | AF1-147 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 122.79 | 117.42 | AF1-147 | PECO_P4_PEACH225_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 2 | 230 | 233 | 793 | 118.02 | 115.25 | AF1-147 | PEPCO_P1_PP1_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 793 | 118.02 | 115.25 | AF1-147 | PEPCO_P1_PP2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 2 | 500/230 | 225/232 | 2168 | 109.65 | 114.96 | AF1-147 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 2 | 500/230 | 225/232 | 2168 | 109.47 | 114.75 | AF1-147 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 2 | 500/230 | 225/232 | 2168 | 109.47 | 114.75 | AF1-147 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 1 | 500/230 | 225/232 | 2168 | 109.42 | 114.72 | AF1-147 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 1 | 500/230 | 225/232 | 2168 | 109.24 | 114.5 | AF1-147 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 1 | 500/230 | 225/232 | 2168 | 109.24 | 114.5 | AF1-147 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 116.19 | 114.23 | AF1-147 | AP_P2-3_PE-500-019C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208031 | MLWD TR2 | 1 | 230 | 229 | 911 | 105.03 | 111.73 | AF1-147 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 793 | 112.09 | 109.44 | AF1-147 | PEPCO_P4_PP19_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 793 | 109.06 | 107.12 | AF1-147 | AP_P2-3_PE-500-019C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 2 | 230 | 233 | 793 | 109.06 | 107.12 | AF1-147 | AP_P2-3_PE-500-019C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 99.47 | 103.38 | AF1-147 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 99.47 | 103.37 | AF1-147 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 99.47 | 103.37 | AF1-147 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 98.54 | 102.04 | AF1-147 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 98.64 | 100.68 | AF1-147 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3464 | 168.87 | 162.85 | AE1-240 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 153.82 | 158.33 | AF1-173 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.3 | 157.43 | AF1-173 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.3 | 157.43 | AF1-173 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 161.81 | 154.59 | AF1-173 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 155.88 | 150.72 | AF1-173 | PN_P1-2_PN-500-010T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.19 | 148.06 | AF1-173 | PJM_500_BG_P4_5_CNSTN_L_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.48 | 148.04 | AF1-173 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.28 | 147.85 | AF1-173 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.3 | 147.84 | AF1-173 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.03 | 147.64 | AF1-173 | PECO_P4_NOTTI85_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.97 | 147.63 | AF1-173 | PECO_P1-2_220-08_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.9 | 147.56 | AF1-173 | PECO_P4_COOPR125_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3464 | 171.16 | 165.09 | AE2-000 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 151.03 | 144.32 | AF1-173 | PECO_P4_PEACH025_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.9 | 144.22 | AF1-173 | PECO_P1-2_PBTIE1_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 136.77 | 139.49 | AF1-173 | DVP_P4-2: 553T564_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 137.16 | 139.12 | AF1-173 | AP_P2-3_WP-500-706T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 136.09 | 138.8 | AF1-173 | DVP_P4-2: 542T553_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 136.16 | 138.43 | AF1-173 | ME_P2-3_ME-115-013C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 135 | 137.68 | AF1-173 | DVP_P1-2: LN 553_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 134.98 | 137.66 | AF1-173 | DVP_P4-2: H2T553_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 134.98 | 137.66 | AF1-173 | DVP_P4-2: H1T553_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 133.96 | 136.2 | AF1-173 | AEP_P4_#7587_05J.FERR 765_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 133.92 | 136.19 | AF1-173 | AEP_P4_#2914_05J.FERR 765_B2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 139.27 | 133.32 | AF1-173 | PECO_P4_PEACH205_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 139.16 | 133 | AF1-173 | PECO_P1-2_PBTIE2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 138.21 | 132.12 | AF1-173 | PECO_P4_PEACH055_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 133.54 | 127.71 | AF1-173 | PECO_P4_PEACH015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 132.21 | 126.38 | AF1-173 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 123.11 | 117.73 | AF1-173 | PECO_P4_PEACH225_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3464 | 170.73 | 164.67 | AE2-020 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 162.18 | 154.94 | AF1-174 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 156.16 | 151 | AF1-174 | PN_P1-2_PN-500-010T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.81 | 148.37 | AF1-174 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.61 | 148.18 | AF1-174 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.64 | 148.16 | AF1-174 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.36 | 147.97 | AF1-174 | PECO_P4_NOTTI85_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.3 | 147.95 | AF1-174 | PECO_P1-2_220-08_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.24 | 147.89 | AF1-174 | PECO_P4_COOPR125_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.06 | 147.73 | AF1-174 | AP_P2-3_PE-500-016_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.1 | 147.71 | AF1-174 | AP_P2-3_PE-500-015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.9 | 147.7 | AF1-174 | PECO_P1-2_220-93_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 151.45 | 144.71 | AF1-174 | PECO_P4_PEACH025_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 151.3 | 144.6 | AF1-174 | PECO_P1-2_PBTIE1_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 139.62 | 133.67 | AF1-174 | PECO_P4_PEACH205_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 139.52 | 133.35 | AF1-174 | PECO_P1-2_PBTIE2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 138.55 | 132.45 | AF1-174 | PECO_P4_PEACH055_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 133.93 | 128.09 | AF1-174 | PECO_P4_PEACH015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 123.47 | 118.08 | AF1-174 | PECO_P4_PEACH225_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 225.91 | 238.24 | AF1-227 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 223.92 | 238.24 | AF1-227 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 222.96 | 236.18 | AF1-227 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 224.95 | 236.18 | AF1-227 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 222.89 | 236.12 | AF1-227 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 224.88 | 236.12 | AF1-227 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 222.89 | 236.12 | AF1-227 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 224.88 | 236.12 | AF1-227 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 213.86 | 228.04 | AF1-227 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 212.93 | 226.04 | AF1-227 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 212.87 | 225.99 | AF1-227 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 212.86 | 225.99 | AF1-227 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 209.6 | 224.84 | AF1-227 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 208.67 | 222.83 | AF1-227 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 208.61 | 222.77 | AF1-227 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 208.61 | 222.77 | AF1-227 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 208.08 | 217.12 | AF1-227 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 210.08 | 217.12 | AF1-227 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 198.57 | 207.57 | AF1-227 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 194.31 | 204.22 | AF1-227 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 172.47 | 167.55 | AF1-227 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 171.49 | 166.11 | AF1-227 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 171.49 | 166.11 | AF1-227 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 171.48 | 166.1 | AF1-227 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 163.3 | 164.56 | AF1-227 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3464 | 170.73 | 164.67 | AE2-021 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 161.41 | 161.47 | AF1-227 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 161.41 | 161.47 | AF1-227 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 161.39 | 161.47 | AF1-227 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 163.56 | 158.68 | AF1-227 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 153.32 | 157.74 | AF1-227 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 161.73 | 156.86 | AF1-227 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 161.72 | 156.86 | AF1-227 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 151.63 | 156.42 | AF1-227 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 161.01 | 153.82 | AF1-227 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 148.27 | 152.77 | AF1-227 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 903 | 144.06 | 151.85 | AF1-227 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 152.48 | 150.91 | AF1-227 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 155.31 | 150.17 | AF1-227 | PN_P1-2_PN-500-010T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 903 | 142.51 | 149.23 | AF1-227 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 903 | 142.51 | 149.23 | AF1-227 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 903 | 142.49 | 149.22 | AF1-227 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.12 | 149.17 | AF1-227 | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.05 | 149.09 | AF1-227 | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.82 | 148.06 | AF1-227 | AP_P2-3_PE-500-016_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.89 | 148.02 | AF1-227 | AP_P2-3_PE-500-015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.63 | 147.51 | AF1-227 | PJM_500_BG_P4_5_CNSTN_L_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.76 | 147.34 | AF1-227 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143 | 147.17 | AF1-227 | AP_P1-2_PE-500-001_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143 | 147.17 | AF1-227 | AP_P1-2_WP-500-DRT17_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.56 | 147.15 | AF1-227 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.59 | 147.14 | AF1-227 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 142.95 | 147.1 | AF1-227 | AP_P2-3_PE-500-018C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.32 | 146.94 | AF1-227 | PECO_P4_NOTTI85_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.26 | 146.93 | AF1-227 | PECO_P1-2_220-08_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.19 | 146.86 | AF1-227 | PECO_P4_COOPR125_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3464 | 169.59 | 163.55 | AE2-022 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.15 | 143.47 | AF1-227 | PECO_P4_PEACH025_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.08 | 143.44 | AF1-227 | PECO_P1-2_PBTIE1_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 911 | 148.74 | 142.95 | AF1-227 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 911 | 147.78 | 141.63 | AF1-227 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 911 | 147.78 | 141.63 | AF1-227 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 911 | 147.77 | 141.62 | AF1-227 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204502 | 27JACKSON | 204514 | 27TMI | 1 | 230 | 227 | 781 | 132.53 | 141.21 | AF1-227 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204502 | 27JACKSON | 204514 | 27TMI | 1 | 230 | 227 | 781 | 132.73 | 141.2 | AF1-227 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204502 | 27JACKSON | 204514 | 27TMI | 1 | 230 | 227 | 781 | 132.73 | 141.19 | AF1-227 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204502 | 27JACKSON | 204514 | 27TMI | 1 | 230 | 227 | 781 | 132.72 | 141.18 | AF1-227 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 903 | 135.45 | 139.4 | AF1-227 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 1031 | 130.6 | 138.84 | AF1-227 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 1031 | 130.1 | 137.77 | AF1-227 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 1031 | 130.1 | 137.77 | AF1-227 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 1031 | 130.09 | 137.76 | AF1-227 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 911 | 139.93 | 134.92 | AF1-227 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208078 | SAKR | 1 | 230 | 229 | 903 | 124.97 | 133.6 | AF1-227 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 207923 | BRISREAC | 208132 | WHEM TR1 | 1 | 230 | 229 | 676 | 124.14 | 132.66 | AF1-227 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 207922 | BRIS | 207923 | BRISREAC | RX | 230 | 229 | 676 | 124.14 | 132.66 | AF1-227 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 207923 | BRISREAC | 208132 | WHEM TR1 | 1 | 230 | 229 | 676 | 124.14 | 132.66 | AF1-227 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 207922 | BRIS | 207923 | BRISREAC | RX | 230 | 229 | 676 | 124.14 | 132.66 | AF1-227 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 207923 | BRISREAC | 208132 | WHEM TR1 | 1 | 230 | 229 | 676 | 124.13 | 132.65 | AF1-227 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 207922 | BRIS | 207923 | BRISREAC | RX | 230 | 229 | 676 | 124.13 | 132.65 | AF1-227 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 138.56 | 132.65 | AF1-227 | PECO_P4_PEACH205_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 138.4 | 132.27 | AF1-227 | PECO_P1-2_PBTIE2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208078 | SAKR | 1 | 230 | 229 | 903 | 124.22 | 132.15 | AF1-227 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208078 | SAKR | 1 | 230 | 229 | 903 | 124.22 | 132.15 | AF1-227 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208078 | SAKR | 1 | 230 | 229 | 903 | 124.21 | 132.15 | AF1-227 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 137.5 | 131.43 | AF1-227 | PECO_P4_PEACH055_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204502 | 27JACKSON | 204514 | 27TMI | 1 | 230 | 227 | 781 | 125.1 | 130.67 | AF1-227 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 1031 | 124.51 | 129.01 | AF1-227 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 128.91 | 127.23 | AF1-227 | DVP_P4-2: 514T595_SRT-SW |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 132.76 | 126.97 | AF1-227 | PECO_P4_PEACH015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208020 | MANO TR3 | 1 | 230 | 229 | 793 | 112.03 | 125.85 | AF1-227 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 131.48 | 125.68 | AF1-227 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220953 | HOWARD12 | 220972 | GRANITE1 | 1 | 230 | 232 | 772 | 129.46 | 125.54 | AF1-227 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 127.17 | 125.52 | AF1-227 | DVP_P4-2: 51482_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 127.17 | 125.38 | AF1-227 | DVP_P1-2: LN 514_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 127.17 | 125.38 | AF1-227 | AP_P1-2_PE-500-407T_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220954 | HOWARD32 | 220973 | GRANITE6 | 1 | 230 | 232 | 772 | 128.33 | 124.86 | AF1-227 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220953 | HOWARD12 | 220972 | GRANITE1 | 1 | 230 | 232 | 772 | 128.55 | 124.57 | AF1-227 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220953 | HOWARD12 | 220972 | GRANITE1 | 1 | 230 | 232 | 772 | 128.55 | 124.57 | AF1-227 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208020 | MANO TR3 | 1 | 230 | 229 | 793 | 111.19 | 124.31 | AF1-227 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208020 | MANO TR3 | 1 | 230 | 229 | 793 | 111.19 | 124.31 | AF1-227 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208020 | MANO TR3 | 1 | 230 | 229 | 793 | 111.19 | 124.31 | AF1-227 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208031 | MLWD TR2 | 1 | 230 | 229 | 911 | 112.25 | 122.23 | AF1-227 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208078 | SAKR | 1 | 230 | 229 | 903 | 116.97 | 122.2 | AF1-227 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204512 | 27S.RDG | 204693 | 27BOONETOWN | 1 | 230 | 227 | 607 | 107.15 | 121.87 | AF1-227 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204512 | 27S.RDG | 204693 | 27BOONETOWN | 1 | 230 | 227 | 607 | 107.12 | 121.84 | AF1-227 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204512 | 27S.RDG | 204693 | 27BOONETOWN | 1 | 230 | 227 | 607 | 107.12 | 121.84 | AF1-227 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200025 | W CHAPEL | 1 | 500 | 225 | 1732 | 123.64 | 121.82 | AF1-227 | PEPCO_P4_PP41_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208031 | MLWD TR2 | 1 | 230 | 229 | 911 | 111.53 | 120.91 | AF1-227 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208031 | MLWD TR2 | 1 | 230 | 229 | 911 | 111.53 | 120.91 | AF1-227 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208031 | MLWD TR2 | 1 | 230 | 229 | 911 | 111.52 | 120.9 | AF1-227 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220965 | NEAST339 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 119.68 | 119.02 | AF1-227 | BG_P1_2315_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220965 | NEAST339 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 119.25 | 118.81 | AF1-227 | BG_P4_5_NEAST_17_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220965 | NEAST339 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 119.41 | 118.81 | AF1-227 | BG_P4_5_NEAST_15_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 114.61 | 118.33 | AF1-227 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220979 | NEAST317 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 118.76 | 118.15 | AF1-227 | BG_P1_2337_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 114.27 | 117.99 | AF1-227 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 114.26 | 117.93 | AF1-227 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 114.26 | 117.93 | AF1-227 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220979 | NEAST317 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 118.43 | 117.89 | AF1-227 | BG_P4_5_NEAST_39_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220979 | NEAST317 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 118.43 | 117.89 | AF1-227 | BG_P4_5_NEAST_37_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 113.93 | 117.6 | AF1-227 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 113.93 | 117.6 | AF1-227 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208131 | WHEM | 208132 | WHEM TR1 | 1 | 230 | 229 | 691 | 108.43 | 117.51 | AF1-227 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208131 | WHEM | 208132 | WHEM TR1 | 1 | 230 | 229 | 691 | 108.43 | 117.51 | AF1-227 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208131 | WHEM | 208132 | WHEM TR1 | 1 | 230 | 229 | 691 | 108.42 | 117.5 | AF1-227 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 122.39 | 117.05 | AF1-227 | PECO_P4_PEACH225_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 117.34 | 115.48 | AF1-227 | AP_P2-3_PE-500-019C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 2 | 500/230 | 225/232 | 2168 | 109.58 | 114.91 | AF1-227 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 2 | 500/230 | 225/232 | 2168 | 109.41 | 114.7 | AF1-227 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 2 | 500/230 | 225/232 | 2168 | 109.41 | 114.7 | AF1-227 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 1 | 500/230 | 225/232 | 2168 | 109.35 | 114.67 | AF1-227 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 1 | 500/230 | 225/232 | 2168 | 109.18 | 114.46 | AF1-227 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 1 | 500/230 | 225/232 | 2168 | 109.18 | 114.46 | AF1-227 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220964 | GRACETON | 220999 | BAGLEY2 | 13 | 230 | 232 | 1795 | 113.36 | 114.39 | AF1-227 | BG_P4_5_GRCTN_3T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204512 | 27S.RDG | 204693 | 27BOONETOWN | 1 | 230 | 227 | 607 | 105.37 | 114.39 | AF1-227 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208020 | MANO TR3 | 1 | 230 | 229 | 793 | 104.02 | 113.83 | AF1-227 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208020 | MANO TR3 | 208031 | MLWD TR2 | 1 | 230 | 229 | 903 | 102.36 | 113.47 | AF1-227 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208020 | MANO TR3 | 208031 | MLWD TR2 | 1 | 230 | 229 | 903 | 101.64 | 112.27 | AF1-227 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208020 | MANO TR3 | 208031 | MLWD TR2 | 1 | 230 | 229 | 903 | 101.64 | 112.27 | AF1-227 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208020 | MANO TR3 | 208031 | MLWD TR2 | 1 | 230 | 229 | 903 | 101.64 | 112.27 | AF1-227 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 2 | 500/230 | 225/232 | 2168 | 108.48 | 111.77 | AF1-227 | PJM_500_BG_P4_5_CNSTN_15_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208031 | MLWD TR2 | 1 | 230 | 229 | 911 | 104.78 | 111.45 | AF1-227 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 106.41 | 111.17 | AF1-227 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220980 | RAPHAEL | 220999 | BAGLEY2 | 13 | 230 | 232 | 1795 | 108.95 | 111.15 | AF1-227 | BG_P4_5_GRCTN_3T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 106.29 | 111.04 | AF1-227 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208131 | WHEM | 208133 | WHEM TR2 | 1 | 230 | 229 | 691 | 100.9 | 108.96 | AF1-227 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220965 | NEAST339 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 108.22 | 106.83 | AF1-227 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220965 | NEAST339 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 108.12 | 106.71 | AF1-227 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220965 | NEAST339 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 108.12 | 106.71 | AF1-227 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 101.53 | 105.69 | AF1-227 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 101.45 | 105.6 | AF1-227 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220979 | NEAST317 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 105.12 | 103.78 | AF1-227 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220979 | NEAST317 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 105.02 | 103.67 | AF1-227 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220979 | NEAST317 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 105.02 | 103.67 | AF1-227 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 99.67 | 103.54 | AF1-227 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 99.67 | 103.54 | AF1-227 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 99.66 | 103.54 | AF1-227 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208020 | MANO TR3 | 208031 | MLWD TR2 | 1 | 230 | 229 | 903 | 95.28 | 103.07 | AF1-227 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220964 | GRACETON | 221000 | BAGLEY | 5 | 230 | 232 | 1795 | 101.42 | 102.17 | AF1-227 | BG_P1_2313_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220964 | GRACETON | 220999 | BAGLEY2 | 13 | 230 | 232 | 1795 | 101.42 | 102.17 | AF1-227 | BG_P1_2305_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220965 | NEAST339 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 102.67 | 101.99 | AF1-227 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 98.84 | 100.87 | AF1-227 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 223960 | BRG 1T 230 | 1 | 500/230 | 225/233 | 1498 | 100.2 | 100.58 | AF1-227 | PEPCO_P4_PP41_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220965 | NEAST339 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 120.64 | 119.99 | AF1-299 | BG_P1_2315_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220965 | NEAST339 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 120.21 | 119.78 | AF1-299 | BG_P4_5_NEAST_17_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220965 | NEAST339 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 120.37 | 119.77 | AF1-299 | BG_P4_5_NEAST_15_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220979 | NEAST317 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 119.71 | 119.11 | AF1-299 | BG_P1_2337_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220979 | NEAST317 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 119.37 | 118.84 | AF1-299 | BG_P4_5_NEAST_39_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220979 | NEAST317 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 119.37 | 118.84 | AF1-299 | BG_P4_5_NEAST_37_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220964 | GRACETON | 220999 | BAGLEY2 | 13 | 230 | 232 | 1795 | 113.34 | 114.38 | AF1-299 | BG_P4_5_GRCTN_3T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220980 | RAPHAEL | 220999 | BAGLEY2 | 13 | 230 | 232 | 1795 | 108.93 | 111.14 | AF1-299 | BG_P4_5_GRCTN_3T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220964 | GRACETON | 221000 | BAGLEY | 5 | 230 | 232 | 1795 | 101.39 | 102.14 | AF1-299 | BG_P1_2313_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220964 | GRACETON | 220999 | BAGLEY2 | 13 | 230 | 232 | 1795 | 101.39 | 102.14 | AF1-299 | BG_P1_2305_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220965 | NEAST339 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 120.64 | 119.99 | AF1-300 | BG_P1_2315_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220965 | NEAST339 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 120.21 | 119.78 | AF1-300 | BG_P4_5_NEAST_17_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220965 | NEAST339 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 120.37 | 119.78 | AF1-300 | BG_P4_5_NEAST_15_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220979 | NEAST317 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 119.71 | 119.11 | AF1-300 | BG_P1_2337_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220979 | NEAST317 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 119.37 | 118.84 | AF1-300 | BG_P4_5_NEAST_39_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220979 | NEAST317 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 119.37 | 118.84 | AF1-300 | BG_P4_5_NEAST_37_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220964 | GRACETON | 220999 | BAGLEY2 | 13 | 230 | 232 | 1795 | 113.34 | 114.38 | AF1-300 | BG_P4_5_GRCTN_3T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220980 | RAPHAEL | 220999 | BAGLEY2 | 13 | 230 | 232 | 1795 | 108.93 | 111.14 | AF1-300 | BG_P4_5_GRCTN_3T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220964 | GRACETON | 221000 | BAGLEY | 5 | 230 | 232 | 1795 | 101.39 | 102.14 | AF1-300 | BG_P1_2313_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220964 | GRACETON | 220999 | BAGLEY2 | 13 | 230 | 232 | 1795 | 101.39 | 102.14 | AF1-300 | BG_P1_2305_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 144.58 | 139.43 | AF2-138 | PL_10_P42_100570_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 144.58 | 139.43 | AF2-138 | PL_10_P42_100570_A_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 143.77 | 138.64 | AF2-138 | PL_10_P12_000085_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 143.68 | 138.55 | AF2-138 | PN_P2-3_PN-500-004-DRT-008_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 143.68 | 138.55 | AF2-138 | PN_P2-3_PN-500-DRT31_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 143.31 | 138.18 | AF2-138 | PL_30_P42_000131_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 143.14 | 138.04 | AF2-138 | PL_10_P42_100569_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 143.14 | 138.04 | AF2-138 | PL_10_P42_100569_A_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 142.36 | 137.28 | AF2-138 | PL_10_P12_000086_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 142.36 | 137.27 | AF2-138 | PN_P2-3_PN-500-001C-DRT_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 154.23 | 158.82 | AF2-144 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.66 | 157.79 | AF2-144 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.66 | 157.78 | AF2-144 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 152.53 | 157.5 | AF2-144 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 149.17 | 153.85 | AF2-144 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 156.22 | 151.07 | AF2-144 | PN_P1-2_PN-500-010T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.99 | 150.19 | AF2-144 | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.92 | 150.12 | AF2-144 | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.64 | 149.05 | AF2-144 | AP_P2-3_PE-500-016_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.71 | 149.02 | AF2-144 | AP_P2-3_PE-500-015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.53 | 148.4 | AF2-144 | PJM_500_BG_P4_5_CNSTN_L_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.77 | 148.33 | AF2-144 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.82 | 148.16 | AF2-144 | AP_P1-2_WP-500-DRT17_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.82 | 148.16 | AF2-144 | AP_P1-2_PE-500-001_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.57 | 148.15 | AF2-144 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.6 | 148.13 | AF2-144 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.77 | 148.08 | AF2-144 | AP_P2-3_PE-500-018C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.33 | 147.94 | AF2-144 | PECO_P4_NOTTI85_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.27 | 147.92 | AF2-144 | PECO_P1-2_220-08_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.2 | 147.86 | AF2-144 | PECO_P4_COOPR125_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3464 | 167.94 | 161.93 | AE2-027 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 151.27 | 144.58 | AF2-144 | PECO_P1-2_PBTIE1_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 911 | 148.74 | 142.8 | AF2-144 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 139.61 | 133.66 | AF2-144 | PECO_P4_PEACH205_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 139.5 | 133.33 | AF2-144 | PECO_P1-2_PBTIE2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 130.13 | 128.49 | AF2-144 | DVP_P4-2: 514T595_SRT-SW |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 133.91 | 128.07 | AF2-144 | PECO_P4_PEACH015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 128.41 | 126.8 | AF2-144 | DVP_P4-2: 51482_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 128.41 | 126.66 | AF2-144 | DVP_P1-2: LN 514_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 128.41 | 126.66 | AF2-144 | AP_P1-2_PE-500-407T_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 793 | 127.95 | 126.28 | AF2-144 | DVP_P4-2: 514T595_SRT-SW |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 2 | 230 | 233 | 793 | 127.95 | 126.28 | AF2-144 | DVP_P4-2: 514T595_SRT-SW |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 2 | 230 | 233 | 793 | 126.72 | 125.09 | AF2-144 | DVP_P4-2: 51482_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 793 | 126.72 | 125.09 | AF2-144 | DVP_P4-2: 51482_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 2 | 230 | 233 | 793 | 126.72 | 124.97 | AF2-144 | DVP_P1-2: LN 514_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 2 | 230 | 233 | 793 | 126.72 | 124.97 | AF2-144 | AP_P1-2_PE-500-407T_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 793 | 126.72 | 124.97 | AF2-144 | DVP_P1-2: LN 514_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 793 | 126.72 | 124.97 | AF2-144 | AP_P1-2_PE-500-407T_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200025 | W CHAPEL | 1 | 500 | 225 | 1732 | 124.37 | 122.59 | AF2-144 | PEPCO_P4_PP41_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 123.45 | 118.06 | AF2-144 | PECO_P4_PEACH225_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 118.57 | 116.76 | AF2-144 | AP_P2-3_PE-500-019C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 2 | 230 | 233 | 793 | 110.85 | 109.06 | AF2-144 | AP_P2-3_PE-500-019C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 793 | 110.85 | 109.06 | AF2-144 | AP_P2-3_PE-500-019C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 99.97 | 104.16 | AF2-144 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 99.97 | 104.16 | AF2-144 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 99.96 | 104.03 | AF2-144 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 99.04 | 102.71 | AF2-144 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 99.14 | 101.38 | AF2-144 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3464 | 168.26 | 162.25 | AE2-029 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 162.18 | 154.94 | AG1-080 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.79 | 148.35 | AG1-080 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.59 | 148.16 | AG1-080 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.62 | 148.15 | AG1-080 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.35 | 147.95 | AG1-080 | PECO_P4_NOTTI85_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.29 | 147.94 | AG1-080 | PECO_P1-2_220-08_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.22 | 147.87 | AG1-080 | PECO_P4_COOPR125_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.05 | 147.72 | AG1-080 | AP_P2-3_PE-500-016_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.09 | 147.71 | AG1-080 | AP_P2-3_PE-500-015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.88 | 147.68 | AG1-080 | PECO_P1-2_220-93_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 151.57 | 147.25 | AG1-080 | AP_P1-2_WP-500-DRT17_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 151.43 | 144.7 | AG1-080 | PECO_P4_PEACH025_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 151.29 | 144.6 | AG1-080 | PECO_P1-2_PBTIE1_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 139.52 | 133.35 | AG1-080 | PECO_P1-2_PBTIE2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 138.54 | 132.44 | AG1-080 | PECO_P4_PEACH055_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 133.93 | 128.09 | AG1-080 | PECO_P4_PEACH015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 132.56 | 126.71 | AG1-080 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 123.47 | 118.07 | AG1-080 | PECO_P4_PEACH225_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3464 | 168.8 | 162.78 | AE2-042 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 153.79 | 158.29 | AG1-086 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.3 | 157.42 | AG1-086 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.29 | 157.42 | AG1-086 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 152.1 | 156.97 | AG1-086 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 161.83 | 154.6 | AG1-086 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 148.74 | 153.32 | AG1-086 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 155.87 | 150.71 | AG1-086 | PN_P1-2_PN-500-010T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.57 | 149.69 | AG1-086 | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.5 | 149.62 | AG1-086 | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.19 | 148.45 | AG1-086 | AP_P2-3_PE-500-016_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.25 | 148.43 | AG1-086 | AP_P2-3_PE-500-015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.49 | 148.05 | AG1-086 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.18 | 148.04 | AG1-086 | PJM_500_BG_P4_5_CNSTN_L_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.29 | 147.87 | AG1-086 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.32 | 147.85 | AG1-086 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.05 | 147.66 | AG1-086 | PECO_P4_NOTTI85_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.99 | 147.64 | AG1-086 | PECO_P1-2_220-08_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.92 | 147.58 | AG1-086 | PECO_P4_COOPR125_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.37 | 147.57 | AG1-086 | AP_P1-2_PE-500-001_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.37 | 147.57 | AG1-086 | AP_P1-2_WP-500-DRT17_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.32 | 147.5 | AG1-086 | AP_P2-3_PE-500-018C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3464 | 168.75 | 162.73 | AE2-046 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.91 | 144.23 | AG1-086 | PECO_P1-2_PBTIE1_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 139.27 | 133.33 | AG1-086 | PECO_P4_PEACH205_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 139.17 | 133.01 | AG1-086 | PECO_P1-2_PBTIE2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 138.22 | 132.13 | AG1-086 | PECO_P4_PEACH055_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 133.55 | 127.72 | AG1-086 | PECO_P4_PEACH015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 132.21 | 126.39 | AG1-086 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 123.12 | 117.74 | AG1-086 | PECO_P4_PEACH225_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 225.26 | 236.68 | AG1-397 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 223.26 | 236.68 | AG1-397 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 225.2 | 236.62 | AG1-397 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 223.2 | 236.62 | AG1-397 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 225.2 | 236.62 | AG1-397 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 223.2 | 236.62 | AG1-397 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 213.22 | 226.54 | AG1-397 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 213.16 | 226.48 | AG1-397 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 213.16 | 226.48 | AG1-397 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 208.97 | 223.32 | AG1-397 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 208.9 | 223.26 | AG1-397 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 208.9 | 223.26 | AG1-397 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 210.35 | 217.51 | AG1-397 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 208.35 | 217.5 | AG1-397 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 198.83 | 207.95 | AG1-397 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 194.57 | 204.6 | AG1-397 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 172.81 | 167.85 | AG1-397 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 163.64 | 164.97 | AG1-397 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 161.77 | 161.88 | AG1-397 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 161.77 | 161.88 | AG1-397 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 161.75 | 161.88 | AG1-397 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3464 | 168.89 | 162.87 | AE2-093 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 153.54 | 158 | AG1-397 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 161.95 | 157.08 | AG1-397 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 161.95 | 157.08 | AG1-397 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 151.85 | 156.67 | AG1-397 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 161.3 | 154.09 | AG1-397 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 148.49 | 153.02 | AG1-397 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 152.82 | 151.24 | AG1-397 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 155.52 | 150.37 | AG1-397 | PN_P1-2_PN-500-010T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 903 | 142.77 | 149.57 | AG1-397 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 903 | 142.77 | 149.57 | AG1-397 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 903 | 142.75 | 149.56 | AG1-397 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.33 | 149.41 | AG1-397 | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.26 | 149.34 | AG1-397 | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.99 | 148.22 | AG1-397 | AP_P2-3_PE-500-016_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.05 | 148.19 | AG1-397 | AP_P2-3_PE-500-015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.85 | 147.73 | AG1-397 | PJM_500_BG_P4_5_CNSTN_L_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.03 | 147.6 | AG1-397 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.83 | 147.42 | AG1-397 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.86 | 147.4 | AG1-397 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.16 | 147.34 | AG1-397 | AP_P1-2_WP-500-DRT17_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.16 | 147.34 | AG1-397 | AP_P1-2_PE-500-001_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.11 | 147.27 | AG1-397 | AP_P2-3_PE-500-018C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.59 | 147.21 | AG1-397 | PECO_P4_NOTTI85_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.53 | 147.19 | AG1-397 | PECO_P1-2_220-08_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.46 | 147.13 | AG1-397 | PECO_P4_COOPR125_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3464 | 168.25 | 162.24 | AE2-104 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.38 | 143.69 | AG1-397 | PECO_P4_PEACH025_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.33 | 143.67 | AG1-397 | PECO_P1-2_PBTIE1_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 911 | 149.04 | 143.18 | AG1-397 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204502 | 27JACKSON | 204514 | 27TMI | 1 | 230 | 227 | 781 | 133.01 | 141.59 | AG1-397 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204502 | 27JACKSON | 204514 | 27TMI | 1 | 230 | 227 | 781 | 133.01 | 141.58 | AG1-397 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204502 | 27JACKSON | 204514 | 27TMI | 1 | 230 | 227 | 781 | 132.99 | 141.58 | AG1-397 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 1031 | 130.35 | 138.13 | AG1-397 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 1031 | 130.35 | 138.13 | AG1-397 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 1031 | 130.34 | 138.12 | AG1-397 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 138.88 | 132.95 | AG1-397 | PECO_P4_PEACH205_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208078 | SAKR | 1 | 230 | 229 | 903 | 124.5 | 132.52 | AG1-397 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208078 | SAKR | 1 | 230 | 229 | 903 | 124.49 | 132.52 | AG1-397 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208078 | SAKR | 1 | 230 | 229 | 903 | 124.5 | 132.52 | AG1-397 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 138.63 | 132.49 | AG1-397 | PECO_P1-2_PBTIE2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 137.69 | 131.62 | AG1-397 | PECO_P4_PEACH055_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 128.92 | 127.21 | AG1-397 | DVP_P4-2: 514T595_SRT-SW |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 132.97 | 127.16 | AG1-397 | PECO_P4_PEACH015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 131.68 | 125.88 | AG1-397 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 127.18 | 125.5 | AG1-397 | DVP_P4-2: 51482_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 127.18 | 125.41 | AG1-397 | DVP_P1-2: LN 514_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 127.18 | 125.41 | AG1-397 | AP_P1-2_PE-500-407T_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208020 | MANO TR3 | 1 | 230 | 229 | 793 | 111.49 | 124.7 | AG1-397 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208020 | MANO TR3 | 1 | 230 | 229 | 793 | 111.49 | 124.7 | AG1-397 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208020 | MANO TR3 | 1 | 230 | 229 | 793 | 111.49 | 124.7 | AG1-397 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208078 | SAKR | 1 | 230 | 229 | 903 | 117.23 | 122.53 | AG1-397 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200025 | W CHAPEL | 1 | 500 | 225 | 1732 | 123.72 | 121.93 | AG1-397 | PEPCO_P4_PP41_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208031 | MLWD TR2 | 1 | 230 | 229 | 911 | 111.79 | 121.26 | AG1-397 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208031 | MLWD TR2 | 1 | 230 | 229 | 911 | 111.79 | 121.26 | AG1-397 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208031 | MLWD TR2 | 1 | 230 | 229 | 911 | 111.79 | 121.26 | AG1-397 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 122.58 | 117.22 | AG1-397 | PECO_P4_PEACH225_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 117.37 | 115.48 | AG1-397 | AP_P2-3_PE-500-019C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 2 | 500/230 | 225/232 | 2168 | 109.67 | 115 | AG1-397 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 2 | 500/230 | 225/232 | 2168 | 109.5 | 114.79 | AG1-397 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 2 | 500/230 | 225/232 | 2168 | 109.49 | 114.79 | AG1-397 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 1 | 500/230 | 225/232 | 2168 | 109.44 | 114.76 | AG1-397 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 1 | 500/230 | 225/232 | 2168 | 109.26 | 114.55 | AG1-397 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 1 | 500/230 | 225/232 | 2168 | 109.26 | 114.55 | AG1-397 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 105 | 104.33 | AG1-397 | PECO_P1-2_5025/* $ CHESCO $ PECO_P1-2_5025 $ L_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 103 | 104.33 | AG1-397 | PECO_P1-2_5025/* $ CHESCO $ PECO_P1-2_5025 $ L_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 104.52 | 103.85 | AG1-397 | PJM500_DPL_P4_2_KEENEY-ROCK AT50_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 104.52 | 103.85 | AG1-397 | PJM500_DPL_P4_2_KEENEY-ROCK AT51_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 102.53 | 103.85 | AG1-397 | PJM500_DPL_P4_2_KEENEY-ROCK AT50_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 102.53 | 103.85 | AG1-397 | PJM500_DPL_P4_2_KEENEY-ROCK AT51_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 99.67 | 103.6 | AG1-397 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 99.67 | 103.6 | AG1-397 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 99.67 | 103.6 | AG1-397 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 237.53 | 260.44 | AG2-055 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 239.82 | 260.44 | AG2-055 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 236.79 | 258.17 | AG2-055 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 239.07 | 258.16 | AG2-055 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 236.72 | 258.09 | AG2-055 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 236.72 | 258.08 | AG2-055 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 239.01 | 258.08 | AG2-055 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 239.01 | 258.08 | AG2-055 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 227 | 249.59 | AG2-055 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 226.28 | 247.38 | AG2-055 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 226.22 | 247.3 | AG2-055 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 226.22 | 247.3 | AG2-055 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 222.71 | 246.59 | AG2-055 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 221.99 | 244.36 | AG2-055 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 221.93 | 244.28 | AG2-055 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 221.93 | 244.27 | AG2-055 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 224.28 | 235.86 | AG2-055 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 221.99 | 235.86 | AG2-055 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 212 | 225.74 | AG2-055 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 207.71 | 222.51 | AG2-055 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 334 | 181.16 | 184.25 | AG2-055 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 334 | 181.16 | 184.25 | AG2-055 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 334 | 181.04 | 184.14 | AG2-055 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204539 | 27HUNTRSTN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 334 | 180.84 | 182.52 | AG2-055 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204539 | 27HUNTRSTN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 334 | 180.84 | 182.52 | AG2-055 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204539 | 27HUNTRSTN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 334 | 180.72 | 182.42 | AG2-055 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 235463 | 01TANEY | 1 | 138 | 227/201 | 317 | 186 | 179.35 | AG2-055 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 235463 | 01TANEY | 1 | 138 | 227/201 | 317 | 186 | 179.35 | AG2-055 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 235463 | 01TANEY | 1 | 138 | 227/201 | 317 | 185.85 | 179.26 | AG2-055 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 171.6 | 176.77 | AG2-055 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204538 | 27STRABAN | 204544 | 27LINCOLN | 1 | 115 | 227 | 371 | 170.36 | 175.75 | AG2-055 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204538 | 27STRABAN | 204544 | 27LINCOLN | 1 | 115 | 227 | 371 | 170.36 | 175.75 | AG2-055 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204538 | 27STRABAN | 204544 | 27LINCOLN | 1 | 115 | 227 | 371 | 170.24 | 175.64 | AG2-055 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 180.19 | 175.48 | AG2-055 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 179.42 | 173.99 | AG2-055 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 179.42 | 173.98 | AG2-055 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 179.4 | 173.97 | AG2-055 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 170.11 | 173.56 | AG2-055 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 170.11 | 173.55 | AG2-055 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 170.09 | 173.55 | AG2-055 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204529 | 27GERMANTN | 204538 | 27STRABAN | 1 | 115 | 227 | 371 | 164.46 | 171.18 | AG2-055 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204529 | 27GERMANTN | 204538 | 27STRABAN | 1 | 115 | 227 | 371 | 164.46 | 171.18 | AG2-055 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3464 | 168.62 | 162.6 | AE2-112 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204529 | 27GERMANTN | 204538 | 27STRABAN | 1 | 115 | 227 | 371 | 164.33 | 171.07 | AG2-055 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 204550 | 27ORRTANNA | 1 | 115 | 227 | 189 | 170.7 | 170.83 | AG2-055 | ME_P1-2_ME-115-068_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 204550 | 27ORRTANNA | 1 | 115 | 227 | 189 | 168.79 | 170.54 | AG2-055 | ME_P2-3_ME-115-035A_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 204550 | 27ORRTANNA | 1 | 115 | 227 | 189 | 170.34 | 169.08 | AG2-055 | ME_P1-2_ME-115-067_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 204550 | 27ORRTANNA | 1 | 115 | 227 | 189 | 168.4 | 168.39 | AG2-055 | ME_P2-3_ME-115-013B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 204550 | 27ORRTANNA | 1 | 115 | 227 | 189 | 166.49 | 168.1 | AG2-055 | ME_P2-3_ME-115-035B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 204550 | 27ORRTANNA | 1 | 115 | 227 | 189 | 168.09 | 168.06 | AG2-055 | ME_P2-3_ME-115-013A_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 221089 | WINDYED1 | 221090 | GLENARM2 | 1 | 115 | 232 | 222 | 162.37 | 167.3 | AG2-055 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 171.53 | 166.45 | AG2-055 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 159.99 | 165.75 | AG2-055 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 158.24 | 164.41 | AG2-055 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 169.26 | 164.32 | AG2-055 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 169.26 | 164.32 | AG2-055 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3464 | 168.07 | 162.06 | AE2-206 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 171.64 | 164 | AG2-055 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 903 | 150.27 | 162.97 | AG2-055 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3464 | 167.96 | 161.95 | AE2-217 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 204550 | 27ORRTANNA | 1 | 115 | 227 | 189 | 163.44 | 161.79 | AG2-055 | ME_P2-2_ME-115-0102-4_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 204550 | 27ORRTANNA | 1 | 115 | 227 | 189 | 163.44 | 161.79 | AG2-055 | ME_P2-3_ME-115-0102-A_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 161.23 | 161.55 | AG2-055 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 154.86 | 160.7 | AG2-055 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 903 | 149.04 | 160.18 | AG2-055 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 903 | 149.04 | 160.18 | AG2-055 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 903 | 149.02 | 160.18 | AG2-055 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204539 | 27HUNTRSTN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 334 | 157.17 | 160.1 | AG2-055 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204539 | 27HUNTRSTN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 334 | 157.16 | 160.1 | AG2-055 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204539 | 27HUNTRSTN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 334 | 157.17 | 160.1 | AG2-055 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204539 | 27HUNTRSTN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 334 | 157.02 | 160.01 | AG2-055 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 334 | 157.48 | 159.24 | AG2-055 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 334 | 157.49 | 159.24 | AG2-055 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 334 | 157.48 | 159.24 | AG2-055 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 334 | 157.34 | 159.1 | AG2-055 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3464 | 167.95 | 161.95 | AE2-218 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.91 | 157.69 | AG2-055 | PN_P1-2_PN-500-010T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 152.47 | 156.72 | AG2-055 | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 152.4 | 156.65 | AG2-055 | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 161.75 | 156.17 | AG2-055 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 161.55 | 155.98 | AG2-055 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 161.58 | 155.97 | AG2-055 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 161.3 | 155.77 | AG2-055 | PECO_P4_NOTTI85_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 161.23 | 155.75 | AG2-055 | PECO_P1-2_220-08_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 161.17 | 155.69 | AG2-055 | PECO_P4_COOPR125_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 160.81 | 155.5 | AG2-055 | PECO_P1-2_220-93_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 149.59 | 154.86 | AG2-055 | AP_P2-3_PE-500-016_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 149.65 | 154.83 | AG2-055 | AP_P2-3_PE-500-015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 221089 | WINDYED1 | 221090 | GLENARM2 | 1 | 115 | 232 | 222 | 148.84 | 154.77 | AG2-055 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 161.87 | 154.72 | AG2-055 | PECO_P4_PEACH025_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 161.76 | 154.65 | AG2-055 | PECO_P1-2_PBTIE1_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3464 | 167.65 | 161.65 | AE2-221 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 148.77 | 153.96 | AG2-055 | AP_P1-2_WP-500-DRT17_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 148.77 | 153.96 | AG2-055 | AP_P1-2_PE-500-001_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 148.72 | 153.9 | AG2-055 | AP_P2-3_PE-500-018C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3464 | 167.93 | 161.92 | AE2-230 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204502 | 27JACKSON | 204514 | 27TMI | 1 | 230 | 227 | 781 | 139.44 | 153.1 | AG2-055 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204502 | 27JACKSON | 204514 | 27TMI | 1 | 230 | 227 | 781 | 139.6 | 152.95 | AG2-055 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204502 | 27JACKSON | 204514 | 27TMI | 1 | 230 | 227 | 781 | 139.6 | 152.94 | AG2-055 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204502 | 27JACKSON | 204514 | 27TMI | 1 | 230 | 227 | 781 | 139.58 | 152.94 | AG2-055 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 150.15 | 151.01 | AG2-055 | BG_P7_GRCTN_CNSTN_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204538 | 27STRABAN | 204544 | 27LINCOLN | 1 | 115 | 227 | 371 | 146.36 | 150.07 | AG2-055 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204538 | 27STRABAN | 204544 | 27LINCOLN | 1 | 115 | 227 | 371 | 146.36 | 150.07 | AG2-055 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204538 | 27STRABAN | 204544 | 27LINCOLN | 1 | 115 | 227 | 371 | 146.35 | 150.07 | AG2-055 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204538 | 27STRABAN | 204544 | 27LINCOLN | 1 | 115 | 227 | 371 | 146.21 | 149.93 | AG2-055 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 911 | 156.34 | 149.8 | AG2-055 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 221092 | FIVE.FOR | 221096 | ROCKRGE1 | 1 | 115 | 232 | 293 | 145.56 | 149.69 | AG2-055 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 1031 | 135.96 | 149.32 | AG2-055 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204539 | 27HUNTRSTN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 334 | 150.16 | 149.25 | AG2-055 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 334 | 150.49 | 149.21 | AG2-055 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 334 | 149.81 | 148.93 | AG2-055 | ME_P2-3_ME-115-019A-A_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 334 | 149.81 | 148.93 | AG2-055 | ME_P1-2_ME-115-061_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 903 | 142.02 | 148.77 | AG2-055 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 911 | 155.59 | 148.47 | AG2-055 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 911 | 155.59 | 148.46 | AG2-055 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 911 | 155.57 | 148.45 | AG2-055 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 1031 | 135.55 | 148.09 | AG2-055 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 1031 | 135.56 | 148.09 | AG2-055 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 1031 | 135.56 | 148.09 | AG2-055 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3464 | 168.04 | 162.03 | AE2-253 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204539 | 27HUNTRSTN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 334 | 149.49 | 147.46 | AG2-055 | ME_P1-2_ME-115-061_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204539 | 27HUNTRSTN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 334 | 149.49 | 147.46 | AG2-055 | ME_P2-3_ME-115-019A-A_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 221055 | HARRIS1A | 221058 | DOLFD T1 | 1 | 115 | 232 | 201 | 146.85 | 147.26 | AG2-055 | BG_P7_NWEST_GRNITE_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204529 | 27GERMANTN | 204538 | 27STRABAN | 1 | 115 | 227 | 371 | 140.45 | 145.87 | AG2-055 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204529 | 27GERMANTN | 204538 | 27STRABAN | 1 | 115 | 227 | 371 | 140.45 | 145.87 | AG2-055 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204529 | 27GERMANTN | 204538 | 27STRABAN | 1 | 115 | 227 | 371 | 140.45 | 145.87 | AG2-055 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 146.02 | 145.85 | AG2-055 | PJM_500_BG_P4_5_CNSTN_15_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208078 | SAKR | 1 | 230 | 229 | 903 | 132.56 | 145.81 | AG2-055 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204529 | 27GERMANTN | 204538 | 27STRABAN | 1 | 115 | 227 | 371 | 140.3 | 145.74 | AG2-055 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200512 | 26LEWISTWN | 200519 | 26REED TAP | 1 | 115 | 226 | 271 | 131.54 | 145.6 | AG2-055 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200512 | 26LEWISTWN | 200519 | 26REED TAP | 1 | 115 | 226 | 271 | 131.6 | 145.35 | AG2-055 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200512 | 26LEWISTWN | 200519 | 26REED TAP | 1 | 115 | 226 | 271 | 131.6 | 145.34 | AG2-055 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200512 | 26LEWISTWN | 200519 | 26REED TAP | 1 | 115 | 226 | 271 | 131.6 | 145.34 | AG2-055 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200504 | 26CARLISLE | 204528 | 27GARDNERS | 1 | 115 | 226/227 | 190 | 135.04 | 144.72 | AG2-055 | PN_P2-3_PN-115-0331-B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208078 | SAKR | 1 | 230 | 229 | 903 | 131.96 | 144.29 | AG2-055 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208078 | SAKR | 1 | 230 | 229 | 903 | 131.97 | 144.28 | AG2-055 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208078 | SAKR | 1 | 230 | 229 | 903 | 131.97 | 144.28 | AG2-055 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 207923 | BRISREAC | 208132 | WHEM TR1 | 1 | 230 | 229 | 676 | 129.58 | 143.53 | AG2-055 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 207922 | BRIS | 207923 | BRISREAC | RX | 230 | 229 | 676 | 129.58 | 143.53 | AG2-055 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200504 | 26CARLISLE | 204528 | 27GARDNERS | 1 | 115 | 226/227 | 190 | 133.46 | 143.35 | AG2-055 | PN_P1-2_PN-115-094_A_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 149.17 | 142.62 | AG2-055 | PECO_P1-2_PBTIE2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200504 | 26CARLISLE | 204528 | 27GARDNERS | 1 | 115 | 226/227 | 190 | 133.37 | 142.45 | AG2-055 | PN_P2-3_PN-115-58B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200504 | 26CARLISLE | 204528 | 27GARDNERS | 1 | 115 | 226/227 | 190 | 134.07 | 142.41 | AG2-055 | PN_P1-3_PN-115-040_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200504 | 26CARLISLE | 204528 | 27GARDNERS | 1 | 115 | 226/227 | 190 | 134.07 | 142.41 | AG2-055 | PN_P2-2_PN-115-030_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200504 | 26CARLISLE | 204528 | 27GARDNERS | 1 | 115 | 226/227 | 190 | 133.16 | 142.38 | AG2-055 | PN_P1-2_PN-115-094_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 148.64 | 142.32 | AG2-055 | PECO_P4_PEACH205_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 911 | 147.77 | 141.96 | AG2-055 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 207923 | BRISREAC | 208132 | WHEM TR1 | 1 | 230 | 229 | 676 | 128.98 | 141.9 | AG2-055 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 207923 | BRISREAC | 208132 | WHEM TR1 | 1 | 230 | 229 | 676 | 128.98 | 141.89 | AG2-055 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 207922 | BRIS | 207923 | BRISREAC | RX | 230 | 229 | 676 | 128.98 | 141.89 | AG2-055 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 207923 | BRISREAC | 208132 | WHEM TR1 | 1 | 230 | 229 | 676 | 128.96 | 141.89 | AG2-055 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 207922 | BRIS | 207923 | BRISREAC | RX | 230 | 229 | 676 | 128.98 | 141.89 | AG2-055 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 207922 | BRIS | 207923 | BRISREAC | RX | 230 | 229 | 676 | 128.96 | 141.89 | AG2-055 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 235463 | 01TANEY | 1 | 138 | 227/201 | 317 | 141.86 | 141.79 | AG2-055 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 235463 | 01TANEY | 1 | 138 | 227/201 | 317 | 141.45 | 141.15 | AG2-055 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 235463 | 01TANEY | 1 | 138 | 227/201 | 317 | 142.79 | 141.13 | AG2-055 | AP_P2-3_PE-500-016_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 235463 | 01TANEY | 1 | 138 | 227/201 | 317 | 142.9 | 141.05 | AG2-055 | AP_P2-3_PE-500-015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 147.16 | 140.74 | AG2-055 | PECO_P4_PEACH055_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204502 | 27JACKSON | 204514 | 27TMI | 1 | 230 | 227 | 781 | 132 | 140.61 | AG2-055 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 203981 | AD2-062_POI | 235188 | 01GREENE | 1 | 138 | 226/201 | 317 | 150.87 | 140.49 | AG2-055 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 203981 | AD2-062_POI | 235188 | 01GREENE | 1 | 138 | 226/201 | 317 | 150.87 | 140.49 | AG2-055 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 203981 | AD2-062_POI | 235188 | 01GREENE | 1 | 138 | 226/201 | 317 | 150.67 | 140.38 | AG2-055 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200519 | 26REED TAP | 200522 | 26SHADE GP | 1 | 115 | 226 | 271 | 123.69 | 140.34 | AG2-055 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 235463 | 01TANEY | 1 | 138 | 227/201 | 317 | 141.48 | 140.23 | AG2-055 | AP_P2-3_PE-500-018C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 235463 | 01TANEY | 1 | 138 | 227/201 | 317 | 141.49 | 140.22 | AG2-055 | AP_P2-3_PE-500-018D_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 221056 | HARRIS0A | 221057 | DOLFD T0 | 1 | 115 | 232 | 201 | 139.87 | 140.15 | AG2-055 | BG_P7_NWEST_GRNITE_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 221092 | FIVE.FOR | 221096 | ROCKRGE1 | 1 | 115 | 232 | 293 | 135.35 | 140.11 | AG2-055 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200519 | 26REED TAP | 200522 | 26SHADE GP | 1 | 115 | 226 | 271 | 123.75 | 140.05 | AG2-055 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200519 | 26REED TAP | 200522 | 26SHADE GP | 1 | 115 | 226 | 271 | 123.75 | 140.04 | AG2-055 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200519 | 26REED TAP | 200522 | 26SHADE GP | 1 | 115 | 226 | 271 | 123.75 | 140.04 | AG2-055 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204538 | 27STRABAN | 204544 | 27LINCOLN | 1 | 115 | 227 | 371 | 139.26 | 140.03 | AG2-055 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 235463 | 01TANEY | 1 | 138 | 227/201 | 317 | 141.33 | 139.96 | AG2-055 | AP_P1-2_PE-500-001_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200532 | 26ROXBURY | 203981 | AD2-062_POI | 1 | 138 | 226 | 317 | 150.19 | 139.16 | AG2-055 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200532 | 26ROXBURY | 203981 | AD2-062_POI | 1 | 138 | 226 | 317 | 150.19 | 139.16 | AG2-055 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200532 | 26ROXBURY | 203981 | AD2-062_POI | 1 | 138 | 226 | 317 | 149.99 | 139.05 | AG2-055 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 144.54 | 138.26 | AG2-055 | PECO_P4_PEACH015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208020 | MANO TR3 | 1 | 230 | 229 | 793 | 119.53 | 138.25 | AG2-055 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200504 | 26CARLISLE | 204528 | 27GARDNERS | 1 | 115 | 226/227 | 190 | 130.78 | 137.73 | AG2-055 | PN_P2-3_PN-230-0014-12_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 1031 | 130 | 137.5 | AG2-055 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200504 | 26CARLISLE | 204528 | 27GARDNERS | 1 | 115 | 226/227 | 190 | 130.77 | 137.29 | AG2-055 | PN_P1-3_PN-230-020A_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200504 | 26CARLISLE | 204528 | 27GARDNERS | 1 | 115 | 226/227 | 190 | 130.77 | 137.29 | AG2-055 | PN_P2-3_PN-230-0014-11_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200504 | 26CARLISLE | 204528 | 27GARDNERS | 1 | 115 | 226/227 | 190 | 130.7 | 137.27 | AG2-055 | PN_P2-2_PN-115-031_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200512 | 26LEWISTWN | 200519 | 26REED TAP | 1 | 115 | 226 | 271 | 128.8 | 137.2 | AG2-055 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204538 | 27STRABAN | 204544 | 27LINCOLN | 1 | 115 | 227 | 371 | 132.65 | 137.03 | AG2-055 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220972 | GRANITE1 | 1 | 230 | 232 | 829 | 141.14 | 136.78 | AG2-055 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204538 | 27STRABAN | 204544 | 27LINCOLN | 1 | 115 | 227 | 371 | 133.44 | 136.76 | AG2-055 | AP_P2-3_PE-500-016_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208020 | MANO TR3 | 1 | 230 | 229 | 793 | 118.86 | 136.7 | AG2-055 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208020 | MANO TR3 | 1 | 230 | 229 | 793 | 118.87 | 136.69 | AG2-055 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208020 | MANO TR3 | 1 | 230 | 229 | 793 | 118.87 | 136.68 | AG2-055 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 204529 | 27GERMANTN | 1 | 138/115 | 227 | 453 | 130.16 | 136.66 | AG2-055 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 204529 | 27GERMANTN | 1 | 138/115 | 227 | 453 | 130.16 | 136.66 | AG2-055 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 204529 | 27GERMANTN | 1 | 138/115 | 227 | 453 | 130.06 | 136.57 | AG2-055 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220972 | GRANITE1 | 1 | 230 | 232 | 829 | 140.54 | 136.16 | AG2-055 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220972 | GRANITE1 | 1 | 230 | 232 | 829 | 140.54 | 136.16 | AG2-055 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 142.12 | 135.9 | AG2-055 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204529 | 27GERMANTN | 204538 | 27STRABAN | 1 | 115 | 227 | 371 | 133.36 | 135.72 | AG2-055 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220973 | GRANITE6 | 1 | 230 | 232 | 829 | 138.93 | 134.77 | AG2-055 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 134.04 | 134.72 | AG2-055 | BG_P7_GRCTN_CNSTN_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 131.75 | 134.72 | AG2-055 | BG_P7_GRCTN_CNSTN_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3464 | 168.29 | 162.28 | AE2-282 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220973 | GRANITE6 | 1 | 230 | 232 | 829 | 138.36 | 134.2 | AG2-055 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220973 | GRANITE6 | 1 | 230 | 232 | 829 | 138.36 | 134.19 | AG2-055 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204512 | 27S.RDG | 204693 | 27BOONETOWN | 1 | 230 | 227 | 607 | 112.11 | 133.66 | AG2-055 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208031 | MLWD TR2 | 1 | 230 | 229 | 911 | 119.26 | 133.53 | AG2-055 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3464 | 168.23 | 162.22 | AE2-290 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204512 | 27S.RDG | 204693 | 27BOONETOWN | 1 | 230 | 227 | 607 | 111.99 | 132.93 | AG2-055 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204512 | 27S.RDG | 204693 | 27BOONETOWN | 1 | 230 | 227 | 607 | 111.96 | 132.89 | AG2-055 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204512 | 27S.RDG | 204693 | 27BOONETOWN | 1 | 230 | 227 | 607 | 111.96 | 132.89 | AG2-055 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208078 | SAKR | 1 | 230 | 229 | 903 | 124.75 | 132.59 | AG2-055 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204529 | 27GERMANTN | 204538 | 27STRABAN | 1 | 115 | 227 | 371 | 126.74 | 132.57 | AG2-055 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220953 | HOWARD12 | 220972 | GRANITE1 | 1 | 230 | 232 | 772 | 136.94 | 132.56 | AG2-055 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 134.27 | 132.42 | AG2-055 | DVP_P4-2: 514T595_SRT-SW |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204529 | 27GERMANTN | 204538 | 27STRABAN | 1 | 115 | 227 | 371 | 127.54 | 132.3 | AG2-055 | AP_P2-3_PE-500-016_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 207922 | BRIS | 207923 | BRISREAC | RX | 230 | 229 | 676 | 123.91 | 132.22 | AG2-055 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 207923 | BRISREAC | 208132 | WHEM TR1 | 1 | 230 | 229 | 676 | 123.91 | 132.22 | AG2-055 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208031 | MLWD TR2 | 1 | 230 | 229 | 911 | 118.68 | 132.1 | AG2-055 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208031 | MLWD TR2 | 1 | 230 | 229 | 911 | 118.68 | 132.09 | AG2-055 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208031 | MLWD TR2 | 1 | 230 | 229 | 911 | 118.68 | 132.09 | AG2-055 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204539 | 27HUNTRSTN | 204550 | 27ORRTANNA | 1 | 115 | 227 | 264 | 131.94 | 132.07 | AG2-055 | ME_P1-2_ME-115-068_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200519 | 26REED TAP | 200522 | 26SHADE GP | 1 | 115 | 226 | 271 | 120.94 | 132.06 | AG2-055 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204539 | 27HUNTRSTN | 204550 | 27ORRTANNA | 1 | 115 | 227 | 264 | 130.57 | 131.86 | AG2-055 | ME_P2-3_ME-115-035A_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220953 | HOWARD12 | 220972 | GRANITE1 | 1 | 230 | 232 | 772 | 136.08 | 131.65 | AG2-055 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220953 | HOWARD12 | 220972 | GRANITE1 | 1 | 230 | 232 | 772 | 136.08 | 131.65 | AG2-055 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220954 | HOWARD32 | 220973 | GRANITE6 | 1 | 230 | 232 | 772 | 135.39 | 131.52 | AG2-055 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 127.38 | 130.93 | AG2-055 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 125.09 | 130.93 | AG2-055 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 132.64 | 130.83 | AG2-055 | DVP_P4-2: 51482_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220954 | HOWARD32 | 220973 | GRANITE6 | 1 | 230 | 232 | 772 | 134.64 | 130.73 | AG2-055 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220954 | HOWARD32 | 220973 | GRANITE6 | 1 | 230 | 232 | 772 | 134.64 | 130.73 | AG2-055 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 132.64 | 130.72 | AG2-055 | AP_P1-2_PE-500-407T_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 132.64 | 130.72 | AG2-055 | DVP_P1-2: LN 514_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204539 | 27HUNTRSTN | 204550 | 27ORRTANNA | 1 | 115 | 227 | 264 | 131.68 | 130.7 | AG2-055 | ME_P1-2_ME-115-067_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 127.2 | 130.7 | AG2-055 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 124.91 | 130.7 | AG2-055 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 127.2 | 130.7 | AG2-055 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 124.91 | 130.7 | AG2-055 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204539 | 27HUNTRSTN | 204550 | 27ORRTANNA | 1 | 115 | 227 | 264 | 130.29 | 130.3 | AG2-055 | ME_P2-3_ME-115-013B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204539 | 27HUNTRSTN | 204550 | 27ORRTANNA | 1 | 115 | 227 | 264 | 128.92 | 130.09 | AG2-055 | ME_P2-3_ME-115-035B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204539 | 27HUNTRSTN | 204550 | 27ORRTANNA | 1 | 115 | 227 | 264 | 130.07 | 130.06 | AG2-055 | ME_P2-3_ME-115-013A_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 911 | 127.02 | 129.97 | AG2-055 | BG_P7_GRCTN_CNSTN_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208394 | PPL-BGE TIE | 221092 | FIVE.FOR | 1 | 115 | 229/232 | 247 | 125.53 | 128.77 | AG2-055 | PL_05_P71_000906_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200512 | 26LEWISTWN | 200519 | 26REED TAP | 1 | 115 | 226 | 271 | 124.59 | 128.62 | AG2-055 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200512 | 26LEWISTWN | 200519 | 26REED TAP | 1 | 115 | 226 | 271 | 124.59 | 128.62 | AG2-055 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200512 | 26LEWISTWN | 200519 | 26REED TAP | 1 | 115 | 226 | 271 | 124.54 | 128.56 | AG2-055 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 2 | 230 | 233 | 793 | 130.04 | 128.24 | AG2-055 | DVP_P4-2: 514T595_SRT-SW |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 793 | 130.04 | 128.24 | AG2-055 | DVP_P4-2: 514T595_SRT-SW |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 124.87 | 127.8 | AG2-055 | BG_P7_GRCTN_CNSTN_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200025 | W CHAPEL | 1 | 500 | 225 | 1732 | 129.17 | 127.62 | AG2-055 | PEPCO_P4_PP41_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208393 | FARO DC TIE | 208395 | FARO FF | 1 | 115/69 | 229 | 120 | 131.77 | 127.58 | AG2-055 | PL_05_P71_000906_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208393 | FARO DC TIE | 208395 | FARO FF | 2 | 115/69 | 229 | 120 | 131.77 | 127.58 | AG2-055 | PL_05_P71_000906_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208131 | WHEM | 208132 | WHEM TR1 | 1 | 230 | 229 | 691 | 113.5 | 127.5 | AG2-055 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 133.25 | 127.41 | AG2-055 | PECO_P4_PEACH225_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 793 | 128.88 | 127.13 | AG2-055 | DVP_P4-2: 51482_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 2 | 230 | 233 | 793 | 128.88 | 127.13 | AG2-055 | DVP_P4-2: 51482_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 126.13 | 127.08 | AG2-055 | PJM_500_BG_P4_5_CNSTN_15_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 123.84 | 127.08 | AG2-055 | PJM_500_BG_P4_5_CNSTN_15_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 793 | 128.88 | 127.04 | AG2-055 | DVP_P1-2: LN 514_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 2 | 230 | 233 | 793 | 128.88 | 127.04 | AG2-055 | AP_P1-2_PE-500-407T_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 793 | 128.88 | 127.04 | AG2-055 | AP_P1-2_PE-500-407T_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 2 | 230 | 233 | 793 | 128.88 | 127.04 | AG2-055 | DVP_P1-2: LN 514_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208131 | WHEM | 208132 | WHEM TR1 | 1 | 230 | 229 | 691 | 112.93 | 125.97 | AG2-055 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208131 | WHEM | 208132 | WHEM TR1 | 1 | 230 | 229 | 691 | 112.92 | 125.97 | AG2-055 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208131 | WHEM | 208132 | WHEM TR1 | 1 | 230 | 229 | 691 | 112.93 | 125.97 | AG2-055 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200532 | 26ROXBURY | 200520 | 26ROXBURY | 2 | 138/115 | 226 | 435 | 109.45 | 125.74 | AG2-055 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200532 | 26ROXBURY | 200520 | 26ROXBURY | 2 | 138/115 | 226 | 435 | 109.45 | 125.74 | AG2-055 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200532 | 26ROXBURY | 200520 | 26ROXBURY | 2 | 138/115 | 226 | 435 | 109.3 | 125.6 | AG2-055 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3464 | 168.04 | 162.03 | AE2-297 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3464 | 168.18 | 162.17 | AE2-318 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204539 | 27HUNTRSTN | 204550 | 27ORRTANNA | 1 | 115 | 227 | 264 | 126.74 | 125.46 | AG2-055 | ME_P2-3_ME-115-0102-A_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204539 | 27HUNTRSTN | 204550 | 27ORRTANNA | 1 | 115 | 227 | 264 | 126.74 | 125.46 | AG2-055 | ME_P2-2_ME-115-0102-4_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208020 | MANO TR3 | 1 | 230 | 229 | 793 | 111.73 | 124.65 | AG2-055 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200532 | 26ROXBURY | 200520 | 26ROXBURY | 2 | 138/115 | 226 | 435 | 105.49 | 124.57 | AG2-055 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200532 | 26ROXBURY | 200520 | 26ROXBURY | 2 | 138/115 | 226 | 435 | 105.5 | 124.57 | AG2-055 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200532 | 26ROXBURY | 200520 | 26ROXBURY | 2 | 138/115 | 226 | 435 | 105.5 | 124.57 | AG2-055 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200532 | 26ROXBURY | 200520 | 26ROXBURY | 2 | 138/115 | 226 | 435 | 105.36 | 124.37 | AG2-055 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 911 | 123 | 124.26 | AG2-055 | PJM_500_BG_P4_5_CNSTN_15_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 203981 | AD2-062_POI | 235188 | 01GREENE | 1 | 138 | 226/201 | 317 | 128.57 | 124.24 | AG2-055 | AP_P2-3_PE-500-016_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 118.43 | 124.15 | AG2-055 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 203981 | AD2-062_POI | 235188 | 01GREENE | 1 | 138 | 226/201 | 317 | 128.77 | 124.08 | AG2-055 | AP_P2-3_PE-500-015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208020 | MANO TR3 | 208031 | MLWD TR2 | 1 | 230 | 229 | 903 | 109.01 | 124.05 | AG2-055 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200512 | 26LEWISTWN | 200519 | 26REED TAP | 1 | 115 | 226 | 271 | 124.86 | 124.01 | AG2-055 | ME_P2-3_ME-115-003DT_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 120.58 | 123.96 | AG2-055 | BG_P7_GRCTN_CNSTN_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200512 | 26LEWISTWN | 200519 | 26REED TAP | 1 | 115 | 226 | 271 | 124.79 | 123.94 | AG2-055 | ME_P2-3_ME-115-003AT_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 118.26 | 123.93 | AG2-055 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 118.26 | 123.93 | AG2-055 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220965 | NEAST339 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 124.36 | 123.82 | AG2-055 | BG_P1_2315_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200519 | 26REED TAP | 200522 | 26SHADE GP | 1 | 115 | 226 | 271 | 116.74 | 123.63 | AG2-055 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200519 | 26REED TAP | 200522 | 26SHADE GP | 1 | 115 | 226 | 271 | 116.74 | 123.63 | AG2-055 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200519 | 26REED TAP | 200522 | 26SHADE GP | 1 | 115 | 226 | 271 | 116.68 | 123.57 | AG2-055 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220965 | NEAST339 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 123.87 | 123.56 | AG2-055 | BG_P4_5_NEAST_17_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220965 | NEAST339 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 124.04 | 123.56 | AG2-055 | BG_P4_5_NEAST_15_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204512 | 27S.RDG | 204693 | 27BOONETOWN | 1 | 230 | 227 | 607 | 110.22 | 123.37 | AG2-055 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 203981 | AD2-062_POI | 235188 | 01GREENE | 1 | 138 | 226/201 | 317 | 126.51 | 123.35 | AG2-055 | AP_P2-3_PE-500-018C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 203981 | AD2-062_POI | 235188 | 01GREENE | 1 | 138 | 226/201 | 317 | 126.52 | 123.34 | AG2-055 | AP_P2-3_PE-500-018D_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 118.87 | 123.23 | AG2-055 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 221092 | FIVE.FOR | 221095 | ROCKRGE2 | 1 | 115 | 232 | 340 | 120.19 | 123.14 | AG2-055 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 203981 | AD2-062_POI | 235188 | 01GREENE | 1 | 138 | 226/201 | 317 | 127.09 | 123 | AG2-055 | AP_P1-2_PE-500-004_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 203981 | AD2-062_POI | 235188 | 01GREENE | 1 | 138 | 226/201 | 317 | 127.09 | 123 | AG2-055 | AP_P2-3_WP-500-DRT19_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 203981 | AD2-062_POI | 235188 | 01GREENE | 1 | 138 | 226/201 | 317 | 127.09 | 123 | AG2-055 | AP_P2-3_WP-500-466_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200532 | 26ROXBURY | 203981 | AD2-062_POI | 1 | 138 | 226 | 317 | 127.89 | 122.95 | AG2-055 | AP_P2-3_PE-500-016_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208394 | PPL-BGE TIE | 221092 | FIVE.FOR | 1 | 115 | 229/232 | 247 | 122.32 | 122.95 | AG2-055 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208394 | PPL-BGE TIE | 221092 | FIVE.FOR | 1 | 115 | 229/232 | 247 | 122.32 | 122.95 | AG2-055 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208394 | PPL-BGE TIE | 221092 | FIVE.FOR | 1 | 115 | 229/232 | 247 | 122.32 | 122.94 | AG2-055 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220979 | NEAST317 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 123.38 | 122.9 | AG2-055 | BG_P1_2337_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 118.51 | 122.87 | AG2-055 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 118.53 | 122.8 | AG2-055 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 118.53 | 122.8 | AG2-055 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200532 | 26ROXBURY | 203981 | AD2-062_POI | 1 | 138 | 226 | 317 | 128.09 | 122.79 | AG2-055 | AP_P2-3_PE-500-015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3464 | 168.19 | 162.18 | AE2-319 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208394 | PPL-BGE TIE | 221092 | FIVE.FOR | 1 | 115 | 229/232 | 247 | 122.38 | 122.71 | AG2-055 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208020 | MANO TR3 | 208031 | MLWD TR2 | 1 | 230 | 229 | 903 | 108.44 | 122.68 | AG2-055 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208020 | MANO TR3 | 208031 | MLWD TR2 | 1 | 230 | 229 | 903 | 108.44 | 122.67 | AG2-055 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208020 | MANO TR3 | 208031 | MLWD TR2 | 1 | 230 | 229 | 903 | 108.44 | 122.67 | AG2-055 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220979 | NEAST317 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 122.99 | 122.58 | AG2-055 | BG_P4_5_NEAST_39_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220979 | NEAST317 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 122.99 | 122.58 | AG2-055 | BG_P4_5_NEAST_37_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 118.18 | 122.45 | AG2-055 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 118.18 | 122.45 | AG2-055 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208394 | PPL-BGE TIE | 221092 | FIVE.FOR | 1 | 115 | 229/232 | 247 | 115.62 | 122.12 | AG2-055 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200532 | 26ROXBURY | 203981 | AD2-062_POI | 1 | 138 | 226 | 317 | 125.83 | 122.04 | AG2-055 | AP_P2-3_PE-500-018C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200532 | 26ROXBURY | 203981 | AD2-062_POI | 1 | 138 | 226 | 317 | 125.84 | 122.03 | AG2-055 | AP_P2-3_PE-500-018D_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200532 | 26ROXBURY | 203981 | AD2-062_POI | 1 | 138 | 226 | 317 | 126.41 | 121.71 | AG2-055 | AP_P2-3_WP-500-466_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200532 | 26ROXBURY | 203981 | AD2-062_POI | 1 | 138 | 226 | 317 | 126.41 | 121.71 | AG2-055 | AP_P1-2_PE-500-004_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200532 | 26ROXBURY | 203981 | AD2-062_POI | 1 | 138 | 226 | 317 | 126.41 | 121.71 | AG2-055 | AP_P2-3_WP-500-DRT19_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3464 | 168.04 | 162.03 | AE2-333 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 122.51 | 121.3 | AG2-055 | PL_04_P12_000260_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 122.51 | 121.3 | AG2-055 | PL_04_P42_000564_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208031 | MLWD TR2 | 1 | 230 | 229 | 911 | 111.98 | 121.25 | AG2-055 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 122.81 | 120.79 | AG2-055 | AP_P2-3_PE-500-019C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 117.22 | 120.49 | AG2-055 | PJM_500_BG_P4_5_CNSTN_15_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 114.14 | 120.32 | AG2-055 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 113.97 | 120.1 | AG2-055 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 113.97 | 120.1 | AG2-055 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208395 | FARO FF | 208396 | FARO | 1 | 69 | 229 | 270 | 117.15 | 119.96 | AG2-055 | PL_05_P71_000906_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208394 | PPL-BGE TIE | 221092 | FIVE.FOR | 1 | 115 | 229/232 | 247 | 117.93 | 119.81 | AG2-055 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208393 | FARO DC TIE | 208395 | FARO FF | 1 | 115/69 | 229 | 120 | 121.56 | 119.66 | AG2-055 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208393 | FARO DC TIE | 208395 | FARO FF | 2 | 115/69 | 229 | 120 | 121.57 | 119.66 | AG2-055 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200519 | 26REED TAP | 200522 | 26SHADE GP | 1 | 115 | 226 | 271 | 117.01 | 119.13 | AG2-055 | ME_P2-3_ME-115-003DT_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3464 | 168.81 | 162.79 | AE2-334 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200519 | 26REED TAP | 200522 | 26SHADE GP | 1 | 115 | 226 | 271 | 116.94 | 119.06 | AG2-055 | ME_P2-3_ME-115-003AT_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 793 | 121.75 | 119 | AG2-055 | PEPCO_P1_PP2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 2 | 230 | 233 | 793 | 121.75 | 119 | AG2-055 | PEPCO_P1_PP1_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 221092 | FIVE.FOR | 221096 | ROCKRGE1 | 1 | 115 | 232 | 293 | 113.4 | 118.81 | AG2-055 | BG_P1_110512_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200504 | 26CARLISLE | 200520 | 26ROXBURY | 1 | 115 | 226 | 190 | 107.11 | 118.74 | AG2-055 | PN_P1-2_PN-115-094_A_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208393 | FARO DC TIE | 208395 | FARO FF | 1 | 115/69 | 229 | 120 | 123.95 | 118.68 | AG2-055 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208393 | FARO DC TIE | 208395 | FARO FF | 2 | 115/69 | 229 | 120 | 123.95 | 118.68 | AG2-055 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208131 | WHEM | 208133 | WHEM TR2 | 1 | 230 | 229 | 691 | 105.97 | 118.62 | AG2-055 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 2 | 500/230 | 225/232 | 2168 | 113.09 | 118.55 | AG2-055 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 221049 | FRED.RD8 | 221051 | CHESTN8A | 1 | 115 | 232 | 215 | 114.01 | 118.5 | AG2-055 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 2 | 500/230 | 225/232 | 2168 | 112.92 | 118.41 | AG2-055 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 2 | 500/230 | 225/232 | 2168 | 112.92 | 118.41 | AG2-055 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220964 | GRACETON | 220999 | BAGLEY2 | 13 | 230 | 232 | 1795 | 117.02 | 118.36 | AG2-055 | BG_P4_5_GRCTN_3T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 1 | 500/230 | 225/232 | 2168 | 112.85 | 118.3 | AG2-055 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3464 | 168.61 | 162.59 | AF1-015 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 1 | 500/230 | 225/232 | 2168 | 112.68 | 118.16 | AG2-055 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 1 | 500/230 | 225/232 | 2168 | 112.68 | 118.16 | AG2-055 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200504 | 26CARLISLE | 200520 | 26ROXBURY | 1 | 115 | 226 | 190 | 107.02 | 117.95 | AG2-055 | PN_P2-3_PN-115-58B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200504 | 26CARLISLE | 200520 | 26ROXBURY | 1 | 115 | 226 | 190 | 107.71 | 117.91 | AG2-055 | PN_P1-3_PN-115-040_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200504 | 26CARLISLE | 200520 | 26ROXBURY | 1 | 115 | 226 | 190 | 107.71 | 117.91 | AG2-055 | PN_P2-2_PN-115-030_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3464 | 168.64 | 162.62 | AF1-036 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200504 | 26CARLISLE | 200520 | 26ROXBURY | 1 | 115 | 226 | 190 | 106.83 | 117.88 | AG2-055 | PN_P1-2_PN-115-094_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 221089 | WINDYED1 | 221090 | GLENARM2 | 1 | 115 | 232 | 222 | 111.39 | 117.83 | AG2-055 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 221089 | WINDYED1 | 221090 | GLENARM2 | 1 | 115 | 232 | 222 | 110.73 | 117.4 | AG2-055 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208394 | PPL-BGE TIE | 221092 | FIVE.FOR | 1 | 115 | 229/232 | 247 | 111.46 | 117.33 | AG2-055 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 221089 | WINDYED1 | 221090 | GLENARM2 | 1 | 115 | 232 | 222 | 110.58 | 117.2 | AG2-055 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 221089 | WINDYED1 | 221090 | GLENARM2 | 1 | 115 | 232 | 222 | 110.58 | 117.2 | AG2-055 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208131 | WHEM | 208133 | WHEM TR2 | 1 | 230 | 229 | 691 | 105.4 | 117.14 | AG2-055 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208131 | WHEM | 208133 | WHEM TR2 | 1 | 230 | 229 | 691 | 105.4 | 117.14 | AG2-055 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208131 | WHEM | 208133 | WHEM TR2 | 1 | 230 | 229 | 691 | 105.39 | 117.14 | AG2-055 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208131 | WHEM | 208132 | WHEM TR1 | 1 | 230 | 229 | 691 | 108.18 | 117.11 | AG2-055 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 221092 | FIVE.FOR | 221096 | ROCKRGE1 | 1 | 115 | 232 | 293 | 111.58 | 117.04 | AG2-055 | BG_P4_5_WE512_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 112.93 | 116.8 | AG2-055 | PJM_500_BG_P4_5_CNSTN_15_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 117.82 | 116.78 | AG2-055 | BG_P4_5_CNSTN_14_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208394 | PPL-BGE TIE | 221092 | FIVE.FOR | 1 | 115 | 229/232 | 247 | 111.98 | 116.14 | AG2-055 | BG_P4_5_GRCTN_2T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200532 | 26ROXBURY | 200520 | 26ROXBURY | 2 | 138/115 | 226 | 435 | 100.39 | 116.05 | AG2-055 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208393 | FARO DC TIE | 208395 | FARO FF | 1 | 115/69 | 229 | 120 | 117.82 | 116.01 | AG2-055 | BG_P4_5_GRCTN_2T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208393 | FARO DC TIE | 208395 | FARO FF | 2 | 115/69 | 229 | 120 | 117.82 | 116.01 | AG2-055 | BG_P4_5_GRCTN_2T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 221089 | WINDYED1 | 221090 | GLENARM2 | 1 | 115 | 232 | 222 | 107.88 | 115.97 | AG2-055 | BG_P4_5_WE_NORTH_TIE_SRT-A/* WINDY EDGE #1(NORTH) BUS BLACK-RED BUS TIE BREAKER 221089 |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 221089 | WINDYED1 | 221090 | GLENARM2 | 1 | 115 | 232 | 222 | 107.74 | 115.9 | AG2-055 | BG_P4_5_WE504_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208394 | PPL-BGE TIE | 221092 | FIVE.FOR | 1 | 115 | 229/232 | 247 | 108.67 | 115.84 | AG2-055 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208393 | FARO DC TIE | 208395 | FARO FF | 1 | 115/69 | 229 | 120 | 117.29 | 115.78 | AG2-055 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208393 | FARO DC TIE | 208395 | FARO FF | 2 | 115/69 | 229 | 120 | 117.3 | 115.78 | AG2-055 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 221089 | WINDYED1 | 221090 | GLENARM2 | 1 | 115 | 232 | 222 | 107.52 | 115.7 | AG2-055 | BG_P2_WE_115-N-RED_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 109.98 | 115.69 | AG2-055 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 204529 | 27GERMANTN | 1 | 138/115 | 227 | 453 | 110.5 | 115.64 | AG2-055 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 204529 | 27GERMANTN | 1 | 138/115 | 227 | 453 | 110.5 | 115.64 | AG2-055 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 204529 | 27GERMANTN | 1 | 138/115 | 227 | 453 | 110.49 | 115.64 | AG2-055 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 109.85 | 115.56 | AG2-055 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 204529 | 27GERMANTN | 1 | 138/115 | 227 | 453 | 110.38 | 115.54 | AG2-055 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3464 | 168.25 | 162.24 | AF1-042 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200504 | 26CARLISLE | 200520 | 26ROXBURY | 1 | 115 | 226 | 190 | 98.02 | 115.22 | AG2-055 | PN_P2-3_PN-115-0331-B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220980 | RAPHAEL | 220999 | BAGLEY2 | 13 | 230 | 232 | 1795 | 112.52 | 115.11 | AG2-055 | BG_P4_5_GRCTN_3T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208393 | FARO DC TIE | 208395 | FARO FF | 1 | 115/69 | 229 | 120 | 114.41 | 114.95 | AG2-055 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208393 | FARO DC TIE | 208395 | FARO FF | 2 | 115/69 | 229 | 120 | 114.42 | 114.95 | AG2-055 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 221092 | FIVE.FOR | 221095 | ROCKRGE2 | 1 | 115 | 232 | 340 | 111.35 | 114.9 | AG2-055 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 2 | 500/230 | 225/232 | 2168 | 111.2 | 114.78 | AG2-055 | PJM_500_BG_P4_5_CNSTN_15_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208393 | FARO DC TIE | 208395 | FARO FF | 1 | 115/69 | 229 | 120 | 114.27 | 114.78 | AG2-055 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208393 | FARO DC TIE | 208395 | FARO FF | 1 | 115/69 | 229 | 120 | 114.27 | 114.78 | AG2-055 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208393 | FARO DC TIE | 208395 | FARO FF | 2 | 115/69 | 229 | 120 | 114.27 | 114.77 | AG2-055 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208393 | FARO DC TIE | 208395 | FARO FF | 2 | 115/69 | 229 | 120 | 114.27 | 114.77 | AG2-055 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 793 | 117.13 | 114.46 | AG2-055 | PEPCO_P4_PP19_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208395 | FARO FF | 208396 | FARO | 1 | 69 | 229 | 270 | 114.21 | 114.45 | AG2-055 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208395 | FARO FF | 208396 | FARO | 1 | 69 | 229 | 270 | 114.21 | 114.44 | AG2-055 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208395 | FARO FF | 208396 | FARO | 1 | 69 | 229 | 270 | 114.21 | 114.44 | AG2-055 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204512 | 27S.RDG | 204693 | 27BOONETOWN | 1 | 230 | 227 | 607 | 114.94 | 114.25 | AG2-055 | PL_04_P42_101307_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208395 | FARO FF | 208396 | FARO | 1 | 69 | 229 | 270 | 114.26 | 114.24 | AG2-055 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 221050 | FRED.RD7 | 221054 | CHESTN7A | 1 | 115 | 232 | 215 | 109.78 | 114.22 | AG2-055 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204512 | 27S.RDG | 204693 | 27BOONETOWN | 1 | 230 | 227 | 607 | 114.96 | 114.19 | AG2-055 | PL_24_P42_102306_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208021 | MANO TR4 | 208133 | WHEM TR2 | 2 | 230 | 229 | 593 | 101 | 113.86 | AG2-055 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208395 | FARO FF | 208396 | FARO | 1 | 69 | 229 | 270 | 108.08 | 113.67 | AG2-055 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200504 | 26CARLISLE | 200520 | 26ROXBURY | 1 | 115 | 226 | 190 | 104.5 | 113.43 | AG2-055 | PN_P2-3_PN-230-0014-12_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3464 | 167.96 | 161.95 | AF1-147 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200504 | 26CARLISLE | 200520 | 26ROXBURY | 1 | 115 | 226 | 190 | 104.49 | 113 | AG2-055 | PN_P2-3_PN-230-0014-11_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200504 | 26CARLISLE | 200520 | 26ROXBURY | 1 | 115 | 226 | 190 | 104.49 | 113 | AG2-055 | PN_P1-3_PN-230-020A_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200504 | 26CARLISLE | 200520 | 26ROXBURY | 1 | 115 | 226 | 190 | 104.42 | 112.98 | AG2-055 | PN_P2-2_PN-115-031_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220973 | GRANITE6 | 1 | 230 | 232 | 829 | 113.63 | 112.76 | AG2-055 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208393 | FARO DC TIE | 208395 | FARO FF | 1 | 115/69 | 229 | 120 | 113.94 | 112.68 | AG2-055 | PL_05_P22_000674_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208393 | FARO DC TIE | 208395 | FARO FF | 1 | 115/69 | 229 | 120 | 113.94 | 112.68 | AG2-055 | PL_04_P12_000257_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208393 | FARO DC TIE | 208395 | FARO FF | 2 | 115/69 | 229 | 120 | 113.94 | 112.68 | AG2-055 | PL_04_P12_000257_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208393 | FARO DC TIE | 208395 | FARO FF | 2 | 115/69 | 229 | 120 | 113.95 | 112.68 | AG2-055 | PL_05_P22_000674_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208020 | MANO TR3 | 208031 | MLWD TR2 | 1 | 230 | 229 | 903 | 102.11 | 112.5 | AG2-055 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 221092 | FIVE.FOR | 221096 | ROCKRGE1 | 1 | 115 | 232 | 293 | 107.45 | 112.26 | AG2-055 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208021 | MANO TR4 | 208133 | WHEM TR2 | 2 | 230 | 229 | 593 | 100.36 | 112.24 | AG2-055 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208021 | MANO TR4 | 208133 | WHEM TR2 | 2 | 230 | 229 | 593 | 100.36 | 112.24 | AG2-055 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208021 | MANO TR4 | 208133 | WHEM TR2 | 2 | 230 | 229 | 593 | 100.34 | 112.24 | AG2-055 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 221089 | WINDYED1 | 221090 | GLENARM2 | 1 | 115 | 232 | 222 | 103.64 | 111.99 | AG2-055 | BG_P4_5_WE506_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204512 | 27S.RDG | 204693 | 27BOONETOWN | 1 | 230 | 227 | 607 | 112.45 | 111.86 | AG2-055 | PL_04_P43_102301_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204512 | 27S.RDG | 204693 | 27BOONETOWN | 1 | 230 | 227 | 607 | 112.45 | 111.86 | AG2-055 | PL_04_P22_102291_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204512 | 27S.RDG | 204693 | 27BOONETOWN | 1 | 230 | 227 | 607 | 112.45 | 111.85 | AG2-055 | PL_04_P13_101211_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220972 | GRANITE1 | 1 | 230 | 232 | 829 | 112.8 | 111.68 | AG2-055 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 221092 | FIVE.FOR | 221094 | GRACE.-1 | 1 | 115 | 232 | 498 | 110.35 | 111.67 | AG2-055 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208395 | FARO FF | 208396 | FARO | 1 | 69 | 229 | 270 | 110.2 | 111.52 | AG2-055 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 221092 | FIVE.FOR | 221096 | ROCKRGE1 | 1 | 115 | 232 | 293 | 106.32 | 111.3 | AG2-055 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220965 | NEAST339 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 112.7 | 111.19 | AG2-055 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 221092 | FIVE.FOR | 221096 | ROCKRGE1 | 1 | 115 | 232 | 293 | 106.2 | 111.14 | AG2-055 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 221092 | FIVE.FOR | 221096 | ROCKRGE1 | 1 | 115 | 232 | 293 | 106.2 | 111.14 | AG2-055 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 2 | 230 | 233 | 793 | 113.04 | 111.12 | AG2-055 | AP_P2-3_PE-500-019C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 793 | 113.04 | 111.12 | AG2-055 | AP_P2-3_PE-500-019C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220965 | NEAST339 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 112.6 | 111.08 | AG2-055 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220965 | NEAST339 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 112.6 | 111.08 | AG2-055 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200099 | LAUS | 208045 | LAUS | 3 | 500/230 | 225/229 | 1200 | 108.49 | 110.75 | AG2-055 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204520 | 27ALLEN | 208142 | WIGR-115 | 1 | 115 | 227/229 | 351.4 | 99.36 | 110.39 | AG2-055 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204520 | 27ALLEN | 208142 | WIGR-115 | 1 | 115 | 227/229 | 351.4 | 99.36 | 110.39 | AG2-055 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204520 | 27ALLEN | 208142 | WIGR-115 | 1 | 115 | 227/229 | 351.4 | 99.36 | 110.39 | AG2-055 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200099 | LAUS | 208045 | LAUS | 3 | 500/230 | 225/229 | 1200 | 108.24 | 110.24 | AG2-055 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200099 | LAUS | 208045 | LAUS | 3 | 500/230 | 225/229 | 1200 | 108.24 | 110.24 | AG2-055 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200099 | LAUS | 208045 | LAUS | 3 | 500/230 | 225/229 | 1200 | 108.23 | 110.23 | AG2-055 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204520 | 27ALLEN | 208142 | WIGR-115 | 1 | 115 | 227/229 | 351.4 | 99.17 | 110.22 | AG2-055 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 105.07 | 110.03 | AG2-055 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 104.99 | 109.95 | AG2-055 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220972 | GRANITE1 | 1 | 230 | 232 | 829 | 110.89 | 109.56 | AG2-055 | BG_P4_5_NW230-4_2326_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 221092 | FIVE.FOR | 221096 | ROCKRGE1 | 1 | 115 | 232 | 293 | 103.74 | 109.49 | AG2-055 | BG_P4_5_WE_EAST_TIE_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3464 | 168.27 | 162.26 | AF1-173 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208395 | FARO FF | 208396 | FARO | 1 | 69 | 229 | 270 | 104.28 | 109.23 | AG2-055 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 221092 | FIVE.FOR | 221096 | ROCKRGE1 | 1 | 115 | 232 | 293 | 103.32 | 109.14 | AG2-055 | BG_P4_5_WE518_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220973 | GRANITE6 | 1 | 230 | 232 | 829 | 110.59 | 109.05 | AG2-055 | BG_P4_5_NW230-5_2311_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200009 | JUNI | 208004 | JUNI | 2 | 500/230 | 225/229 | 1040 | 109.46 | 108.98 | AG2-055 | PL_10_P42_000140_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 221049 | FRED.RD8 | 221051 | CHESTN8A | 1 | 115 | 232 | 215 | 104.97 | 108.83 | AG2-055 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208021 | MANO TR4 | 1 | 230 | 229 | 600 | 93.96 | 108.78 | AG2-055 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208131 | WHEM | 208133 | WHEM TR2 | 1 | 230 | 229 | 691 | 100.66 | 108.58 | AG2-055 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3464 | 168.62 | 162.6 | AF1-174 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 106.1 | 108.44 | AG2-055 | BG_P1_2322_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 106.02 | 108.35 | AG2-055 | BG_P1_2310_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 106.02 | 108.31 | AG2-055 | BG_P4_5_NW2322_230-4_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 105.94 | 108.27 | AG2-055 | BG_P4_5_NW2310_230-5_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208395 | FARO FF | 208396 | FARO | 1 | 69 | 229 | 270 | 104.75 | 108.12 | AG2-055 | BG_P4_5_GRCTN_2T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220979 | NEAST317 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 109.39 | 107.95 | AG2-055 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3464 | 167.49 | 161.49 | AF1-227 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220979 | NEAST317 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 109.29 | 107.84 | AG2-055 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220979 | NEAST317 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 109.29 | 107.84 | AG2-055 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208395 | FARO FF | 208396 | FARO | 1 | 69 | 229 | 270 | 101.72 | 107.83 | AG2-055 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200101 | VINCO | 200102 | AA1-076 MAIN | 1 | 500 | 225 | 999 | 102.07 | 107.7 | AG2-055 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220973 | GRANITE6 | 1 | 230 | 232 | 829 | 108.3 | 107.56 | AG2-055 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 204529 | 27GERMANTN | 1 | 138/115 | 227 | 453 | 104.69 | 107.26 | AG2-055 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208021 | MANO TR4 | 1 | 230 | 229 | 600 | 93.3 | 107.18 | AG2-055 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208021 | MANO TR4 | 1 | 230 | 229 | 600 | 93.29 | 107.18 | AG2-055 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208021 | MANO TR4 | 1 | 230 | 229 | 600 | 93.3 | 107.18 | AG2-055 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 100.52 | 107.12 | AG2-055 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 100.53 | 107.12 | AG2-055 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 100.53 | 107.12 | AG2-055 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 221088 | WINDYED2 | 221100 | GLENARM1 | 1 | 115 | 232 | 353 | 104.15 | 107.02 | AG2-055 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220965 | NEAST339 | 220977 | RIV2339 | 1 | 230 | 232 | 991 | 108.55 | 106.98 | AG2-055 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 104.59 | 106.97 | AG2-055 | BG_P4_5_NW230-2_2322_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220965 | NEAST339 | 220977 | RIV2339 | 1 | 230 | 232 | 991 | 108.51 | 106.92 | AG2-055 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220965 | NEAST339 | 220977 | RIV2339 | 1 | 230 | 232 | 991 | 108.51 | 106.92 | AG2-055 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220966 | RIV2317 | 220979 | NEAST317 | 1 | 230 | 232 | 940 | 108.03 | 106.89 | AG2-055 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 104.48 | 106.85 | AG2-055 | BG_P4_5_NW2371_2310_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 104.48 | 106.84 | AG2-055 | BG_P4_5_NW230-3_2310_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220966 | RIV2317 | 220979 | NEAST317 | 1 | 230 | 232 | 940 | 107.98 | 106.83 | AG2-055 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220966 | RIV2317 | 220979 | NEAST317 | 1 | 230 | 232 | 940 | 107.98 | 106.83 | AG2-055 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220972 | GRANITE1 | 1 | 230 | 232 | 829 | 107.73 | 106.79 | AG2-055 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200532 | 26ROXBURY | 200520 | 26ROXBURY | 2 | 138/115 | 226 | 435 | 93.2 | 106.67 | AG2-055 | AP_P2-3_PE-500-016_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200532 | 26ROXBURY | 200520 | 26ROXBURY | 2 | 138/115 | 226 | 435 | 93.34 | 106.52 | AG2-055 | AP_P2-3_PE-500-015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220965 | NEAST339 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 106.54 | 106.24 | AG2-055 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 103.59 | 105.89 | AG2-055 | BG_P4_5_CNSTN_14_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 99.78 | 105.86 | AG2-055 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220964 | GRACETON | 220999 | BAGLEY2 | 13 | 230 | 232 | 1795 | 104.79 | 105.78 | AG2-055 | BG_P1_2305_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220964 | GRACETON | 221000 | BAGLEY | 5 | 230 | 232 | 1795 | 104.78 | 105.78 | AG2-055 | BG_P1_2313_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208393 | FARO DC TIE | 208394 | PPL-BGE TIE | 1 | 115 | 229 | 302 | 104.44 | 105.35 | AG2-055 | PL_05_P71_000906_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220964 | GRACETON | 221094 | GRACE.-1 | 1 | 230/115 | 232 | 510 | 107.94 | 105.31 | AG2-055 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 204529 | 27GERMANTN | 1 | 138/115 | 227 | 453 | 99.27 | 105.04 | AG2-055 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3464 | 168.62 | 162.6 | AG1-080 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 204529 | 27GERMANTN | 1 | 138/115 | 227 | 453 | 99.92 | 104.81 | AG2-055 | AP_P2-3_PE-500-016_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3464 | 168.29 | 162.28 | AG1-086 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 221050 | FRED.RD7 | 221054 | CHESTN7A | 1 | 115 | 232 | 215 | 100.74 | 104.55 | AG2-055 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220972 | GRANITE1 | 1 | 230 | 232 | 829 | 105.5 | 104.42 | AG2-055 | BG_P4_5_GRNITE26_32_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 2 | 500/230 | 225/232 | 2168 | 101.34 | 104.31 | AG2-055 | BG_P1_CNSTN_500-2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 2 | 500/230 | 225/232 | 2168 | 101.34 | 104.31 | AG2-055 | PJM_500_BG_P2_CNSTN_230-N_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 1 | 500/230 | 225/232 | 2168 | 101.23 | 104.2 | AG2-055 | BG_P1_CNSTN_500-4_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 1 | 500/230 | 225/232 | 2168 | 101.23 | 104.2 | AG2-055 | PJM_500_BG_P2_CNSTN_230-S_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200099 | LAUS | 208045 | LAUS | 3 | 500/230 | 225/229 | 1200 | 102.32 | 104.1 | AG2-055 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220941 | H.RDGE16 | 221010 | COLUMB12 | 1 | 230 | 232 | 876 | 107.67 | 104.1 | AG2-055 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 223960 | BRG 1T 230 | 1 | 500/230 | 225/233 | 1498 | 103.46 | 104.08 | AG2-055 | PEPCO_P4_PP41_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220979 | NEAST317 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 104.29 | 103.98 | AG2-055 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200065 | PCHBTM2S | 200066 | PCHBTM1N | 2 | 500 | 225 | 3022 | 108.74 | 103.95 | AG2-055 | PECO_P4_PEACH205_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220973 | GRANITE6 | 1 | 230 | 232 | 829 | 105.3 | 103.94 | AG2-055 | BBG_P1_2311_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220972 | GRANITE1 | 1 | 230 | 232 | 829 | 104.96 | 103.86 | AG2-055 | BG_P1_2326_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220973 | GRANITE6 | 1 | 230 | 232 | 829 | 104.64 | 103.82 | AG2-055 | BG_P1_2312_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220973 | GRANITE6 | 1 | 230 | 232 | 829 | 104.8 | 103.81 | AG2-055 | BG_P4_5_GRNITE11_12_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3464 | 167.8 | 161.79 | AG1-397 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 99.7 | 103.5 | AG2-055 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220941 | H.RDGE16 | 221010 | COLUMB12 | 1 | 230 | 232 | 876 | 106.91 | 103.3 | AG2-055 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220941 | H.RDGE16 | 221010 | COLUMB12 | 1 | 230 | 232 | 876 | 106.91 | 103.3 | AG2-055 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208021 | MANO TR4 | 208133 | WHEM TR2 | 2 | 230 | 229 | 593 | 95.04 | 103.17 | AG2-055 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 221092 | FIVE.FOR | 221094 | GRACE.-1 | 1 | 115 | 232 | 498 | 100.37 | 102.85 | AG2-055 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204520 | 27ALLEN | 208142 | WIGR-115 | 1 | 115 | 227/229 | 351.4 | 95.48 | 102.84 | AG2-055 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220966 | RIV2317 | 220979 | NEAST317 | 1 | 230 | 232 | 940 | 102.09 | 102.68 | AG2-055 | BG_P4_5_NEAST_37_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220966 | RIV2317 | 220979 | NEAST317 | 1 | 230 | 232 | 940 | 102.09 | 102.68 | AG2-055 | BG_P4_5_NEAST_39_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220980 | RAPHAEL | 221000 | BAGLEY | 5 | 230 | 232 | 1795 | 100.28 | 102.54 | AG2-055 | BG_P1_2313_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220980 | RAPHAEL | 220999 | BAGLEY2 | 13 | 230 | 232 | 1795 | 100.28 | 102.54 | AG2-055 | BG_P1_2305_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208045 | LAUS | 208078 | SAKR | 3 | 230 | 229 | 903 | 92.13 | 102.1 | AG2-055 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 221092 | FIVE.FOR | 221095 | ROCKRGE2 | 1 | 115 | 232 | 340 | 97.21 | 101.98 | AG2-055 | BG_P1_110511_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220973 | GRANITE6 | 1 | 230 | 232 | 829 | 102.72 | 101.95 | AG2-055 | BG_P7_HIRDG_SNWDNRVR_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 2 | 500/230 | 225/232 | 2168 | 98.66 | 101.65 | AG2-055 | PJM_500_BG_P4_5_CNSTN_9_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 2 | 500/230 | 225/232 | 2168 | 98.66 | 101.65 | AG2-055 | PJM_500_BG_P4_5_CNSTN_10_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 1 | 500/230 | 225/232 | 2168 | 98.56 | 101.54 | AG2-055 | PJM_500_BG_P4_5_CNSTN_12_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 221049 | FRED.RD8 | 221051 | CHESTN8A | 1 | 115 | 232 | 215 | 98.32 | 101.51 | AG2-055 | BG_P7_GRNITE_HIRDG_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208045 | LAUS | 208078 | SAKR | 3 | 230 | 229 | 903 | 91.87 | 101.29 | AG2-055 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208045 | LAUS | 208078 | SAKR | 3 | 230 | 229 | 903 | 91.87 | 101.28 | AG2-055 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208045 | LAUS | 208078 | SAKR | 3 | 230 | 229 | 903 | 91.87 | 101.28 | AG2-055 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200762 | 26GARRETT | 235470 | 01GARRET | 1 | 115 | 226/201 | 190 | 99 | 101.19 | AG2-055 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200762 | 26GARRETT | 235470 | 01GARRET | 1 | 115 | 226/201 | 190 | 99 | 101.19 | AG2-055 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200762 | 26GARRETT | 235470 | 01GARRET | 1 | 115 | 226/201 | 190 | 98.84 | 101.05 | AG2-055 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220966 | RIV2317 | 220979 | NEAST317 | 1 | 230 | 232 | 940 | 99.98 | 100.83 | AG2-055 | BG_P1_2337_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208393 | FARO DC TIE | 208394 | PPL-BGE TIE | 1 | 115 | 229 | 302 | 101.82 | 100.58 | AG2-055 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208393 | FARO DC TIE | 208394 | PPL-BGE TIE | 1 | 115 | 229 | 302 | 101.82 | 100.58 | AG2-055 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208393 | FARO DC TIE | 208394 | PPL-BGE TIE | 1 | 115 | 229 | 302 | 101.82 | 100.58 | AG2-055 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 221092 | FIVE.FOR | 221095 | ROCKRGE2 | 1 | 115 | 232 | 340 | 95.54 | 100.52 | AG2-055 | BG_P4_5_WE511_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208393 | FARO DC TIE | 208394 | PPL-BGE TIE | 1 | 115 | 229 | 302 | 101.87 | 100.39 | AG2-055 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 911 | 100.05 | 100.23 | AG2-055 | PL_04_P12_000260_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 911 | 100.05 | 100.23 | AG2-055 | PL_04_P42_000564_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200762 | 26GARRETT | 235470 | 01GARRET | 1 | 115 | 226/201 | 190 | 95.47 | 100.09 | AG2-055 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200762 | 26GARRETT | 235470 | 01GARRET | 1 | 115 | 226/201 | 190 | 95.5 | 100 | AG2-055 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200762 | 26GARRETT | 235470 | 01GARRET | 1 | 115 | 226/201 | 190 | 95.5 | 100 | AG2-055 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200762 | 26GARRETT | 235470 | 01GARRET | 1 | 115 | 226/201 | 190 | 95.5 | 100 | AG2-055 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3464 | 177.27 | 171.1 | AG2-055 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 154.19 | 158.77 | ALDENE_AB | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.69 | 157.81 | ALDENE_AB | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.69 | 157.81 | ALDENE_AB | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 152.5 | 157.44 | ALDENE_AB | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 162.33 | 155.08 | ALDENE_AB | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 149.13 | 153.79 | ALDENE_AB | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 156.26 | 151.11 | ALDENE_AB | PN_P1-2_PN-500-010T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.95 | 150.14 | ALDENE_AB | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.88 | 150.07 | ALDENE_AB | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.55 | 148.89 | ALDENE_AB | AP_P2-3_PE-500-016_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.62 | 148.86 | ALDENE_AB | AP_P2-3_PE-500-015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.91 | 148.47 | ALDENE_AB | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.56 | 148.42 | ALDENE_AB | PJM_500_BG_P4_5_CNSTN_L_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.71 | 148.28 | ALDENE_AB | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.74 | 148.27 | ALDENE_AB | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.47 | 148.07 | ALDENE_AB | PECO_P4_NOTTI85_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.41 | 148.06 | ALDENE_AB | PECO_P1-2_220-08_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.73 | 148 | ALDENE_AB | AP_P1-2_WP-500-DRT17_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.73 | 148 | ALDENE_AB | AP_P1-2_PE-500-001_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.34 | 147.99 | ALDENE_AB | PECO_P4_COOPR125_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.68 | 147.93 | ALDENE_AB | AP_P2-3_PE-500-018C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3464 | 168.75 | 162.73 | ALDENE_AB | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 151.57 | 144.83 | ALDENE_AB | PECO_P4_PEACH025_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 151.46 | 144.76 | ALDENE_AB | PECO_P1-2_PBTIE1_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 139.76 | 133.8 | ALDENE_AB | PECO_P4_PEACH205_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 139.67 | 133.49 | ALDENE_AB | PECO_P1-2_PBTIE2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 138.67 | 132.56 | ALDENE_AB | PECO_P4_PEACH055_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 134.09 | 128.25 | ALDENE_AB | PECO_P4_PEACH015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 132.71 | 126.85 | ALDENE_AB | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 123.62 | 118.22 | ALDENE_AB | PECO_P4_PEACH225_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 225.72 | 237.28 | BIGSKY | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 223.72 | 237.28 | BIGSKY | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 225.66 | 237.22 | BIGSKY | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 223.65 | 237.22 | BIGSKY | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 225.66 | 237.22 | BIGSKY | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 223.65 | 237.22 | BIGSKY | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 213.66 | 227.12 | BIGSKY | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 213.6 | 227.06 | BIGSKY | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 213.6 | 227.06 | BIGSKY | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 209.4 | 223.91 | BIGSKY | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 209.34 | 223.85 | BIGSKY | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 209.34 | 223.85 | BIGSKY | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3464 | 168.06 | 162.05 | BIGSKY | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 153.69 | 158.17 | BIGSKY | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.15 | 157.28 | BIGSKY | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.15 | 157.27 | BIGSKY | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 152 | 156.85 | BIGSKY | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 161.59 | 154.37 | BIGSKY | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 148.64 | 153.2 | BIGSKY | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 155.72 | 150.58 | BIGSKY | PN_P1-2_PN-500-010T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.48 | 149.58 | BIGSKY | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.4 | 149.51 | BIGSKY | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.12 | 148.39 | BIGSKY | AP_P2-3_PE-500-016_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.19 | 148.36 | BIGSKY | AP_P2-3_PE-500-015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.04 | 147.91 | BIGSKY | PJM_500_BG_P4_5_CNSTN_L_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.28 | 147.84 | BIGSKY | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.08 | 147.66 | BIGSKY | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.1 | 147.64 | BIGSKY | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.3 | 147.5 | BIGSKY | AP_P1-2_WP-500-DRT17_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.3 | 147.5 | BIGSKY | AP_P1-2_PE-500-001_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.83 | 147.45 | BIGSKY | PECO_P4_NOTTI85_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.25 | 147.43 | BIGSKY | AP_P2-3_PE-500-018C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.77 | 147.43 | BIGSKY | PECO_P1-2_220-08_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.71 | 147.37 | BIGSKY | PECO_P4_COOPR125_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3464 | 168.12 | 162.11 | BISHOP | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.79 | 144.08 | BIGSKY | PECO_P4_PEACH025_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.68 | 144.01 | BIGSKY | PECO_P1-2_PBTIE1_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 139.07 | 133.14 | BIGSKY | PECO_P4_PEACH205_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 138.95 | 132.8 | BIGSKY | PECO_P1-2_PBTIE2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 138.01 | 131.93 | BIGSKY | PECO_P4_PEACH055_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 133.33 | 127.51 | BIGSKY | PECO_P4_PEACH015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 132.01 | 126.19 | BIGSKY | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 122.91 | 117.54 | BIGSKY | PECO_P4_PEACH225_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3464 | 168.64 | 162.62 | BRUNSWCK_AB | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 153.73 | 158.23 | BISHOP | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.2 | 157.33 | BISHOP | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.2 | 157.33 | BISHOP | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 152.05 | 156.91 | BISHOP | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 161.66 | 154.44 | BISHOP | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 148.68 | 153.26 | BISHOP | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 155.77 | 150.62 | BISHOP | PN_P1-2_PN-500-010T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.52 | 149.63 | BISHOP | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.45 | 149.56 | BISHOP | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.16 | 148.43 | BISHOP | AP_P2-3_PE-500-016_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.23 | 148.4 | BISHOP | AP_P2-3_PE-500-015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.09 | 147.96 | BISHOP | PJM_500_BG_P4_5_CNSTN_L_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.34 | 147.9 | BISHOP | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.14 | 147.72 | BISHOP | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.16 | 147.7 | BISHOP | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.34 | 147.55 | BISHOP | AP_P1-2_WP-500-DRT17_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.34 | 147.55 | BISHOP | AP_P1-2_PE-500-001_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.89 | 147.51 | BISHOP | PECO_P4_NOTTI85_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.83 | 147.49 | BISHOP | PECO_P1-2_220-08_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.29 | 147.48 | BISHOP | AP_P2-3_PE-500-018C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.77 | 147.43 | BISHOP | PECO_P4_COOPR125_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3464 | 168.21 | 162.19 | CAMPGROVE;RU | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.86 | 144.15 | BISHOP | PECO_P4_PEACH025_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.75 | 144.07 | BISHOP | PECO_P1-2_PBTIE1_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 139.13 | 133.2 | BISHOP | PECO_P4_PEACH205_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 139.01 | 132.86 | BISHOP | PECO_P1-2_PBTIE2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 138.07 | 131.99 | BISHOP | PECO_P4_PEACH055_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 133.39 | 127.57 | BISHOP | PECO_P4_PEACH015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 132.07 | 126.25 | BISHOP | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 122.97 | 117.6 | BISHOP | PECO_P4_PEACH225_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3464 | 167.96 | 161.95 | CAYUGA | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.6 | 157.73 | BRUNSWCK_AB | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.6 | 157.73 | BRUNSWCK_AB | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 162.2 | 154.96 | BRUNSWCK_AB | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 156.17 | 151.02 | BRUNSWCK_AB | PN_P1-2_PN-500-010T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.81 | 148.37 | BRUNSWCK_AB | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.47 | 148.34 | BRUNSWCK_AB | PJM_500_BG_P4_5_CNSTN_L_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.61 | 148.18 | BRUNSWCK_AB | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.64 | 148.17 | BRUNSWCK_AB | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.37 | 147.97 | BRUNSWCK_AB | PECO_P4_NOTTI85_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.31 | 147.96 | BRUNSWCK_AB | PECO_P1-2_220-08_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.24 | 147.89 | BRUNSWCK_AB | PECO_P4_COOPR125_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 151.44 | 144.71 | BRUNSWCK_AB | PECO_P4_PEACH025_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 151.32 | 144.62 | BRUNSWCK_AB | PECO_P1-2_PBTIE1_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 139.64 | 133.68 | BRUNSWCK_AB | PECO_P4_PEACH205_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 139.54 | 133.37 | BRUNSWCK_AB | PECO_P1-2_PBTIE2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 138.56 | 132.46 | BRUNSWCK_AB | PECO_P4_PEACH055_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 133.95 | 128.11 | BRUNSWCK_AB | PECO_P4_PEACH015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 132.58 | 126.73 | BRUNSWCK_AB | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 123.49 | 118.1 | BRUNSWCK_AB | PECO_P4_PEACH225_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 143.3 | 138.18 | CAMDEN_26 | PL_30_P42_000131_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3464 | 168.66 | 162.64 | CHERRYDALE C | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 153.8 | 158.3 | CAMPGROVE;RU | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.27 | 157.39 | CAMPGROVE;RU | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.26 | 157.39 | CAMPGROVE;RU | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 152.11 | 156.98 | CAMPGROVE;RU | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 161.75 | 154.52 | CAMPGROVE;RU | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 148.75 | 153.33 | CAMPGROVE;RU | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 155.84 | 150.69 | CAMPGROVE;RU | PN_P1-2_PN-500-010T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.58 | 149.7 | CAMPGROVE;RU | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.51 | 149.63 | CAMPGROVE;RU | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.21 | 148.49 | CAMPGROVE;RU | AP_P2-3_PE-500-016_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.28 | 148.46 | CAMPGROVE;RU | AP_P2-3_PE-500-015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.15 | 148.02 | CAMPGROVE;RU | PJM_500_BG_P4_5_CNSTN_L_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.42 | 147.98 | CAMPGROVE;RU | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.21 | 147.79 | CAMPGROVE;RU | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.24 | 147.78 | CAMPGROVE;RU | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.39 | 147.61 | CAMPGROVE;RU | AP_P1-2_WP-500-DRT17_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.39 | 147.61 | CAMPGROVE;RU | AP_P1-2_PE-500-001_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.97 | 147.58 | CAMPGROVE;RU | PECO_P4_NOTTI85_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.91 | 147.57 | CAMPGROVE;RU | PECO_P1-2_220-08_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.34 | 147.54 | CAMPGROVE;RU | AP_P2-3_PE-500-018C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.84 | 147.5 | CAMPGROVE;RU | PECO_P4_COOPR125_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3464 | 168.69 | 162.67 | D05 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.95 | 144.24 | CAMPGROVE;RU | PECO_P4_PEACH025_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.83 | 144.16 | CAMPGROVE;RU | PECO_P1-2_PBTIE1_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 139.21 | 133.27 | CAMPGROVE;RU | PECO_P4_PEACH205_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 139.1 | 132.94 | CAMPGROVE;RU | PECO_P1-2_PBTIE2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 138.15 | 132.06 | CAMPGROVE;RU | PECO_P4_PEACH055_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 133.48 | 127.66 | CAMPGROVE;RU | PECO_P4_PEACH015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 132.15 | 126.32 | CAMPGROVE;RU | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 123.05 | 117.68 | CAMPGROVE;RU | PECO_P4_PEACH225_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 225.59 | 237.1 | CAYUGA | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 223.59 | 237.1 | CAYUGA | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 225.53 | 237.04 | CAYUGA | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 223.52 | 237.04 | CAYUGA | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 225.53 | 237.04 | CAYUGA | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 223.52 | 237.03 | CAYUGA | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 213.54 | 226.94 | CAYUGA | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 213.47 | 226.88 | CAYUGA | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 213.47 | 226.88 | CAYUGA | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 209.28 | 223.73 | CAYUGA | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 209.21 | 223.67 | CAYUGA | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 209.21 | 223.67 | CAYUGA | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 210.7 | 217.91 | CAYUGA | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 208.69 | 217.9 | CAYUGA | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 199.15 | 208.34 | CAYUGA | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 194.9 | 204.99 | CAYUGA | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 172.83 | 167.9 | CAYUGA | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 161.82 | 161.96 | CAYUGA | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 161.82 | 161.96 | CAYUGA | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3464 | 168.73 | 162.7 | DC1 NUG | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 161.8 | 161.95 | CAYUGA | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 153.62 | 158.1 | CAYUGA | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.07 | 157.2 | CAYUGA | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.07 | 157.2 | CAYUGA | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 151.93 | 156.77 | CAYUGA | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 161.5 | 154.28 | CAYUGA | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 148.57 | 153.12 | CAYUGA | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 155.65 | 150.51 | CAYUGA | PN_P1-2_PN-500-010T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.41 | 149.51 | CAYUGA | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.34 | 149.43 | CAYUGA | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.07 | 148.33 | CAYUGA | AP_P2-3_PE-500-016_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.13 | 148.3 | CAYUGA | AP_P2-3_PE-500-015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.97 | 147.84 | CAYUGA | PJM_500_BG_P4_5_CNSTN_L_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.19 | 147.76 | CAYUGA | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.99 | 147.57 | CAYUGA | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.02 | 147.56 | CAYUGA | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.24 | 147.44 | CAYUGA | AP_P1-2_PE-500-001_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.24 | 147.44 | CAYUGA | AP_P1-2_WP-500-DRT17_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.19 | 147.37 | CAYUGA | AP_P2-3_PE-500-018C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.75 | 147.36 | CAYUGA | PECO_P4_NOTTI85_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.69 | 147.35 | CAYUGA | PECO_P1-2_220-08_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.62 | 147.28 | CAYUGA | PECO_P4_COOPR125_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3464 | 168.73 | 162.7 | DC2 NUG | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.68 | 143.98 | CAYUGA | PECO_P4_PEACH025_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.57 | 143.91 | CAYUGA | PECO_P1-2_PBTIE1_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 911 | 149.07 | 143.23 | CAYUGA | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 1031 | 130.36 | 138.2 | CAYUGA | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 138.99 | 133.05 | CAYUGA | PECO_P4_PEACH205_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 138.86 | 132.71 | CAYUGA | PECO_P1-2_PBTIE2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208078 | SAKR | 1 | 230 | 229 | 903 | 124.55 | 132.65 | CAYUGA | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 137.93 | 131.85 | CAYUGA | PECO_P4_PEACH055_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 133.23 | 127.42 | CAYUGA | PECO_P4_PEACH015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 131.92 | 126.1 | CAYUGA | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208020 | MANO TR3 | 1 | 230 | 229 | 793 | 111.54 | 124.75 | CAYUGA | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208020 | MANO TR3 | 1 | 230 | 229 | 793 | 111.53 | 124.74 | CAYUGA | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208020 | MANO TR3 | 1 | 230 | 229 | 793 | 111.54 | 124.74 | CAYUGA | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 122.82 | 117.46 | CAYUGA | PECO_P4_PEACH225_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 99.67 | 103.64 | CAYUGA | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 99.67 | 103.64 | CAYUGA | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 99.67 | 103.64 | CAYUGA | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3464 | 168.29 | 162.28 | ECOGROVE ;U1 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.62 | 157.74 | CHERRYDALE C | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.61 | 157.74 | CHERRYDALE C | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 162.23 | 154.98 | CHERRYDALE C | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 156.19 | 151.03 | CHERRYDALE C | PN_P1-2_PN-500-010T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.83 | 148.39 | CHERRYDALE C | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.49 | 148.35 | CHERRYDALE C | PJM_500_BG_P4_5_CNSTN_L_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.63 | 148.2 | CHERRYDALE C | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.66 | 148.19 | CHERRYDALE C | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.39 | 147.99 | CHERRYDALE C | PECO_P4_NOTTI85_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.33 | 147.97 | CHERRYDALE C | PECO_P1-2_220-08_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.26 | 147.91 | CHERRYDALE C | PECO_P4_COOPR125_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 151.5 | 144.77 | CHERRYDALE C | PECO_P4_PEACH025_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 151.34 | 144.64 | CHERRYDALE C | PECO_P1-2_PBTIE1_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 139.56 | 133.39 | CHERRYDALE C | PECO_P1-2_PBTIE2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 138.6 | 132.49 | CHERRYDALE C | PECO_P4_PEACH055_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 133.98 | 128.13 | CHERRYDALE C | PECO_P4_PEACH015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 132.6 | 126.75 | CHERRYDALE C | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204512 | 27S.RDG | 204693 | 27BOONETOWN | 1 | 230 | 227 | 607 | 107.73 | 122.16 | CHERRYDALE C | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 123.51 | 118.12 | CHERRYDALE C | PECO_P4_PEACH225_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3464 | 168.98 | 162.95 | FAIRLAWN_AB | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 154.16 | 158.74 | D05 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.65 | 157.77 | D05 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.65 | 157.77 | D05 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 152.47 | 157.41 | D05 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 162.27 | 155.02 | D05 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 149.11 | 153.76 | D05 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 156.22 | 151.07 | D05 | PN_P1-2_PN-500-010T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.93 | 150.11 | D05 | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.85 | 150.04 | D05 | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.53 | 148.86 | D05 | AP_P2-3_PE-500-016_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.59 | 148.83 | D05 | AP_P2-3_PE-500-015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.86 | 148.41 | D05 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.52 | 148.39 | D05 | PJM_500_BG_P4_5_CNSTN_L_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.66 | 148.23 | D05 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.68 | 148.21 | D05 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.41 | 148.02 | D05 | PECO_P4_NOTTI85_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.35 | 148 | D05 | PECO_P1-2_220-08_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.71 | 147.97 | D05 | AP_P1-2_PE-500-001_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.71 | 147.97 | D05 | AP_P1-2_WP-500-DRT17_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.29 | 147.94 | D05 | PECO_P4_COOPR125_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.66 | 147.9 | D05 | AP_P2-3_PE-500-018C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3464 | 167.66 | 161.66 | G07 NFTWR | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 151.47 | 144.74 | D05 | PECO_P4_PEACH025_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 151.39 | 144.69 | D05 | PECO_P1-2_PBTIE1_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 139.71 | 133.76 | D05 | PECO_P4_PEACH205_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 139.61 | 133.43 | D05 | PECO_P1-2_PBTIE2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 138.62 | 132.51 | D05 | PECO_P4_PEACH055_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 134.03 | 128.18 | D05 | PECO_P4_PEACH015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 132.65 | 126.79 | D05 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 123.56 | 118.16 | D05 | PECO_P4_PEACH225_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3464 | 168.69 | 162.66 | GLOUCSTR_26 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 154.15 | 158.72 | DC1 NUG | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.67 | 157.79 | DC1 NUG | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.67 | 157.79 | DC1 NUG | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 152.46 | 157.4 | DC1 NUG | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 162.3 | 155.05 | DC1 NUG | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 149.09 | 153.74 | DC1 NUG | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 156.24 | 151.08 | DC1 NUG | PN_P1-2_PN-500-010T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.92 | 150.1 | DC1 NUG | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.84 | 150.03 | DC1 NUG | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.9 | 148.45 | DC1 NUG | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.53 | 148.4 | DC1 NUG | PJM_500_BG_P4_5_CNSTN_L_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.7 | 148.27 | DC1 NUG | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.72 | 148.25 | DC1 NUG | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.45 | 148.05 | DC1 NUG | PECO_P4_NOTTI85_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.39 | 148.04 | DC1 NUG | PECO_P1-2_220-08_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.33 | 147.97 | DC1 NUG | PECO_P4_COOPR125_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3464 | 167.95 | 161.94 | GR RIDGE | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 151.6 | 144.86 | DC1 NUG | PECO_P4_PEACH025_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 151.42 | 144.72 | DC1 NUG | PECO_P1-2_PBTIE1_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 141.54 | 144.4 | DC1 NUG | PJM_500_BG_P4_5_CNSTN_15_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 141.53 | 144.33 | DC1 NUG | BG_P7_GRNITE_HIRDG_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 141.64 | 144.27 | DC1 NUG | PJM_500_BG_P4_5_CNSTN_12_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 141.61 | 144.24 | DC1 NUG | PJM_500_BG_P4_5_CNSTN_10_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 141.61 | 144.24 | DC1 NUG | PJM_500_BG_P4_5_CNSTN_9_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 139.67 | 133.71 | DC1 NUG | PECO_P4_PEACH205_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 139.64 | 133.46 | DC1 NUG | PECO_P1-2_PBTIE2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 138.68 | 132.57 | DC1 NUG | PECO_P4_PEACH055_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 134.06 | 128.22 | DC1 NUG | PECO_P4_PEACH015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 132.68 | 126.82 | DC1 NUG | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 123.59 | 118.19 | DC1 NUG | PECO_P4_PEACH225_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3464 | 168.28 | 162.27 | K28 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 154.15 | 158.72 | DC2 NUG | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.67 | 157.79 | DC2 NUG | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.67 | 157.79 | DC2 NUG | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 152.46 | 157.4 | DC2 NUG | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 162.3 | 155.05 | DC2 NUG | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 149.09 | 153.74 | DC2 NUG | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 156.24 | 151.08 | DC2 NUG | PN_P1-2_PN-500-010T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.92 | 150.1 | DC2 NUG | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.84 | 150.03 | DC2 NUG | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.9 | 148.45 | DC2 NUG | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.53 | 148.4 | DC2 NUG | PJM_500_BG_P4_5_CNSTN_L_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.7 | 148.27 | DC2 NUG | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.72 | 148.25 | DC2 NUG | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.45 | 148.05 | DC2 NUG | PECO_P4_NOTTI85_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.39 | 148.04 | DC2 NUG | PECO_P1-2_220-08_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.33 | 147.97 | DC2 NUG | PECO_P4_COOPR125_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3464 | 168.17 | 162.16 | KELLY CRK;1U | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 151.6 | 144.86 | DC2 NUG | PECO_P4_PEACH025_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 151.42 | 144.72 | DC2 NUG | PECO_P1-2_PBTIE1_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 141.54 | 144.4 | DC2 NUG | PJM_500_BG_P4_5_CNSTN_15_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 141.53 | 144.33 | DC2 NUG | BG_P7_GRNITE_HIRDG_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 141.64 | 144.27 | DC2 NUG | PJM_500_BG_P4_5_CNSTN_12_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 141.61 | 144.24 | DC2 NUG | PJM_500_BG_P4_5_CNSTN_10_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 141.61 | 144.24 | DC2 NUG | PJM_500_BG_P4_5_CNSTN_9_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 139.67 | 133.71 | DC2 NUG | PECO_P4_PEACH205_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 139.64 | 133.46 | DC2 NUG | PECO_P1-2_PBTIE2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 138.68 | 132.57 | DC2 NUG | PECO_P4_PEACH055_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 134.06 | 128.22 | DC2 NUG | PECO_P4_PEACH015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 132.68 | 126.82 | DC2 NUG | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 123.59 | 118.19 | DC2 NUG | PECO_P4_PEACH225_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3464 | 168.61 | 162.59 | LINDEN_26 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.33 | 157.46 | ECOGROVE ;U1 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.33 | 157.46 | ECOGROVE ;U1 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 161.83 | 154.61 | ECOGROVE ;U1 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 155.9 | 150.75 | ECOGROVE ;U1 | PN_P1-2_PN-500-010T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.49 | 148.05 | ECOGROVE ;U1 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.29 | 147.87 | ECOGROVE ;U1 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.32 | 147.85 | ECOGROVE ;U1 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.05 | 147.66 | ECOGROVE ;U1 | PECO_P4_NOTTI85_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.99 | 147.64 | ECOGROVE ;U1 | PECO_P1-2_220-08_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.92 | 147.58 | ECOGROVE ;U1 | PECO_P4_COOPR125_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.58 | 147.39 | ECOGROVE ;U1 | PECO_P1-2_220-93_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 151.04 | 144.33 | ECOGROVE ;U1 | PECO_P4_PEACH025_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.92 | 144.24 | ECOGROVE ;U1 | PECO_P1-2_PBTIE1_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 139.18 | 133.02 | ECOGROVE ;U1 | PECO_P1-2_PBTIE2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 227.95 | 240.39 | FAIRLAWN_AB | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 225.91 | 240.39 | FAIRLAWN_AB | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 215.78 | 230.12 | FAIRLAWN_AB | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 211.52 | 226.94 | FAIRLAWN_AB | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 210.08 | 219.76 | FAIRLAWN_AB | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 212.11 | 219.76 | FAIRLAWN_AB | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 200.49 | 210.14 | FAIRLAWN_AB | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 196.23 | 206.8 | FAIRLAWN_AB | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 172.74 | 167.54 | FAIRLAWN_AB | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 172.74 | 167.54 | FAIRLAWN_AB | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 172.73 | 167.51 | FAIRLAWN_AB | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 164.6 | 166.23 | FAIRLAWN_AB | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 162.78 | 163.19 | FAIRLAWN_AB | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 162.77 | 163.18 | FAIRLAWN_AB | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 162.76 | 163.18 | FAIRLAWN_AB | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3464 | 168.1 | 162.09 | M24 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 154.36 | 158.97 | FAIRLAWN_AB | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.87 | 157.99 | FAIRLAWN_AB | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.87 | 157.99 | FAIRLAWN_AB | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 152.66 | 157.64 | FAIRLAWN_AB | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 162.57 | 155.32 | FAIRLAWN_AB | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 149.3 | 153.99 | FAIRLAWN_AB | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 903 | 145.03 | 153.22 | FAIRLAWN_AB | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 153.83 | 152.42 | FAIRLAWN_AB | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 156.44 | 151.29 | FAIRLAWN_AB | PN_P1-2_PN-500-010T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 147.11 | 150.33 | FAIRLAWN_AB | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 147.04 | 150.26 | FAIRLAWN_AB | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.7 | 149.06 | FAIRLAWN_AB | AP_P2-3_PE-500-016_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.76 | 149.03 | FAIRLAWN_AB | AP_P2-3_PE-500-015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 154.12 | 148.67 | FAIRLAWN_AB | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.73 | 148.59 | FAIRLAWN_AB | PJM_500_BG_P4_5_CNSTN_L_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.92 | 148.48 | FAIRLAWN_AB | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.95 | 148.47 | FAIRLAWN_AB | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.67 | 148.27 | FAIRLAWN_AB | PECO_P4_NOTTI85_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.61 | 148.26 | FAIRLAWN_AB | PECO_P1-2_220-08_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.55 | 148.19 | FAIRLAWN_AB | PECO_P4_COOPR125_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.88 | 148.17 | FAIRLAWN_AB | AP_P1-2_WP-500-DRT17_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.88 | 148.17 | FAIRLAWN_AB | AP_P1-2_PE-500-001_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.83 | 148.1 | FAIRLAWN_AB | AP_P2-3_PE-500-018C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3464 | 168.13 | 162.12 | MINONK ;1U | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 151.83 | 145.08 | FAIRLAWN_AB | PECO_P4_PEACH025_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 151.73 | 145.02 | FAIRLAWN_AB | PECO_P1-2_PBTIE1_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 911 | 148.98 | 142.95 | FAIRLAWN_AB | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 911 | 148.98 | 142.95 | FAIRLAWN_AB | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 911 | 148.96 | 142.94 | FAIRLAWN_AB | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 1031 | 131.47 | 140.05 | FAIRLAWN_AB | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208078 | SAKR | 1 | 230 | 229 | 903 | 126.1 | 134.91 | FAIRLAWN_AB | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 140.01 | 134.04 | FAIRLAWN_AB | PECO_P4_PEACH205_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 139.92 | 133.73 | FAIRLAWN_AB | PECO_P1-2_PBTIE2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 138.9 | 132.78 | FAIRLAWN_AB | PECO_P4_PEACH055_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 134.37 | 128.51 | FAIRLAWN_AB | PECO_P4_PEACH015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208020 | MANO TR3 | 1 | 230 | 229 | 793 | 113.16 | 127.3 | FAIRLAWN_AB | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 132.96 | 127.09 | FAIRLAWN_AB | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208078 | SAKR | 1 | 230 | 229 | 903 | 118.1 | 123.74 | FAIRLAWN_AB | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208031 | MLWD TR2 | 1 | 230 | 229 | 911 | 113.3 | 123.54 | FAIRLAWN_AB | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200025 | W CHAPEL | 1 | 500 | 225 | 1732 | 124.4 | 122.64 | FAIRLAWN_AB | PEPCO_P4_PP41_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 123.88 | 118.46 | FAIRLAWN_AB | PECO_P4_PEACH225_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208020 | MANO TR3 | 208031 | MLWD TR2 | 1 | 230 | 229 | 903 | 103.36 | 114.82 | FAIRLAWN_AB | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208031 | MLWD TR2 | 1 | 230 | 229 | 911 | 105.84 | 112.89 | FAIRLAWN_AB | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208020 | MANO TR3 | 208031 | MLWD TR2 | 1 | 230 | 229 | 903 | 96.29 | 104.45 | FAIRLAWN_AB | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 98.89 | 102.57 | FAIRLAWN_AB | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 226.07 | 238.44 | G07 NFTWR | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 224.07 | 238.44 | G07 NFTWR | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 225.11 | 236.38 | G07 NFTWR | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 223.12 | 236.38 | G07 NFTWR | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 225.04 | 236.32 | G07 NFTWR | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 223.05 | 236.31 | G07 NFTWR | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 225.04 | 236.31 | G07 NFTWR | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 223.05 | 236.31 | G07 NFTWR | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 214.01 | 228.24 | G07 NFTWR | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 213.08 | 226.24 | G07 NFTWR | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 213.02 | 226.18 | G07 NFTWR | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 213.02 | 226.18 | G07 NFTWR | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 209.75 | 225.04 | G07 NFTWR | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 208.82 | 223.02 | G07 NFTWR | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 208.76 | 222.96 | G07 NFTWR | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 208.76 | 222.96 | G07 NFTWR | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 210.19 | 217.23 | G07 NFTWR | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 208.19 | 217.23 | G07 NFTWR | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 198.67 | 207.69 | G07 NFTWR | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 194.41 | 204.33 | G07 NFTWR | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 172.59 | 167.65 | G07 NFTWR | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 171.61 | 166.21 | G07 NFTWR | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 171.61 | 166.21 | G07 NFTWR | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 171.6 | 166.2 | G07 NFTWR | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 163.43 | 164.7 | G07 NFTWR | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3464 | 168.1 | 162.09 | O09 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 161.55 | 161.62 | G07 NFTWR | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 161.54 | 161.61 | G07 NFTWR | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 161.53 | 161.61 | G07 NFTWR | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 163.65 | 158.75 | G07 NFTWR | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 153.42 | 157.86 | G07 NFTWR | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 161.84 | 156.98 | G07 NFTWR | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 161.84 | 156.97 | G07 NFTWR | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 151.74 | 156.54 | G07 NFTWR | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 161.13 | 153.93 | G07 NFTWR | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 148.38 | 152.88 | G07 NFTWR | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 903 | 144.15 | 151.96 | G07 NFTWR | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 152.59 | 151 | G07 NFTWR | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 155.41 | 150.26 | G07 NFTWR | PN_P1-2_PN-500-010T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 903 | 142.6 | 149.34 | G07 NFTWR | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 903 | 142.6 | 149.34 | G07 NFTWR | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 903 | 142.59 | 149.33 | G07 NFTWR | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.22 | 149.28 | G07 NFTWR | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.15 | 149.21 | G07 NFTWR | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.89 | 148.11 | G07 NFTWR | AP_P2-3_PE-500-016_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.95 | 148.08 | G07 NFTWR | AP_P2-3_PE-500-015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.75 | 147.62 | G07 NFTWR | PJM_500_BG_P4_5_CNSTN_L_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.91 | 147.48 | G07 NFTWR | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.71 | 147.3 | G07 NFTWR | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.73 | 147.28 | G07 NFTWR | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.06 | 147.22 | G07 NFTWR | AP_P1-2_PE-500-001_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.06 | 147.22 | G07 NFTWR | AP_P1-2_WP-500-DRT17_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.02 | 147.15 | G07 NFTWR | AP_P2-3_PE-500-018C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.46 | 147.09 | G07 NFTWR | PECO_P4_NOTTI85_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.4 | 147.07 | G07 NFTWR | PECO_P1-2_220-08_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.34 | 147 | G07 NFTWR | PECO_P4_COOPR125_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3464 | 168.08 | 162.07 | O29 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.27 | 143.59 | G07 NFTWR | PECO_P4_PEACH025_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.13 | 143.49 | G07 NFTWR | PECO_P1-2_PBTIE1_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 911 | 148.81 | 143 | G07 NFTWR | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 911 | 147.86 | 141.68 | G07 NFTWR | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 911 | 147.86 | 141.68 | G07 NFTWR | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 911 | 147.85 | 141.67 | G07 NFTWR | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204502 | 27JACKSON | 204514 | 27TMI | 1 | 230 | 227 | 781 | 132.84 | 141.33 | G07 NFTWR | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204502 | 27JACKSON | 204514 | 27TMI | 1 | 230 | 227 | 781 | 132.84 | 141.33 | G07 NFTWR | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204502 | 27JACKSON | 204514 | 27TMI | 1 | 230 | 227 | 781 | 132.82 | 141.32 | G07 NFTWR | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 903 | 135.52 | 139.47 | G07 NFTWR | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 1031 | 130.71 | 138.99 | G07 NFTWR | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 1031 | 130.21 | 137.91 | G07 NFTWR | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 1031 | 130.21 | 137.91 | G07 NFTWR | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 1031 | 130.2 | 137.91 | G07 NFTWR | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 911 | 139.98 | 134.95 | G07 NFTWR | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208078 | SAKR | 1 | 230 | 229 | 903 | 125.01 | 133.67 | G07 NFTWR | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 138.6 | 132.68 | G07 NFTWR | PECO_P4_PEACH205_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 138.45 | 132.32 | G07 NFTWR | PECO_P1-2_PBTIE2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208078 | SAKR | 1 | 230 | 229 | 903 | 124.26 | 132.22 | G07 NFTWR | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208078 | SAKR | 1 | 230 | 229 | 903 | 124.26 | 132.21 | G07 NFTWR | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208078 | SAKR | 1 | 230 | 229 | 903 | 124.26 | 132.21 | G07 NFTWR | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 137.59 | 131.52 | G07 NFTWR | PECO_P4_PEACH055_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204502 | 27JACKSON | 204514 | 27TMI | 1 | 230 | 227 | 781 | 125.18 | 130.76 | G07 NFTWR | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 1031 | 124.6 | 129.11 | G07 NFTWR | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 128.84 | 127.14 | G07 NFTWR | DVP_P4-2: 514T595_SRT-SW |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 132.75 | 126.96 | G07 NFTWR | PECO_P4_PEACH015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208020 | MANO TR3 | 1 | 230 | 229 | 793 | 112.09 | 125.94 | G07 NFTWR | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 131.5 | 125.7 | G07 NFTWR | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 127.1 | 125.42 | G07 NFTWR | DVP_P4-2: 51482_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 127.1 | 125.33 | G07 NFTWR | DVP_P1-2: LN 514_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 127.1 | 125.33 | G07 NFTWR | AP_P1-2_PE-500-407T_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208020 | MANO TR3 | 1 | 230 | 229 | 793 | 111.26 | 124.39 | G07 NFTWR | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208020 | MANO TR3 | 1 | 230 | 229 | 793 | 111.25 | 124.39 | G07 NFTWR | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208020 | MANO TR3 | 1 | 230 | 229 | 793 | 111.26 | 124.39 | G07 NFTWR | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208031 | MLWD TR2 | 1 | 230 | 229 | 911 | 112.29 | 122.3 | G07 NFTWR | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208078 | SAKR | 1 | 230 | 229 | 903 | 116.98 | 122.23 | G07 NFTWR | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204512 | 27S.RDG | 204693 | 27BOONETOWN | 1 | 230 | 227 | 607 | 107.23 | 122.02 | G07 NFTWR | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204512 | 27S.RDG | 204693 | 27BOONETOWN | 1 | 230 | 227 | 607 | 107.2 | 121.99 | G07 NFTWR | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204512 | 27S.RDG | 204693 | 27BOONETOWN | 1 | 230 | 227 | 607 | 107.2 | 121.99 | G07 NFTWR | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200025 | W CHAPEL | 1 | 500 | 225 | 1732 | 123.6 | 121.81 | G07 NFTWR | PEPCO_P4_PP41_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208031 | MLWD TR2 | 1 | 230 | 229 | 911 | 111.57 | 120.97 | G07 NFTWR | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208031 | MLWD TR2 | 1 | 230 | 229 | 911 | 111.57 | 120.97 | G07 NFTWR | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208031 | MLWD TR2 | 1 | 230 | 229 | 911 | 111.57 | 120.97 | G07 NFTWR | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220965 | NEAST339 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 119.71 | 119.06 | G07 NFTWR | BG_P1_2315_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220965 | NEAST339 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 119.29 | 118.85 | G07 NFTWR | BG_P4_5_NEAST_17_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220965 | NEAST339 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 119.45 | 118.85 | G07 NFTWR | BG_P4_5_NEAST_15_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 114.67 | 118.38 | G07 NFTWR | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220979 | NEAST317 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 118.79 | 118.19 | G07 NFTWR | BG_P1_2337_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 114.33 | 118.04 | G07 NFTWR | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 114.31 | 117.98 | G07 NFTWR | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 114.31 | 117.98 | G07 NFTWR | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220979 | NEAST317 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 118.46 | 117.92 | G07 NFTWR | BG_P4_5_NEAST_39_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220979 | NEAST317 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 118.46 | 117.92 | G07 NFTWR | BG_P4_5_NEAST_37_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 113.98 | 117.65 | G07 NFTWR | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 113.98 | 117.65 | G07 NFTWR | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 122.38 | 117.04 | G07 NFTWR | PECO_P4_PEACH225_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 117.29 | 115.4 | G07 NFTWR | AP_P2-3_PE-500-019C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 2 | 500/230 | 225/232 | 2168 | 109.63 | 114.95 | G07 NFTWR | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 2 | 500/230 | 225/232 | 2168 | 109.45 | 114.74 | G07 NFTWR | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 2 | 500/230 | 225/232 | 2168 | 109.45 | 114.74 | G07 NFTWR | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 1 | 500/230 | 225/232 | 2168 | 109.4 | 114.71 | G07 NFTWR | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 1 | 500/230 | 225/232 | 2168 | 109.22 | 114.5 | G07 NFTWR | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 1 | 500/230 | 225/232 | 2168 | 109.22 | 114.5 | G07 NFTWR | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220964 | GRACETON | 220999 | BAGLEY2 | 13 | 230 | 232 | 1795 | 113.39 | 114.42 | G07 NFTWR | BG_P4_5_GRCTN_3T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208020 | MANO TR3 | 1 | 230 | 229 | 793 | 104.06 | 113.87 | G07 NFTWR | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208020 | MANO TR3 | 208031 | MLWD TR2 | 1 | 230 | 229 | 903 | 102.41 | 113.54 | G07 NFTWR | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208020 | MANO TR3 | 208031 | MLWD TR2 | 1 | 230 | 229 | 903 | 101.7 | 112.34 | G07 NFTWR | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208020 | MANO TR3 | 208031 | MLWD TR2 | 1 | 230 | 229 | 903 | 101.69 | 112.34 | G07 NFTWR | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208020 | MANO TR3 | 208031 | MLWD TR2 | 1 | 230 | 229 | 903 | 101.69 | 112.34 | G07 NFTWR | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208031 | MLWD TR2 | 1 | 230 | 229 | 911 | 104.81 | 111.47 | G07 NFTWR | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 106.45 | 111.21 | G07 NFTWR | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220980 | RAPHAEL | 220999 | BAGLEY2 | 13 | 230 | 232 | 1795 | 108.98 | 111.18 | G07 NFTWR | BG_P4_5_GRCTN_3T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 106.32 | 111.08 | G07 NFTWR | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200099 | LAUS | 208045 | LAUS | 3 | 500/230 | 225/229 | 1200 | 103.07 | 104.84 | G07 NFTWR | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200099 | LAUS | 208045 | LAUS | 3 | 500/230 | 225/229 | 1200 | 102.76 | 104.34 | G07 NFTWR | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200099 | LAUS | 208045 | LAUS | 3 | 500/230 | 225/229 | 1200 | 102.76 | 104.34 | G07 NFTWR | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200099 | LAUS | 208045 | LAUS | 3 | 500/230 | 225/229 | 1200 | 102.75 | 104.33 | G07 NFTWR | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 99.66 | 103.55 | G07 NFTWR | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 99.65 | 103.54 | G07 NFTWR | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 99.66 | 103.54 | G07 NFTWR | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208020 | MANO TR3 | 208031 | MLWD TR2 | 1 | 230 | 229 | 903 | 95.31 | 103.11 | G07 NFTWR | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220964 | GRACETON | 221000 | BAGLEY | 5 | 230 | 232 | 1795 | 101.45 | 102.2 | G07 NFTWR | BG_P1_2313_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220964 | GRACETON | 220999 | BAGLEY2 | 13 | 230 | 232 | 1795 | 101.45 | 102.2 | G07 NFTWR | BG_P1_2305_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 98.83 | 100.86 | G07 NFTWR | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200762 | 26GARRETT | 235470 | 01GARRET | 1 | 115 | 226/201 | 190 | 99.51 | 101.86 | G21 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200762 | 26GARRETT | 235470 | 01GARRET | 1 | 115 | 226/201 | 190 | 99.51 | 101.86 | G21 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200762 | 26GARRETT | 235470 | 01GARRET | 1 | 115 | 226/201 | 190 | 99.35 | 101.69 | G21 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3464 | 163.29 | 157.37 | O66 NFTWR | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.64 | 157.76 | GLOUCSTR_26 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.64 | 157.76 | GLOUCSTR_26 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 162.26 | 155.01 | GLOUCSTR_26 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 156.21 | 151.05 | GLOUCSTR_26 | PN_P1-2_PN-500-010T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.86 | 148.41 | GLOUCSTR_26 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.51 | 148.37 | GLOUCSTR_26 | PJM_500_BG_P4_5_CNSTN_L_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.66 | 148.23 | GLOUCSTR_26 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.68 | 148.21 | GLOUCSTR_26 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.41 | 148.02 | GLOUCSTR_26 | PECO_P4_NOTTI85_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.35 | 148 | GLOUCSTR_26 | PECO_P1-2_220-08_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.29 | 147.94 | GLOUCSTR_26 | PECO_P4_COOPR125_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3464 | 168.73 | 162.7 | P28 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 151.52 | 144.78 | GLOUCSTR_26 | PECO_P4_PEACH025_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 151.38 | 144.68 | GLOUCSTR_26 | PECO_P1-2_PBTIE1_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 139.06 | 141.27 | GLOUCSTR_26 | AP_P1-2_WP-500-008_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 139.06 | 141.27 | GLOUCSTR_26 | AP_P2-3_WP-500-DRT45_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 137.45 | 139.5 | GLOUCSTR_26 | AP_P2-3_WP-500-696_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 137.45 | 139.49 | GLOUCSTR_26 | AP_P2-3_WP-500-707T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 137.47 | 139.48 | GLOUCSTR_26 | AP_P2-3_WP-500-706T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 137.43 | 139.47 | GLOUCSTR_26 | AP_P2-3_WP-500-440T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 136.96 | 139.21 | GLOUCSTR_26 | PN_P2-3_PN-500-DRT32_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 136.96 | 139.21 | GLOUCSTR_26 | PN_P2-3_PN-500-004-DRT-002_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 134.38 | 136.49 | GLOUCSTR_26 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 134.37 | 136.43 | GLOUCSTR_26 | PECO_P4_COOPR125_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 139.67 | 133.71 | GLOUCSTR_26 | PECO_P4_PEACH205_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 139.6 | 133.42 | GLOUCSTR_26 | PECO_P1-2_PBTIE2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 138.61 | 132.51 | GLOUCSTR_26 | PECO_P4_PEACH055_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 134.01 | 128.17 | GLOUCSTR_26 | PECO_P4_PEACH015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 132.63 | 126.78 | GLOUCSTR_26 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 123.54 | 118.15 | GLOUCSTR_26 | PECO_P4_PEACH225_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 225.57 | 237.07 | GR RIDGE | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 223.57 | 237.07 | GR RIDGE | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 225.51 | 237.01 | GR RIDGE | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 223.5 | 237.01 | GR RIDGE | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 225.51 | 237 | GR RIDGE | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 223.5 | 237 | GR RIDGE | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 213.52 | 226.91 | GR RIDGE | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 213.45 | 226.85 | GR RIDGE | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 213.45 | 226.85 | GR RIDGE | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 209.26 | 223.7 | GR RIDGE | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 209.2 | 223.64 | GR RIDGE | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 209.19 | 223.64 | GR RIDGE | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 210.68 | 217.88 | GR RIDGE | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 208.67 | 217.88 | GR RIDGE | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 199.14 | 208.32 | GR RIDGE | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 194.88 | 204.97 | GR RIDGE | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 172.82 | 167.89 | GR RIDGE | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 161.8 | 161.94 | GR RIDGE | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 161.8 | 161.94 | GR RIDGE | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3464 | 168.29 | 162.28 | P59 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 161.79 | 161.93 | GR RIDGE | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 153.61 | 158.08 | GR RIDGE | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.06 | 157.19 | GR RIDGE | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.06 | 157.19 | GR RIDGE | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 151.92 | 156.76 | GR RIDGE | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 161.48 | 154.27 | GR RIDGE | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 148.56 | 153.11 | GR RIDGE | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 155.64 | 150.49 | GR RIDGE | PN_P1-2_PN-500-010T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.4 | 149.5 | GR RIDGE | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.33 | 149.42 | GR RIDGE | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.06 | 148.32 | GR RIDGE | AP_P2-3_PE-500-016_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.12 | 148.29 | GR RIDGE | AP_P2-3_PE-500-015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.95 | 147.83 | GR RIDGE | PJM_500_BG_P4_5_CNSTN_L_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.18 | 147.75 | GR RIDGE | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.98 | 147.56 | GR RIDGE | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153 | 147.55 | GR RIDGE | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.24 | 147.43 | GR RIDGE | AP_P1-2_WP-500-DRT17_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.24 | 147.43 | GR RIDGE | AP_P1-2_PE-500-001_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.19 | 147.36 | GR RIDGE | AP_P2-3_PE-500-018C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.73 | 147.35 | GR RIDGE | PECO_P4_NOTTI85_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.67 | 147.33 | GR RIDGE | PECO_P1-2_220-08_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.61 | 147.27 | GR RIDGE | PECO_P4_COOPR125_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3464 | 167.21 | 161.22 | Q01/Q03 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.67 | 143.96 | GR RIDGE | PECO_P4_PEACH025_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.56 | 143.89 | GR RIDGE | PECO_P1-2_PBTIE1_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 911 | 149.06 | 143.23 | GR RIDGE | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 1031 | 130.36 | 138.2 | GR RIDGE | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 1031 | 130.36 | 138.2 | GR RIDGE | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 1031 | 130.35 | 138.19 | GR RIDGE | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 138.97 | 133.04 | GR RIDGE | PECO_P4_PEACH205_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 138.84 | 132.7 | GR RIDGE | PECO_P1-2_PBTIE2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208078 | SAKR | 1 | 230 | 229 | 903 | 124.54 | 132.63 | GR RIDGE | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208078 | SAKR | 1 | 230 | 229 | 903 | 124.54 | 132.63 | GR RIDGE | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208078 | SAKR | 1 | 230 | 229 | 903 | 124.54 | 132.63 | GR RIDGE | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 137.91 | 131.83 | GR RIDGE | PECO_P4_PEACH055_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 133.22 | 127.4 | GR RIDGE | PECO_P4_PEACH015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 131.9 | 126.09 | GR RIDGE | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208020 | MANO TR3 | 1 | 230 | 229 | 793 | 111.52 | 124.73 | GR RIDGE | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208020 | MANO TR3 | 1 | 230 | 229 | 793 | 111.52 | 124.73 | GR RIDGE | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208020 | MANO TR3 | 1 | 230 | 229 | 793 | 111.52 | 124.73 | GR RIDGE | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 122.81 | 117.45 | GR RIDGE | PECO_P4_PEACH225_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 99.67 | 103.64 | GR RIDGE | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 99.67 | 103.64 | GR RIDGE | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 99.67 | 103.63 | GR RIDGE | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 144.32 | 139.17 | GSG-6 ;RU | PL_10_P42_100570_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 144.32 | 139.17 | GSG-6 ;RU | PL_10_P42_100570_A_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 143.51 | 138.38 | GSG-6 ;RU | PL_10_P12_000085_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 143.41 | 138.29 | GSG-6 ;RU | PN_P2-3_PN-500-004-DRT-008_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 143.41 | 138.29 | GSG-6 ;RU | PN_P2-3_PN-500-DRT31_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 143.04 | 137.92 | GSG-6 ;RU | PL_30_P42_000131_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3464 | 168.78 | 162.76 | Q27 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.33 | 157.45 | K28 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.33 | 157.45 | K28 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 161.83 | 154.6 | K28 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 155.9 | 150.75 | K28 | PN_P1-2_PN-500-010T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.21 | 148.08 | K28 | PJM_500_BG_P4_5_CNSTN_L_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.49 | 148.05 | K28 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.29 | 147.86 | K28 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.31 | 147.85 | K28 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.04 | 147.65 | K28 | PECO_P4_NOTTI85_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.98 | 147.64 | K28 | PECO_P1-2_220-08_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.92 | 147.57 | K28 | PECO_P4_COOPR125_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 142.88 | 146.97 | K28 | AP_P2-3_PE-500-014_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 142.88 | 146.97 | K28 | AP_P2-3_WP-500-466_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 142.88 | 146.97 | K28 | AP_P1-2_PE-500-004_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 142.88 | 146.97 | K28 | AP_P1-2_WP-500-006_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 142.88 | 146.97 | K28 | AP_P2-3_WP-500-DRT19_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 151.04 | 144.32 | K28 | PECO_P4_PEACH025_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.92 | 144.24 | K28 | PECO_P1-2_PBTIE1_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 137.17 | 139.14 | K28 | AP_P2-3_WP-500-706T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 132.51 | 134.53 | K28 | AP_P2-3_MP-138-150_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 132.3 | 134.29 | K28 | AP_P2-3_MP-138-160_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 139.17 | 133.01 | K28 | PECO_P1-2_PBTIE2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 133.56 | 127.73 | K28 | PECO_P4_PEACH015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 132.22 | 126.39 | K28 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 123.12 | 117.75 | K28 | PECO_P4_PEACH225_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3464 | 168.05 | 162.04 | Q57 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 153.77 | 158.28 | KELLY CRK;1U | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.24 | 157.37 | KELLY CRK;1U | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.24 | 157.36 | KELLY CRK;1U | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 152.08 | 156.95 | KELLY CRK;1U | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 161.71 | 154.49 | KELLY CRK;1U | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 148.72 | 153.3 | KELLY CRK;1U | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 155.81 | 150.66 | KELLY CRK;1U | PN_P1-2_PN-500-010T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.56 | 149.68 | KELLY CRK;1U | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.49 | 149.6 | KELLY CRK;1U | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.19 | 148.47 | KELLY CRK;1U | AP_P2-3_PE-500-016_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.26 | 148.44 | KELLY CRK;1U | AP_P2-3_PE-500-015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.12 | 147.99 | KELLY CRK;1U | PJM_500_BG_P4_5_CNSTN_L_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.38 | 147.95 | KELLY CRK;1U | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.18 | 147.76 | KELLY CRK;1U | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.21 | 147.75 | KELLY CRK;1U | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.37 | 147.59 | KELLY CRK;1U | AP_P1-2_PE-500-001_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.37 | 147.59 | KELLY CRK;1U | AP_P1-2_WP-500-DRT17_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.94 | 147.55 | KELLY CRK;1U | PECO_P4_NOTTI85_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.88 | 147.53 | KELLY CRK;1U | PECO_P1-2_220-08_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.32 | 147.52 | KELLY CRK;1U | AP_P2-3_PE-500-018C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.81 | 147.47 | KELLY CRK;1U | PECO_P4_COOPR125_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3464 | 168.22 | 162.21 | R49 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.91 | 144.2 | KELLY CRK;1U | PECO_P4_PEACH025_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.8 | 144.12 | KELLY CRK;1U | PECO_P1-2_PBTIE1_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 139.18 | 133.24 | KELLY CRK;1U | PECO_P4_PEACH205_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 139.06 | 132.91 | KELLY CRK;1U | PECO_P1-2_PBTIE2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 138.12 | 132.03 | KELLY CRK;1U | PECO_P4_PEACH055_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 133.44 | 127.62 | KELLY CRK;1U | PECO_P4_PEACH015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 132.11 | 126.29 | KELLY CRK;1U | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204512 | 27S.RDG | 204693 | 27BOONETOWN | 1 | 230 | 227 | 607 | 107.67 | 123.43 | KELLY CRK;1U | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 123.02 | 117.64 | KELLY CRK;1U | PECO_P4_PEACH225_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.59 | 157.71 | LAURHILL-G | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.59 | 157.71 | LAURHILL-G | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 156.16 | 151 | LAURHILL-G | PN_P1-2_PN-500-010T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.46 | 148.33 | LAURHILL-G | PJM_500_BG_P4_5_CNSTN_L_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 151.27 | 144.58 | LAURHILL-G | PECO_P1-2_PBTIE1_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 148.73 | 143.5 | LAURHILL-G | AP_P1-2_WP-500-005A_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 148.73 | 143.5 | LAURHILL-G | AP_P1-2_WP-500-DRT21_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 148.73 | 143.5 | LAURHILL-G | AP_P2-2_WP-500-DRT16_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 148.73 | 143.5 | LAURHILL-G | AP_P2-3_WP-500-465_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 148.73 | 143.5 | LAURHILL-G | AP_P2-3_WP-500-DRT20_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 148.6 | 143.25 | LAURHILL-G | AP_P2-3_WP-500-696_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 139.29 | 141.64 | LAURHILL-G | AP_P1-2_WP-500-DRT21_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 139.29 | 141.64 | LAURHILL-G | AP_P1-2_WP-500-005A_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 139.29 | 141.64 | LAURHILL-G | AP_P2-2_WP-500-DRT16_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 139.29 | 141.64 | LAURHILL-G | AP_P2-3_WP-500-DRT20_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 139.29 | 141.64 | LAURHILL-G | AP_P2-3_WP-500-465_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 139.08 | 141.29 | LAURHILL-G | AP_P1-2_WP-500-008_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 139.08 | 141.29 | LAURHILL-G | AP_P2-3_WP-500-DRT45_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 137.47 | 139.52 | LAURHILL-G | AP_P2-3_WP-500-696_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 137.47 | 139.51 | LAURHILL-G | AP_P2-3_WP-500-707T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 137.49 | 139.5 | LAURHILL-G | AP_P2-3_WP-500-706T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 139.62 | 133.66 | LAURHILL-G | PECO_P4_PEACH205_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 139.5 | 133.33 | LAURHILL-G | PECO_P1-2_PBTIE2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 133.92 | 128.08 | LAURHILL-G | PECO_P4_PEACH015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 123.46 | 118.06 | LAURHILL-G | PECO_P4_PEACH225_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3464 | 167.91 | 161.9 | R60 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 162.18 | 154.93 | LINDEN_26 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.79 | 148.34 | LINDEN_26 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.59 | 148.16 | LINDEN_26 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.61 | 148.14 | LINDEN_26 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.34 | 147.95 | LINDEN_26 | PECO_P4_NOTTI85_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.28 | 147.93 | LINDEN_26 | PECO_P1-2_220-08_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.21 | 147.87 | LINDEN_26 | PECO_P4_COOPR125_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.05 | 147.72 | LINDEN_26 | AP_P2-3_PE-500-016_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.09 | 147.7 | LINDEN_26 | AP_P2-3_PE-500-015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.87 | 147.67 | LINDEN_26 | PECO_P1-2_220-93_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 151.57 | 147.24 | LINDEN_26 | AP_P1-2_WP-500-DRT17_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 151.41 | 144.68 | LINDEN_26 | PECO_P4_PEACH025_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 151.29 | 144.59 | LINDEN_26 | PECO_P1-2_PBTIE1_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 139.51 | 133.34 | LINDEN_26 | PECO_P1-2_PBTIE2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 133.92 | 128.08 | LINDEN_26 | PECO_P4_PEACH015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 123.46 | 118.07 | LINDEN_26 | PECO_P4_PEACH225_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3464 | 168.66 | 162.63 | RUTGERS | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 153.71 | 158.21 | M24 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.18 | 157.31 | M24 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.18 | 157.3 | M24 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 152.03 | 156.88 | M24 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 161.64 | 154.42 | M24 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 148.66 | 153.23 | M24 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 155.75 | 150.61 | M24 | PN_P1-2_PN-500-010T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.5 | 149.61 | M24 | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.43 | 149.54 | M24 | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.15 | 148.42 | M24 | AP_P2-3_PE-500-016_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.21 | 148.39 | M24 | AP_P2-3_PE-500-015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.07 | 147.94 | M24 | PJM_500_BG_P4_5_CNSTN_L_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.32 | 147.88 | M24 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.12 | 147.7 | M24 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.14 | 147.68 | M24 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.33 | 147.54 | M24 | AP_P1-2_PE-500-001_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.33 | 147.54 | M24 | AP_P1-2_WP-500-DRT17_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.87 | 147.49 | M24 | PECO_P4_NOTTI85_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.81 | 147.47 | M24 | PECO_P1-2_220-08_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.28 | 147.47 | M24 | AP_P2-3_PE-500-018C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.75 | 147.41 | M24 | PECO_P4_COOPR125_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3464 | 168.13 | 162.12 | S06 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.83 | 144.13 | M24 | PECO_P4_PEACH025_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.72 | 144.05 | M24 | PECO_P1-2_PBTIE1_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 139.11 | 133.17 | M24 | PECO_P4_PEACH205_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 138.99 | 132.84 | M24 | PECO_P1-2_PBTIE2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 138.05 | 131.96 | M24 | PECO_P4_PEACH055_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 133.37 | 127.55 | M24 | PECO_P4_PEACH015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 132.04 | 126.22 | M24 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 122.95 | 117.58 | M24 | PECO_P4_PEACH225_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3464 | 168.17 | 162.15 | S36 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 153.74 | 158.24 | MINONK ;1U | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.2 | 157.33 | MINONK ;1U | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.2 | 157.33 | MINONK ;1U | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 152.05 | 156.91 | MINONK ;1U | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 161.67 | 154.44 | MINONK ;1U | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 148.69 | 153.26 | MINONK ;1U | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 155.78 | 150.63 | MINONK ;1U | PN_P1-2_PN-500-010T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.53 | 149.64 | MINONK ;1U | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.46 | 149.57 | MINONK ;1U | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.17 | 148.44 | MINONK ;1U | AP_P2-3_PE-500-016_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.23 | 148.41 | MINONK ;1U | AP_P2-3_PE-500-015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.09 | 147.96 | MINONK ;1U | PJM_500_BG_P4_5_CNSTN_L_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.34 | 147.91 | MINONK ;1U | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.14 | 147.72 | MINONK ;1U | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.17 | 147.71 | MINONK ;1U | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.35 | 147.56 | MINONK ;1U | AP_P1-2_WP-500-DRT17_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.35 | 147.56 | MINONK ;1U | AP_P1-2_PE-500-001_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.9 | 147.51 | MINONK ;1U | PECO_P4_NOTTI85_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.84 | 147.5 | MINONK ;1U | PECO_P1-2_220-08_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.3 | 147.49 | MINONK ;1U | AP_P2-3_PE-500-018C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.77 | 147.43 | MINONK ;1U | PECO_P4_COOPR125_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3464 | 168.26 | 162.25 | S71 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.86 | 144.15 | MINONK ;1U | PECO_P4_PEACH025_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.75 | 144.08 | MINONK ;1U | PECO_P1-2_PBTIE1_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 139.14 | 133.2 | MINONK ;1U | PECO_P4_PEACH205_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 139.02 | 132.87 | MINONK ;1U | PECO_P1-2_PBTIE2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 138.08 | 131.99 | MINONK ;1U | PECO_P4_PEACH055_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 133.4 | 127.58 | MINONK ;1U | PECO_P4_PEACH015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 132.07 | 126.25 | MINONK ;1U | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 122.98 | 117.61 | MINONK ;1U | PECO_P4_PEACH225_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 144.58 | 139.43 | MINUEST_L1 | PL_10_P42_100570_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 144.58 | 139.43 | MINUEST_L1 | PL_10_P42_100570_A_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 143.77 | 138.64 | MINUEST_L1 | PL_10_P12_000085_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 143.68 | 138.55 | MINUEST_L1 | PN_P2-3_PN-500-DRT31_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 143.3 | 138.18 | MINUEST_L1 | PL_30_P42_000131_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 144.58 | 139.43 | MINUEST_L2 | PL_10_P42_100570_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 144.58 | 139.43 | MINUEST_L2 | PL_10_P42_100570_A_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 143.77 | 138.64 | MINUEST_L2 | PL_10_P12_000085_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 143.68 | 138.55 | MINUEST_L2 | PN_P2-3_PN-500-004-DRT-008_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 143.68 | 138.55 | MINUEST_L2 | PN_P2-3_PN-500-DRT31_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 143.3 | 138.18 | MINUEST_L2 | PL_30_P42_000131_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 143.14 | 138.04 | MINUEST_L2 | PL_10_P42_100569_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 143.14 | 138.04 | MINUEST_L2 | PL_10_P42_100569_A_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.34 | 157.46 | NIH23MW | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.34 | 157.46 | NIH23MW | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 129.69 | 127.99 | NIH23MW | DVP_P4-2: 514T595_SRT-SW |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 127.97 | 126.23 | NIH23MW | DVP_P4-2: 51482_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 127.97 | 126.14 | NIH23MW | AP_P1-2_PE-500-407T_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 127.97 | 126.14 | NIH23MW | DVP_P1-2: LN 514_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 118.17 | 116.23 | NIH23MW | AP_P2-3_PE-500-019C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3464 | 168.82 | 162.79 | SALEM G3 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 153.72 | 158.21 | O09 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.18 | 157.31 | O09 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.18 | 157.31 | O09 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 152.03 | 156.89 | O09 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 161.64 | 154.42 | O09 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 148.67 | 153.24 | O09 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 155.76 | 150.61 | O09 | PN_P1-2_PN-500-010T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.51 | 149.62 | O09 | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.44 | 149.55 | O09 | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.15 | 148.42 | O09 | AP_P2-3_PE-500-016_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.21 | 148.39 | O09 | AP_P2-3_PE-500-015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.07 | 147.94 | O09 | PJM_500_BG_P4_5_CNSTN_L_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.32 | 147.89 | O09 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.12 | 147.7 | O09 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.15 | 147.69 | O09 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.33 | 147.54 | O09 | AP_P1-2_PE-500-001_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.33 | 147.54 | O09 | AP_P1-2_WP-500-DRT17_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.88 | 147.49 | O09 | PECO_P4_NOTTI85_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.82 | 147.47 | O09 | PECO_P1-2_220-08_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.28 | 147.47 | O09 | AP_P2-3_PE-500-018C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.75 | 147.41 | O09 | PECO_P4_COOPR125_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3464 | 168.73 | 162.7 | SEWAREN_IM | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.84 | 144.13 | O09 | PECO_P4_PEACH025_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.72 | 144.05 | O09 | PECO_P1-2_PBTIE1_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 139.12 | 133.18 | O09 | PECO_P4_PEACH205_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 139 | 132.84 | O09 | PECO_P1-2_PBTIE2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 138.06 | 131.97 | O09 | PECO_P4_PEACH055_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 133.37 | 127.55 | O09 | PECO_P4_PEACH015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 132.05 | 126.23 | O09 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 122.95 | 117.58 | O09 | PECO_P4_PEACH225_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3464 | 168.13 | 162.12 | T126 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 153.7 | 158.19 | O29 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.17 | 157.29 | O29 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.17 | 157.29 | O29 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 152.02 | 156.87 | O29 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 161.62 | 154.4 | O29 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 148.65 | 153.22 | O29 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 155.74 | 150.59 | O29 | PN_P1-2_PN-500-010T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.49 | 149.6 | O29 | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.42 | 149.53 | O29 | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.14 | 148.4 | O29 | AP_P2-3_PE-500-016_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.2 | 148.37 | O29 | AP_P2-3_PE-500-015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.05 | 147.93 | O29 | PJM_500_BG_P4_5_CNSTN_L_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.3 | 147.87 | O29 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.1 | 147.68 | O29 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.13 | 147.67 | O29 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.31 | 147.52 | O29 | AP_P1-2_PE-500-001_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.31 | 147.52 | O29 | AP_P1-2_WP-500-DRT17_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.85 | 147.47 | O29 | PECO_P4_NOTTI85_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.79 | 147.45 | O29 | PECO_P1-2_220-08_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.26 | 147.45 | O29 | AP_P2-3_PE-500-018C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.73 | 147.39 | O29 | PECO_P4_COOPR125_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3464 | 168.13 | 162.12 | T127 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.81 | 144.11 | O29 | PECO_P4_PEACH025_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.7 | 144.03 | O29 | PECO_P1-2_PBTIE1_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 139.09 | 133.16 | O29 | PECO_P4_PEACH205_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 138.97 | 132.82 | O29 | PECO_P1-2_PBTIE2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 138.04 | 131.95 | O29 | PECO_P4_PEACH055_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 133.35 | 127.53 | O29 | PECO_P4_PEACH015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 132.03 | 126.21 | O29 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 122.93 | 117.56 | O29 | PECO_P4_PEACH225_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 219.89 | 229.23 | O66 NFTWR | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 218.02 | 229.22 | O66 NFTWR | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 218.83 | 227.23 | O66 NFTWR | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 216.96 | 227.22 | O66 NFTWR | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 218.77 | 227.17 | O66 NFTWR | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 216.9 | 227.17 | O66 NFTWR | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 218.77 | 227.17 | O66 NFTWR | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 216.89 | 227.17 | O66 NFTWR | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 208.16 | 219.31 | O66 NFTWR | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 207.14 | 217.37 | O66 NFTWR | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 207.08 | 217.31 | O66 NFTWR | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 207.07 | 217.31 | O66 NFTWR | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 203.91 | 216.04 | O66 NFTWR | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 202.89 | 214.09 | O66 NFTWR | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 202.83 | 214.03 | O66 NFTWR | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 202.83 | 214.03 | O66 NFTWR | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 203.85 | 208.66 | O66 NFTWR | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 201.98 | 208.66 | O66 NFTWR | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 192.67 | 199.4 | O66 NFTWR | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 188.43 | 196.01 | O66 NFTWR | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 334 | 170.3 | 173.03 | O66 NFTWR | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 334 | 170.3 | 173.03 | O66 NFTWR | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 334 | 170.17 | 172.88 | O66 NFTWR | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204539 | 27HUNTRSTN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 334 | 169.83 | 171.35 | O66 NFTWR | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204539 | 27HUNTRSTN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 334 | 169.83 | 171.35 | O66 NFTWR | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204539 | 27HUNTRSTN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 334 | 169.7 | 171.2 | O66 NFTWR | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 235463 | 01TANEY | 1 | 138 | 227/201 | 317 | 173.68 | 168.35 | O66 NFTWR | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 235463 | 01TANEY | 1 | 138 | 227/201 | 317 | 173.68 | 168.35 | O66 NFTWR | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 235463 | 01TANEY | 1 | 138 | 227/201 | 317 | 173.52 | 168.21 | O66 NFTWR | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204538 | 27STRABAN | 204544 | 27LINCOLN | 1 | 115 | 227 | 371 | 159.62 | 164.4 | O66 NFTWR | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204538 | 27STRABAN | 204544 | 27LINCOLN | 1 | 115 | 227 | 371 | 159.62 | 164.4 | O66 NFTWR | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204538 | 27STRABAN | 204544 | 27LINCOLN | 1 | 115 | 227 | 371 | 159.48 | 164.25 | O66 NFTWR | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 168.88 | 164.07 | O66 NFTWR | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 167.81 | 162.62 | O66 NFTWR | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 167.81 | 162.62 | O66 NFTWR | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 167.79 | 162.61 | O66 NFTWR | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 204550 | 27ORRTANNA | 1 | 115 | 227 | 189 | 160.3 | 159.97 | O66 NFTWR | ME_P1-2_ME-115-068_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204529 | 27GERMANTN | 204538 | 27STRABAN | 1 | 115 | 227 | 371 | 153.91 | 159.87 | O66 NFTWR | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204529 | 27GERMANTN | 204538 | 27STRABAN | 1 | 115 | 227 | 371 | 153.91 | 159.86 | O66 NFTWR | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204529 | 27GERMANTN | 204538 | 27STRABAN | 1 | 115 | 227 | 371 | 153.78 | 159.71 | O66 NFTWR | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 204550 | 27ORRTANNA | 1 | 115 | 227 | 189 | 158.58 | 159.68 | O66 NFTWR | ME_P2-3_ME-115-035A_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 159.49 | 159.53 | O66 NFTWR | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 221089 | WINDYED1 | 221090 | GLENARM2 | 1 | 115 | 232 | 222 | 154.98 | 158.62 | O66 NFTWR | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 204550 | 27ORRTANNA | 1 | 115 | 227 | 189 | 159.76 | 158.21 | O66 NFTWR | ME_P1-2_ME-115-067_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 204550 | 27ORRTANNA | 1 | 115 | 227 | 189 | 158 | 157.54 | O66 NFTWR | ME_P2-3_ME-115-013B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3464 | 168.22 | 162.2 | T157 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 204550 | 27ORRTANNA | 1 | 115 | 227 | 189 | 156.28 | 157.26 | O66 NFTWR | ME_P2-3_ME-115-035B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 204550 | 27ORRTANNA | 1 | 115 | 227 | 189 | 157.69 | 157.22 | O66 NFTWR | ME_P2-3_ME-115-013A_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 157.43 | 156.43 | O66 NFTWR | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 157.43 | 156.43 | O66 NFTWR | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 157.41 | 156.42 | O66 NFTWR | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 159.82 | 155.37 | O66 NFTWR | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3464 | 167.96 | 161.95 | TOP CROP | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 150.33 | 154.21 | O66 NFTWR | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 158.46 | 153.62 | O66 NFTWR | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 158.46 | 153.62 | O66 NFTWR | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 148.67 | 152.89 | O66 NFTWR | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3464 | 168.3 | 162.28 | TR3_G114 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 204550 | 27ORRTANNA | 1 | 115 | 227 | 189 | 153.22 | 151.38 | O66 NFTWR | ME_P2-2_ME-115-0102-4_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 204550 | 27ORRTANNA | 1 | 115 | 227 | 189 | 153.22 | 151.38 | O66 NFTWR | ME_P2-3_ME-115-0102-A_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 156.36 | 149.35 | O66 NFTWR | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 145.32 | 149.24 | O66 NFTWR | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3464 | 167.8 | 161.8 | TWINGROVE | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 903 | 141.23 | 147.28 | O66 NFTWR | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152 | 146.88 | O66 NFTWR | PN_P1-2_PN-500-010T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 148.44 | 146.47 | O66 NFTWR | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 221089 | WINDYED1 | 221090 | GLENARM2 | 1 | 115 | 232 | 222 | 141.54 | 146.3 | O66 NFTWR | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.29 | 145.85 | O66 NFTWR | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.22 | 145.78 | O66 NFTWR | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 334 | 147.66 | 145.16 | O66 NFTWR | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 334 | 147.66 | 145.16 | O66 NFTWR | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 334 | 147.65 | 145.15 | O66 NFTWR | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 141.2 | 145 | O66 NFTWR | AP_P2-3_PE-500-016_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204539 | 27HUNTRSTN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 334 | 147.18 | 144.98 | O66 NFTWR | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204539 | 27HUNTRSTN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 334 | 147.18 | 144.98 | O66 NFTWR | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204539 | 27HUNTRSTN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 334 | 147.18 | 144.97 | O66 NFTWR | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 141.27 | 144.95 | O66 NFTWR | AP_P2-3_PE-500-015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 334 | 147.45 | 144.9 | O66 NFTWR | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204539 | 27HUNTRSTN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 334 | 146.98 | 144.75 | O66 NFTWR | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 903 | 139.54 | 144.65 | O66 NFTWR | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 903 | 139.54 | 144.65 | O66 NFTWR | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 903 | 139.52 | 144.64 | O66 NFTWR | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 149.49 | 144.42 | O66 NFTWR | PJM_500_BG_P4_5_CNSTN_L_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 144.14 | 144.41 | O66 NFTWR | BG_P7_GRCTN_CNSTN_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 140.38 | 144.11 | O66 NFTWR | AP_P1-2_WP-500-DRT17_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 140.38 | 144.11 | O66 NFTWR | AP_P1-2_PE-500-001_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 140.33 | 144.04 | O66 NFTWR | AP_P2-3_PE-500-018C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 148.89 | 143.54 | O66 NFTWR | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 148.69 | 143.36 | O66 NFTWR | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 148.72 | 143.34 | O66 NFTWR | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 147.52 | 143.32 | O66 NFTWR | AP_P2-3_PE-500-016_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 147.56 | 143.29 | O66 NFTWR | AP_P2-3_PE-500-015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3464 | 168.07 | 162.06 | U2-072 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 148.45 | 143.15 | O66 NFTWR | PECO_P4_NOTTI85_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3464 | 168.2 | 162.19 | U2-073 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 221092 | FIVE.FOR | 221096 | ROCKRGE1 | 1 | 115 | 232 | 293 | 139.89 | 143.07 | O66 NFTWR | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 334 | 141.2 | 140.13 | O66 NFTWR | ME_P2-3_ME-115-019A-A_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 334 | 141.2 | 140.13 | O66 NFTWR | ME_P1-2_ME-115-061_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 911 | 145.15 | 139.81 | O66 NFTWR | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 145.19 | 138.71 | O66 NFTWR | PECO_P4_PEACH025_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204539 | 27HUNTRSTN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 334 | 140.73 | 138.66 | O66 NFTWR | ME_P1-2_ME-115-061_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204539 | 27HUNTRSTN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 334 | 140.73 | 138.66 | O66 NFTWR | ME_P2-3_ME-115-019A-A_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 911 | 144.1 | 138.47 | O66 NFTWR | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 911 | 144.1 | 138.47 | O66 NFTWR | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 911 | 144.09 | 138.47 | O66 NFTWR | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 144.85 | 138.42 | O66 NFTWR | PECO_P1-2_PBTIE1_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204544 | 27LINCOLN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 334 | 137.31 | 138.07 | O66 NFTWR | AP_P2-3_PE-500-016_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 138.44 | 137.97 | O66 NFTWR | PJM_500_BG_P4_5_CNSTN_15_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3464 | 168.13 | 162.12 | U2-090 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 221055 | HARRIS1A | 221058 | DOLFD T1 | 1 | 115 | 232 | 201 | 137.16 | 137.16 | O66 NFTWR | BG_P7_NWEST_GRNITE_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204539 | 27HUNTRSTN | 205912 | AD1-020 TAP | 1 | 115 | 227 | 334 | 136.84 | 136.53 | O66 NFTWR | AP_P2-3_PE-500-016_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204502 | 27JACKSON | 204514 | 27TMI | 1 | 230 | 227 | 781 | 129.54 | 136.32 | O66 NFTWR | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204502 | 27JACKSON | 204514 | 27TMI | 1 | 230 | 227 | 781 | 129.54 | 136.32 | O66 NFTWR | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204502 | 27JACKSON | 204514 | 27TMI | 1 | 230 | 227 | 781 | 129.52 | 136.31 | O66 NFTWR | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204502 | 27JACKSON | 204514 | 27TMI | 1 | 230 | 227 | 781 | 129.32 | 136.28 | O66 NFTWR | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204538 | 27STRABAN | 204544 | 27LINCOLN | 1 | 115 | 227 | 371 | 136.66 | 135.98 | O66 NFTWR | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204538 | 27STRABAN | 204544 | 27LINCOLN | 1 | 115 | 227 | 371 | 136.66 | 135.98 | O66 NFTWR | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204538 | 27STRABAN | 204544 | 27LINCOLN | 1 | 115 | 227 | 371 | 136.65 | 135.97 | O66 NFTWR | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204538 | 27STRABAN | 204544 | 27LINCOLN | 1 | 115 | 227 | 371 | 136.45 | 135.72 | O66 NFTWR | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 903 | 132.43 | 135.48 | O66 NFTWR | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200504 | 26CARLISLE | 204528 | 27GARDNERS | 1 | 115 | 226/227 | 190 | 126.65 | 135.25 | O66 NFTWR | PN_P2-3_PN-115-0331-B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 1031 | 128.16 | 134.64 | O66 NFTWR | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 203981 | AD2-062_POI | 235188 | 01GREENE | 1 | 138 | 226/201 | 317 | 142.05 | 134.12 | O66 NFTWR | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 203981 | AD2-062_POI | 235188 | 01GREENE | 1 | 138 | 226/201 | 317 | 142.05 | 134.12 | O66 NFTWR | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 203981 | AD2-062_POI | 235188 | 01GREENE | 1 | 138 | 226/201 | 317 | 141.84 | 133.97 | O66 NFTWR | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200512 | 26LEWISTWN | 200519 | 26REED TAP | 1 | 115 | 226 | 271 | 126.41 | 133.73 | O66 NFTWR | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200512 | 26LEWISTWN | 200519 | 26REED TAP | 1 | 115 | 226 | 271 | 126.49 | 133.71 | O66 NFTWR | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200512 | 26LEWISTWN | 200519 | 26REED TAP | 1 | 115 | 226 | 271 | 126.49 | 133.71 | O66 NFTWR | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200512 | 26LEWISTWN | 200519 | 26REED TAP | 1 | 115 | 226 | 271 | 126.49 | 133.71 | O66 NFTWR | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 221092 | FIVE.FOR | 221096 | ROCKRGE1 | 1 | 115 | 232 | 293 | 129.75 | 133.65 | O66 NFTWR | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 1031 | 127.61 | 133.6 | O66 NFTWR | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 1031 | 127.61 | 133.6 | O66 NFTWR | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 1031 | 127.6 | 133.59 | O66 NFTWR | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200504 | 26CARLISLE | 204528 | 27GARDNERS | 1 | 115 | 226/227 | 190 | 125.04 | 133.38 | O66 NFTWR | PN_P1-2_PN-115-094_A_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 235463 | 01TANEY | 1 | 138 | 227/201 | 317 | 134.53 | 133.12 | O66 NFTWR | AP_P2-3_PE-500-016_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 235463 | 01TANEY | 1 | 138 | 227/201 | 317 | 134.65 | 133.04 | O66 NFTWR | AP_P2-3_PE-500-015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200532 | 26ROXBURY | 203981 | AD2-062_POI | 1 | 138 | 226 | 317 | 141.3 | 132.78 | O66 NFTWR | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200532 | 26ROXBURY | 203981 | AD2-062_POI | 1 | 138 | 226 | 317 | 141.3 | 132.78 | O66 NFTWR | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200532 | 26ROXBURY | 203981 | AD2-062_POI | 1 | 138 | 226 | 317 | 141.09 | 132.63 | O66 NFTWR | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200504 | 26CARLISLE | 204528 | 27GARDNERS | 1 | 115 | 226/227 | 190 | 124.88 | 132.45 | O66 NFTWR | PN_P2-3_PN-115-58B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200504 | 26CARLISLE | 204528 | 27GARDNERS | 1 | 115 | 226/227 | 190 | 125.53 | 132.4 | O66 NFTWR | PN_P1-3_PN-115-040_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200504 | 26CARLISLE | 204528 | 27GARDNERS | 1 | 115 | 226/227 | 190 | 125.53 | 132.4 | O66 NFTWR | PN_P2-2_PN-115-030_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200504 | 26CARLISLE | 204528 | 27GARDNERS | 1 | 115 | 226/227 | 190 | 124.68 | 132.38 | O66 NFTWR | PN_P1-2_PN-115-094_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 235463 | 01TANEY | 1 | 138 | 227/201 | 317 | 133.21 | 132.23 | O66 NFTWR | AP_P2-3_PE-500-018D_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 235463 | 01TANEY | 1 | 138 | 227/201 | 317 | 133.21 | 132.22 | O66 NFTWR | AP_P2-3_PE-500-018C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 235463 | 01TANEY | 1 | 138 | 227/201 | 317 | 132.55 | 132.06 | O66 NFTWR | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 235463 | 01TANEY | 1 | 138 | 227/201 | 317 | 133.06 | 131.97 | O66 NFTWR | AP_P1-2_WP-500-DRT17_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 235463 | 01TANEY | 1 | 138 | 227/201 | 317 | 133.06 | 131.97 | O66 NFTWR | AP_P1-2_PE-500-001_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 911 | 136.19 | 131.94 | O66 NFTWR | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204529 | 27GERMANTN | 204538 | 27STRABAN | 1 | 115 | 227 | 371 | 130.95 | 131.65 | O66 NFTWR | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204529 | 27GERMANTN | 204538 | 27STRABAN | 1 | 115 | 227 | 371 | 130.95 | 131.65 | O66 NFTWR | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204529 | 27GERMANTN | 204538 | 27STRABAN | 1 | 115 | 227 | 371 | 130.94 | 131.64 | O66 NFTWR | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204529 | 27GERMANTN | 204538 | 27STRABAN | 1 | 115 | 227 | 371 | 130.74 | 131.39 | O66 NFTWR | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 207922 | BRIS | 207923 | BRISREAC | RX | 230 | 229 | 676 | 122.75 | 130.32 | O66 NFTWR | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 207923 | BRISREAC | 208132 | WHEM TR1 | 1 | 230 | 229 | 676 | 122.75 | 130.32 | O66 NFTWR | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 221056 | HARRIS0A | 221057 | DOLFD T0 | 1 | 115 | 232 | 201 | 130.17 | 130.07 | O66 NFTWR | BG_P7_NWEST_GRNITE_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204538 | 27STRABAN | 204544 | 27LINCOLN | 1 | 115 | 227 | 371 | 126.17 | 129.03 | O66 NFTWR | AP_P2-3_PE-500-016_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204538 | 27STRABAN | 204544 | 27LINCOLN | 1 | 115 | 227 | 371 | 126.27 | 128.93 | O66 NFTWR | AP_P2-3_PE-500-015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 207922 | BRIS | 207923 | BRISREAC | RX | 230 | 229 | 676 | 121.92 | 128.86 | O66 NFTWR | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 207923 | BRISREAC | 208132 | WHEM TR1 | 1 | 230 | 229 | 676 | 121.92 | 128.86 | O66 NFTWR | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 207922 | BRIS | 207923 | BRISREAC | RX | 230 | 229 | 676 | 121.92 | 128.85 | O66 NFTWR | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 207923 | BRISREAC | 208132 | WHEM TR1 | 1 | 230 | 229 | 676 | 121.92 | 128.85 | O66 NFTWR | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 207922 | BRIS | 207923 | BRISREAC | RX | 230 | 229 | 676 | 121.91 | 128.85 | O66 NFTWR | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 207923 | BRISREAC | 208132 | WHEM TR1 | 1 | 230 | 229 | 676 | 121.91 | 128.85 | O66 NFTWR | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200519 | 26REED TAP | 200522 | 26SHADE GP | 1 | 115 | 226 | 271 | 118.74 | 128.64 | O66 NFTWR | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200519 | 26REED TAP | 200522 | 26SHADE GP | 1 | 115 | 226 | 271 | 118.82 | 128.63 | O66 NFTWR | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200519 | 26REED TAP | 200522 | 26SHADE GP | 1 | 115 | 226 | 271 | 118.82 | 128.63 | O66 NFTWR | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200519 | 26REED TAP | 200522 | 26SHADE GP | 1 | 115 | 226 | 271 | 118.82 | 128.63 | O66 NFTWR | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208078 | SAKR | 1 | 230 | 229 | 903 | 121.3 | 128.34 | O66 NFTWR | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 133.89 | 128.15 | O66 NFTWR | PECO_P4_PEACH205_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204538 | 27STRABAN | 204544 | 27LINCOLN | 1 | 115 | 227 | 371 | 125.05 | 128.11 | O66 NFTWR | AP_P2-3_PE-500-018D_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200512 | 26LEWISTWN | 200519 | 26REED TAP | 1 | 115 | 226 | 271 | 123.65 | 128.04 | O66 NFTWR | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220972 | GRANITE1 | 1 | 230 | 232 | 829 | 131.85 | 128.03 | O66 NFTWR | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200504 | 26CARLISLE | 204528 | 27GARDNERS | 1 | 115 | 226/227 | 190 | 122.34 | 127.94 | O66 NFTWR | PN_P2-3_PN-230-0014-12_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 133.58 | 127.65 | O66 NFTWR | PECO_P1-2_PBTIE2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200504 | 26CARLISLE | 204528 | 27GARDNERS | 1 | 115 | 226/227 | 190 | 122.33 | 127.52 | O66 NFTWR | PN_P2-3_PN-230-0014-11_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200504 | 26CARLISLE | 204528 | 27GARDNERS | 1 | 115 | 226/227 | 190 | 122.33 | 127.52 | O66 NFTWR | PN_P1-3_PN-230-020A_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200504 | 26CARLISLE | 204528 | 27GARDNERS | 1 | 115 | 226/227 | 190 | 122.25 | 127.51 | O66 NFTWR | PN_P2-2_PN-115-031_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 133.28 | 127.37 | O66 NFTWR | PECO_P4_PEACH055_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 204529 | 27GERMANTN | 1 | 138/115 | 227 | 453 | 121.54 | 127.37 | O66 NFTWR | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 204529 | 27GERMANTN | 1 | 138/115 | 227 | 453 | 121.54 | 127.37 | O66 NFTWR | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220972 | GRANITE1 | 1 | 230 | 232 | 829 | 131.2 | 127.36 | O66 NFTWR | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220972 | GRANITE1 | 1 | 230 | 232 | 829 | 131.2 | 127.36 | O66 NFTWR | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 204529 | 27GERMANTN | 1 | 138/115 | 227 | 453 | 121.43 | 127.25 | O66 NFTWR | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3464 | 167.97 | 161.96 | U3-002 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208078 | SAKR | 1 | 230 | 229 | 903 | 120.49 | 126.92 | O66 NFTWR | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208078 | SAKR | 1 | 230 | 229 | 903 | 120.49 | 126.92 | O66 NFTWR | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208078 | SAKR | 1 | 230 | 229 | 903 | 120.48 | 126.92 | O66 NFTWR | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204502 | 27JACKSON | 204514 | 27TMI | 1 | 230 | 227 | 781 | 121.85 | 126.46 | O66 NFTWR | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220973 | GRANITE6 | 1 | 230 | 232 | 829 | 129.84 | 126.19 | O66 NFTWR | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220973 | GRANITE6 | 1 | 230 | 232 | 829 | 129.23 | 125.56 | O66 NFTWR | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220973 | GRANITE6 | 1 | 230 | 232 | 829 | 129.23 | 125.56 | O66 NFTWR | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 1031 | 121.98 | 125.53 | O66 NFTWR | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3464 | 168.3 | 162.28 | V1-011 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 126.24 | 124.62 | O66 NFTWR | DVP_P4-2: 514T595_SRT-SW |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204529 | 27GERMANTN | 204538 | 27STRABAN | 1 | 115 | 227 | 371 | 120.46 | 124.58 | O66 NFTWR | AP_P2-3_PE-500-016_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204529 | 27GERMANTN | 204538 | 27STRABAN | 1 | 115 | 227 | 371 | 120.56 | 124.49 | O66 NFTWR | AP_P2-3_PE-500-015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204539 | 27HUNTRSTN | 204550 | 27ORRTANNA | 1 | 115 | 227 | 264 | 124.46 | 124.22 | O66 NFTWR | ME_P1-2_ME-115-068_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204539 | 27HUNTRSTN | 204550 | 27ORRTANNA | 1 | 115 | 227 | 264 | 123.23 | 124.01 | O66 NFTWR | ME_P2-3_ME-115-035A_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 123.83 | 123.95 | O66 NFTWR | BG_P7_GRCTN_CNSTN_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 121.96 | 123.95 | O66 NFTWR | BG_P7_GRCTN_CNSTN_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 2 | 230 | 233 | 793 | 125.5 | 123.82 | O66 NFTWR | DVP_P4-2: 514T595_SRT-SW |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 793 | 125.5 | 123.82 | O66 NFTWR | DVP_P4-2: 514T595_SRT-SW |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204529 | 27GERMANTN | 204538 | 27STRABAN | 1 | 115 | 227 | 371 | 123.76 | 123.74 | O66 NFTWR | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 911 | 121 | 123.23 | O66 NFTWR | BG_P7_GRCTN_CNSTN_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200512 | 26LEWISTWN | 200519 | 26REED TAP | 1 | 115 | 226 | 271 | 120.36 | 123.19 | O66 NFTWR | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200512 | 26LEWISTWN | 200519 | 26REED TAP | 1 | 115 | 226 | 271 | 120.36 | 123.19 | O66 NFTWR | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200512 | 26LEWISTWN | 200519 | 26REED TAP | 1 | 115 | 226 | 271 | 120.3 | 123.11 | O66 NFTWR | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200519 | 26REED TAP | 200522 | 26SHADE GP | 1 | 115 | 226 | 271 | 115.98 | 123.02 | O66 NFTWR | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204539 | 27HUNTRSTN | 204550 | 27ORRTANNA | 1 | 115 | 227 | 264 | 124.07 | 122.86 | O66 NFTWR | ME_P1-2_ME-115-067_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 124.44 | 122.86 | O66 NFTWR | DVP_P4-2: 51482_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 124.44 | 122.76 | O66 NFTWR | DVP_P1-2: LN 514_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 124.44 | 122.76 | O66 NFTWR | AP_P1-2_PE-500-407T_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 2 | 230 | 233 | 793 | 124.21 | 122.58 | O66 NFTWR | DVP_P4-2: 51482_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 793 | 124.21 | 122.58 | O66 NFTWR | DVP_P4-2: 51482_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 793 | 124.21 | 122.5 | O66 NFTWR | DVP_P1-2: LN 514_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 2 | 230 | 233 | 793 | 124.21 | 122.5 | O66 NFTWR | AP_P1-2_PE-500-407T_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 2 | 230 | 233 | 793 | 124.21 | 122.5 | O66 NFTWR | DVP_P1-2: LN 514_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 793 | 124.21 | 122.5 | O66 NFTWR | AP_P1-2_PE-500-407T_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204539 | 27HUNTRSTN | 204550 | 27ORRTANNA | 1 | 115 | 227 | 264 | 122.81 | 122.47 | O66 NFTWR | ME_P2-3_ME-115-013B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208394 | PPL-BGE TIE | 221092 | FIVE.FOR | 1 | 115 | 229/232 | 247 | 119.59 | 122.35 | O66 NFTWR | PL_05_P71_000906_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220953 | HOWARD12 | 220972 | GRANITE1 | 1 | 230 | 232 | 772 | 126.11 | 122.26 | O66 NFTWR | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204539 | 27HUNTRSTN | 204550 | 27ORRTANNA | 1 | 115 | 227 | 264 | 121.58 | 122.26 | O66 NFTWR | ME_P2-3_ME-115-035B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204539 | 27HUNTRSTN | 204550 | 27ORRTANNA | 1 | 115 | 227 | 264 | 122.59 | 122.23 | O66 NFTWR | ME_P2-3_ME-115-013A_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208393 | FARO DC TIE | 208395 | FARO FF | 1 | 115/69 | 229 | 120 | 125.46 | 121.98 | O66 NFTWR | PL_05_P71_000906_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208393 | FARO DC TIE | 208395 | FARO FF | 2 | 115/69 | 229 | 120 | 125.46 | 121.98 | O66 NFTWR | PL_05_P71_000906_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 127.4 | 121.86 | O66 NFTWR | PECO_P4_PEACH015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220954 | HOWARD32 | 220973 | GRANITE6 | 1 | 230 | 232 | 772 | 125.15 | 121.74 | O66 NFTWR | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 207922 | BRIS | 207923 | BRISREAC | RX | 230 | 229 | 676 | 116.79 | 121.34 | O66 NFTWR | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 207923 | BRISREAC | 208132 | WHEM TR1 | 1 | 230 | 229 | 676 | 116.79 | 121.34 | O66 NFTWR | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220953 | HOWARD12 | 220972 | GRANITE1 | 1 | 230 | 232 | 772 | 125.17 | 121.28 | O66 NFTWR | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220953 | HOWARD12 | 220972 | GRANITE1 | 1 | 230 | 232 | 772 | 125.17 | 121.27 | O66 NFTWR | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 126.68 | 121.06 | O66 NFTWR | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220954 | HOWARD32 | 220973 | GRANITE6 | 1 | 230 | 232 | 772 | 124.34 | 120.88 | O66 NFTWR | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220954 | HOWARD32 | 220973 | GRANITE6 | 1 | 230 | 232 | 772 | 124.34 | 120.88 | O66 NFTWR | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208020 | MANO TR3 | 1 | 230 | 229 | 793 | 108.43 | 120.24 | O66 NFTWR | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200025 | W CHAPEL | 1 | 500 | 225 | 1732 | 120.99 | 119.08 | O66 NFTWR | PEPCO_P4_PP41_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200512 | 26LEWISTWN | 200519 | 26REED TAP | 1 | 115 | 226 | 271 | 120.12 | 119.02 | O66 NFTWR | ME_P2-3_ME-115-003DT_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 203981 | AD2-062_POI | 235188 | 01GREENE | 1 | 138 | 226/201 | 317 | 122.9 | 118.99 | O66 NFTWR | AP_P2-3_PE-500-016_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200512 | 26LEWISTWN | 200519 | 26REED TAP | 1 | 115 | 226 | 271 | 120.05 | 118.95 | O66 NFTWR | ME_P2-3_ME-115-003AT_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 114.48 | 118.86 | O66 NFTWR | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 116.35 | 118.86 | O66 NFTWR | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 203981 | AD2-062_POI | 235188 | 01GREENE | 1 | 138 | 226/201 | 317 | 123.1 | 118.81 | O66 NFTWR | AP_P2-3_PE-500-015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208020 | MANO TR3 | 1 | 230 | 229 | 793 | 107.52 | 118.72 | O66 NFTWR | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208020 | MANO TR3 | 1 | 230 | 229 | 793 | 107.52 | 118.72 | O66 NFTWR | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208020 | MANO TR3 | 1 | 230 | 229 | 793 | 107.52 | 118.72 | O66 NFTWR | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 116.16 | 118.64 | O66 NFTWR | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 114.29 | 118.64 | O66 NFTWR | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 114.29 | 118.64 | O66 NFTWR | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 116.16 | 118.64 | O66 NFTWR | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200519 | 26REED TAP | 200522 | 26SHADE GP | 1 | 115 | 226 | 271 | 112.69 | 118.26 | O66 NFTWR | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200519 | 26REED TAP | 200522 | 26SHADE GP | 1 | 115 | 226 | 271 | 112.69 | 118.26 | O66 NFTWR | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200519 | 26REED TAP | 200522 | 26SHADE GP | 1 | 115 | 226 | 271 | 112.63 | 118.18 | O66 NFTWR | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 203981 | AD2-062_POI | 235188 | 01GREENE | 1 | 138 | 226/201 | 317 | 120.82 | 118.12 | O66 NFTWR | AP_P2-3_PE-500-018D_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 203981 | AD2-062_POI | 235188 | 01GREENE | 1 | 138 | 226/201 | 317 | 120.81 | 118.1 | O66 NFTWR | AP_P2-3_PE-500-018C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204539 | 27HUNTRSTN | 204550 | 27ORRTANNA | 1 | 115 | 227 | 264 | 119.39 | 117.96 | O66 NFTWR | ME_P2-2_ME-115-0102-4_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204539 | 27HUNTRSTN | 204550 | 27ORRTANNA | 1 | 115 | 227 | 264 | 119.39 | 117.96 | O66 NFTWR | ME_P2-3_ME-115-0102-A_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208394 | PPL-BGE TIE | 221092 | FIVE.FOR | 1 | 115 | 229/232 | 247 | 116.62 | 117.82 | O66 NFTWR | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208394 | PPL-BGE TIE | 221092 | FIVE.FOR | 1 | 115 | 229/232 | 247 | 116.54 | 117.7 | O66 NFTWR | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208394 | PPL-BGE TIE | 221092 | FIVE.FOR | 1 | 115 | 229/232 | 247 | 116.54 | 117.7 | O66 NFTWR | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208394 | PPL-BGE TIE | 221092 | FIVE.FOR | 1 | 115 | 229/232 | 247 | 116.54 | 117.7 | O66 NFTWR | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200532 | 26ROXBURY | 203981 | AD2-062_POI | 1 | 138 | 226 | 317 | 122.15 | 117.68 | O66 NFTWR | AP_P2-3_PE-500-016_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208078 | SAKR | 1 | 230 | 229 | 903 | 113.18 | 117.63 | O66 NFTWR | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 203981 | AD2-062_POI | 235188 | 01GREENE | 1 | 138 | 226/201 | 317 | 121.38 | 117.61 | O66 NFTWR | AP_P2-3_WP-500-466_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 203981 | AD2-062_POI | 235188 | 01GREENE | 1 | 138 | 226/201 | 317 | 121.38 | 117.61 | O66 NFTWR | AP_P1-2_PE-500-004_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 203981 | AD2-062_POI | 235188 | 01GREENE | 1 | 138 | 226/201 | 317 | 121.38 | 117.61 | O66 NFTWR | AP_P1-2_WP-500-006_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200532 | 26ROXBURY | 203981 | AD2-062_POI | 1 | 138 | 226 | 317 | 122.36 | 117.5 | O66 NFTWR | AP_P2-3_PE-500-015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 221092 | FIVE.FOR | 221095 | ROCKRGE2 | 1 | 115 | 232 | 340 | 115.26 | 117.42 | O66 NFTWR | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 115.41 | 117.4 | O66 NFTWR | BG_P7_GRCTN_CNSTN_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208031 | MLWD TR2 | 1 | 230 | 229 | 911 | 108.88 | 117.24 | O66 NFTWR | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208393 | FARO DC TIE | 208395 | FARO FF | 1 | 115/69 | 229 | 120 | 122.4 | 117.07 | O66 NFTWR | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208393 | FARO DC TIE | 208395 | FARO FF | 2 | 115/69 | 229 | 120 | 122.41 | 117.07 | O66 NFTWR | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204512 | 27S.RDG | 204693 | 27BOONETOWN | 1 | 230 | 227 | 607 | 104.64 | 116.98 | O66 NFTWR | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200532 | 26ROXBURY | 200520 | 26ROXBURY | 2 | 138/115 | 226 | 435 | 102.97 | 116.98 | O66 NFTWR | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200532 | 26ROXBURY | 200520 | 26ROXBURY | 2 | 138/115 | 226 | 435 | 102.97 | 116.97 | O66 NFTWR | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208393 | FARO DC TIE | 208395 | FARO FF | 1 | 115/69 | 229 | 120 | 122.32 | 116.93 | O66 NFTWR | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208393 | FARO DC TIE | 208395 | FARO FF | 1 | 115/69 | 229 | 120 | 122.32 | 116.93 | O66 NFTWR | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208393 | FARO DC TIE | 208395 | FARO FF | 2 | 115/69 | 229 | 120 | 122.33 | 116.92 | O66 NFTWR | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208393 | FARO DC TIE | 208395 | FARO FF | 2 | 115/69 | 229 | 120 | 122.33 | 116.92 | O66 NFTWR | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208393 | FARO DC TIE | 208395 | FARO FF | 1 | 115/69 | 229 | 120 | 122.32 | 116.92 | O66 NFTWR | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208393 | FARO DC TIE | 208395 | FARO FF | 2 | 115/69 | 229 | 120 | 122.32 | 116.92 | O66 NFTWR | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220965 | NEAST339 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 117.53 | 116.83 | O66 NFTWR | BG_P1_2315_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200532 | 26ROXBURY | 200520 | 26ROXBURY | 2 | 138/115 | 226 | 435 | 102.82 | 116.81 | O66 NFTWR | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200532 | 26ROXBURY | 203981 | AD2-062_POI | 1 | 138 | 226 | 317 | 120.07 | 116.8 | O66 NFTWR | AP_P2-3_PE-500-018D_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200532 | 26ROXBURY | 203981 | AD2-062_POI | 1 | 138 | 226 | 317 | 120.06 | 116.78 | O66 NFTWR | AP_P2-3_PE-500-018C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208394 | PPL-BGE TIE | 221092 | FIVE.FOR | 1 | 115 | 229/232 | 247 | 111.29 | 116.74 | O66 NFTWR | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220965 | NEAST339 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 117.14 | 116.64 | O66 NFTWR | BG_P4_5_NEAST_17_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220965 | NEAST339 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 117.29 | 116.64 | O66 NFTWR | BG_P4_5_NEAST_15_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 911 | 115.44 | 116.33 | O66 NFTWR | PJM_500_BG_P4_5_CNSTN_15_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200532 | 26ROXBURY | 203981 | AD2-062_POI | 1 | 138 | 226 | 317 | 120.63 | 116.31 | O66 NFTWR | AP_P2-3_WP-500-DRT19_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200532 | 26ROXBURY | 203981 | AD2-062_POI | 1 | 138 | 226 | 317 | 120.63 | 116.31 | O66 NFTWR | AP_P2-3_WP-500-466_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200532 | 26ROXBURY | 203981 | AD2-062_POI | 1 | 138 | 226 | 317 | 120.63 | 116.31 | O66 NFTWR | AP_P1-2_PE-500-004_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204512 | 27S.RDG | 204693 | 27BOONETOWN | 1 | 230 | 227 | 607 | 104.46 | 116.28 | O66 NFTWR | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204512 | 27S.RDG | 204693 | 27BOONETOWN | 1 | 230 | 227 | 607 | 104.44 | 116.26 | O66 NFTWR | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204512 | 27S.RDG | 204693 | 27BOONETOWN | 1 | 230 | 227 | 607 | 104.43 | 116.26 | O66 NFTWR | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 112.69 | 116.18 | O66 NFTWR | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 115.65 | 116.05 | O66 NFTWR | PJM_500_BG_P4_5_CNSTN_15_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 113.78 | 116.05 | O66 NFTWR | PJM_500_BG_P4_5_CNSTN_15_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220979 | NEAST317 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 116.64 | 115.98 | O66 NFTWR | BG_P1_2337_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208031 | MLWD TR2 | 1 | 230 | 229 | 911 | 108.08 | 115.95 | O66 NFTWR | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208031 | MLWD TR2 | 1 | 230 | 229 | 911 | 108.08 | 115.95 | O66 NFTWR | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208031 | MLWD TR2 | 1 | 230 | 229 | 911 | 108.08 | 115.95 | O66 NFTWR | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 112.37 | 115.85 | O66 NFTWR | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 112.33 | 115.77 | O66 NFTWR | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 112.33 | 115.77 | O66 NFTWR | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220979 | NEAST317 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 116.34 | 115.74 | O66 NFTWR | BG_P4_5_NEAST_39_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220979 | NEAST317 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 116.34 | 115.74 | O66 NFTWR | BG_P4_5_NEAST_37_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 112.01 | 115.44 | O66 NFTWR | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 112.01 | 115.44 | O66 NFTWR | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208131 | WHEM | 208132 | WHEM TR1 | 1 | 230 | 229 | 691 | 107.16 | 115.39 | O66 NFTWR | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 793 | 117.58 | 114.87 | O66 NFTWR | PEPCO_P1_PP2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 2 | 230 | 233 | 793 | 117.58 | 114.87 | O66 NFTWR | PEPCO_P1_PP1_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 115.76 | 114.42 | O66 NFTWR | PL_04_P12_000260_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 115.76 | 114.42 | O66 NFTWR | PL_04_P42_000564_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200519 | 26REED TAP | 200522 | 26SHADE GP | 1 | 115 | 226 | 271 | 112.45 | 114.16 | O66 NFTWR | ME_P2-3_ME-115-003DT_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200519 | 26REED TAP | 200522 | 26SHADE GP | 1 | 115 | 226 | 271 | 112.38 | 114.1 | O66 NFTWR | ME_P2-3_ME-115-003AT_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208131 | WHEM | 208132 | WHEM TR1 | 1 | 230 | 229 | 691 | 106.38 | 114.02 | O66 NFTWR | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208131 | WHEM | 208132 | WHEM TR1 | 1 | 230 | 229 | 691 | 106.38 | 114.02 | O66 NFTWR | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208131 | WHEM | 208132 | WHEM TR1 | 1 | 230 | 229 | 691 | 106.36 | 114.01 | O66 NFTWR | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208395 | FARO FF | 208396 | FARO | 1 | 69 | 229 | 270 | 111.54 | 113.96 | O66 NFTWR | PL_05_P71_000906_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 111.16 | 113.56 | O66 NFTWR | BG_P7_GRCTN_CNSTN_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208394 | PPL-BGE TIE | 221092 | FIVE.FOR | 1 | 115 | 229/232 | 247 | 112.1 | 113.56 | O66 NFTWR | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3464 | 168.63 | 162.61 | V2-046 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3464 | 168.12 | 162.11 | V3-007 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 2 | 500/230 | 225/232 | 2168 | 108.06 | 113.16 | O66 NFTWR | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208393 | FARO DC TIE | 208395 | FARO FF | 1 | 115/69 | 229 | 120 | 117.75 | 113.11 | O66 NFTWR | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208393 | FARO DC TIE | 208395 | FARO FF | 2 | 115/69 | 229 | 120 | 117.75 | 113.11 | O66 NFTWR | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 2 | 500/230 | 225/232 | 2168 | 107.88 | 112.94 | O66 NFTWR | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 2 | 500/230 | 225/232 | 2168 | 107.88 | 112.94 | O66 NFTWR | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 1 | 500/230 | 225/232 | 2168 | 107.83 | 112.92 | O66 NFTWR | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 114.63 | 112.85 | O66 NFTWR | AP_P2-3_PE-500-019C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 1 | 500/230 | 225/232 | 2168 | 107.65 | 112.7 | O66 NFTWR | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 1 | 500/230 | 225/232 | 2168 | 107.65 | 112.7 | O66 NFTWR | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220964 | GRACETON | 220999 | BAGLEY2 | 13 | 230 | 232 | 1795 | 111.68 | 112.59 | O66 NFTWR | BG_P4_5_GRCTN_3T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 108.18 | 112.5 | O66 NFTWR | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 117.45 | 112.33 | O66 NFTWR | PECO_P4_PEACH225_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 108 | 112.29 | O66 NFTWR | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 108 | 112.29 | O66 NFTWR | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200532 | 26ROXBURY | 200520 | 26ROXBURY | 2 | 138/115 | 226 | 435 | 98.8 | 112.17 | O66 NFTWR | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200532 | 26ROXBURY | 200520 | 26ROXBURY | 2 | 138/115 | 226 | 435 | 98.8 | 112.17 | O66 NFTWR | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200532 | 26ROXBURY | 200520 | 26ROXBURY | 2 | 138/115 | 226 | 435 | 98.79 | 112.16 | O66 NFTWR | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200532 | 26ROXBURY | 200520 | 26ROXBURY | 2 | 138/115 | 226 | 435 | 98.61 | 111.96 | O66 NFTWR | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 221089 | WINDYED1 | 221090 | GLENARM2 | 1 | 115 | 232 | 222 | 106.4 | 111.59 | O66 NFTWR | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 221089 | WINDYED1 | 221090 | GLENARM2 | 1 | 115 | 232 | 222 | 105.27 | 110.99 | O66 NFTWR | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 221089 | WINDYED1 | 221090 | GLENARM2 | 1 | 115 | 232 | 222 | 105.1 | 110.82 | O66 NFTWR | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 221089 | WINDYED1 | 221090 | GLENARM2 | 1 | 115 | 232 | 222 | 105.1 | 110.82 | O66 NFTWR | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3464 | 167.63 | 161.63 | V3-028 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3464 | 168.7 | 162.68 | W1-003 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 2 | 500/230 | 225/232 | 2168 | 107.3 | 110.48 | O66 NFTWR | PJM_500_BG_P4_5_CNSTN_15_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 111.29 | 110.09 | O66 NFTWR | BG_P4_5_CNSTN_14_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 107.51 | 109.84 | O66 NFTWR | PJM_500_BG_P4_5_CNSTN_15_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204512 | 27S.RDG | 204693 | 27BOONETOWN | 1 | 230 | 227 | 607 | 102.67 | 109.76 | O66 NFTWR | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208395 | FARO FF | 208396 | FARO | 1 | 69 | 229 | 270 | 108.82 | 109.69 | O66 NFTWR | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208395 | FARO FF | 208396 | FARO | 1 | 69 | 229 | 270 | 108.75 | 109.58 | O66 NFTWR | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208395 | FARO FF | 208396 | FARO | 1 | 69 | 229 | 270 | 108.75 | 109.58 | O66 NFTWR | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208395 | FARO FF | 208396 | FARO | 1 | 69 | 229 | 270 | 108.74 | 109.58 | O66 NFTWR | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220980 | RAPHAEL | 220999 | BAGLEY2 | 13 | 230 | 232 | 1795 | 107.31 | 109.35 | O66 NFTWR | BG_P4_5_GRCTN_3T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 221092 | FIVE.FOR | 221095 | ROCKRGE2 | 1 | 115 | 232 | 340 | 106.48 | 109.32 | O66 NFTWR | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 104.79 | 109.19 | O66 NFTWR | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200504 | 26CARLISLE | 200520 | 26ROXBURY | 1 | 115 | 226 | 190 | 98.92 | 109.07 | O66 NFTWR | PN_P1-2_PN-115-094_A_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 104.66 | 109.05 | O66 NFTWR | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208020 | MANO TR3 | 1 | 230 | 229 | 793 | 100.3 | 108.92 | O66 NFTWR | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 103.94 | 108.68 | O66 NFTWR | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208395 | FARO FF | 208396 | FARO | 1 | 69 | 229 | 270 | 103.94 | 108.67 | O66 NFTWR | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208020 | MANO TR3 | 208031 | MLWD TR2 | 1 | 230 | 229 | 903 | 99.16 | 108.65 | O66 NFTWR | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 793 | 111.14 | 108.56 | O66 NFTWR | PEPCO_P4_PP19_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 103.76 | 108.47 | O66 NFTWR | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 103.76 | 108.47 | O66 NFTWR | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200504 | 26CARLISLE | 200520 | 26ROXBURY | 1 | 115 | 226 | 190 | 98.76 | 108.23 | O66 NFTWR | PN_P2-3_PN-115-58B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200504 | 26CARLISLE | 200520 | 26ROXBURY | 1 | 115 | 226 | 190 | 99.4 | 108.18 | O66 NFTWR | PN_P2-2_PN-115-030_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200504 | 26CARLISLE | 200520 | 26ROXBURY | 1 | 115 | 226 | 190 | 99.4 | 108.18 | O66 NFTWR | PN_P1-3_PN-115-040_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200504 | 26CARLISLE | 200520 | 26ROXBURY | 1 | 115 | 226 | 190 | 98.57 | 108.17 | O66 NFTWR | PN_P1-2_PN-115-094_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 221092 | FIVE.FOR | 221096 | ROCKRGE1 | 1 | 115 | 232 | 293 | 103.58 | 107.5 | O66 NFTWR | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208020 | MANO TR3 | 208031 | MLWD TR2 | 1 | 230 | 229 | 903 | 98.38 | 107.48 | O66 NFTWR | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208020 | MANO TR3 | 208031 | MLWD TR2 | 1 | 230 | 229 | 903 | 98.38 | 107.48 | O66 NFTWR | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208020 | MANO TR3 | 208031 | MLWD TR2 | 1 | 230 | 229 | 903 | 98.38 | 107.48 | O66 NFTWR | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3464 | 168.7 | 162.68 | W1-004 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208131 | WHEM | 208132 | WHEM TR1 | 1 | 230 | 229 | 691 | 101.56 | 107.06 | O66 NFTWR | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208031 | MLWD TR2 | 1 | 230 | 229 | 911 | 101.29 | 107.05 | O66 NFTWR | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208131 | WHEM | 208133 | WHEM TR2 | 1 | 230 | 229 | 691 | 99.64 | 106.95 | O66 NFTWR | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200009 | JUNI | 208004 | JUNI | 2 | 500/230 | 225/229 | 1040 | 107.44 | 106.85 | O66 NFTWR | PL_10_P42_000140_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 2 | 230 | 233 | 793 | 108.41 | 106.61 | O66 NFTWR | AP_P2-3_PE-500-019C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 793 | 108.41 | 106.61 | O66 NFTWR | AP_P2-3_PE-500-019C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 221092 | FIVE.FOR | 221094 | GRACE.-1 | 1 | 115 | 232 | 498 | 105.8 | 106.53 | O66 NFTWR | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 221092 | FIVE.FOR | 221096 | ROCKRGE1 | 1 | 115 | 232 | 293 | 102.12 | 106.43 | O66 NFTWR | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 221092 | FIVE.FOR | 221096 | ROCKRGE1 | 1 | 115 | 232 | 293 | 101.99 | 106.3 | O66 NFTWR | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 221092 | FIVE.FOR | 221096 | ROCKRGE1 | 1 | 115 | 232 | 293 | 101.99 | 106.3 | O66 NFTWR | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3464 | 168.7 | 162.68 | W1-005 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 103.26 | 106.13 | O66 NFTWR | PJM_500_BG_P4_5_CNSTN_15_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204512 | 27S.RDG | 204693 | 27BOONETOWN | 1 | 230 | 227 | 607 | 106.46 | 105.81 | O66 NFTWR | PL_04_P42_101307_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204512 | 27S.RDG | 204693 | 27BOONETOWN | 1 | 230 | 227 | 607 | 106.47 | 105.76 | O66 NFTWR | PL_24_P42_102306_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208395 | FARO FF | 208396 | FARO | 1 | 69 | 229 | 270 | 104.68 | 105.72 | O66 NFTWR | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208131 | WHEM | 208133 | WHEM TR2 | 1 | 230 | 229 | 691 | 98.86 | 105.63 | O66 NFTWR | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208131 | WHEM | 208133 | WHEM TR2 | 1 | 230 | 229 | 691 | 98.86 | 105.63 | O66 NFTWR | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208131 | WHEM | 208133 | WHEM TR2 | 1 | 230 | 229 | 691 | 98.85 | 105.62 | O66 NFTWR | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200532 | 26ROXBURY | 200520 | 26ROXBURY | 2 | 138/115 | 226 | 435 | 93.62 | 105.56 | O66 NFTWR | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220973 | GRANITE6 | 1 | 230 | 232 | 829 | 106.54 | 105.12 | O66 NFTWR | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220965 | NEAST339 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 106.18 | 104.8 | O66 NFTWR | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220965 | NEAST339 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 106.08 | 104.68 | O66 NFTWR | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220965 | NEAST339 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 106.08 | 104.68 | O66 NFTWR | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200504 | 26CARLISLE | 200520 | 26ROXBURY | 1 | 115 | 226 | 190 | 89.64 | 104.63 | O66 NFTWR | PN_P2-3_PN-115-0331-B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204512 | 27S.RDG | 204693 | 27BOONETOWN | 1 | 230 | 227 | 607 | 105.19 | 104.58 | O66 NFTWR | PL_04_P22_102291_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204512 | 27S.RDG | 204693 | 27BOONETOWN | 1 | 230 | 227 | 607 | 105.19 | 104.58 | O66 NFTWR | PL_04_P43_102301_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204512 | 27S.RDG | 204693 | 27BOONETOWN | 1 | 230 | 227 | 607 | 105.19 | 104.56 | O66 NFTWR | PL_04_P13_101211_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220972 | GRANITE1 | 1 | 230 | 232 | 829 | 105.67 | 104.04 | O66 NFTWR | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200504 | 26CARLISLE | 200520 | 26ROXBURY | 1 | 115 | 226 | 190 | 96.29 | 104 | O66 NFTWR | PN_P2-3_PN-230-0014-12_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 204529 | 27GERMANTN | 1 | 138/115 | 227 | 453 | 102.73 | 103.85 | O66 NFTWR | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 204529 | 27GERMANTN | 1 | 138/115 | 227 | 453 | 102.73 | 103.85 | O66 NFTWR | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 204529 | 27GERMANTN | 1 | 138/115 | 227 | 453 | 102.73 | 103.84 | O66 NFTWR | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 99.92 | 103.82 | O66 NFTWR | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 99.84 | 103.73 | O66 NFTWR | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204530 | 27GERMANTN | 204529 | 27GERMANTN | 1 | 138/115 | 227 | 453 | 102.56 | 103.63 | O66 NFTWR | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200504 | 26CARLISLE | 200520 | 26ROXBURY | 1 | 115 | 226 | 190 | 96.28 | 103.59 | O66 NFTWR | PN_P1-3_PN-230-020A_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200504 | 26CARLISLE | 200520 | 26ROXBURY | 1 | 115 | 226 | 190 | 96.28 | 103.59 | O66 NFTWR | PN_P2-3_PN-230-0014-11_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200504 | 26CARLISLE | 200520 | 26ROXBURY | 1 | 115 | 226 | 190 | 96.21 | 103.57 | O66 NFTWR | PN_P2-2_PN-115-031_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208395 | FARO FF | 208396 | FARO | 1 | 69 | 229 | 270 | 100.47 | 103.4 | O66 NFTWR | BG_P4_5_GRCTN_2T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 221089 | WINDYED1 | 221090 | GLENARM2 | 1 | 115 | 232 | 222 | 98.1 | 103.01 | O66 NFTWR | BG_P4_5_RPHLRD05_15_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 101.08 | 102.95 | O66 NFTWR | BG_P1_2322_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 221089 | WINDYED1 | 221090 | GLENARM2 | 1 | 115 | 232 | 222 | 98 | 102.89 | O66 NFTWR | BG_P4_5_RPHLRD37_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 101.02 | 102.88 | O66 NFTWR | BG_P1_2310_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 101.03 | 102.85 | O66 NFTWR | BG_P4_5_NW2322_230-4_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 100.96 | 102.82 | O66 NFTWR | BG_P4_5_NW2310_230-5_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200099 | LAUS | 208045 | LAUS | 3 | 500/230 | 225/229 | 1200 | 100.65 | 102.24 | O66 NFTWR | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220972 | GRANITE1 | 1 | 230 | 232 | 829 | 103.51 | 102.17 | O66 NFTWR | BG_P4_5_NW230-4_2326_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 99.22 | 102.15 | O66 NFTWR | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 99.21 | 102.15 | O66 NFTWR | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 99.21 | 102.15 | O66 NFTWR | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220979 | NEAST317 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 103.17 | 101.84 | O66 NFTWR | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200099 | LAUS | 208045 | LAUS | 3 | 500/230 | 225/229 | 1200 | 100.31 | 101.74 | O66 NFTWR | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200099 | LAUS | 208045 | LAUS | 3 | 500/230 | 225/229 | 1200 | 100.31 | 101.74 | O66 NFTWR | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200099 | LAUS | 208045 | LAUS | 3 | 500/230 | 225/229 | 1200 | 100.3 | 101.73 | O66 NFTWR | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220979 | NEAST317 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 103.07 | 101.72 | O66 NFTWR | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220979 | NEAST317 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 103.07 | 101.72 | O66 NFTWR | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 221088 | WINDYED2 | 221100 | GLENARM1 | 1 | 115 | 232 | 353 | 99.55 | 101.67 | O66 NFTWR | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 99.73 | 101.63 | O66 NFTWR | BG_P4_5_NW230-2_2322_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220973 | GRANITE6 | 1 | 230 | 232 | 829 | 103.16 | 101.62 | O66 NFTWR | BG_P4_5_NW230-5_2311_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 99.63 | 101.52 | O66 NFTWR | BG_P4_5_NW2371_2310_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 99.63 | 101.52 | O66 NFTWR | BG_P4_5_NW230-3_2310_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208021 | MANO TR4 | 208133 | WHEM TR2 | 2 | 230 | 229 | 593 | 93.93 | 101.5 | O66 NFTWR | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200532 | 26ROXBURY | 200520 | 26ROXBURY | 2 | 138/115 | 226 | 435 | 89.02 | 101.21 | O66 NFTWR | AP_P2-3_PE-500-016_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200532 | 26ROXBURY | 200520 | 26ROXBURY | 2 | 138/115 | 226 | 435 | 89.16 | 101.04 | O66 NFTWR | AP_P2-3_PE-500-015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 98.19 | 100.77 | O66 NFTWR | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220964 | GRACETON | 221094 | GRACE.-1 | 1 | 230/115 | 232 | 510 | 103.48 | 100.67 | O66 NFTWR | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 2 | 500/230 | 225/232 | 2168 | 98 | 100.65 | O66 NFTWR | PJM_500_BG_P2_CNSTN_230-N_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 2 | 500/230 | 225/232 | 2168 | 98 | 100.65 | O66 NFTWR | BG_P1_CNSTN_500-2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 98.76 | 100.6 | O66 NFTWR | BG_P4_5_CNSTN_14_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 1 | 500/230 | 225/232 | 2168 | 97.89 | 100.54 | O66 NFTWR | BG_P1_CNSTN_500-4_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 1 | 500/230 | 225/232 | 2168 | 97.89 | 100.54 | O66 NFTWR | PJM_500_BG_P2_CNSTN_230-S_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200101 | VINCO | 200102 | AA1-076 MAIN | 1 | 500 | 225 | 999 | 103.01 | 100.54 | O66 NFTWR | AP_P2-3_WP-500-696_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220964 | GRACETON | 220999 | BAGLEY2 | 13 | 230 | 232 | 1795 | 99.88 | 100.52 | O66 NFTWR | BG_P1_2305_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220964 | GRACETON | 221000 | BAGLEY | 5 | 230 | 232 | 1795 | 99.88 | 100.52 | O66 NFTWR | BG_P1_2313_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200101 | VINCO | 200102 | AA1-076 MAIN | 1 | 500 | 225 | 999 | 103 | 100.51 | O66 NFTWR | AP_P2-3_WP-500-706T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200101 | VINCO | 200102 | AA1-076 MAIN | 1 | 500 | 225 | 999 | 103 | 100.5 | O66 NFTWR | AP_P2-3_WP-500-440T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200101 | VINCO | 200102 | AA1-076 MAIN | 1 | 500 | 225 | 999 | 103.01 | 100.5 | O66 NFTWR | AP_P2-3_WP-500-707T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220973 | GRANITE6 | 1 | 230 | 232 | 829 | 101.26 | 100.17 | O66 NFTWR | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208021 | MANO TR4 | 208133 | WHEM TR2 | 2 | 230 | 229 | 593 | 93.04 | 100.1 | O66 NFTWR | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208021 | MANO TR4 | 208133 | WHEM TR2 | 2 | 230 | 229 | 593 | 93.04 | 100.1 | O66 NFTWR | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208393 | FARO DC TIE | 208394 | PPL-BGE TIE | 1 | 115 | 229 | 302 | 99.45 | 100.09 | O66 NFTWR | PL_05_P71_000906_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208021 | MANO TR4 | 208133 | WHEM TR2 | 2 | 230 | 229 | 593 | 93.03 | 100.09 | O66 NFTWR | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220965 | NEAST339 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 100.9 | 100.07 | O66 NFTWR | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3464 | 168.7 | 162.68 | W1-006 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 154.22 | 158.81 | P28 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.7 | 157.82 | P28 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.7 | 157.82 | P28 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 152.53 | 157.49 | P28 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 162.31 | 155.06 | P28 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 149.17 | 153.84 | P28 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 156.27 | 151.11 | P28 | PN_P1-2_PN-500-010T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.98 | 150.18 | P28 | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.91 | 150.11 | P28 | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.59 | 148.93 | P28 | AP_P2-3_PE-500-016_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.65 | 148.9 | P28 | AP_P2-3_PE-500-015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.89 | 148.45 | P28 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.57 | 148.43 | P28 | PJM_500_BG_P4_5_CNSTN_L_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.69 | 148.26 | P28 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.72 | 148.25 | P28 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.44 | 148.05 | P28 | PECO_P4_NOTTI85_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.76 | 148.04 | P28 | AP_P1-2_WP-500-DRT17_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.76 | 148.04 | P28 | AP_P1-2_PE-500-001_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.38 | 148.03 | P28 | PECO_P1-2_220-08_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.71 | 147.97 | P28 | AP_P2-3_PE-500-018C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.32 | 147.97 | P28 | PECO_P4_COOPR125_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3464 | 167.92 | 161.91 | W1-029 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 151.5 | 144.77 | P28 | PECO_P4_PEACH025_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 151.44 | 144.74 | P28 | PECO_P1-2_PBTIE1_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 911 | 148.83 | 142.81 | P28 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 911 | 148.83 | 142.81 | P28 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 911 | 148.81 | 142.8 | P28 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 139.77 | 133.81 | P28 | PECO_P4_PEACH205_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 139.66 | 133.48 | P28 | PECO_P1-2_PBTIE2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 138.66 | 132.55 | P28 | PECO_P4_PEACH055_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 134.09 | 128.24 | P28 | PECO_P4_PEACH015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 132.7 | 126.85 | P28 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 123.61 | 118.21 | P28 | PECO_P4_PEACH225_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 98.91 | 102.55 | P28 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3464 | 167.95 | 161.94 | W4-005 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.34 | 157.46 | P59 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.33 | 157.46 | P59 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 161.84 | 154.61 | P59 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.5 | 148.06 | P59 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.29 | 147.87 | P59 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.32 | 147.86 | P59 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.05 | 147.66 | P59 | PECO_P4_NOTTI85_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.99 | 147.64 | P59 | PECO_P1-2_220-08_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.92 | 147.58 | P59 | PECO_P4_COOPR125_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 151.78 | 147.47 | P59 | AP_P2-3_PE-500-016_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 151.82 | 147.44 | P59 | AP_P2-3_PE-500-015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 151.05 | 144.33 | P59 | PECO_P4_PEACH025_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.93 | 144.25 | P59 | PECO_P1-2_PBTIE1_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 139.18 | 133.02 | P59 | PECO_P1-2_PBTIE2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 225.53 | 237.62 | Q01/Q03 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 223.55 | 237.62 | Q01/Q03 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 224.57 | 235.53 | Q01/Q03 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 222.58 | 235.52 | Q01/Q03 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 224.5 | 235.47 | Q01/Q03 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 222.52 | 235.47 | Q01/Q03 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 224.5 | 235.47 | Q01/Q03 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 222.51 | 235.47 | Q01/Q03 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 213.5 | 227.45 | Q01/Q03 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 212.56 | 225.41 | Q01/Q03 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 212.5 | 225.35 | Q01/Q03 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 212.5 | 225.35 | Q01/Q03 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 209.24 | 224.25 | Q01/Q03 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 208.31 | 222.19 | Q01/Q03 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 208.24 | 222.13 | Q01/Q03 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 208.24 | 222.13 | Q01/Q03 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 209.7 | 216.6 | Q01/Q03 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 207.72 | 216.59 | Q01/Q03 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 198.21 | 207.07 | Q01/Q03 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 193.95 | 203.71 | Q01/Q03 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 172.22 | 167.31 | Q01/Q03 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 171.24 | 165.93 | Q01/Q03 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 171.23 | 165.93 | Q01/Q03 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 171.22 | 165.92 | Q01/Q03 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 163.03 | 164.21 | Q01/Q03 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3464 | 168.15 | 162.14 | X2-022 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 161.13 | 161.13 | Q01/Q03 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 161.13 | 161.13 | Q01/Q03 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 161.12 | 161.12 | Q01/Q03 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 163.31 | 158.51 | Q01/Q03 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 153.09 | 157.46 | Q01/Q03 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 161.49 | 156.63 | Q01/Q03 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 161.49 | 156.62 | Q01/Q03 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 151.41 | 156.15 | Q01/Q03 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 160.73 | 153.54 | Q01/Q03 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 148.04 | 152.49 | Q01/Q03 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 903 | 143.85 | 151.5 | Q01/Q03 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 152.21 | 150.62 | Q01/Q03 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 155.09 | 149.94 | Q01/Q03 | PN_P1-2_PN-500-010T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 145.9 | 148.91 | Q01/Q03 | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 145.83 | 148.84 | Q01/Q03 | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 903 | 142.29 | 148.84 | Q01/Q03 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 903 | 142.29 | 148.83 | Q01/Q03 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 903 | 142.28 | 148.82 | Q01/Q03 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.61 | 147.81 | Q01/Q03 | AP_P2-3_PE-500-016_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.68 | 147.78 | Q01/Q03 | AP_P2-3_PE-500-015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.4 | 147.29 | Q01/Q03 | PJM_500_BG_P4_5_CNSTN_L_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.51 | 147.09 | Q01/Q03 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 142.79 | 146.93 | Q01/Q03 | AP_P1-2_WP-500-DRT17_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 142.79 | 146.93 | Q01/Q03 | AP_P1-2_PE-500-001_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.31 | 146.91 | Q01/Q03 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.33 | 146.89 | Q01/Q03 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 142.74 | 146.86 | Q01/Q03 | AP_P2-3_PE-500-018C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.07 | 146.7 | Q01/Q03 | PECO_P4_NOTTI85_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.01 | 146.68 | Q01/Q03 | PECO_P1-2_220-08_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 151.94 | 146.62 | Q01/Q03 | PECO_P4_COOPR125_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 145.97 | 146.4 | Q01/Q03 | BG_P7_GRCTN_CNSTN_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3464 | 168.18 | 162.17 | X2-060 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 149.86 | 143.2 | Q01/Q03 | PECO_P4_PEACH025_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 149.79 | 143.15 | Q01/Q03 | PECO_P1-2_PBTIE1_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 911 | 148.5 | 142.75 | Q01/Q03 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 911 | 147.54 | 141.5 | Q01/Q03 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 911 | 147.54 | 141.5 | Q01/Q03 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 911 | 147.52 | 141.49 | Q01/Q03 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204502 | 27JACKSON | 204514 | 27TMI | 1 | 230 | 227 | 781 | 132.33 | 140.87 | Q01/Q03 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204502 | 27JACKSON | 204514 | 27TMI | 1 | 230 | 227 | 781 | 132.54 | 140.83 | Q01/Q03 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204502 | 27JACKSON | 204514 | 27TMI | 1 | 230 | 227 | 781 | 132.53 | 140.83 | Q01/Q03 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204502 | 27JACKSON | 204514 | 27TMI | 1 | 230 | 227 | 781 | 132.52 | 140.82 | Q01/Q03 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 140.79 | 140.4 | Q01/Q03 | PJM_500_BG_P4_5_CNSTN_15_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 903 | 135.23 | 139.05 | Q01/Q03 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 1031 | 130.43 | 138.52 | Q01/Q03 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 1031 | 129.93 | 137.43 | Q01/Q03 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 1031 | 129.93 | 137.43 | Q01/Q03 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 1031 | 129.92 | 137.42 | Q01/Q03 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 911 | 139.69 | 134.79 | Q01/Q03 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 207923 | BRISREAC | 208132 | WHEM TR1 | 1 | 230 | 229 | 676 | 124.74 | 133.88 | Q01/Q03 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 207922 | BRIS | 207923 | BRISREAC | RX | 230 | 229 | 676 | 124.74 | 133.88 | Q01/Q03 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208078 | SAKR | 1 | 230 | 229 | 903 | 124.76 | 133.24 | Q01/Q03 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 138.3 | 132.39 | Q01/Q03 | PECO_P4_PEACH205_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 207922 | BRIS | 207923 | BRISREAC | RX | 230 | 229 | 676 | 123.98 | 132.33 | Q01/Q03 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 207923 | BRISREAC | 208132 | WHEM TR1 | 1 | 230 | 229 | 676 | 123.98 | 132.33 | Q01/Q03 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 207922 | BRIS | 207923 | BRISREAC | RX | 230 | 229 | 676 | 123.98 | 132.32 | Q01/Q03 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 207923 | BRISREAC | 208132 | WHEM TR1 | 1 | 230 | 229 | 676 | 123.98 | 132.32 | Q01/Q03 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 207922 | BRIS | 207923 | BRISREAC | RX | 230 | 229 | 676 | 123.96 | 132.32 | Q01/Q03 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 207923 | BRISREAC | 208132 | WHEM TR1 | 1 | 230 | 229 | 676 | 123.96 | 132.31 | Q01/Q03 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 138.13 | 132.01 | Q01/Q03 | PECO_P1-2_PBTIE2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208078 | SAKR | 1 | 230 | 229 | 903 | 124 | 131.87 | Q01/Q03 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208078 | SAKR | 1 | 230 | 229 | 903 | 124 | 131.87 | Q01/Q03 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208078 | SAKR | 1 | 230 | 229 | 903 | 124 | 131.86 | Q01/Q03 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 137.25 | 131.19 | Q01/Q03 | PECO_P4_PEACH055_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220972 | GRANITE1 | 1 | 230 | 232 | 829 | 134.51 | 130.61 | Q01/Q03 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204502 | 27JACKSON | 204514 | 27TMI | 1 | 230 | 227 | 781 | 124.9 | 130.38 | Q01/Q03 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220972 | GRANITE1 | 1 | 230 | 232 | 829 | 133.88 | 129.95 | Q01/Q03 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220972 | GRANITE1 | 1 | 230 | 232 | 829 | 133.88 | 129.95 | Q01/Q03 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 1031 | 124.34 | 128.74 | Q01/Q03 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220973 | GRANITE6 | 1 | 230 | 232 | 829 | 132.45 | 128.72 | Q01/Q03 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220973 | GRANITE6 | 1 | 230 | 232 | 829 | 131.85 | 128.1 | Q01/Q03 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220973 | GRANITE6 | 1 | 230 | 232 | 829 | 131.85 | 128.1 | Q01/Q03 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 126.73 | 127 | Q01/Q03 | BG_P7_GRCTN_CNSTN_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 124.75 | 127 | Q01/Q03 | BG_P7_GRCTN_CNSTN_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 128.62 | 126.95 | Q01/Q03 | DVP_P4-2: 514T595_SRT-SW |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 132.48 | 126.69 | Q01/Q03 | PECO_P4_PEACH015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208020 | MANO TR3 | 1 | 230 | 229 | 793 | 111.82 | 125.56 | Q01/Q03 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 131.21 | 125.43 | Q01/Q03 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 911 | 122.89 | 125.3 | Q01/Q03 | BG_P7_GRCTN_CNSTN_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220953 | HOWARD12 | 220972 | GRANITE1 | 1 | 230 | 232 | 772 | 129.2 | 125.29 | Q01/Q03 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 126.87 | 125.23 | Q01/Q03 | DVP_P4-2: 51482_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 126.87 | 125.09 | Q01/Q03 | DVP_P1-2: LN 514_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 126.87 | 125.09 | Q01/Q03 | AP_P1-2_PE-500-407T_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220954 | HOWARD32 | 220973 | GRANITE6 | 1 | 230 | 232 | 772 | 128.08 | 124.62 | Q01/Q03 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220953 | HOWARD12 | 220972 | GRANITE1 | 1 | 230 | 232 | 772 | 128.29 | 124.32 | Q01/Q03 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220953 | HOWARD12 | 220972 | GRANITE1 | 1 | 230 | 232 | 772 | 128.29 | 124.31 | Q01/Q03 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 207922 | BRIS | 207923 | BRISREAC | RX | 230 | 229 | 676 | 118.89 | 124.27 | Q01/Q03 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 207923 | BRISREAC | 208132 | WHEM TR1 | 1 | 230 | 229 | 676 | 118.89 | 124.27 | Q01/Q03 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208020 | MANO TR3 | 1 | 230 | 229 | 793 | 110.98 | 123.85 | Q01/Q03 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208020 | MANO TR3 | 1 | 230 | 229 | 793 | 110.98 | 123.85 | Q01/Q03 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208020 | MANO TR3 | 1 | 230 | 229 | 793 | 110.97 | 123.84 | Q01/Q03 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220954 | HOWARD32 | 220973 | GRANITE6 | 1 | 230 | 232 | 772 | 127.29 | 123.77 | Q01/Q03 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220954 | HOWARD32 | 220973 | GRANITE6 | 1 | 230 | 232 | 772 | 127.29 | 123.77 | Q01/Q03 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 117.51 | 122.26 | Q01/Q03 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 119.49 | 122.26 | Q01/Q03 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 117.33 | 122.04 | Q01/Q03 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 119.31 | 122.04 | Q01/Q03 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 119.31 | 122.04 | Q01/Q03 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 117.33 | 122.04 | Q01/Q03 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208078 | SAKR | 1 | 230 | 229 | 903 | 116.75 | 122 | Q01/Q03 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208031 | MLWD TR2 | 1 | 230 | 229 | 911 | 112.05 | 121.89 | Q01/Q03 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200025 | W CHAPEL | 1 | 500 | 225 | 1732 | 123.45 | 121.63 | Q01/Q03 | PEPCO_P4_PP41_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204512 | 27S.RDG | 204693 | 27BOONETOWN | 1 | 230 | 227 | 607 | 107.01 | 120.83 | Q01/Q03 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204512 | 27S.RDG | 204693 | 27BOONETOWN | 1 | 230 | 227 | 607 | 106.98 | 120.81 | Q01/Q03 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204512 | 27S.RDG | 204693 | 27BOONETOWN | 1 | 230 | 227 | 607 | 106.98 | 120.81 | Q01/Q03 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208031 | MLWD TR2 | 1 | 230 | 229 | 911 | 111.32 | 120.55 | Q01/Q03 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208031 | MLWD TR2 | 1 | 230 | 229 | 911 | 111.32 | 120.55 | Q01/Q03 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208031 | MLWD TR2 | 1 | 230 | 229 | 911 | 111.32 | 120.55 | Q01/Q03 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 118.1 | 120.35 | Q01/Q03 | BG_P7_GRCTN_CNSTN_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 118.64 | 119.18 | Q01/Q03 | PJM_500_BG_P4_5_CNSTN_15_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 116.65 | 119.18 | Q01/Q03 | PJM_500_BG_P4_5_CNSTN_15_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220965 | NEAST339 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 119.52 | 118.86 | Q01/Q03 | BG_P1_2315_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 911 | 117.83 | 118.82 | Q01/Q03 | PJM_500_BG_P4_5_CNSTN_15_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220965 | NEAST339 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 119.1 | 118.66 | Q01/Q03 | BG_P4_5_NEAST_17_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220965 | NEAST339 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 119.26 | 118.66 | Q01/Q03 | BG_P4_5_NEAST_15_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208131 | WHEM | 208132 | WHEM TR1 | 1 | 230 | 229 | 691 | 109 | 118.6 | Q01/Q03 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 114.47 | 118.17 | Q01/Q03 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220979 | NEAST317 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 118.6 | 118 | Q01/Q03 | BG_P1_2337_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 114.13 | 117.83 | Q01/Q03 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 114.11 | 117.77 | Q01/Q03 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 114.11 | 117.77 | Q01/Q03 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220979 | NEAST317 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 118.28 | 117.73 | Q01/Q03 | BG_P4_5_NEAST_39_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220979 | NEAST317 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 118.28 | 117.73 | Q01/Q03 | BG_P4_5_NEAST_37_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 113.78 | 117.43 | Q01/Q03 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 113.78 | 117.43 | Q01/Q03 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208131 | WHEM | 208132 | WHEM TR1 | 1 | 230 | 229 | 691 | 108.28 | 117.21 | Q01/Q03 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208131 | WHEM | 208132 | WHEM TR1 | 1 | 230 | 229 | 691 | 108.28 | 117.21 | Q01/Q03 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208131 | WHEM | 208132 | WHEM TR1 | 1 | 230 | 229 | 691 | 108.27 | 117.2 | Q01/Q03 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 122.13 | 116.79 | Q01/Q03 | PECO_P4_PEACH225_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 117.88 | 116.61 | Q01/Q03 | PL_04_P42_000564_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 117.88 | 116.61 | Q01/Q03 | PL_04_P12_000260_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 113.84 | 116.51 | Q01/Q03 | BG_P7_GRCTN_CNSTN_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 111.11 | 115.78 | Q01/Q03 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 110.93 | 115.58 | Q01/Q03 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 110.93 | 115.58 | Q01/Q03 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 117.04 | 115.2 | Q01/Q03 | AP_P2-3_PE-500-019C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 2 | 500/230 | 225/232 | 2168 | 109.46 | 114.77 | Q01/Q03 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 2 | 500/230 | 225/232 | 2168 | 109.29 | 114.56 | Q01/Q03 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 2 | 500/230 | 225/232 | 2168 | 109.29 | 114.56 | Q01/Q03 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 1 | 500/230 | 225/232 | 2168 | 109.23 | 114.53 | Q01/Q03 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 1 | 500/230 | 225/232 | 2168 | 109.06 | 114.32 | Q01/Q03 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 1 | 500/230 | 225/232 | 2168 | 109.06 | 114.32 | Q01/Q03 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220964 | GRACETON | 220999 | BAGLEY2 | 13 | 230 | 232 | 1795 | 113.24 | 114.26 | Q01/Q03 | BG_P4_5_GRCTN_3T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208020 | MANO TR3 | 1 | 230 | 229 | 793 | 103.81 | 113.46 | Q01/Q03 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204512 | 27S.RDG | 204693 | 27BOONETOWN | 1 | 230 | 227 | 607 | 105.23 | 113.41 | Q01/Q03 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208020 | MANO TR3 | 208031 | MLWD TR2 | 1 | 230 | 229 | 903 | 102.17 | 113.16 | Q01/Q03 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 110.28 | 112.86 | Q01/Q03 | PJM_500_BG_P4_5_CNSTN_15_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 113.35 | 112.19 | Q01/Q03 | BG_P4_5_CNSTN_14_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 106.85 | 111.96 | Q01/Q03 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208020 | MANO TR3 | 208031 | MLWD TR2 | 1 | 230 | 229 | 903 | 101.45 | 111.81 | Q01/Q03 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208020 | MANO TR3 | 208031 | MLWD TR2 | 1 | 230 | 229 | 903 | 101.45 | 111.8 | Q01/Q03 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208020 | MANO TR3 | 208031 | MLWD TR2 | 1 | 230 | 229 | 903 | 101.45 | 111.8 | Q01/Q03 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 106.68 | 111.75 | Q01/Q03 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 106.68 | 111.75 | Q01/Q03 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 2 | 500/230 | 225/232 | 2168 | 108.39 | 111.67 | Q01/Q03 | PJM_500_BG_P4_5_CNSTN_15_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208031 | MLWD TR2 | 1 | 230 | 229 | 911 | 104.58 | 111.17 | Q01/Q03 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220980 | RAPHAEL | 220999 | BAGLEY2 | 13 | 230 | 232 | 1795 | 108.83 | 111.02 | Q01/Q03 | BG_P4_5_GRCTN_3T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 106.29 | 111.02 | Q01/Q03 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 106.16 | 110.88 | Q01/Q03 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208131 | WHEM | 208133 | WHEM TR2 | 1 | 230 | 229 | 691 | 101.48 | 110.02 | Q01/Q03 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208131 | WHEM | 208132 | WHEM TR1 | 1 | 230 | 229 | 691 | 103.5 | 109.76 | Q01/Q03 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 106.03 | 109.16 | Q01/Q03 | PJM_500_BG_P4_5_CNSTN_15_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208131 | WHEM | 208133 | WHEM TR2 | 1 | 230 | 229 | 691 | 100.76 | 108.68 | Q01/Q03 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208131 | WHEM | 208133 | WHEM TR2 | 1 | 230 | 229 | 691 | 100.76 | 108.68 | Q01/Q03 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208131 | WHEM | 208133 | WHEM TR2 | 1 | 230 | 229 | 691 | 100.75 | 108.67 | Q01/Q03 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220973 | GRANITE6 | 1 | 230 | 232 | 829 | 108.59 | 107.28 | Q01/Q03 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220965 | NEAST339 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 108.07 | 106.68 | Q01/Q03 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220965 | NEAST339 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 107.97 | 106.56 | Q01/Q03 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220965 | NEAST339 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 107.97 | 106.56 | Q01/Q03 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220972 | GRANITE1 | 1 | 230 | 232 | 829 | 107.72 | 106.19 | Q01/Q03 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 101.41 | 105.55 | Q01/Q03 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 101.33 | 105.46 | Q01/Q03 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200099 | LAUS | 208045 | LAUS | 3 | 500/230 | 225/229 | 1200 | 103.05 | 104.81 | Q01/Q03 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208021 | MANO TR4 | 208133 | WHEM TR2 | 2 | 230 | 229 | 593 | 95.98 | 104.63 | Q01/Q03 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 102.53 | 104.53 | Q01/Q03 | BG_P1_2322_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 102.46 | 104.45 | Q01/Q03 | BG_P1_2310_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 102.47 | 104.42 | Q01/Q03 | BG_P4_5_NW2322_230-4_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 102.4 | 104.38 | Q01/Q03 | BG_P4_5_NW2310_230-5_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220972 | GRANITE1 | 1 | 230 | 232 | 829 | 105.63 | 104.3 | Q01/Q03 | BG_P4_5_NW230-4_2326_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200099 | LAUS | 208045 | LAUS | 3 | 500/230 | 225/229 | 1200 | 102.74 | 104.27 | Q01/Q03 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200099 | LAUS | 208045 | LAUS | 3 | 500/230 | 225/229 | 1200 | 102.74 | 104.27 | Q01/Q03 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200099 | LAUS | 208045 | LAUS | 3 | 500/230 | 225/229 | 1200 | 102.73 | 104.26 | Q01/Q03 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220973 | GRANITE6 | 1 | 230 | 232 | 829 | 105.3 | 103.76 | Q01/Q03 | BG_P4_5_NW230-5_2311_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220979 | NEAST317 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 104.97 | 103.64 | Q01/Q03 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220979 | NEAST317 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 104.87 | 103.52 | Q01/Q03 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220979 | NEAST317 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 104.87 | 103.52 | Q01/Q03 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 99.59 | 103.38 | Q01/Q03 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 99.59 | 103.37 | Q01/Q03 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 99.58 | 103.37 | Q01/Q03 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208021 | MANO TR4 | 208133 | WHEM TR2 | 2 | 230 | 229 | 593 | 95.16 | 103.29 | Q01/Q03 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208021 | MANO TR4 | 208133 | WHEM TR2 | 2 | 230 | 229 | 593 | 95.16 | 103.29 | Q01/Q03 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208021 | MANO TR4 | 208133 | WHEM TR2 | 2 | 230 | 229 | 593 | 95.15 | 103.28 | Q01/Q03 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 101.13 | 103.16 | Q01/Q03 | BG_P4_5_NW230-2_2322_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 101.03 | 103.05 | Q01/Q03 | BG_P4_5_NW2371_2310_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 101.03 | 103.05 | Q01/Q03 | BG_P4_5_NW230-3_2310_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208020 | MANO TR3 | 208031 | MLWD TR2 | 1 | 230 | 229 | 903 | 95.09 | 102.7 | Q01/Q03 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220973 | GRANITE6 | 1 | 230 | 232 | 829 | 103.29 | 102.23 | Q01/Q03 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 100.15 | 102.11 | Q01/Q03 | BG_P4_5_CNSTN_14_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220964 | GRACETON | 220999 | BAGLEY2 | 13 | 230 | 232 | 1795 | 101.31 | 102.05 | Q01/Q03 | BG_P1_2305_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220964 | GRACETON | 221000 | BAGLEY | 5 | 230 | 232 | 1795 | 101.31 | 102.05 | Q01/Q03 | BG_P1_2313_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 98.64 | 102.05 | Q01/Q03 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220965 | NEAST339 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 102.54 | 101.84 | Q01/Q03 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220965 | NEAST339 | 220977 | RIV2339 | 1 | 230 | 232 | 991 | 103.11 | 101.71 | Q01/Q03 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220966 | RIV2317 | 220979 | NEAST317 | 1 | 230 | 232 | 940 | 102.71 | 101.69 | Q01/Q03 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220965 | NEAST339 | 220977 | RIV2339 | 1 | 230 | 232 | 991 | 103.07 | 101.65 | Q01/Q03 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220965 | NEAST339 | 220977 | RIV2339 | 1 | 230 | 232 | 991 | 103.07 | 101.65 | Q01/Q03 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 2 | 500/230 | 225/232 | 2168 | 98.91 | 101.65 | Q01/Q03 | PJM_500_BG_P2_CNSTN_230-N_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 2 | 500/230 | 225/232 | 2168 | 98.91 | 101.65 | Q01/Q03 | BG_P1_CNSTN_500-2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220966 | RIV2317 | 220979 | NEAST317 | 1 | 230 | 232 | 940 | 102.66 | 101.63 | Q01/Q03 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220966 | RIV2317 | 220979 | NEAST317 | 1 | 230 | 232 | 940 | 102.66 | 101.63 | Q01/Q03 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 1 | 500/230 | 225/232 | 2168 | 98.8 | 101.54 | Q01/Q03 | PJM_500_BG_P2_CNSTN_230-S_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 1 | 500/230 | 225/232 | 2168 | 98.8 | 101.54 | Q01/Q03 | BG_P1_CNSTN_500-4_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208131 | WHEM | 208133 | WHEM TR2 | 1 | 230 | 229 | 691 | 95.99 | 101.52 | Q01/Q03 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220972 | GRANITE1 | 1 | 230 | 232 | 829 | 102.69 | 101.46 | Q01/Q03 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 98.76 | 100.73 | Q01/Q03 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 223960 | BRG 1T 230 | 1 | 500/230 | 225/233 | 1498 | 100.08 | 100.46 | Q01/Q03 | PEPCO_P4_PP41_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3464 | 168.66 | 162.64 | X3-008 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 154.23 | 158.82 | Q27 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.72 | 157.84 | Q27 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.72 | 157.84 | Q27 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 152.54 | 157.5 | Q27 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 162.36 | 155.11 | Q27 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 149.18 | 153.85 | Q27 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 156.29 | 151.13 | Q27 | PN_P1-2_PN-500-010T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.99 | 150.19 | Q27 | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.92 | 150.12 | Q27 | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.59 | 148.93 | Q27 | AP_P2-3_PE-500-016_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.66 | 148.9 | Q27 | AP_P2-3_PE-500-015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.94 | 148.49 | Q27 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.59 | 148.45 | Q27 | PJM_500_BG_P4_5_CNSTN_L_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.74 | 148.3 | Q27 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.76 | 148.29 | Q27 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.49 | 148.09 | Q27 | PECO_P4_NOTTI85_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.43 | 148.08 | Q27 | PECO_P1-2_220-08_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.77 | 148.05 | Q27 | AP_P1-2_PE-500-001_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.77 | 148.05 | Q27 | AP_P1-2_WP-500-DRT17_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.36 | 148.01 | Q27 | PECO_P4_COOPR125_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.72 | 147.98 | Q27 | AP_P2-3_PE-500-018C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3464 | 168.64 | 162.62 | Y3-058 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 151.54 | 144.81 | Q27 | PECO_P4_PEACH025_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 151.49 | 144.79 | Q27 | PECO_P1-2_PBTIE1_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 139.82 | 133.86 | Q27 | PECO_P4_PEACH205_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 139.7 | 133.52 | Q27 | PECO_P1-2_PBTIE2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 138.71 | 132.6 | Q27 | PECO_P4_PEACH055_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 134.13 | 128.29 | Q27 | PECO_P4_PEACH015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 132.75 | 126.89 | Q27 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 123.66 | 118.25 | Q27 | PECO_P4_PEACH225_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 225.71 | 237.28 | Q57 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 223.71 | 237.28 | Q57 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 213.65 | 227.12 | Q57 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 213.59 | 227.06 | Q57 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 213.59 | 227.06 | Q57 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 209.39 | 223.91 | Q57 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 209.33 | 223.85 | Q57 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 209.33 | 223.85 | Q57 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3464 | 167.68 | 161.68 | Z1-036 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 153.69 | 158.18 | Q57 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.14 | 157.28 | Q57 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.14 | 157.28 | Q57 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 152 | 156.86 | Q57 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 161.58 | 154.38 | Q57 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 148.64 | 153.2 | Q57 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 155.72 | 150.58 | Q57 | PN_P1-2_PN-500-010T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.48 | 149.58 | Q57 | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.41 | 149.51 | Q57 | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.12 | 148.39 | Q57 | AP_P2-3_PE-500-016_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.19 | 148.36 | Q57 | AP_P2-3_PE-500-015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.03 | 147.91 | Q57 | PJM_500_BG_P4_5_CNSTN_L_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.27 | 147.85 | Q57 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.07 | 147.66 | Q57 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.1 | 147.65 | Q57 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.3 | 147.51 | Q57 | AP_P1-2_PE-500-001_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.3 | 147.51 | Q57 | AP_P1-2_WP-500-DRT17_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.83 | 147.45 | Q57 | PECO_P4_NOTTI85_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.25 | 147.44 | Q57 | AP_P2-3_PE-500-018C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.77 | 147.43 | Q57 | PECO_P1-2_220-08_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.7 | 147.37 | Q57 | PECO_P4_COOPR125_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3464 | 168.12 | 162.11 | Z2-087 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.78 | 144.08 | Q57 | PECO_P4_PEACH025_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.67 | 144.01 | Q57 | PECO_P1-2_PBTIE1_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 139.06 | 133.14 | Q57 | PECO_P4_PEACH205_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 138.94 | 132.8 | Q57 | PECO_P1-2_PBTIE2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 138.01 | 131.93 | Q57 | PECO_P4_PEACH055_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 133.32 | 127.51 | Q57 | PECO_P4_PEACH015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 132 | 126.19 | Q57 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 122.9 | 117.54 | Q57 | PECO_P4_PEACH225_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 3464 | 168.07 | 162.06 | Z2-088 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 153.82 | 158.33 | R49 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.28 | 157.41 | R49 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.28 | 157.41 | R49 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 152.13 | 157 | R49 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 161.76 | 154.54 | R49 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 148.76 | 153.35 | R49 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 155.85 | 150.7 | R49 | PN_P1-2_PN-500-010T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.16 | 148.04 | R49 | PJM_500_BG_P4_5_CNSTN_L_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.43 | 147.99 | R49 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.23 | 147.81 | R49 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.25 | 147.79 | R49 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.98 | 147.6 | R49 | PECO_P4_NOTTI85_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.92 | 147.58 | R49 | PECO_P1-2_220-08_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.86 | 147.51 | R49 | PECO_P4_COOPR125_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 521 | 108.96 | 111.98 | AA1-102 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 142.88 | 147 | R49 | AP_P2-3_PE-500-014_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 142.88 | 146.99 | R49 | AP_P2-3_WP-500-466_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 142.88 | 146.99 | R49 | AP_P1-2_WP-500-006_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 142.88 | 146.99 | R49 | AP_P1-2_PE-500-004_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 142.88 | 146.99 | R49 | AP_P2-3_WP-500-DRT19_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.96 | 144.25 | R49 | PECO_P4_PEACH025_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.85 | 144.17 | R49 | PECO_P1-2_PBTIE1_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 141.2 | 143.95 | R49 | BG_P7_GRNITE_HIRDG_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 138.97 | 141.26 | R49 | AP_P2-3_WP-500-465_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 139.23 | 133.29 | R49 | PECO_P4_PEACH205_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 139.11 | 132.95 | R49 | PECO_P1-2_PBTIE2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 138.17 | 132.07 | R49 | PECO_P4_PEACH055_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 133.49 | 127.67 | R49 | PECO_P4_PEACH015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 132.16 | 126.34 | R49 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 123.07 | 117.69 | R49 | PECO_P4_PEACH225_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 225.52 | 237.01 | R60 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 223.51 | 237.01 | R60 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 225.45 | 236.95 | R60 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 223.45 | 236.95 | R60 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 225.45 | 236.95 | R60 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 223.45 | 236.95 | R60 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 213.47 | 226.85 | R60 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 213.4 | 226.79 | R60 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 213.4 | 226.79 | R60 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 209.21 | 223.64 | R60 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 209.15 | 223.58 | R60 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 209.14 | 223.58 | R60 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 208.62 | 217.83 | R60 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 210.63 | 217.82 | R60 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 199.09 | 208.26 | R60 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 194.83 | 204.91 | R60 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 172.8 | 167.87 | R60 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 163.65 | 165.02 | R60 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 161.78 | 161.92 | R60 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 161.78 | 161.92 | R60 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 161.77 | 161.91 | R60 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 521 | 108.83 | 111.84 | AB1-056 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 153.6 | 158.07 | R60 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.04 | 157.17 | R60 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.04 | 157.17 | R60 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 151.91 | 156.75 | R60 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 161.44 | 154.23 | R60 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 148.55 | 153.1 | R60 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 155.62 | 150.47 | R60 | PN_P1-2_PN-500-010T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.39 | 149.48 | R60 | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.32 | 149.41 | R60 | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.05 | 148.32 | R60 | AP_P2-3_PE-500-016_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.12 | 148.29 | R60 | AP_P2-3_PE-500-015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.93 | 147.81 | R60 | PJM_500_BG_P4_5_CNSTN_L_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.14 | 147.71 | R60 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.94 | 147.53 | R60 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.97 | 147.51 | R60 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.23 | 147.43 | R60 | AP_P1-2_PE-500-001_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.23 | 147.43 | R60 | AP_P1-2_WP-500-DRT17_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.18 | 147.36 | R60 | AP_P2-3_PE-500-018C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.7 | 147.32 | R60 | PECO_P4_NOTTI85_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.64 | 147.3 | R60 | PECO_P1-2_220-08_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.57 | 147.23 | R60 | PECO_P4_COOPR125_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 521 | 108.57 | 111.56 | AB2-036 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.62 | 143.92 | R60 | PECO_P4_PEACH025_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.52 | 143.86 | R60 | PECO_P1-2_PBTIE1_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 911 | 149.05 | 143.22 | R60 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 1031 | 130.35 | 138.18 | R60 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 1031 | 130.35 | 138.18 | R60 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 1031 | 130.34 | 138.17 | R60 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 138.94 | 133.01 | R60 | PECO_P4_PEACH205_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 138.81 | 132.66 | R60 | PECO_P1-2_PBTIE2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208078 | SAKR | 1 | 230 | 229 | 903 | 124.52 | 132.61 | R60 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208078 | SAKR | 1 | 230 | 229 | 903 | 124.52 | 132.61 | R60 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208078 | SAKR | 1 | 230 | 229 | 903 | 124.52 | 132.61 | R60 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 137.88 | 131.8 | R60 | PECO_P4_PEACH055_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 133.18 | 127.37 | R60 | PECO_P4_PEACH015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 131.87 | 126.06 | R60 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208020 | MANO TR3 | 1 | 230 | 229 | 793 | 111.5 | 124.7 | R60 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208020 | MANO TR3 | 1 | 230 | 229 | 793 | 111.5 | 124.7 | R60 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208020 | MANO TR3 | 1 | 230 | 229 | 793 | 111.5 | 124.7 | R60 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 122.78 | 117.41 | R60 | PECO_P4_PEACH225_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 521 | 109.55 | 112.63 | AB2-037 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.62 | 157.74 | RUTGERS | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.62 | 157.74 | RUTGERS | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 162.22 | 154.98 | RUTGERS | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 156.19 | 151.03 | RUTGERS | PN_P1-2_PN-500-010T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.83 | 148.38 | RUTGERS | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.49 | 148.35 | RUTGERS | PJM_500_BG_P4_5_CNSTN_L_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.63 | 148.2 | RUTGERS | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.65 | 148.18 | RUTGERS | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.38 | 147.99 | RUTGERS | PECO_P4_NOTTI85_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.32 | 147.97 | RUTGERS | PECO_P1-2_220-08_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.26 | 147.91 | RUTGERS | PECO_P4_COOPR125_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 151.46 | 144.73 | RUTGERS | PECO_P4_PEACH025_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 151.34 | 144.64 | RUTGERS | PECO_P1-2_PBTIE1_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 139.05 | 141.26 | RUTGERS | AP_P2-3_WP-500-DRT45_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 139.05 | 141.26 | RUTGERS | AP_P1-2_WP-500-008_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 137.44 | 139.48 | RUTGERS | AP_P2-3_WP-500-696_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 137.44 | 139.48 | RUTGERS | AP_P2-3_WP-500-707T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 137.46 | 139.47 | RUTGERS | AP_P2-3_WP-500-706T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 137.41 | 139.45 | RUTGERS | AP_P2-3_WP-500-440T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 136.95 | 139.2 | RUTGERS | PN_P2-3_PN-500-004-DRT-002_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 136.95 | 139.2 | RUTGERS | PN_P2-3_PN-500-DRT32_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 131.89 | 133.92 | RUTGERS | PL_10_P42_100570_A_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 131.89 | 133.92 | RUTGERS | PL_10_P42_100570_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 139.65 | 133.7 | RUTGERS | PECO_P4_PEACH205_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 139.56 | 133.39 | RUTGERS | PECO_P1-2_PBTIE2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 138.58 | 132.47 | RUTGERS | PECO_P4_PEACH055_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 133.98 | 128.13 | RUTGERS | PECO_P4_PEACH015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 132.6 | 126.75 | RUTGERS | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 123.51 | 118.12 | RUTGERS | PECO_P4_PEACH225_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 521 | 105.38 | 108.08 | AC1-158 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 153.74 | 158.24 | S06 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.21 | 157.33 | S06 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.2 | 157.33 | S06 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 152.05 | 156.92 | S06 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 161.67 | 154.44 | S06 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 148.69 | 153.27 | S06 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 155.78 | 150.63 | S06 | PN_P1-2_PN-500-010T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.53 | 149.64 | S06 | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.46 | 149.57 | S06 | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.17 | 148.44 | S06 | AP_P2-3_PE-500-016_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.24 | 148.41 | S06 | AP_P2-3_PE-500-015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.09 | 147.96 | S06 | PJM_500_BG_P4_5_CNSTN_L_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.34 | 147.91 | S06 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.14 | 147.72 | S06 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.17 | 147.71 | S06 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.35 | 147.56 | S06 | AP_P1-2_PE-500-001_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.35 | 147.56 | S06 | AP_P1-2_WP-500-DRT17_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.9 | 147.51 | S06 | PECO_P4_NOTTI85_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.84 | 147.5 | S06 | PECO_P1-2_220-08_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.3 | 147.49 | S06 | AP_P2-3_PE-500-018C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.77 | 147.43 | S06 | PECO_P4_COOPR125_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 521 | 108.98 | 112.01 | AE1-104 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.86 | 144.15 | S06 | PECO_P4_PEACH025_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.75 | 144.08 | S06 | PECO_P1-2_PBTIE1_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 139.14 | 133.2 | S06 | PECO_P4_PEACH205_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 139.02 | 132.87 | S06 | PECO_P1-2_PBTIE2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 138.08 | 131.99 | S06 | PECO_P4_PEACH055_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 133.4 | 127.58 | S06 | PECO_P4_PEACH015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 132.07 | 126.25 | S06 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 122.98 | 117.61 | S06 | PECO_P4_PEACH225_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 151 | 146.64 | S14 | AP_P2-3_WP-500-466_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 151 | 146.64 | S14 | AP_P2-3_WP-500-DRT19_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 151 | 146.64 | S14 | AP_P1-2_WP-500-006_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 151 | 146.64 | S14 | AP_P1-2_PE-500-004_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 151 | 146.64 | S14 | AP_P2-3_PE-500-014_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 145.12 | 139.96 | S14 | AP_P7-1_PE-138-012A_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 521 | 108.75 | 111.76 | AE1-229 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 153.77 | 158.27 | S36 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.24 | 157.36 | S36 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.24 | 157.36 | S36 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 152.08 | 156.95 | S36 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 161.71 | 154.48 | S36 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 148.72 | 153.3 | S36 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 155.81 | 150.66 | S36 | PN_P1-2_PN-500-010T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.55 | 149.67 | S36 | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.48 | 149.6 | S36 | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.19 | 148.47 | S36 | AP_P2-3_PE-500-016_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.26 | 148.44 | S36 | AP_P2-3_PE-500-015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.12 | 147.99 | S36 | PJM_500_BG_P4_5_CNSTN_L_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.38 | 147.94 | S36 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.18 | 147.76 | S36 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.2 | 147.74 | S36 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.37 | 147.59 | S36 | AP_P1-2_PE-500-001_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.37 | 147.59 | S36 | AP_P1-2_WP-500-DRT17_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.93 | 147.55 | S36 | PECO_P4_NOTTI85_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.87 | 147.53 | S36 | PECO_P1-2_220-08_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.32 | 147.52 | S36 | AP_P2-3_PE-500-018C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.81 | 147.47 | S36 | PECO_P4_COOPR125_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 521 | 109.9 | 113.02 | AE2-000 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.91 | 144.2 | S36 | PECO_P4_PEACH025_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.79 | 144.12 | S36 | PECO_P1-2_PBTIE1_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 139.18 | 133.24 | S36 | PECO_P4_PEACH205_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 139.06 | 132.9 | S36 | PECO_P1-2_PBTIE2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 138.12 | 132.03 | S36 | PECO_P4_PEACH055_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 133.44 | 127.62 | S36 | PECO_P4_PEACH015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 132.11 | 126.29 | S36 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204512 | 27S.RDG | 204693 | 27BOONETOWN | 1 | 230 | 227 | 607 | 107.67 | 123.42 | S36 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 123.01 | 117.64 | S36 | PECO_P4_PEACH225_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 521 | 109.59 | 112.68 | AE2-020 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.31 | 157.44 | S71 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.31 | 157.44 | S71 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 161.81 | 154.58 | S71 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 155.89 | 150.73 | S71 | PN_P1-2_PN-500-010T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.2 | 148.07 | S71 | PJM_500_BG_P4_5_CNSTN_L_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.47 | 148.03 | S71 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.27 | 147.84 | S71 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.29 | 147.83 | S71 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.02 | 147.63 | S71 | PECO_P4_NOTTI85_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.96 | 147.62 | S71 | PECO_P1-2_220-08_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.9 | 147.55 | S71 | PECO_P4_COOPR125_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 151.01 | 144.3 | S71 | PECO_P4_PEACH025_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.89 | 144.22 | S71 | PECO_P1-2_PBTIE1_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 138.99 | 141.29 | S71 | AP_P2-2_WP-500-DRT16_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 138.99 | 141.29 | S71 | AP_P2-3_WP-500-465_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 138.99 | 141.29 | S71 | AP_P1-2_WP-500-005A_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 138.99 | 141.29 | S71 | AP_P2-3_WP-500-DRT20_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 138.99 | 141.29 | S71 | AP_P1-2_WP-500-DRT21_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 138.76 | 140.93 | S71 | AP_P2-3_WP-500-DRT45_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 138.76 | 140.93 | S71 | AP_P1-2_WP-500-008_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 137.18 | 139.14 | S71 | AP_P2-3_WP-500-706T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 136.68 | 138.88 | S71 | PN_P2-3_PN-500-004-DRT-002_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 136.68 | 138.88 | S71 | PN_P2-3_PN-500-DRT32_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 139.27 | 133.32 | S71 | PECO_P4_PEACH205_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 139.15 | 132.99 | S71 | PECO_P1-2_PBTIE2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 138.2 | 132.11 | S71 | PECO_P4_PEACH055_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 133.54 | 127.71 | S71 | PECO_P4_PEACH015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 132.2 | 126.38 | S71 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 123.11 | 117.73 | S71 | PECO_P4_PEACH225_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 521 | 109.59 | 112.68 | AE2-021 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 154.2 | 158.79 | SALEM G3 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.74 | 157.86 | SALEM G3 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.74 | 157.86 | SALEM G3 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 152.51 | 157.46 | SALEM G3 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 162.4 | 155.15 | SALEM G3 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 149.15 | 153.81 | SALEM G3 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 156.31 | 151.15 | SALEM G3 | PN_P1-2_PN-500-010T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.97 | 150.16 | SALEM G3 | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.9 | 150.09 | SALEM G3 | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.57 | 148.9 | SALEM G3 | AP_P2-3_PE-500-016_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.63 | 148.87 | SALEM G3 | AP_P2-3_PE-500-015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.97 | 148.53 | SALEM G3 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.6 | 148.46 | SALEM G3 | PJM_500_BG_P4_5_CNSTN_L_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.77 | 148.34 | SALEM G3 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.8 | 148.33 | SALEM G3 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.53 | 148.13 | SALEM G3 | PECO_P4_NOTTI85_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.47 | 148.11 | SALEM G3 | PECO_P1-2_220-08_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.4 | 148.05 | SALEM G3 | PECO_P4_COOPR125_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.74 | 148.02 | SALEM G3 | AP_P1-2_PE-500-001_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.74 | 148.02 | SALEM G3 | AP_P1-2_WP-500-DRT17_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.69 | 147.95 | SALEM G3 | AP_P2-3_PE-500-018C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 521 | 108.61 | 111.61 | AE2-022 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 151.71 | 144.97 | SALEM G3 | PECO_P4_PEACH025_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 151.53 | 144.83 | SALEM G3 | PECO_P1-2_PBTIE1_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 139.75 | 133.79 | SALEM G3 | PECO_P4_PEACH205_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 139.74 | 133.56 | SALEM G3 | PECO_P1-2_PBTIE2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 138.77 | 132.66 | SALEM G3 | PECO_P4_PEACH055_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 134.17 | 128.32 | SALEM G3 | PECO_P4_PEACH015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 132.78 | 126.92 | SALEM G3 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 123.69 | 118.29 | SALEM G3 | PECO_P4_PEACH225_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 521 | 114.59 | 118.18 | AG2-055 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 154.17 | 158.75 | SEWAREN_IM | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.67 | 157.79 | SEWAREN_IM | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.67 | 157.79 | SEWAREN_IM | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 152.48 | 157.42 | SEWAREN_IM | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 162.3 | 155.05 | SEWAREN_IM | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 149.11 | 153.77 | SEWAREN_IM | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 156.24 | 151.09 | SEWAREN_IM | PN_P1-2_PN-500-010T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.93 | 150.12 | SEWAREN_IM | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.86 | 150.05 | SEWAREN_IM | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.54 | 148.87 | SEWAREN_IM | AP_P2-3_PE-500-016_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.6 | 148.84 | SEWAREN_IM | AP_P2-3_PE-500-015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.89 | 148.45 | SEWAREN_IM | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.54 | 148.41 | SEWAREN_IM | PJM_500_BG_P4_5_CNSTN_L_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.69 | 148.26 | SEWAREN_IM | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.72 | 148.25 | SEWAREN_IM | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.45 | 148.05 | SEWAREN_IM | PECO_P4_NOTTI85_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.39 | 148.03 | SEWAREN_IM | PECO_P1-2_220-08_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.71 | 147.98 | SEWAREN_IM | AP_P1-2_WP-500-DRT17_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.71 | 147.98 | SEWAREN_IM | AP_P1-2_PE-500-001_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.32 | 147.97 | SEWAREN_IM | PECO_P4_COOPR125_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.66 | 147.91 | SEWAREN_IM | AP_P2-3_PE-500-018C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 521 | 103.65 | 106.21 | O66 NFTWR | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 151.55 | 144.81 | SEWAREN_IM | PECO_P4_PEACH025_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 151.43 | 144.73 | SEWAREN_IM | PECO_P1-2_PBTIE1_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 139.73 | 133.77 | SEWAREN_IM | PECO_P4_PEACH205_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 139.64 | 133.47 | SEWAREN_IM | PECO_P1-2_PBTIE2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 138.65 | 132.54 | SEWAREN_IM | PECO_P4_PEACH055_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 134.06 | 128.22 | SEWAREN_IM | PECO_P4_PEACH015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 132.68 | 126.83 | SEWAREN_IM | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 123.59 | 118.19 | SEWAREN_IM | PECO_P4_PEACH225_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208393 | FARO DC TIE | 208395 | FARO FF | 1 | 115/69 | 229 | 96.9 | 114.35 | 115.88 | AE1-226 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 153.74 | 158.24 | T126 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.21 | 157.33 | T126 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.2 | 157.33 | T126 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 152.05 | 156.92 | T126 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 161.67 | 154.44 | T126 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 148.69 | 153.27 | T126 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 155.78 | 150.63 | T126 | PN_P1-2_PN-500-010T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.53 | 149.64 | T126 | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.46 | 149.57 | T126 | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.17 | 148.44 | T126 | AP_P2-3_PE-500-016_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.24 | 148.41 | T126 | AP_P2-3_PE-500-015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.09 | 147.96 | T126 | PJM_500_BG_P4_5_CNSTN_L_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.34 | 147.91 | T126 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.14 | 147.72 | T126 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.17 | 147.71 | T126 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.35 | 147.56 | T126 | AP_P1-2_WP-500-DRT17_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.35 | 147.56 | T126 | AP_P1-2_PE-500-001_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.9 | 147.51 | T126 | PECO_P4_NOTTI85_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.84 | 147.5 | T126 | PECO_P1-2_220-08_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.3 | 147.49 | T126 | AP_P2-3_PE-500-018C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.77 | 147.43 | T126 | PECO_P4_COOPR125_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208393 | FARO DC TIE | 208395 | FARO FF | 2 | 115/69 | 229 | 102.9 | 107.69 | 109.12 | AE1-226 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.86 | 144.15 | T126 | PECO_P4_PEACH025_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.75 | 144.08 | T126 | PECO_P1-2_PBTIE1_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 139.14 | 133.2 | T126 | PECO_P4_PEACH205_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 139.02 | 132.87 | T126 | PECO_P1-2_PBTIE2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 138.08 | 131.99 | T126 | PECO_P4_PEACH055_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 133.4 | 127.58 | T126 | PECO_P4_PEACH015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 132.07 | 126.25 | T126 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 122.98 | 117.61 | T126 | PECO_P4_PEACH225_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208393 | FARO DC TIE | 208395 | FARO FF | 1 | 115/69 | 229 | 96.9 | 113.75 | 115.29 | AG2-055 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 153.74 | 158.24 | T127 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.21 | 157.33 | T127 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.21 | 157.33 | T127 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 152.06 | 156.92 | T127 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 161.67 | 154.45 | T127 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 148.69 | 153.27 | T127 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 155.78 | 150.63 | T127 | PN_P1-2_PN-500-010T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.53 | 149.65 | T127 | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.46 | 149.57 | T127 | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.17 | 148.45 | T127 | AP_P2-3_PE-500-016_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.24 | 148.42 | T127 | AP_P2-3_PE-500-015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.09 | 147.97 | T127 | PJM_500_BG_P4_5_CNSTN_L_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.35 | 147.91 | T127 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.14 | 147.72 | T127 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.17 | 147.71 | T127 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.35 | 147.56 | T127 | AP_P1-2_PE-500-001_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.35 | 147.56 | T127 | AP_P1-2_WP-500-DRT17_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.9 | 147.51 | T127 | PECO_P4_NOTTI85_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.84 | 147.5 | T127 | PECO_P1-2_220-08_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.3 | 147.49 | T127 | AP_P2-3_PE-500-018C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.77 | 147.43 | T127 | PECO_P4_COOPR125_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208393 | FARO DC TIE | 208395 | FARO FF | 2 | 115/69 | 229 | 102.9 | 107.13 | 108.57 | AG2-055 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.87 | 144.16 | T127 | PECO_P4_PEACH025_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.75 | 144.08 | T127 | PECO_P1-2_PBTIE1_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 139.14 | 133.2 | T127 | PECO_P4_PEACH205_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 139.02 | 132.87 | T127 | PECO_P1-2_PBTIE2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 138.08 | 131.99 | T127 | PECO_P4_PEACH055_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 133.4 | 127.58 | T127 | PECO_P4_PEACH015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 132.08 | 126.25 | T127 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 122.98 | 117.61 | T127 | PECO_P4_PEACH225_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208395 | FARO FF | 208396 | FARO | 1 | 69 | 229 | 223 | 99.45 | 103.9 | AE1-226 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 153.76 | 158.25 | T157 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.25 | 157.37 | T157 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.25 | 157.37 | T157 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 152.07 | 156.93 | T157 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 161.76 | 154.53 | T157 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 148.71 | 153.28 | T157 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 155.82 | 150.67 | T157 | PN_P1-2_PN-500-010T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.54 | 149.66 | T157 | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.47 | 149.58 | T157 | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.17 | 148.42 | T157 | AP_P2-3_PE-500-016_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.23 | 148.39 | T157 | AP_P2-3_PE-500-015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.14 | 148 | T157 | PJM_500_BG_P4_5_CNSTN_L_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.42 | 147.99 | T157 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.22 | 147.8 | T157 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.25 | 147.78 | T157 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.98 | 147.59 | T157 | PECO_P4_NOTTI85_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.92 | 147.57 | T157 | PECO_P1-2_220-08_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.35 | 147.54 | T157 | AP_P1-2_PE-500-001_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.35 | 147.54 | T157 | AP_P1-2_WP-500-DRT17_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.85 | 147.51 | T157 | PECO_P4_COOPR125_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.3 | 147.47 | T157 | AP_P2-3_PE-500-018C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208395 | FARO FF | 208396 | FARO | 1 | 69 | 229 | 223 | 98.94 | 103.56 | AG2-055 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.97 | 144.26 | T157 | PECO_P4_PEACH025_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.84 | 144.16 | T157 | PECO_P1-2_PBTIE1_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 139.21 | 133.27 | T157 | PECO_P4_PEACH205_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 139.1 | 132.94 | T157 | PECO_P1-2_PBTIE2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 138.16 | 132.06 | T157 | PECO_P4_PEACH055_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 133.48 | 127.65 | T157 | PECO_P4_PEACH015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 132.15 | 126.32 | T157 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 123.05 | 117.67 | T157 | PECO_P4_PEACH225_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 225.59 | 237.1 | TOP CROP | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 223.59 | 237.1 | TOP CROP | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 225.53 | 237.04 | TOP CROP | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 223.52 | 237.04 | TOP CROP | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 225.53 | 237.04 | TOP CROP | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 223.52 | 237.04 | TOP CROP | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 213.54 | 226.94 | TOP CROP | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 213.48 | 226.88 | TOP CROP | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 213.47 | 226.88 | TOP CROP | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 209.28 | 223.73 | TOP CROP | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 209.22 | 223.67 | TOP CROP | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 209.22 | 223.67 | TOP CROP | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 210.7 | 217.91 | TOP CROP | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 208.69 | 217.91 | TOP CROP | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 199.16 | 208.34 | TOP CROP | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 194.9 | 204.99 | TOP CROP | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 172.83 | 167.9 | TOP CROP | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 161.82 | 161.96 | TOP CROP | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 161.82 | 161.96 | TOP CROP | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 521 | 119.52 | 119.32 | AA1-102 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 161.81 | 161.95 | TOP CROP | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 153.62 | 158.1 | TOP CROP | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.08 | 157.2 | TOP CROP | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.08 | 157.2 | TOP CROP | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 151.94 | 156.78 | TOP CROP | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 161.5 | 154.28 | TOP CROP | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 148.57 | 153.13 | TOP CROP | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 155.65 | 150.51 | TOP CROP | PN_P1-2_PN-500-010T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.41 | 149.51 | TOP CROP | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.34 | 149.44 | TOP CROP | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.07 | 148.33 | TOP CROP | AP_P2-3_PE-500-016_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.13 | 148.3 | TOP CROP | AP_P2-3_PE-500-015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.97 | 147.84 | TOP CROP | PJM_500_BG_P4_5_CNSTN_L_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.19 | 147.76 | TOP CROP | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.99 | 147.58 | TOP CROP | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.02 | 147.56 | TOP CROP | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.25 | 147.44 | TOP CROP | AP_P1-2_PE-500-001_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.25 | 147.44 | TOP CROP | AP_P1-2_WP-500-DRT17_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.2 | 147.37 | TOP CROP | AP_P2-3_PE-500-018C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.75 | 147.37 | TOP CROP | PECO_P4_NOTTI85_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.69 | 147.35 | TOP CROP | PECO_P1-2_220-08_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.62 | 147.28 | TOP CROP | PECO_P4_COOPR125_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 521 | 119.38 | 119.17 | AB1-056 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.68 | 143.98 | TOP CROP | PECO_P4_PEACH025_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.58 | 143.91 | TOP CROP | PECO_P1-2_PBTIE1_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 911 | 149.08 | 143.23 | TOP CROP | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 1031 | 130.36 | 138.21 | TOP CROP | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 138.99 | 133.06 | TOP CROP | PECO_P4_PEACH205_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 138.86 | 132.71 | TOP CROP | PECO_P1-2_PBTIE2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 137.93 | 131.85 | TOP CROP | PECO_P4_PEACH055_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 133.23 | 127.42 | TOP CROP | PECO_P4_PEACH015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 131.92 | 126.1 | TOP CROP | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208020 | MANO TR3 | 1 | 230 | 229 | 793 | 111.54 | 124.75 | TOP CROP | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208020 | MANO TR3 | 1 | 230 | 229 | 793 | 111.53 | 124.75 | TOP CROP | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208020 | MANO TR3 | 1 | 230 | 229 | 793 | 111.54 | 124.75 | TOP CROP | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 122.82 | 117.46 | TOP CROP | PECO_P4_PEACH225_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 99.67 | 103.64 | TOP CROP | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 99.67 | 103.64 | TOP CROP | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 99.67 | 103.64 | TOP CROP | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 521 | 119.11 | 118.89 | AB2-036 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 161.84 | 154.61 | TR3_G114 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.5 | 148.06 | TR3_G114 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.3 | 147.87 | TR3_G114 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.32 | 147.86 | TR3_G114 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.05 | 147.66 | TR3_G114 | PECO_P4_NOTTI85_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.99 | 147.65 | TR3_G114 | PECO_P1-2_220-08_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.93 | 147.58 | TR3_G114 | PECO_P4_COOPR125_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 151.79 | 147.46 | TR3_G114 | AP_P2-3_PE-500-016_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 151.82 | 147.45 | TR3_G114 | AP_P2-3_PE-500-015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.59 | 147.39 | TR3_G114 | PECO_P1-2_220-93_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 151.3 | 146.99 | TR3_G114 | AP_P1-2_WP-500-DRT17_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 151.05 | 144.33 | TR3_G114 | PECO_P4_PEACH025_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 225.37 | 236.77 | TWINGROVE | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 223.37 | 236.77 | TWINGROVE | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 225.3 | 236.7 | TWINGROVE | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 223.3 | 236.7 | TWINGROVE | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 225.3 | 236.7 | TWINGROVE | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 223.3 | 236.7 | TWINGROVE | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 213.33 | 226.62 | TWINGROVE | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 213.26 | 226.56 | TWINGROVE | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 213.26 | 226.56 | TWINGROVE | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 209.07 | 223.4 | TWINGROVE | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 209 | 223.34 | TWINGROVE | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 209 | 223.34 | TWINGROVE | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 208.48 | 217.63 | TWINGROVE | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 210.48 | 217.62 | TWINGROVE | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 198.95 | 208.07 | TWINGROVE | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 194.69 | 204.72 | TWINGROVE | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 172.7 | 167.77 | TWINGROVE | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 163.54 | 164.87 | TWINGROVE | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 521 | 120.14 | 119.96 | AB2-037 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 161.67 | 161.78 | TWINGROVE | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 161.67 | 161.78 | TWINGROVE | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 161.65 | 161.78 | TWINGROVE | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 153.5 | 157.96 | TWINGROVE | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 161.95 | 157.08 | TWINGROVE | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 161.95 | 157.08 | TWINGROVE | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 151.82 | 156.63 | TWINGROVE | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 161.33 | 154.12 | TWINGROVE | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 148.46 | 152.98 | TWINGROVE | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 152.73 | 151.17 | TWINGROVE | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 155.53 | 150.38 | TWINGROVE | PN_P1-2_PN-500-010T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 903 | 142.7 | 149.5 | TWINGROVE | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 903 | 142.69 | 149.49 | TWINGROVE | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 903 | 142.68 | 149.49 | TWINGROVE | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.3 | 149.37 | TWINGROVE | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.23 | 149.3 | TWINGROVE | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.96 | 148.21 | TWINGROVE | AP_P2-3_PE-500-016_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.03 | 148.18 | TWINGROVE | AP_P2-3_PE-500-015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.84 | 147.72 | TWINGROVE | PJM_500_BG_P4_5_CNSTN_L_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.04 | 147.62 | TWINGROVE | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.84 | 147.43 | TWINGROVE | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.87 | 147.41 | TWINGROVE | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.14 | 147.33 | TWINGROVE | AP_P1-2_WP-500-DRT17_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.14 | 147.33 | TWINGROVE | AP_P1-2_PE-500-001_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.09 | 147.26 | TWINGROVE | AP_P2-3_PE-500-018C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.6 | 147.22 | TWINGROVE | PECO_P4_NOTTI85_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.54 | 147.2 | TWINGROVE | PECO_P1-2_220-08_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.47 | 147.14 | TWINGROVE | PECO_P4_COOPR125_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 521 | 115.77 | 115.42 | AC1-158 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.51 | 143.81 | TWINGROVE | PECO_P4_PEACH025_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.4 | 143.74 | TWINGROVE | PECO_P1-2_PBTIE1_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 911 | 148.95 | 143.13 | TWINGROVE | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204502 | 27JACKSON | 204514 | 27TMI | 1 | 230 | 227 | 781 | 132.95 | 141.51 | TWINGROVE | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204502 | 27JACKSON | 204514 | 27TMI | 1 | 230 | 227 | 781 | 132.95 | 141.51 | TWINGROVE | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204502 | 27JACKSON | 204514 | 27TMI | 1 | 230 | 227 | 781 | 132.93 | 141.5 | TWINGROVE | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 903 | 135.62 | 139.64 | TWINGROVE | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 1031 | 130.27 | 138.04 | TWINGROVE | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 1031 | 130.27 | 138.04 | TWINGROVE | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 1031 | 130.26 | 138.04 | TWINGROVE | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 138.84 | 132.91 | TWINGROVE | PECO_P4_PEACH205_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 138.7 | 132.56 | TWINGROVE | PECO_P1-2_PBTIE2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208078 | SAKR | 1 | 230 | 229 | 903 | 124.43 | 132.45 | TWINGROVE | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208078 | SAKR | 1 | 230 | 229 | 903 | 124.43 | 132.45 | TWINGROVE | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208078 | SAKR | 1 | 230 | 229 | 903 | 124.43 | 132.45 | TWINGROVE | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 137.78 | 131.7 | TWINGROVE | PECO_P4_PEACH055_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 1031 | 124.68 | 129.24 | TWINGROVE | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 133.07 | 127.26 | TWINGROVE | PECO_P4_PEACH015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 128.92 | 127.23 | TWINGROVE | DVP_P4-2: 514T595_SRT-SW |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 131.76 | 125.96 | TWINGROVE | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 127.18 | 125.51 | TWINGROVE | DVP_P4-2: 51482_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 127.18 | 125.43 | TWINGROVE | AP_P1-2_PE-500-407T_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 127.18 | 125.43 | TWINGROVE | DVP_P1-2: LN 514_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208020 | MANO TR3 | 1 | 230 | 229 | 793 | 111.41 | 124.62 | TWINGROVE | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208020 | MANO TR3 | 1 | 230 | 229 | 793 | 111.41 | 124.62 | TWINGROVE | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208020 | MANO TR3 | 1 | 230 | 229 | 793 | 111.41 | 124.61 | TWINGROVE | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208078 | SAKR | 1 | 230 | 229 | 903 | 117.17 | 122.48 | TWINGROVE | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200025 | W CHAPEL | 1 | 500 | 225 | 1732 | 123.74 | 121.94 | TWINGROVE | PEPCO_P4_PP41_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208031 | MLWD TR2 | 1 | 230 | 229 | 911 | 111.73 | 121.19 | TWINGROVE | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208031 | MLWD TR2 | 1 | 230 | 229 | 911 | 111.72 | 121.19 | TWINGROVE | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208031 | MLWD TR2 | 1 | 230 | 229 | 911 | 111.73 | 121.19 | TWINGROVE | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 122.67 | 117.31 | TWINGROVE | PECO_P4_PEACH225_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 117.36 | 115.49 | TWINGROVE | AP_P2-3_PE-500-019C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 2 | 500/230 | 225/232 | 2168 | 109.67 | 115.01 | TWINGROVE | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 2 | 500/230 | 225/232 | 2168 | 109.5 | 114.8 | TWINGROVE | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 2 | 500/230 | 225/232 | 2168 | 109.5 | 114.79 | TWINGROVE | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 1 | 500/230 | 225/232 | 2168 | 109.44 | 114.77 | TWINGROVE | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 1 | 500/230 | 225/232 | 2168 | 109.27 | 114.55 | TWINGROVE | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 1 | 500/230 | 225/232 | 2168 | 109.27 | 114.55 | TWINGROVE | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208020 | MANO TR3 | 1 | 230 | 229 | 793 | 104.23 | 114.05 | TWINGROVE | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208031 | MLWD TR2 | 1 | 230 | 229 | 911 | 104.98 | 111.7 | TWINGROVE | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 99.65 | 103.58 | TWINGROVE | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 99.65 | 103.58 | TWINGROVE | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 99.65 | 103.58 | TWINGROVE | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208020 | MANO TR3 | 208031 | MLWD TR2 | 1 | 230 | 229 | 903 | 95.47 | 103.34 | TWINGROVE | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 98.82 | 100.89 | TWINGROVE | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 209.42 | 223.95 | U2-072 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 521 | 119.54 | 119.34 | AE1-104 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 153.71 | 158.2 | U2-072 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.17 | 157.29 | U2-072 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.16 | 157.29 | U2-072 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 152.02 | 156.88 | U2-072 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 161.6 | 154.39 | U2-072 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 148.66 | 153.23 | U2-072 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 155.74 | 150.59 | U2-072 | PN_P1-2_PN-500-010T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.5 | 149.61 | U2-072 | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.43 | 149.54 | U2-072 | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.15 | 148.42 | U2-072 | AP_P2-3_PE-500-016_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.21 | 148.39 | U2-072 | AP_P2-3_PE-500-015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.05 | 147.93 | U2-072 | PJM_500_BG_P4_5_CNSTN_L_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.29 | 147.85 | U2-072 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.09 | 147.67 | U2-072 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.11 | 147.65 | U2-072 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.33 | 147.54 | U2-072 | AP_P1-2_PE-500-001_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.33 | 147.54 | U2-072 | AP_P1-2_WP-500-DRT17_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.28 | 147.47 | U2-072 | AP_P2-3_PE-500-018C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.84 | 147.46 | U2-072 | PECO_P4_NOTTI85_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.78 | 147.44 | U2-072 | PECO_P1-2_220-08_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.72 | 147.38 | U2-072 | PECO_P4_COOPR125_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 521 | 119.31 | 119.1 | AE1-229 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.79 | 144.09 | U2-072 | PECO_P4_PEACH025_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.69 | 144.02 | U2-072 | PECO_P1-2_PBTIE1_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 139.09 | 133.15 | U2-072 | PECO_P4_PEACH205_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 138.96 | 132.81 | U2-072 | PECO_P1-2_PBTIE2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 138.03 | 131.94 | U2-072 | PECO_P4_PEACH055_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 133.34 | 127.52 | U2-072 | PECO_P4_PEACH015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 132.02 | 126.2 | U2-072 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 122.92 | 117.56 | U2-072 | PECO_P4_PEACH225_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 521 | 120.51 | 120.35 | AE2-000 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 153.77 | 158.27 | U2-073 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.25 | 157.37 | U2-073 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.25 | 157.37 | U2-073 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 152.08 | 156.95 | U2-073 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 161.74 | 154.51 | U2-073 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 148.72 | 153.3 | U2-073 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 155.82 | 150.67 | U2-073 | PN_P1-2_PN-500-010T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.56 | 149.67 | U2-073 | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.48 | 149.6 | U2-073 | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.19 | 148.46 | U2-073 | AP_P2-3_PE-500-016_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.25 | 148.43 | U2-073 | AP_P2-3_PE-500-015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.13 | 148 | U2-073 | PJM_500_BG_P4_5_CNSTN_L_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.41 | 147.97 | U2-073 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.21 | 147.78 | U2-073 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.23 | 147.77 | U2-073 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.39 | 147.62 | U2-073 | AP_P1-2_WP-500-DRT17_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.39 | 147.62 | U2-073 | AP_P1-2_PE-500-001_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.96 | 147.57 | U2-073 | PECO_P4_NOTTI85_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.9 | 147.56 | U2-073 | PECO_P1-2_220-08_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.84 | 147.49 | U2-073 | PECO_P4_COOPR125_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 521 | 120.19 | 120.02 | AE2-020 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 142.78 | 146.86 | U2-073 | AP_P2-3_PE-500-014_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.95 | 144.24 | U2-073 | PECO_P4_PEACH025_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.82 | 144.15 | U2-073 | PECO_P1-2_PBTIE1_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 139.2 | 133.26 | U2-073 | PECO_P4_PEACH205_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 139.09 | 132.93 | U2-073 | PECO_P1-2_PBTIE2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 138.14 | 132.05 | U2-073 | PECO_P4_PEACH055_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 133.47 | 127.64 | U2-073 | PECO_P4_PEACH015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 132.14 | 126.31 | U2-073 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 123.04 | 117.66 | U2-073 | PECO_P4_PEACH225_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 521 | 120.19 | 120.02 | AE2-021 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 153.75 | 158.25 | U2-090 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.21 | 157.34 | U2-090 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.21 | 157.34 | U2-090 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 152.06 | 156.92 | U2-090 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 161.67 | 154.45 | U2-090 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 148.7 | 153.27 | U2-090 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 155.79 | 150.63 | U2-090 | PN_P1-2_PN-500-010T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.53 | 149.65 | U2-090 | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.46 | 149.58 | U2-090 | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.18 | 148.45 | U2-090 | AP_P2-3_PE-500-016_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.24 | 148.42 | U2-090 | AP_P2-3_PE-500-015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.1 | 147.97 | U2-090 | PJM_500_BG_P4_5_CNSTN_L_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.35 | 147.91 | U2-090 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.15 | 147.73 | U2-090 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.17 | 147.71 | U2-090 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.35 | 147.57 | U2-090 | AP_P1-2_WP-500-DRT17_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.35 | 147.57 | U2-090 | AP_P1-2_PE-500-001_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.9 | 147.52 | U2-090 | PECO_P4_NOTTI85_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.84 | 147.5 | U2-090 | PECO_P1-2_220-08_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.3 | 147.5 | U2-090 | AP_P2-3_PE-500-018C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.78 | 147.44 | U2-090 | PECO_P4_COOPR125_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 521 | 119.16 | 118.95 | AE2-022 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.87 | 144.16 | U2-090 | PECO_P4_PEACH025_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.76 | 144.08 | U2-090 | PECO_P1-2_PBTIE1_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 139.14 | 133.21 | U2-090 | PECO_P4_PEACH205_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 139.02 | 132.87 | U2-090 | PECO_P1-2_PBTIE2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 138.08 | 132 | U2-090 | PECO_P4_PEACH055_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 133.4 | 127.58 | U2-090 | PECO_P4_PEACH015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 132.08 | 126.26 | U2-090 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 122.98 | 117.61 | U2-090 | PECO_P4_PEACH225_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 225.61 | 237.12 | U3-002 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 223.6 | 237.12 | U3-002 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 225.54 | 237.06 | U3-002 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 223.54 | 237.06 | U3-002 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 225.54 | 237.06 | U3-002 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 223.53 | 237.06 | U3-002 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 213.55 | 226.96 | U3-002 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 213.49 | 226.9 | U3-002 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 213.49 | 226.9 | U3-002 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 209.29 | 223.75 | U3-002 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 209.23 | 223.69 | U3-002 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 209.23 | 223.69 | U3-002 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 208.71 | 217.93 | U3-002 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 210.71 | 217.92 | U3-002 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 199.17 | 208.36 | U3-002 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 194.91 | 205.01 | U3-002 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 172.84 | 167.91 | U3-002 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 161.83 | 161.97 | U3-002 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 161.83 | 161.97 | U3-002 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 161.82 | 161.97 | U3-002 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 521 | 125.44 | 125.5 | AG2-055 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 153.63 | 158.11 | U3-002 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.08 | 157.21 | U3-002 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.08 | 157.21 | U3-002 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 151.94 | 156.79 | U3-002 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 161.51 | 154.29 | U3-002 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 148.58 | 153.13 | U3-002 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 155.66 | 150.51 | U3-002 | PN_P1-2_PN-500-010T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.42 | 149.52 | U3-002 | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.35 | 149.45 | U3-002 | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.08 | 148.34 | U3-002 | AP_P2-3_PE-500-016_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.14 | 148.31 | U3-002 | AP_P2-3_PE-500-015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.97 | 147.85 | U3-002 | PJM_500_BG_P4_5_CNSTN_L_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.2 | 147.77 | U3-002 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153 | 147.58 | U3-002 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.03 | 147.57 | U3-002 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.25 | 147.46 | U3-002 | AP_P1-2_WP-500-DRT17_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.25 | 147.46 | U3-002 | AP_P1-2_PE-500-001_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.2 | 147.39 | U3-002 | AP_P2-3_PE-500-018C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.76 | 147.37 | U3-002 | PECO_P4_NOTTI85_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.7 | 147.36 | U3-002 | PECO_P1-2_220-08_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.63 | 147.29 | U3-002 | PECO_P4_COOPR125_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 521 | 113.96 | 113.55 | O66 NFTWR | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.69 | 143.99 | U3-002 | PECO_P4_PEACH025_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.59 | 143.92 | U3-002 | PECO_P1-2_PBTIE1_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 911 | 149.09 | 143.24 | U3-002 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 1031 | 130.37 | 138.22 | U3-002 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 139 | 133.06 | U3-002 | PECO_P4_PEACH205_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 138.87 | 132.72 | U3-002 | PECO_P1-2_PBTIE2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 137.94 | 131.85 | U3-002 | PECO_P4_PEACH055_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 133.24 | 127.43 | U3-002 | PECO_P4_PEACH015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 131.93 | 126.11 | U3-002 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208020 | MANO TR3 | 1 | 230 | 229 | 793 | 111.54 | 124.76 | U3-002 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208020 | MANO TR3 | 1 | 230 | 229 | 793 | 111.54 | 124.76 | U3-002 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208020 | MANO TR3 | 1 | 230 | 229 | 793 | 111.54 | 124.76 | U3-002 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 122.83 | 117.47 | U3-002 | PECO_P4_PEACH225_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 99.68 | 103.65 | U3-002 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 521 | 117.07 | 119.32 | AA1-102 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 161.84 | 154.61 | V1-011 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.5 | 148.06 | V1-011 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.3 | 147.88 | V1-011 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.32 | 147.86 | V1-011 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.05 | 147.66 | V1-011 | PECO_P4_NOTTI85_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.99 | 147.65 | V1-011 | PECO_P1-2_220-08_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.93 | 147.58 | V1-011 | PECO_P4_COOPR125_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 151.79 | 147.46 | V1-011 | AP_P2-3_PE-500-016_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 151.82 | 147.45 | V1-011 | AP_P2-3_PE-500-015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.59 | 147.39 | V1-011 | PECO_P1-2_220-93_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 151.31 | 146.99 | V1-011 | AP_P1-2_WP-500-DRT17_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 151.05 | 144.33 | V1-011 | PECO_P4_PEACH025_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 521 | 116.94 | 119.17 | AB1-056 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.59 | 157.72 | V2-046 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.59 | 157.72 | V2-046 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 162.19 | 154.95 | V2-046 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 156.17 | 151.01 | V2-046 | PN_P1-2_PN-500-010T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.8 | 148.36 | V2-046 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.6 | 148.17 | V2-046 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.63 | 148.16 | V2-046 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.36 | 147.96 | V2-046 | PECO_P4_NOTTI85_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.3 | 147.95 | V2-046 | PECO_P1-2_220-08_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.23 | 147.88 | V2-046 | PECO_P4_COOPR125_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.89 | 147.69 | V2-046 | PECO_P1-2_220-93_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 151.45 | 144.72 | V2-046 | PECO_P4_PEACH025_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 151.31 | 144.61 | V2-046 | PECO_P1-2_PBTIE1_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 139.53 | 133.36 | V2-046 | PECO_P1-2_PBTIE2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 138.56 | 132.45 | V2-046 | PECO_P4_PEACH055_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 133.94 | 128.1 | V2-046 | PECO_P4_PEACH015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 132.57 | 126.72 | V2-046 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 123.48 | 118.09 | V2-046 | PECO_P4_PEACH225_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 521 | 116.68 | 118.89 | AB2-036 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 153.74 | 158.24 | V3-007 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.2 | 157.33 | V3-007 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.2 | 157.33 | V3-007 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 152.05 | 156.92 | V3-007 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 161.66 | 154.44 | V3-007 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 148.69 | 153.26 | V3-007 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 155.78 | 150.63 | V3-007 | PN_P1-2_PN-500-010T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.53 | 149.64 | V3-007 | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.46 | 149.57 | V3-007 | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.17 | 148.44 | V3-007 | AP_P2-3_PE-500-016_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.24 | 148.41 | V3-007 | AP_P2-3_PE-500-015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.09 | 147.96 | V3-007 | PJM_500_BG_P4_5_CNSTN_L_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.34 | 147.9 | V3-007 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.14 | 147.72 | V3-007 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.16 | 147.7 | V3-007 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.35 | 147.56 | V3-007 | AP_P1-2_PE-500-001_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.35 | 147.56 | V3-007 | AP_P1-2_WP-500-DRT17_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.89 | 147.51 | V3-007 | PECO_P4_NOTTI85_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.83 | 147.49 | V3-007 | PECO_P1-2_220-08_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.3 | 147.49 | V3-007 | AP_P2-3_PE-500-018C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.77 | 147.43 | V3-007 | PECO_P4_COOPR125_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 521 | 117.67 | 119.96 | AB2-037 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.86 | 144.15 | V3-007 | PECO_P4_PEACH025_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.75 | 144.07 | V3-007 | PECO_P1-2_PBTIE1_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 139.14 | 133.2 | V3-007 | PECO_P4_PEACH205_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 139.02 | 132.86 | V3-007 | PECO_P1-2_PBTIE2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 138.08 | 131.99 | V3-007 | PECO_P4_PEACH055_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 133.4 | 127.58 | V3-007 | PECO_P4_PEACH015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 132.07 | 126.25 | V3-007 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 122.97 | 117.6 | V3-007 | PECO_P4_PEACH225_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 223.14 | 236.43 | V3-028 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 225.14 | 236.43 | V3-028 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 223.08 | 236.37 | V3-028 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 225.08 | 236.37 | V3-028 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 223.08 | 236.37 | V3-028 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 225.07 | 236.37 | V3-028 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 213.11 | 226.29 | V3-028 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 213.05 | 226.24 | V3-028 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 213.05 | 226.23 | V3-028 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 208.85 | 223.08 | V3-028 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 208.79 | 223.02 | V3-028 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 208.79 | 223.02 | V3-028 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 210.26 | 217.37 | V3-028 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 208.27 | 217.37 | V3-028 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 198.74 | 207.82 | V3-028 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 194.48 | 204.46 | V3-028 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 172.59 | 167.67 | V3-028 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 171.61 | 166.23 | V3-028 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 171.61 | 166.23 | V3-028 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 171.59 | 166.22 | V3-028 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 163.42 | 164.72 | V3-028 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 521 | 113.48 | 115.42 | AC1-158 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 161.54 | 161.63 | V3-028 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 161.53 | 161.63 | V3-028 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 161.52 | 161.62 | V3-028 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 163.67 | 158.77 | V3-028 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 153.42 | 157.86 | V3-028 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 161.83 | 156.97 | V3-028 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 161.83 | 156.96 | V3-028 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 151.73 | 156.54 | V3-028 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 161.16 | 153.96 | V3-028 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 148.37 | 152.88 | V3-028 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 903 | 144.15 | 152 | V3-028 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 152.61 | 151.04 | V3-028 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 155.42 | 150.27 | V3-028 | PN_P1-2_PN-500-010T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 903 | 142.61 | 149.36 | V3-028 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 903 | 142.61 | 149.35 | V3-028 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 903 | 142.59 | 149.35 | V3-028 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.22 | 149.28 | V3-028 | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.15 | 149.21 | V3-028 | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.91 | 148.15 | V3-028 | AP_P2-3_PE-500-016_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.97 | 148.12 | V3-028 | AP_P2-3_PE-500-015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.73 | 147.62 | V3-028 | PJM_500_BG_P4_5_CNSTN_L_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.89 | 147.46 | V3-028 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.69 | 147.28 | V3-028 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.08 | 147.26 | V3-028 | AP_P1-2_PE-500-001_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.08 | 147.26 | V3-028 | AP_P1-2_WP-500-DRT17_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.71 | 147.26 | V3-028 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.03 | 147.19 | V3-028 | AP_P2-3_PE-500-018C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.44 | 147.07 | V3-028 | PECO_P4_NOTTI85_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.38 | 147.05 | V3-028 | PECO_P1-2_220-08_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.32 | 146.99 | V3-028 | PECO_P4_COOPR125_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 521 | 117.09 | 119.34 | AE1-104 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.31 | 143.62 | V3-028 | PECO_P4_PEACH025_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.23 | 143.58 | V3-028 | PECO_P1-2_PBTIE1_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 911 | 148.85 | 143.05 | V3-028 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204502 | 27JACKSON | 204514 | 27TMI | 1 | 230 | 227 | 781 | 132.83 | 141.33 | V3-028 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204502 | 27JACKSON | 204514 | 27TMI | 1 | 230 | 227 | 781 | 132.83 | 141.33 | V3-028 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204502 | 27JACKSON | 204514 | 27TMI | 1 | 230 | 227 | 781 | 132.82 | 141.32 | V3-028 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 903 | 135.54 | 139.54 | V3-028 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 1031 | 130.69 | 138.98 | V3-028 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 1031 | 130.19 | 137.89 | V3-028 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 1031 | 130.19 | 137.89 | V3-028 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 1031 | 130.18 | 137.88 | V3-028 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 138.69 | 132.77 | V3-028 | PECO_P4_PEACH205_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 138.54 | 132.4 | V3-028 | PECO_P1-2_PBTIE2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208078 | SAKR | 1 | 230 | 229 | 903 | 124.32 | 132.29 | V3-028 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208078 | SAKR | 1 | 230 | 229 | 903 | 124.32 | 132.28 | V3-028 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208078 | SAKR | 1 | 230 | 229 | 903 | 124.32 | 132.28 | V3-028 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 137.63 | 131.56 | V3-028 | PECO_P4_PEACH055_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204502 | 27JACKSON | 204514 | 27TMI | 1 | 230 | 227 | 781 | 125.19 | 130.81 | V3-028 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 1031 | 124.59 | 129.13 | V3-028 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 132.9 | 127.1 | V3-028 | PECO_P4_PEACH015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208020 | MANO TR3 | 1 | 230 | 229 | 793 | 112.13 | 126 | V3-028 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 131.61 | 125.81 | V3-028 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208020 | MANO TR3 | 1 | 230 | 229 | 793 | 111.3 | 124.45 | V3-028 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208020 | MANO TR3 | 1 | 230 | 229 | 793 | 111.29 | 124.45 | V3-028 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208020 | MANO TR3 | 1 | 230 | 229 | 793 | 111.3 | 124.45 | V3-028 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208078 | SAKR | 1 | 230 | 229 | 903 | 117.07 | 122.35 | V3-028 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204512 | 27S.RDG | 204693 | 27BOONETOWN | 1 | 230 | 227 | 607 | 107.22 | 122 | V3-028 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204512 | 27S.RDG | 204693 | 27BOONETOWN | 1 | 230 | 227 | 607 | 107.19 | 121.98 | V3-028 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204512 | 27S.RDG | 204693 | 27BOONETOWN | 1 | 230 | 227 | 607 | 107.19 | 121.98 | V3-028 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200025 | W CHAPEL | 1 | 500 | 225 | 1732 | 123.7 | 121.9 | V3-028 | PEPCO_P4_PP41_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208031 | MLWD TR2 | 1 | 230 | 229 | 911 | 111.62 | 121.03 | V3-028 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208031 | MLWD TR2 | 1 | 230 | 229 | 911 | 111.62 | 121.03 | V3-028 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208031 | MLWD TR2 | 1 | 230 | 229 | 911 | 111.62 | 121.03 | V3-028 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 114.67 | 118.4 | V3-028 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 114.34 | 118.06 | V3-028 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 114.32 | 118 | V3-028 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 114.32 | 118 | V3-028 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 113.99 | 117.67 | V3-028 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 113.99 | 117.66 | V3-028 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 122.52 | 117.17 | V3-028 | PECO_P4_PEACH225_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 2 | 500/230 | 225/232 | 2168 | 109.63 | 114.97 | V3-028 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 2 | 500/230 | 225/232 | 2168 | 109.46 | 114.75 | V3-028 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 2 | 500/230 | 225/232 | 2168 | 109.46 | 114.75 | V3-028 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 1 | 500/230 | 225/232 | 2168 | 109.4 | 114.73 | V3-028 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 1 | 500/230 | 225/232 | 2168 | 109.23 | 114.51 | V3-028 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 1 | 500/230 | 225/232 | 2168 | 109.23 | 114.51 | V3-028 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220964 | GRACETON | 220999 | BAGLEY2 | 13 | 230 | 232 | 1795 | 113.41 | 114.45 | V3-028 | BG_P4_5_GRCTN_3T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208020 | MANO TR3 | 1 | 230 | 229 | 793 | 104.12 | 113.91 | V3-028 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208020 | MANO TR3 | 208031 | MLWD TR2 | 1 | 230 | 229 | 903 | 102.45 | 113.6 | V3-028 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208020 | MANO TR3 | 208031 | MLWD TR2 | 1 | 230 | 229 | 903 | 101.74 | 112.39 | V3-028 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208020 | MANO TR3 | 208031 | MLWD TR2 | 1 | 230 | 229 | 903 | 101.73 | 112.39 | V3-028 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208020 | MANO TR3 | 208031 | MLWD TR2 | 1 | 230 | 229 | 903 | 101.73 | 112.39 | V3-028 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208031 | MLWD TR2 | 1 | 230 | 229 | 911 | 104.87 | 111.58 | V3-028 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220980 | RAPHAEL | 220999 | BAGLEY2 | 13 | 230 | 232 | 1795 | 109 | 111.21 | V3-028 | BG_P4_5_GRCTN_3T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 99.68 | 103.58 | V3-028 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 99.68 | 103.58 | V3-028 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 99.68 | 103.58 | V3-028 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208020 | MANO TR3 | 208031 | MLWD TR2 | 1 | 230 | 229 | 903 | 95.37 | 103.2 | V3-028 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 223960 | BRG 1T 230 | 1 | 500/230 | 225/233 | 1498 | 100.26 | 100.64 | V3-028 | PEPCO_P4_PP41_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 521 | 116.87 | 119.1 | AE1-229 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.65 | 157.77 | W1-003 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.65 | 157.77 | W1-003 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 162.27 | 155.03 | W1-003 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 156.22 | 151.07 | W1-003 | PN_P1-2_PN-500-010T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.87 | 148.43 | W1-003 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.52 | 148.38 | W1-003 | PJM_500_BG_P4_5_CNSTN_L_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.67 | 148.24 | W1-003 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.7 | 148.23 | W1-003 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.43 | 148.03 | W1-003 | PECO_P4_NOTTI85_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.37 | 148.01 | W1-003 | PECO_P1-2_220-08_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.3 | 147.95 | W1-003 | PECO_P4_COOPR125_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 521 | 118.02 | 120.35 | AE2-000 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 151.56 | 144.82 | W1-003 | PECO_P4_PEACH025_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 151.39 | 144.7 | W1-003 | PECO_P1-2_PBTIE1_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 137.45 | 139.5 | W1-003 | AP_P2-3_WP-500-696_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 137.45 | 139.49 | W1-003 | AP_P2-3_WP-500-707T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 134.38 | 136.49 | W1-003 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 134.37 | 136.43 | W1-003 | PECO_P4_COOPR125_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 134.34 | 136.4 | W1-003 | PECO_P1-2_220-08_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 134.36 | 136.4 | W1-003 | PECO_P4_NOTTI85_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 134.24 | 136.35 | W1-003 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 134.25 | 136.34 | W1-003 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 134.12 | 136.29 | W1-003 | PECO_P1-2_220-93_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 133.12 | 135.27 | W1-003 | PN_P2-3_PN-115-10T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 139.65 | 133.69 | W1-003 | PECO_P4_PEACH205_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 139.61 | 133.44 | W1-003 | PECO_P1-2_PBTIE2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 138.65 | 132.54 | W1-003 | PECO_P4_PEACH055_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 134.03 | 128.19 | W1-003 | PECO_P4_PEACH015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 132.65 | 126.8 | W1-003 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 123.56 | 118.16 | W1-003 | PECO_P4_PEACH225_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 521 | 117.72 | 120.02 | AE2-020 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.65 | 157.77 | W1-004 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.65 | 157.77 | W1-004 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 162.27 | 155.03 | W1-004 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 156.22 | 151.07 | W1-004 | PN_P1-2_PN-500-010T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.87 | 148.43 | W1-004 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.52 | 148.38 | W1-004 | PJM_500_BG_P4_5_CNSTN_L_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.67 | 148.24 | W1-004 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.7 | 148.23 | W1-004 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.43 | 148.03 | W1-004 | PECO_P4_NOTTI85_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.37 | 148.01 | W1-004 | PECO_P1-2_220-08_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.3 | 147.95 | W1-004 | PECO_P4_COOPR125_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 521 | 117.72 | 120.02 | AE2-021 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 151.56 | 144.82 | W1-004 | PECO_P4_PEACH025_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 151.39 | 144.7 | W1-004 | PECO_P1-2_PBTIE1_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 137.45 | 139.5 | W1-004 | AP_P2-3_WP-500-696_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 137.45 | 139.49 | W1-004 | AP_P2-3_WP-500-707T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 134.38 | 136.49 | W1-004 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 134.37 | 136.43 | W1-004 | PECO_P4_COOPR125_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 134.34 | 136.4 | W1-004 | PECO_P1-2_220-08_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 134.36 | 136.4 | W1-004 | PECO_P4_NOTTI85_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 134.24 | 136.35 | W1-004 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 134.25 | 136.34 | W1-004 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 134.12 | 136.29 | W1-004 | PECO_P1-2_220-93_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 133.12 | 135.27 | W1-004 | PN_P2-3_PN-115-10T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 139.65 | 133.69 | W1-004 | PECO_P4_PEACH205_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 139.61 | 133.44 | W1-004 | PECO_P1-2_PBTIE2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 138.65 | 132.54 | W1-004 | PECO_P4_PEACH055_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 134.03 | 128.19 | W1-004 | PECO_P4_PEACH015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 132.65 | 126.8 | W1-004 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 123.56 | 118.16 | W1-004 | PECO_P4_PEACH225_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 521 | 116.73 | 118.95 | AE2-022 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.65 | 157.77 | W1-005 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.65 | 157.77 | W1-005 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 162.27 | 155.03 | W1-005 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 156.22 | 151.07 | W1-005 | PN_P1-2_PN-500-010T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.87 | 148.43 | W1-005 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.52 | 148.38 | W1-005 | PJM_500_BG_P4_5_CNSTN_L_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.67 | 148.24 | W1-005 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.7 | 148.23 | W1-005 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.43 | 148.03 | W1-005 | PECO_P4_NOTTI85_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.37 | 148.01 | W1-005 | PECO_P1-2_220-08_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.3 | 147.95 | W1-005 | PECO_P4_COOPR125_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 521 | 122.74 | 125.5 | AG2-055 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 151.56 | 144.82 | W1-005 | PECO_P4_PEACH025_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 151.39 | 144.7 | W1-005 | PECO_P1-2_PBTIE1_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 137.45 | 139.5 | W1-005 | AP_P2-3_WP-500-696_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 137.45 | 139.49 | W1-005 | AP_P2-3_WP-500-707T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 134.38 | 136.49 | W1-005 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 134.37 | 136.43 | W1-005 | PECO_P4_COOPR125_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 134.34 | 136.4 | W1-005 | PECO_P1-2_220-08_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 134.36 | 136.4 | W1-005 | PECO_P4_NOTTI85_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 134.24 | 136.35 | W1-005 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 134.25 | 136.34 | W1-005 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 134.12 | 136.29 | W1-005 | PECO_P1-2_220-93_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 133.12 | 135.27 | W1-005 | PN_P2-3_PN-115-10T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 139.65 | 133.69 | W1-005 | PECO_P4_PEACH205_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 139.61 | 133.44 | W1-005 | PECO_P1-2_PBTIE2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 138.65 | 132.54 | W1-005 | PECO_P4_PEACH055_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 134.03 | 128.19 | W1-005 | PECO_P4_PEACH015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 132.65 | 126.8 | W1-005 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 123.56 | 118.16 | W1-005 | PECO_P4_PEACH225_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 521 | 111.74 | 113.55 | O66 NFTWR | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.65 | 157.77 | W1-006 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.65 | 157.77 | W1-006 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 162.27 | 155.03 | W1-006 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 156.22 | 151.07 | W1-006 | PN_P1-2_PN-500-010T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.87 | 148.43 | W1-006 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.52 | 148.38 | W1-006 | PJM_500_BG_P4_5_CNSTN_L_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.67 | 148.24 | W1-006 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.7 | 148.23 | W1-006 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.43 | 148.03 | W1-006 | PECO_P4_NOTTI85_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.37 | 148.01 | W1-006 | PECO_P1-2_220-08_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.3 | 147.95 | W1-006 | PECO_P4_COOPR125_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 521 | 114.19 | 116.58 | AA1-102 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 151.56 | 144.82 | W1-006 | PECO_P4_PEACH025_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 151.39 | 144.7 | W1-006 | PECO_P1-2_PBTIE1_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 137.45 | 139.5 | W1-006 | AP_P2-3_WP-500-696_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 137.45 | 139.49 | W1-006 | AP_P2-3_WP-500-707T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 134.38 | 136.49 | W1-006 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 134.37 | 136.43 | W1-006 | PECO_P4_COOPR125_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 134.34 | 136.4 | W1-006 | PECO_P1-2_220-08_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 134.36 | 136.4 | W1-006 | PECO_P4_NOTTI85_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 134.24 | 136.35 | W1-006 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 134.25 | 136.34 | W1-006 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 134.12 | 136.29 | W1-006 | PECO_P1-2_220-93_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 133.12 | 135.27 | W1-006 | PN_P2-3_PN-115-10T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 139.65 | 133.69 | W1-006 | PECO_P4_PEACH205_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 139.61 | 133.44 | W1-006 | PECO_P1-2_PBTIE2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 138.65 | 132.54 | W1-006 | PECO_P4_PEACH055_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 134.03 | 128.19 | W1-006 | PECO_P4_PEACH015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 132.65 | 126.8 | W1-006 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 123.56 | 118.16 | W1-006 | PECO_P4_PEACH225_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 225.52 | 236.85 | W1-029 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 223.52 | 236.85 | W1-029 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 225.45 | 236.79 | W1-029 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 225.45 | 236.79 | W1-029 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 223.45 | 236.79 | W1-029 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 223.45 | 236.79 | W1-029 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 213.47 | 226.7 | W1-029 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 213.4 | 226.64 | W1-029 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 213.4 | 226.64 | W1-029 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 209.21 | 223.49 | W1-029 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 209.15 | 223.43 | W1-029 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 209.15 | 223.43 | W1-029 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 210.62 | 217.7 | W1-029 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 208.62 | 217.69 | W1-029 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 199.08 | 208.14 | W1-029 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 194.82 | 204.79 | W1-029 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 172.7 | 167.71 | W1-029 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 171.73 | 166.27 | W1-029 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 171.73 | 166.27 | W1-029 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 171.71 | 166.26 | W1-029 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 163.56 | 164.83 | W1-029 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 521 | 114.06 | 116.44 | AB1-056 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 161.7 | 161.75 | W1-029 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 161.7 | 161.75 | W1-029 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 161.69 | 161.74 | W1-029 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 163.78 | 158.81 | W1-029 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 153.47 | 157.91 | W1-029 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 161.97 | 157.1 | W1-029 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 161.97 | 157.09 | W1-029 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 151.79 | 156.59 | W1-029 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 161.44 | 154.23 | W1-029 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 148.42 | 152.93 | W1-029 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 903 | 144.21 | 152.05 | W1-029 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 152.76 | 151.12 | W1-029 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 155.55 | 150.4 | W1-029 | PN_P1-2_PN-500-010T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 903 | 142.68 | 149.42 | W1-029 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 903 | 142.68 | 149.42 | W1-029 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 903 | 142.66 | 149.41 | W1-029 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.27 | 149.33 | W1-029 | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.2 | 149.26 | W1-029 | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.89 | 148.07 | W1-029 | AP_P2-3_PE-500-016_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.95 | 148.04 | W1-029 | AP_P2-3_PE-500-015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.87 | 147.73 | W1-029 | PJM_500_BG_P4_5_CNSTN_L_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.15 | 147.72 | W1-029 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.95 | 147.53 | W1-029 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.98 | 147.52 | W1-029 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.71 | 147.32 | W1-029 | PECO_P4_NOTTI85_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.65 | 147.3 | W1-029 | PECO_P1-2_220-08_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.58 | 147.24 | W1-029 | PECO_P4_COOPR125_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.07 | 147.19 | W1-029 | AP_P1-2_PE-500-001_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.07 | 147.19 | W1-029 | AP_P1-2_WP-500-DRT17_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.02 | 147.13 | W1-029 | AP_P2-3_PE-500-018C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 521 | 113.8 | 116.15 | AB2-036 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.67 | 143.97 | W1-029 | PECO_P4_PEACH025_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.51 | 143.85 | W1-029 | PECO_P1-2_PBTIE1_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 911 | 148.94 | 143.06 | W1-029 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204502 | 27JACKSON | 204514 | 27TMI | 1 | 230 | 227 | 781 | 133.02 | 141.55 | W1-029 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204502 | 27JACKSON | 204514 | 27TMI | 1 | 230 | 227 | 781 | 133.02 | 141.54 | W1-029 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204502 | 27JACKSON | 204514 | 27TMI | 1 | 230 | 227 | 781 | 133.01 | 141.54 | W1-029 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 903 | 135.6 | 139.56 | W1-029 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 1031 | 130.3 | 138.03 | W1-029 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 1031 | 130.3 | 138.03 | W1-029 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 1031 | 130.29 | 138.02 | W1-029 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 138.91 | 132.98 | W1-029 | PECO_P4_PEACH205_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 138.8 | 132.65 | W1-029 | PECO_P1-2_PBTIE2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208078 | SAKR | 1 | 230 | 229 | 903 | 124.47 | 132.45 | W1-029 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208078 | SAKR | 1 | 230 | 229 | 903 | 124.47 | 132.45 | W1-029 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208078 | SAKR | 1 | 230 | 229 | 903 | 124.47 | 132.45 | W1-029 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 137.87 | 131.79 | W1-029 | PECO_P4_PEACH055_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 1031 | 124.7 | 129.23 | W1-029 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 133.16 | 127.35 | W1-029 | PECO_P4_PEACH015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 128.39 | 126.68 | W1-029 | DVP_P4-2: 514T595_SRT-SW |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 131.85 | 126.04 | W1-029 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 126.63 | 124.9 | W1-029 | DVP_P4-2: 51482_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 2 | 230 | 233 | 793 | 126.56 | 124.83 | W1-029 | DVP_P4-2: 514T595_SRT-SW |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 793 | 126.56 | 124.83 | W1-029 | DVP_P4-2: 514T595_SRT-SW |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 126.63 | 124.81 | W1-029 | DVP_P1-2: LN 514_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 126.63 | 124.81 | W1-029 | AP_P1-2_PE-500-407T_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208020 | MANO TR3 | 1 | 230 | 229 | 793 | 111.46 | 124.62 | W1-029 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208020 | MANO TR3 | 1 | 230 | 229 | 793 | 111.46 | 124.62 | W1-029 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208020 | MANO TR3 | 1 | 230 | 229 | 793 | 111.46 | 124.62 | W1-029 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 2 | 230 | 233 | 793 | 125.31 | 123.57 | W1-029 | DVP_P4-2: 51482_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 793 | 125.31 | 123.57 | W1-029 | DVP_P4-2: 51482_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 2 | 230 | 233 | 793 | 125.31 | 123.5 | W1-029 | AP_P1-2_PE-500-407T_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 793 | 125.31 | 123.5 | W1-029 | DVP_P1-2: LN 514_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 793 | 125.31 | 123.5 | W1-029 | AP_P1-2_PE-500-407T_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 2 | 230 | 233 | 793 | 125.31 | 123.5 | W1-029 | DVP_P1-2: LN 514_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208078 | SAKR | 1 | 230 | 229 | 903 | 117.21 | 122.47 | W1-029 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200025 | W CHAPEL | 1 | 500 | 225 | 1732 | 123.61 | 121.82 | W1-029 | PEPCO_P4_PP41_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208031 | MLWD TR2 | 1 | 230 | 229 | 911 | 111.77 | 121.19 | W1-029 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208031 | MLWD TR2 | 1 | 230 | 229 | 911 | 111.76 | 121.19 | W1-029 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208031 | MLWD TR2 | 1 | 230 | 229 | 911 | 111.77 | 121.19 | W1-029 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 114.69 | 118.39 | W1-029 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 114.35 | 118.05 | W1-029 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 114.34 | 117.99 | W1-029 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 114.34 | 117.99 | W1-029 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 114.01 | 117.65 | W1-029 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 114.01 | 117.65 | W1-029 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 122.76 | 117.39 | W1-029 | PECO_P4_PEACH225_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 2 | 500/230 | 225/232 | 2168 | 109.64 | 114.95 | W1-029 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 116.84 | 114.9 | W1-029 | AP_P2-3_PE-500-019C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 2 | 500/230 | 225/232 | 2168 | 109.47 | 114.74 | W1-029 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 2 | 500/230 | 225/232 | 2168 | 109.47 | 114.74 | W1-029 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 1 | 500/230 | 225/232 | 2168 | 109.41 | 114.71 | W1-029 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 1 | 500/230 | 225/232 | 2168 | 109.24 | 114.5 | W1-029 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 1 | 500/230 | 225/232 | 2168 | 109.24 | 114.5 | W1-029 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208020 | MANO TR3 | 1 | 230 | 229 | 793 | 104.28 | 114.05 | W1-029 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208031 | MLWD TR2 | 1 | 230 | 229 | 911 | 105.01 | 111.7 | W1-029 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 793 | 112.78 | 110.15 | W1-029 | PEPCO_P4_PP19_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 2 | 230 | 233 | 793 | 109.53 | 107.63 | W1-029 | AP_P2-3_PE-500-019C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 793 | 109.53 | 107.63 | W1-029 | AP_P2-3_PE-500-019C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 99.49 | 103.38 | W1-029 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 99.49 | 103.38 | W1-029 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 99.49 | 103.38 | W1-029 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208020 | MANO TR3 | 208031 | MLWD TR2 | 1 | 230 | 229 | 903 | 95.5 | 103.32 | W1-029 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 98.56 | 102.06 | W1-029 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 98.66 | 100.69 | W1-029 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 203981 | AD2-062_POI | 235188 | 01GREENE | 1 | 138 | 226/201 | 317 | 148.21 | 139.76 | W1-045 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 203981 | AD2-062_POI | 235188 | 01GREENE | 1 | 138 | 226/201 | 317 | 148.21 | 139.76 | W1-045 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 203981 | AD2-062_POI | 235188 | 01GREENE | 1 | 138 | 226/201 | 317 | 148.01 | 139.61 | W1-045 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200532 | 26ROXBURY | 203981 | AD2-062_POI | 1 | 138 | 226 | 317 | 147.52 | 138.44 | W1-045 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200532 | 26ROXBURY | 203981 | AD2-062_POI | 1 | 138 | 226 | 317 | 147.52 | 138.44 | W1-045 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200532 | 26ROXBURY | 203981 | AD2-062_POI | 1 | 138 | 226 | 317 | 147.32 | 138.28 | W1-045 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200504 | 26CARLISLE | 204528 | 27GARDNERS | 1 | 115 | 226/227 | 190 | 125.69 | 133.97 | W1-045 | PN_P2-3_PN-115-0331-B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 521 | 114.78 | 117.23 | AB2-037 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200504 | 26CARLISLE | 204528 | 27GARDNERS | 1 | 115 | 226/227 | 190 | 125.17 | 133.3 | W1-045 | PN_P1-2_PN-115-094_A_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200504 | 26CARLISLE | 204528 | 27GARDNERS | 1 | 115 | 226/227 | 190 | 125.01 | 132.37 | W1-045 | PN_P2-3_PN-115-58B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200504 | 26CARLISLE | 204528 | 27GARDNERS | 1 | 115 | 226/227 | 190 | 125.65 | 132.33 | W1-045 | PN_P1-3_PN-115-040_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200504 | 26CARLISLE | 204528 | 27GARDNERS | 1 | 115 | 226/227 | 190 | 125.65 | 132.33 | W1-045 | PN_P2-2_PN-115-030_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200504 | 26CARLISLE | 204528 | 27GARDNERS | 1 | 115 | 226/227 | 190 | 124.81 | 132.3 | W1-045 | PN_P1-2_PN-115-094_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 521 | 110.6 | 112.68 | AC1-158 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200504 | 26CARLISLE | 204528 | 27GARDNERS | 1 | 115 | 226/227 | 190 | 122.47 | 127.91 | W1-045 | PN_P2-3_PN-230-0014-12_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200504 | 26CARLISLE | 204528 | 27GARDNERS | 1 | 115 | 226/227 | 190 | 122.46 | 127.49 | W1-045 | PN_P1-3_PN-230-020A_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200504 | 26CARLISLE | 204528 | 27GARDNERS | 1 | 115 | 226/227 | 190 | 122.46 | 127.49 | W1-045 | PN_P2-3_PN-230-0014-11_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200504 | 26CARLISLE | 204528 | 27GARDNERS | 1 | 115 | 226/227 | 190 | 122.39 | 127.47 | W1-045 | PN_P2-2_PN-115-031_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 203981 | AD2-062_POI | 235188 | 01GREENE | 1 | 138 | 226/201 | 317 | 142.34 | 125.04 | W1-045 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 203981 | AD2-062_POI | 235188 | 01GREENE | 1 | 138 | 226/201 | 317 | 142.57 | 124.65 | W1-045 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 203981 | AD2-062_POI | 235188 | 01GREENE | 1 | 138 | 226/201 | 317 | 142.57 | 124.65 | W1-045 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 203981 | AD2-062_POI | 235188 | 01GREENE | 1 | 138 | 226/201 | 317 | 142.56 | 124.64 | W1-045 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 203981 | AD2-062_POI | 235188 | 01GREENE | 1 | 138 | 226/201 | 317 | 127.86 | 123.93 | W1-045 | AP_P2-3_PE-500-016_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 203981 | AD2-062_POI | 235188 | 01GREENE | 1 | 138 | 226/201 | 317 | 128.06 | 123.78 | W1-045 | AP_P2-3_PE-500-015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200532 | 26ROXBURY | 203981 | AD2-062_POI | 1 | 138 | 226 | 317 | 141.65 | 123.74 | W1-045 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200532 | 26ROXBURY | 203981 | AD2-062_POI | 1 | 138 | 226 | 317 | 141.88 | 123.35 | W1-045 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200532 | 26ROXBURY | 203981 | AD2-062_POI | 1 | 138 | 226 | 317 | 141.88 | 123.35 | W1-045 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200532 | 26ROXBURY | 203981 | AD2-062_POI | 1 | 138 | 226 | 317 | 141.87 | 123.35 | W1-045 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200532 | 26ROXBURY | 203981 | AD2-062_POI | 1 | 138 | 226 | 317 | 127.17 | 122.64 | W1-045 | AP_P2-3_PE-500-016_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 203981 | AD2-062_POI | 235188 | 01GREENE | 1 | 138 | 226/201 | 317 | 126.35 | 122.63 | W1-045 | AP_P2-3_PE-500-014_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200532 | 26ROXBURY | 203981 | AD2-062_POI | 1 | 138 | 226 | 317 | 127.37 | 122.49 | W1-045 | AP_P2-3_PE-500-015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200532 | 26ROXBURY | 203981 | AD2-062_POI | 1 | 138 | 226 | 317 | 125.65 | 121.35 | W1-045 | AP_P2-3_PE-500-014_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200512 | 26LEWISTWN | 200519 | 26REED TAP | 1 | 115 | 226 | 271 | 119.85 | 118.61 | W1-045 | ME_P2-3_ME-115-003DT_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200512 | 26LEWISTWN | 200519 | 26REED TAP | 1 | 115 | 226 | 271 | 119.78 | 118.54 | W1-045 | ME_P2-3_ME-115-003AT_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200512 | 26LEWISTWN | 200519 | 26REED TAP | 1 | 115 | 226 | 271 | 119.78 | 118.54 | W1-045 | ME_P2-2_ME-115-002T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200512 | 26LEWISTWN | 200519 | 26REED TAP | 1 | 115 | 226 | 271 | 119.78 | 118.54 | W1-045 | ME_P2-3_ME-115-003BT_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200512 | 26LEWISTWN | 200519 | 26REED TAP | 1 | 115 | 226 | 271 | 119.53 | 118.31 | W1-045 | ME_P1-2_ME-115-058T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200512 | 26LEWISTWN | 200519 | 26REED TAP | 1 | 115 | 226 | 271 | 116.71 | 115.67 | W1-045 | PN_P2-3_PN-115-10T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200512 | 26LEWISTWN | 200519 | 26REED TAP | 1 | 115 | 226 | 271 | 116.67 | 115.6 | W1-045 | PN_P1-2_PN-115-095_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200512 | 26LEWISTWN | 200519 | 26REED TAP | 1 | 115 | 226 | 271 | 116.96 | 115.42 | W1-045 | ME_P2-3_ME-115-003CT_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200512 | 26LEWISTWN | 200519 | 26REED TAP | 1 | 115 | 226 | 271 | 116.71 | 115.18 | W1-045 | PN_P1-2_PN-115-107T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200519 | 26REED TAP | 200522 | 26SHADE GP | 1 | 115 | 226 | 271 | 112.2 | 113.76 | W1-045 | ME_P2-3_ME-115-003DT_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200519 | 26REED TAP | 200522 | 26SHADE GP | 1 | 115 | 226 | 271 | 112.14 | 113.69 | W1-045 | ME_P2-3_ME-115-003AT_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200519 | 26REED TAP | 200522 | 26SHADE GP | 1 | 115 | 226 | 271 | 112.14 | 113.69 | W1-045 | ME_P2-2_ME-115-002T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200519 | 26REED TAP | 200522 | 26SHADE GP | 1 | 115 | 226 | 271 | 112.14 | 113.69 | W1-045 | ME_P2-3_ME-115-003BT_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200519 | 26REED TAP | 200522 | 26SHADE GP | 1 | 115 | 226 | 271 | 111.89 | 113.46 | W1-045 | ME_P1-2_ME-115-058T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200519 | 26REED TAP | 200522 | 26SHADE GP | 1 | 115 | 226 | 271 | 109.07 | 110.84 | W1-045 | PN_P2-3_PN-115-10T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200519 | 26REED TAP | 200522 | 26SHADE GP | 1 | 115 | 226 | 271 | 109.03 | 110.76 | W1-045 | PN_P1-2_PN-115-095_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200519 | 26REED TAP | 200522 | 26SHADE GP | 1 | 115 | 226 | 271 | 109.32 | 110.59 | W1-045 | ME_P2-3_ME-115-003CT_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200504 | 26CARLISLE | 200520 | 26ROXBURY | 1 | 115 | 226 | 190 | 100.56 | 110.46 | W1-045 | PN_P1-2_PN-115-094_A_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200519 | 26REED TAP | 200522 | 26SHADE GP | 1 | 115 | 226 | 271 | 109.07 | 110.36 | W1-045 | PN_P1-2_PN-115-107T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200504 | 26CARLISLE | 200520 | 26ROXBURY | 1 | 115 | 226 | 190 | 100.4 | 109.61 | W1-045 | PN_P2-3_PN-115-58B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200504 | 26CARLISLE | 200520 | 26ROXBURY | 1 | 115 | 226 | 190 | 101.03 | 109.57 | W1-045 | PN_P2-2_PN-115-030_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200504 | 26CARLISLE | 200520 | 26ROXBURY | 1 | 115 | 226 | 190 | 101.03 | 109.57 | W1-045 | PN_P1-3_PN-115-040_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200504 | 26CARLISLE | 200520 | 26ROXBURY | 1 | 115 | 226 | 190 | 100.21 | 109.55 | W1-045 | PN_P1-2_PN-115-094_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200504 | 26CARLISLE | 200520 | 26ROXBURY | 1 | 115 | 226 | 190 | 97.92 | 105.37 | W1-045 | PN_P2-3_PN-230-0014-12_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200504 | 26CARLISLE | 200520 | 26ROXBURY | 1 | 115 | 226 | 190 | 97.91 | 105 | W1-045 | PN_P1-3_PN-230-020A_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200504 | 26CARLISLE | 200520 | 26ROXBURY | 1 | 115 | 226 | 190 | 97.91 | 105 | W1-045 | PN_P2-3_PN-230-0014-11_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200504 | 26CARLISLE | 200520 | 26ROXBURY | 1 | 115 | 226 | 190 | 97.85 | 104.98 | W1-045 | PN_P2-2_PN-115-031_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200504 | 26CARLISLE | 200520 | 26ROXBURY | 1 | 115 | 226 | 190 | 94.26 | 102.37 | W1-045 | PN_P2-3_PN-115-40A_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 521 | 114.21 | 116.6 | AE1-104 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 143.3 | 138.17 | W1-124 | PL_30_P42_000131_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 144.58 | 139.43 | W2-082 | PL_10_P42_100570_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 144.58 | 139.43 | W2-082 | PL_10_P42_100570_A_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 143.77 | 138.64 | W2-082 | PL_10_P12_000085_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 143.68 | 138.55 | W2-082 | PN_P2-3_PN-500-DRT31_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 143.3 | 138.18 | W2-082 | PL_30_P42_000131_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 144.58 | 139.43 | W3-044 | PL_10_P42_100570_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 144.58 | 139.43 | W3-044 | PL_10_P42_100570_A_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 143.77 | 138.64 | W3-044 | PL_10_P12_000085_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 143.68 | 138.55 | W3-044 | PN_P2-3_PN-500-004-DRT-008_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 143.68 | 138.55 | W3-044 | PN_P2-3_PN-500-DRT31_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 143.3 | 138.18 | W3-044 | PL_30_P42_000131_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 143.14 | 138.04 | W3-044 | PL_10_P42_100569_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 143.14 | 138.04 | W3-044 | PL_10_P42_100569_A_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 142.36 | 137.27 | W3-044 | PL_10_P12_000086_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 142.36 | 137.27 | W3-044 | PN_P2-3_PN-500-001C-DRT_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 223.57 | 237.08 | W4-005 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 225.57 | 237.08 | W4-005 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 223.5 | 237.01 | W4-005 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 223.5 | 237.01 | W4-005 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 225.51 | 237.01 | W4-005 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 225.51 | 237.01 | W4-005 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 213.52 | 226.92 | W4-005 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 213.45 | 226.85 | W4-005 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 213.45 | 226.85 | W4-005 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 209.26 | 223.71 | W4-005 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 209.2 | 223.64 | W4-005 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 209.2 | 223.64 | W4-005 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 210.68 | 217.88 | W4-005 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 208.67 | 217.88 | W4-005 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 199.14 | 208.31 | W4-005 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 194.88 | 204.96 | W4-005 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 172.82 | 167.88 | W4-005 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 161.8 | 161.94 | W4-005 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 161.8 | 161.94 | W4-005 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 521 | 113.99 | 116.36 | AE1-229 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 161.79 | 161.93 | W4-005 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 153.61 | 158.08 | W4-005 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.06 | 157.19 | W4-005 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.06 | 157.19 | W4-005 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 151.92 | 156.76 | W4-005 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 161.48 | 154.27 | W4-005 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 148.56 | 153.11 | W4-005 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 155.64 | 150.49 | W4-005 | PN_P1-2_PN-500-010T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.4 | 149.49 | W4-005 | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.33 | 149.42 | W4-005 | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.05 | 148.31 | W4-005 | AP_P2-3_PE-500-016_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.12 | 148.28 | W4-005 | AP_P2-3_PE-500-015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.95 | 147.83 | W4-005 | PJM_500_BG_P4_5_CNSTN_L_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.18 | 147.75 | W4-005 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.98 | 147.56 | W4-005 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153 | 147.55 | W4-005 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.23 | 147.43 | W4-005 | AP_P1-2_WP-500-DRT17_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.23 | 147.43 | W4-005 | AP_P1-2_PE-500-001_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.18 | 147.36 | W4-005 | AP_P2-3_PE-500-018C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.73 | 147.35 | W4-005 | PECO_P4_NOTTI85_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.67 | 147.34 | W4-005 | PECO_P1-2_220-08_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.61 | 147.27 | W4-005 | PECO_P4_COOPR125_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 521 | 115.14 | 117.61 | AE2-000 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.67 | 143.97 | W4-005 | PECO_P4_PEACH025_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.56 | 143.89 | W4-005 | PECO_P1-2_PBTIE1_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 911 | 149.06 | 143.22 | W4-005 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 1031 | 130.36 | 138.2 | W4-005 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 1031 | 130.36 | 138.2 | W4-005 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 1031 | 130.35 | 138.2 | W4-005 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 138.97 | 133.04 | W4-005 | PECO_P4_PEACH205_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 138.84 | 132.7 | W4-005 | PECO_P1-2_PBTIE2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208078 | SAKR | 1 | 230 | 229 | 903 | 124.54 | 132.64 | W4-005 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 137.91 | 131.83 | W4-005 | PECO_P4_PEACH055_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 133.22 | 127.4 | W4-005 | PECO_P4_PEACH015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 131.9 | 126.09 | W4-005 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208020 | MANO TR3 | 1 | 230 | 229 | 793 | 111.52 | 124.73 | W4-005 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208020 | MANO TR3 | 1 | 230 | 229 | 793 | 111.52 | 124.73 | W4-005 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208020 | MANO TR3 | 1 | 230 | 229 | 793 | 111.52 | 124.73 | W4-005 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 122.81 | 117.45 | W4-005 | PECO_P4_PEACH225_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 99.67 | 103.63 | W4-005 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 99.66 | 103.63 | W4-005 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 99.67 | 103.63 | W4-005 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 521 | 114.83 | 117.28 | AE2-020 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 153.75 | 158.25 | X2-022 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.22 | 157.35 | X2-022 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.22 | 157.35 | X2-022 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 152.07 | 156.93 | X2-022 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 161.69 | 154.46 | X2-022 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 148.7 | 153.28 | X2-022 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 155.79 | 150.64 | X2-022 | PN_P1-2_PN-500-010T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.54 | 149.65 | X2-022 | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.47 | 149.58 | X2-022 | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.18 | 148.45 | X2-022 | AP_P2-3_PE-500-016_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.24 | 148.42 | X2-022 | AP_P2-3_PE-500-015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.1 | 147.98 | X2-022 | PJM_500_BG_P4_5_CNSTN_L_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.36 | 147.93 | X2-022 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.16 | 147.74 | X2-022 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.19 | 147.73 | X2-022 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.36 | 147.57 | X2-022 | AP_P1-2_WP-500-DRT17_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.36 | 147.57 | X2-022 | AP_P1-2_PE-500-001_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.92 | 147.53 | X2-022 | PECO_P4_NOTTI85_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.86 | 147.51 | X2-022 | PECO_P1-2_220-08_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.31 | 147.5 | X2-022 | AP_P2-3_PE-500-018C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.79 | 147.45 | X2-022 | PECO_P4_COOPR125_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 521 | 114.83 | 117.28 | AE2-021 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.89 | 144.18 | X2-022 | PECO_P4_PEACH025_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.77 | 144.1 | X2-022 | PECO_P1-2_PBTIE1_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 139.16 | 133.22 | X2-022 | PECO_P4_PEACH205_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 139.04 | 132.89 | X2-022 | PECO_P1-2_PBTIE2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 138.1 | 132.01 | X2-022 | PECO_P4_PEACH055_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 133.42 | 127.6 | X2-022 | PECO_P4_PEACH015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 132.09 | 126.27 | X2-022 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204512 | 27S.RDG | 204693 | 27BOONETOWN | 1 | 230 | 227 | 607 | 107.66 | 123.4 | X2-022 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 123 | 117.62 | X2-022 | PECO_P4_PEACH225_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 521 | 113.84 | 116.21 | AE2-022 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 153.73 | 158.22 | X2-060 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.22 | 157.34 | X2-060 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.22 | 157.34 | X2-060 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 152.04 | 156.9 | X2-060 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 161.72 | 154.49 | X2-060 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 148.68 | 153.25 | X2-060 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 155.79 | 150.64 | X2-060 | PN_P1-2_PN-500-010T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.52 | 149.63 | X2-060 | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.45 | 149.55 | X2-060 | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.14 | 148.38 | X2-060 | AP_P2-3_PE-500-016_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.21 | 148.35 | X2-060 | AP_P2-3_PE-500-015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.1 | 147.97 | X2-060 | PJM_500_BG_P4_5_CNSTN_L_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.39 | 147.95 | X2-060 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.19 | 147.77 | X2-060 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.22 | 147.75 | X2-060 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.95 | 147.56 | X2-060 | PECO_P4_NOTTI85_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.89 | 147.54 | X2-060 | PECO_P1-2_220-08_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.32 | 147.5 | X2-060 | AP_P1-2_PE-500-001_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.32 | 147.5 | X2-060 | AP_P1-2_WP-500-DRT17_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.82 | 147.48 | X2-060 | PECO_P4_COOPR125_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.27 | 147.43 | X2-060 | AP_P2-3_PE-500-018C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 521 | 119.85 | 122.77 | AG2-055 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.94 | 144.22 | X2-060 | PECO_P4_PEACH025_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.8 | 144.12 | X2-060 | PECO_P1-2_PBTIE1_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 139.17 | 133.23 | X2-060 | PECO_P4_PEACH205_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 139.06 | 132.91 | X2-060 | PECO_P1-2_PBTIE2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 138.12 | 132.03 | X2-060 | PECO_P4_PEACH055_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 133.44 | 127.62 | X2-060 | PECO_P4_PEACH015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 132.11 | 126.29 | X2-060 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 123.02 | 117.64 | X2-060 | PECO_P4_PEACH225_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 521 | 108.86 | 110.81 | O66 NFTWR | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.62 | 157.74 | X3-008 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.61 | 157.74 | X3-008 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 162.23 | 154.98 | X3-008 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 156.19 | 151.03 | X3-008 | PN_P1-2_PN-500-010T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.83 | 148.39 | X3-008 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.49 | 148.35 | X3-008 | PJM_500_BG_P4_5_CNSTN_L_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.63 | 148.2 | X3-008 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.66 | 148.19 | X3-008 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.39 | 147.99 | X3-008 | PECO_P4_NOTTI85_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.33 | 147.97 | X3-008 | PECO_P1-2_220-08_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.26 | 147.91 | X3-008 | PECO_P4_COOPR125_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 151.5 | 144.77 | X3-008 | PECO_P4_PEACH025_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 151.34 | 144.64 | X3-008 | PECO_P1-2_PBTIE1_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 139.56 | 133.39 | X3-008 | PECO_P1-2_PBTIE2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 138.6 | 132.49 | X3-008 | PECO_P4_PEACH055_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 133.98 | 128.13 | X3-008 | PECO_P4_PEACH015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 132.6 | 126.75 | X3-008 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204512 | 27S.RDG | 204693 | 27BOONETOWN | 1 | 230 | 227 | 607 | 107.73 | 122.16 | X3-008 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 123.51 | 118.12 | X3-008 | PECO_P4_PEACH225_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200762 | 26GARRETT | 235470 | 01GARRET | 1 | 115 | 226/201 | 190 | 100.83 | 103.25 | Y1-033 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200762 | 26GARRETT | 235470 | 01GARRET | 1 | 115 | 226/201 | 190 | 100.83 | 103.25 | Y1-033 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200762 | 26GARRETT | 235470 | 01GARRET | 1 | 115 | 226/201 | 190 | 100.67 | 103.08 | Y1-033 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200762 | 26GARRETT | 235470 | 01GARRET | 1 | 115 | 226/201 | 190 | 97.23 | 100.8 | Y1-033 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200762 | 26GARRETT | 235470 | 01GARRET | 1 | 115 | 226/201 | 190 | 97.23 | 100.79 | Y1-033 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200762 | 26GARRETT | 235470 | 01GARRET | 1 | 115 | 226/201 | 190 | 97.23 | 100.79 | Y1-033 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200762 | 26GARRETT | 235470 | 01GARRET | 1 | 115 | 226/201 | 190 | 97.19 | 100.71 | Y1-033 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 746 | 109.19 | 107.62 | AC1-158 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 746 | 112.31 | 110.75 | AD1-020 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.6 | 157.72 | Y3-058 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.6 | 157.72 | Y3-058 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 162.21 | 154.96 | Y3-058 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 156.17 | 151.02 | Y3-058 | PN_P1-2_PN-500-010T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.81 | 148.37 | Y3-058 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.47 | 148.34 | Y3-058 | PJM_500_BG_P4_5_CNSTN_L_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.61 | 148.18 | Y3-058 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.64 | 148.17 | Y3-058 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.37 | 147.97 | Y3-058 | PECO_P4_NOTTI85_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.31 | 147.96 | Y3-058 | PECO_P1-2_220-08_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.24 | 147.89 | Y3-058 | PECO_P4_COOPR125_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 151.48 | 144.74 | Y3-058 | PECO_P4_PEACH025_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 151.32 | 144.62 | Y3-058 | PECO_P1-2_PBTIE1_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 139.54 | 133.37 | Y3-058 | PECO_P1-2_PBTIE2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 138.58 | 132.47 | Y3-058 | PECO_P4_PEACH055_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 133.95 | 128.11 | Y3-058 | PECO_P4_PEACH015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 132.58 | 126.73 | Y3-058 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204512 | 27S.RDG | 204693 | 27BOONETOWN | 1 | 230 | 227 | 607 | 107.72 | 122.15 | Y3-058 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 123.49 | 118.1 | Y3-058 | PECO_P4_PEACH225_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 226.14 | 238.38 | Z1-036 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 224.14 | 238.38 | Z1-036 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 225.19 | 236.33 | Z1-036 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 223.19 | 236.33 | Z1-036 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 225.12 | 236.27 | Z1-036 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 223.12 | 236.27 | Z1-036 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 225.12 | 236.27 | Z1-036 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 223.12 | 236.26 | Z1-036 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 214.07 | 228.18 | Z1-036 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 213.15 | 226.19 | Z1-036 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 213.09 | 226.14 | Z1-036 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 213.09 | 226.13 | Z1-036 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 209.81 | 224.98 | Z1-036 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 208.89 | 222.98 | Z1-036 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 208.83 | 222.92 | Z1-036 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 208.83 | 222.92 | Z1-036 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 208.3 | 217.23 | Z1-036 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 210.29 | 217.23 | Z1-036 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 198.77 | 207.69 | Z1-036 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 194.51 | 204.33 | Z1-036 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 172.46 | 167.46 | Z1-036 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 171.49 | 166.02 | Z1-036 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 171.49 | 166.02 | Z1-036 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 171.47 | 166.02 | Z1-036 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 163.32 | 164.48 | Z1-036 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 746 | 112.18 | 110.61 | AE1-129 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 161.45 | 161.41 | Z1-036 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 161.45 | 161.41 | Z1-036 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 161.44 | 161.4 | Z1-036 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 163.54 | 158.59 | Z1-036 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 153.25 | 157.64 | Z1-036 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 161.76 | 156.88 | Z1-036 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 161.76 | 156.88 | Z1-036 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 151.56 | 156.32 | Z1-036 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 161.19 | 153.99 | Z1-036 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 148.2 | 152.67 | Z1-036 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 903 | 144 | 151.72 | Z1-036 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208048 | OTCR | 220963 | CONASTON | 1 | 230 | 229/232 | 897 | 152.51 | 150.83 | Z1-036 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 155.34 | 150.19 | Z1-036 | PN_P1-2_PN-500-010T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 903 | 142.47 | 149.11 | Z1-036 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 903 | 142.47 | 149.11 | Z1-036 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 903 | 142.45 | 149.1 | Z1-036 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.06 | 149.08 | Z1-036 | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 145.99 | 149.01 | Z1-036 | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.67 | 147.81 | Z1-036 | AP_P2-3_PE-500-016_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.74 | 147.79 | Z1-036 | AP_P2-3_PE-500-015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.66 | 147.53 | Z1-036 | PJM_500_BG_P4_5_CNSTN_L_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.93 | 147.51 | Z1-036 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.73 | 147.32 | Z1-036 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.76 | 147.31 | Z1-036 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.49 | 147.11 | Z1-036 | PECO_P4_NOTTI85_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.43 | 147.09 | Z1-036 | PECO_P1-2_220-08_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.36 | 147.03 | Z1-036 | PECO_P4_COOPR125_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 142.85 | 146.94 | Z1-036 | AP_P1-2_WP-500-DRT17_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 142.85 | 146.94 | Z1-036 | AP_P1-2_PE-500-001_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 142.81 | 146.88 | Z1-036 | AP_P2-3_PE-500-018C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 746 | 112.19 | 110.65 | AE2-000 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.42 | 143.73 | Z1-036 | PECO_P4_PEACH025_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.25 | 143.6 | Z1-036 | PECO_P1-2_PBTIE1_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 911 | 148.71 | 142.85 | Z1-036 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 911 | 147.76 | 141.53 | Z1-036 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 911 | 147.76 | 141.53 | Z1-036 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 911 | 147.75 | 141.52 | Z1-036 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204502 | 27JACKSON | 204514 | 27TMI | 1 | 230 | 227 | 781 | 132.65 | 141.27 | Z1-036 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204502 | 27JACKSON | 204514 | 27TMI | 1 | 230 | 227 | 781 | 132.85 | 141.26 | Z1-036 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204502 | 27JACKSON | 204514 | 27TMI | 1 | 230 | 227 | 781 | 132.85 | 141.26 | Z1-036 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204502 | 27JACKSON | 204514 | 27TMI | 1 | 230 | 227 | 781 | 132.83 | 141.24 | Z1-036 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 140.84 | 140.45 | Z1-036 | PJM_500_BG_P4_5_CNSTN_15_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 208048 | OTCR | 1 | 230 | 227/229 | 903 | 135.4 | 139.27 | Z1-036 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 1031 | 130.64 | 138.82 | Z1-036 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 1031 | 130.14 | 137.76 | Z1-036 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 1031 | 130.14 | 137.76 | Z1-036 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 1031 | 130.13 | 137.75 | Z1-036 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 911 | 139.9 | 134.82 | Z1-036 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208078 | SAKR | 1 | 230 | 229 | 903 | 125.02 | 133.59 | Z1-036 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 138.68 | 132.76 | Z1-036 | PECO_P4_PEACH205_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 207922 | BRIS | 207923 | BRISREAC | RX | 230 | 229 | 676 | 124.12 | 132.6 | Z1-036 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 207922 | BRIS | 207923 | BRISREAC | RX | 230 | 229 | 676 | 124.12 | 132.6 | Z1-036 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 207923 | BRISREAC | 208132 | WHEM TR1 | 1 | 230 | 229 | 676 | 124.12 | 132.6 | Z1-036 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 207923 | BRISREAC | 208132 | WHEM TR1 | 1 | 230 | 229 | 676 | 124.12 | 132.59 | Z1-036 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 207922 | BRIS | 207923 | BRISREAC | RX | 230 | 229 | 676 | 124.11 | 132.59 | Z1-036 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 207923 | BRISREAC | 208132 | WHEM TR1 | 1 | 230 | 229 | 676 | 124.11 | 132.59 | Z1-036 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 138.56 | 132.43 | Z1-036 | PECO_P1-2_PBTIE2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208078 | SAKR | 1 | 230 | 229 | 903 | 124.28 | 132.15 | Z1-036 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208078 | SAKR | 1 | 230 | 229 | 903 | 124.28 | 132.15 | Z1-036 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208078 | SAKR | 1 | 230 | 229 | 903 | 124.27 | 132.15 | Z1-036 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 137.65 | 131.58 | Z1-036 | PECO_P4_PEACH055_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204502 | 27JACKSON | 204514 | 27TMI | 1 | 230 | 227 | 781 | 125.2 | 130.71 | Z1-036 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220972 | GRANITE1 | 1 | 230 | 232 | 829 | 134.64 | 130.68 | Z1-036 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220972 | GRANITE1 | 1 | 230 | 232 | 829 | 134.01 | 130.03 | Z1-036 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220972 | GRANITE1 | 1 | 230 | 232 | 829 | 134.01 | 130.03 | Z1-036 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204515 | 27YORKANA | 207922 | BRIS | 1 | 230 | 227/229 | 1031 | 124.54 | 128.98 | Z1-036 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220973 | GRANITE6 | 1 | 230 | 232 | 829 | 132.57 | 128.8 | Z1-036 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220973 | GRANITE6 | 1 | 230 | 232 | 829 | 131.98 | 128.18 | Z1-036 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220973 | GRANITE6 | 1 | 230 | 232 | 829 | 131.98 | 128.18 | Z1-036 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 132.91 | 127.1 | Z1-036 | PECO_P4_PEACH015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 127.98 | 126.26 | Z1-036 | DVP_P4-2: 514T595_SRT-SW |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208020 | MANO TR3 | 1 | 230 | 229 | 793 | 112.09 | 125.86 | Z1-036 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 131.62 | 125.82 | Z1-036 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220953 | HOWARD12 | 220972 | GRANITE1 | 1 | 230 | 232 | 772 | 129.36 | 125.38 | Z1-036 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220954 | HOWARD32 | 220973 | GRANITE6 | 1 | 230 | 232 | 772 | 128.23 | 124.7 | Z1-036 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 2 | 230 | 233 | 793 | 126.26 | 124.5 | Z1-036 | DVP_P4-2: 514T595_SRT-SW |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 793 | 126.26 | 124.5 | Z1-036 | DVP_P4-2: 514T595_SRT-SW |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 207922 | BRIS | 207923 | BRISREAC | RX | 230 | 229 | 676 | 119.02 | 124.48 | Z1-036 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 207923 | BRISREAC | 208132 | WHEM TR1 | 1 | 230 | 229 | 676 | 119.02 | 124.48 | Z1-036 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 126.22 | 124.47 | Z1-036 | DVP_P4-2: 51482_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220953 | HOWARD12 | 220972 | GRANITE1 | 1 | 230 | 232 | 772 | 128.45 | 124.41 | Z1-036 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220953 | HOWARD12 | 220972 | GRANITE1 | 1 | 230 | 232 | 772 | 128.45 | 124.41 | Z1-036 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 126.22 | 124.38 | Z1-036 | DVP_P1-2: LN 514_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 126.22 | 124.38 | Z1-036 | AP_P1-2_PE-500-407T_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208020 | MANO TR3 | 1 | 230 | 229 | 793 | 111.27 | 124.33 | Z1-036 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208020 | MANO TR3 | 1 | 230 | 229 | 793 | 111.27 | 124.33 | Z1-036 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208020 | MANO TR3 | 1 | 230 | 229 | 793 | 111.26 | 124.33 | Z1-036 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220954 | HOWARD32 | 220973 | GRANITE6 | 1 | 230 | 232 | 772 | 127.44 | 123.86 | Z1-036 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220954 | HOWARD32 | 220973 | GRANITE6 | 1 | 230 | 232 | 772 | 127.44 | 123.86 | Z1-036 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 2 | 230 | 233 | 793 | 125 | 123.24 | Z1-036 | DVP_P4-2: 51482_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 793 | 125 | 123.24 | Z1-036 | DVP_P4-2: 51482_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 793 | 125 | 123.16 | Z1-036 | DVP_P1-2: LN 514_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 2 | 230 | 233 | 793 | 125 | 123.16 | Z1-036 | DVP_P1-2: LN 514_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 2 | 230 | 233 | 793 | 125 | 123.16 | Z1-036 | AP_P1-2_PE-500-407T_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 793 | 125 | 123.16 | Z1-036 | AP_P1-2_PE-500-407T_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208031 | MLWD TR2 | 1 | 230 | 229 | 911 | 112.3 | 122.23 | Z1-036 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208078 | SAKR | 1 | 230 | 229 | 903 | 117.01 | 122.18 | Z1-036 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204512 | 27S.RDG | 204693 | 27BOONETOWN | 1 | 230 | 227 | 607 | 107.31 | 122.04 | Z1-036 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204512 | 27S.RDG | 204693 | 27BOONETOWN | 1 | 230 | 227 | 607 | 107.28 | 122.02 | Z1-036 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204512 | 27S.RDG | 204693 | 27BOONETOWN | 1 | 230 | 227 | 607 | 107.28 | 122 | Z1-036 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200025 | W CHAPEL | 1 | 500 | 225 | 1732 | 123.41 | 121.62 | Z1-036 | PEPCO_P4_PP41_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208031 | MLWD TR2 | 1 | 230 | 229 | 911 | 111.58 | 120.91 | Z1-036 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208031 | MLWD TR2 | 1 | 230 | 229 | 911 | 111.59 | 120.91 | Z1-036 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208031 | MLWD TR2 | 1 | 230 | 229 | 911 | 111.58 | 120.91 | Z1-036 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220965 | NEAST339 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 119.59 | 118.94 | Z1-036 | BG_P1_2315_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 911 | 117.85 | 118.84 | Z1-036 | PJM_500_BG_P4_5_CNSTN_15_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220965 | NEAST339 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 119.17 | 118.73 | Z1-036 | BG_P4_5_NEAST_17_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220965 | NEAST339 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 119.33 | 118.73 | Z1-036 | BG_P4_5_NEAST_15_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 114.55 | 118.22 | Z1-036 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220979 | NEAST317 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 118.68 | 118.07 | Z1-036 | BG_P1_2337_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 114.21 | 117.88 | Z1-036 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 114.2 | 117.82 | Z1-036 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 114.2 | 117.82 | Z1-036 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220979 | NEAST317 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 118.35 | 117.81 | Z1-036 | BG_P4_5_NEAST_39_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220979 | NEAST317 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 118.35 | 117.81 | Z1-036 | BG_P4_5_NEAST_37_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 113.86 | 117.49 | Z1-036 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 113.86 | 117.49 | Z1-036 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208131 | WHEM | 208132 | WHEM TR1 | 1 | 230 | 229 | 691 | 108.42 | 117.45 | Z1-036 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208131 | WHEM | 208132 | WHEM TR1 | 1 | 230 | 229 | 691 | 108.42 | 117.45 | Z1-036 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208131 | WHEM | 208132 | WHEM TR1 | 1 | 230 | 229 | 691 | 108.41 | 117.44 | Z1-036 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 122.52 | 117.17 | Z1-036 | PECO_P4_PEACH225_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 793 | 118.37 | 115.59 | Z1-036 | PEPCO_P1_PP2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 2 | 230 | 233 | 793 | 118.37 | 115.59 | Z1-036 | PEPCO_P1_PP1_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 2 | 500/230 | 225/232 | 2168 | 109.52 | 114.81 | Z1-036 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 2 | 500/230 | 225/232 | 2168 | 109.35 | 114.6 | Z1-036 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 2 | 500/230 | 225/232 | 2168 | 109.35 | 114.6 | Z1-036 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 1 | 500/230 | 225/232 | 2168 | 109.29 | 114.57 | Z1-036 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 116.44 | 114.48 | Z1-036 | AP_P2-3_PE-500-019C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 1 | 500/230 | 225/232 | 2168 | 109.12 | 114.35 | Z1-036 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 1 | 500/230 | 225/232 | 2168 | 109.12 | 114.35 | Z1-036 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220964 | GRACETON | 220999 | BAGLEY2 | 13 | 230 | 232 | 1795 | 113.3 | 114.33 | Z1-036 | BG_P4_5_GRCTN_3T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208020 | MANO TR3 | 1 | 230 | 229 | 793 | 104.09 | 113.83 | Z1-036 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208020 | MANO TR3 | 208031 | MLWD TR2 | 1 | 230 | 229 | 903 | 102.41 | 113.47 | Z1-036 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208020 | MANO TR3 | 208031 | MLWD TR2 | 1 | 230 | 229 | 903 | 101.7 | 112.28 | Z1-036 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208020 | MANO TR3 | 208031 | MLWD TR2 | 1 | 230 | 229 | 903 | 101.71 | 112.28 | Z1-036 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208020 | MANO TR3 | 208031 | MLWD TR2 | 1 | 230 | 229 | 903 | 101.7 | 112.28 | Z1-036 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 113.38 | 112.23 | Z1-036 | BG_P4_5_CNSTN_14_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 2 | 500/230 | 225/232 | 2168 | 108.41 | 111.69 | Z1-036 | PJM_500_BG_P4_5_CNSTN_15_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208030 | MLWD TR1 | 208031 | MLWD TR2 | 1 | 230 | 229 | 911 | 104.83 | 111.43 | Z1-036 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 106.35 | 111.09 | Z1-036 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220980 | RAPHAEL | 220999 | BAGLEY2 | 13 | 230 | 232 | 1795 | 108.89 | 111.08 | Z1-036 | BG_P4_5_GRCTN_3T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 106.22 | 110.95 | Z1-036 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208131 | WHEM | 208132 | WHEM TR1 | 1 | 230 | 229 | 691 | 103.63 | 109.95 | Z1-036 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 793 | 112.48 | 109.82 | Z1-036 | PEPCO_P4_PP19_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208131 | WHEM | 208133 | WHEM TR2 | 1 | 230 | 229 | 691 | 100.9 | 108.91 | Z1-036 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208131 | WHEM | 208133 | WHEM TR2 | 1 | 230 | 229 | 691 | 100.9 | 108.91 | Z1-036 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208131 | WHEM | 208133 | WHEM TR2 | 1 | 230 | 229 | 691 | 100.89 | 108.9 | Z1-036 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 1 | 230 | 233 | 793 | 109.24 | 107.31 | Z1-036 | AP_P2-3_PE-500-019C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 223938 | DICKH230 | 2 | 230 | 233 | 793 | 109.24 | 107.31 | Z1-036 | AP_P2-3_PE-500-019C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220965 | NEAST339 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 108.15 | 106.73 | Z1-036 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220965 | NEAST339 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 108.06 | 106.61 | Z1-036 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220965 | NEAST339 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 108.06 | 106.61 | Z1-036 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 101.47 | 105.61 | Z1-036 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 101.38 | 105.53 | Z1-036 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 102.58 | 104.59 | Z1-036 | BG_P1_2322_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 102.51 | 104.51 | Z1-036 | BG_P1_2310_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 102.52 | 104.48 | Z1-036 | BG_P4_5_NW2322_230-4_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 102.45 | 104.44 | Z1-036 | BG_P4_5_NW2310_230-5_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220979 | NEAST317 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 105.05 | 103.68 | Z1-036 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220979 | NEAST317 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 104.96 | 103.57 | Z1-036 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220979 | NEAST317 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 104.96 | 103.57 | Z1-036 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220962 | NWEST311 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 101.18 | 103.22 | Z1-036 | BG_P4_5_NW230-2_2322_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 99.38 | 103.21 | Z1-036 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 99.38 | 103.21 | Z1-036 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 99.38 | 103.21 | Z1-036 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 101.08 | 103.11 | Z1-036 | BG_P4_5_NW2371_2310_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 101.08 | 103.11 | Z1-036 | BG_P4_5_NW230-3_2310_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208020 | MANO TR3 | 208031 | MLWD TR2 | 1 | 230 | 229 | 903 | 95.33 | 103.07 | Z1-036 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220961 | NWEST326 | 220963 | CONASTON | 1 | 230 | 232 | 1381 | 100.2 | 102.17 | Z1-036 | BG_P4_5_CNSTN_14_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220964 | GRACETON | 221000 | BAGLEY | 5 | 230 | 232 | 1795 | 101.36 | 102.11 | Z1-036 | BG_P1_2313_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220964 | GRACETON | 220999 | BAGLEY2 | 13 | 230 | 232 | 1795 | 101.37 | 102.11 | Z1-036 | BG_P1_2305_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220965 | NEAST339 | 220980 | RAPHAEL | 1 | 230 | 232 | 1340 | 102.6 | 101.91 | Z1-036 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 98.45 | 101.88 | Z1-036 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220965 | NEAST339 | 220977 | RIV2339 | 1 | 230 | 232 | 991 | 103.21 | 101.77 | Z1-036 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220966 | RIV2317 | 220979 | NEAST317 | 1 | 230 | 232 | 940 | 102.81 | 101.75 | Z1-036 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220965 | NEAST339 | 220977 | RIV2339 | 1 | 230 | 232 | 991 | 103.17 | 101.71 | Z1-036 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220965 | NEAST339 | 220977 | RIV2339 | 1 | 230 | 232 | 991 | 103.17 | 101.71 | Z1-036 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220966 | RIV2317 | 220979 | NEAST317 | 1 | 230 | 232 | 940 | 102.76 | 101.69 | Z1-036 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 220966 | RIV2317 | 220979 | NEAST317 | 1 | 230 | 232 | 940 | 102.76 | 101.69 | Z1-036 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208131 | WHEM | 208133 | WHEM TR2 | 1 | 230 | 229 | 691 | 96.12 | 101.68 | Z1-036 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 2 | 500/230 | 225/232 | 2168 | 98.93 | 101.67 | Z1-036 | PJM_500_BG_P2_CNSTN_230-N_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 2 | 500/230 | 225/232 | 2168 | 98.93 | 101.67 | Z1-036 | BG_P1_CNSTN_500-2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 1 | 500/230 | 225/232 | 2168 | 98.82 | 101.56 | Z1-036 | PJM_500_BG_P2_CNSTN_230-S_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 220963 | CONASTON | 1 | 500/230 | 225/232 | 2168 | 98.82 | 101.56 | Z1-036 | BG_P1_CNSTN_500-4_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 223960 | BRG 1T 230 | 1 | 500/230 | 225/233 | 1498 | 100.23 | 100.6 | Z1-036 | PEPCO_P4_PP41_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 98.56 | 100.54 | Z1-036 | PECO_P4_PEACH245_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204512 | 27S.RDG | 204693 | 27BOONETOWN | 1 | 230 | 227 | 607 | 107.69 | 122.13 | Z1-069 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204512 | 27S.RDG | 204693 | 27BOONETOWN | 1 | 230 | 227 | 607 | 107.67 | 122.1 | Z1-069 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 204512 | 27S.RDG | 204693 | 27BOONETOWN | 1 | 230 | 227 | 607 | 107.67 | 122.1 | Z1-069 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 746 | 114.83 | 113.32 | AG2-055 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 153.73 | 158.23 | Z2-087 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.2 | 157.32 | Z2-087 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.19 | 157.32 | Z2-087 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 152.04 | 156.9 | Z2-087 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 161.65 | 154.43 | Z2-087 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 148.68 | 153.25 | Z2-087 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 155.77 | 150.62 | Z2-087 | PN_P1-2_PN-500-010T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.52 | 149.63 | Z2-087 | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.45 | 149.56 | Z2-087 | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.16 | 148.43 | Z2-087 | AP_P2-3_PE-500-016_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.23 | 148.4 | Z2-087 | AP_P2-3_PE-500-015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.08 | 147.95 | Z2-087 | PJM_500_BG_P4_5_CNSTN_L_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.33 | 147.9 | Z2-087 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.13 | 147.71 | Z2-087 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.16 | 147.7 | Z2-087 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.34 | 147.55 | Z2-087 | AP_P1-2_WP-500-DRT17_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.34 | 147.55 | Z2-087 | AP_P1-2_PE-500-001_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.89 | 147.5 | Z2-087 | PECO_P4_NOTTI85_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.83 | 147.49 | Z2-087 | PECO_P1-2_220-08_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.29 | 147.48 | Z2-087 | AP_P2-3_PE-500-018C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.76 | 147.42 | Z2-087 | PECO_P4_COOPR125_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 746 | 108.83 | 107.26 | O66 NFTWR | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.85 | 144.14 | Z2-087 | PECO_P4_PEACH025_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.74 | 144.07 | Z2-087 | PECO_P1-2_PBTIE1_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 139.13 | 133.19 | Z2-087 | PECO_P4_PEACH205_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 139.01 | 132.86 | Z2-087 | PECO_P1-2_PBTIE2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 138.07 | 131.98 | Z2-087 | PECO_P4_PEACH055_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 133.39 | 127.57 | Z2-087 | PECO_P4_PEACH015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 132.06 | 126.24 | Z2-087 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 122.97 | 117.6 | Z2-087 | PECO_P4_PEACH225_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 225.74 | 237.23 | Z2-088 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 223.73 | 237.23 | Z2-088 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 225.67 | 237.17 | Z2-088 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 223.67 | 237.17 | Z2-088 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213844 | NOTTNGHM | 213846 | NOTTREAC | 1 | 230 | 230 | 617 | 225.67 | 237.17 | Z2-088 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213846 | NOTTREAC | 213869 | PCHBTMTP | 1 | 230 | 230 | 617 | 223.66 | 237.17 | Z2-088 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 213.67 | 227.07 | Z2-088 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 213.61 | 227.01 | Z2-088 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 213869 | PCHBTMTP | 214087 | COOPER2 | 1 | 230 | 230 | 639 | 213.61 | 227.01 | Z2-088 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 209.42 | 223.86 | Z2-088 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 209.35 | 223.8 | Z2-088 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 214084 | COOPER | 220964 | GRACETON | 1 | 230 | 230/232 | 639 | 209.35 | 223.8 | Z2-088 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208071 | SAHA34TP | 220964 | GRACETON | 1 | 230 | 229/232 | 889 | 172.86 | 167.9 | Z2-088 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200017 | SMITHBRG | 967451 | AG2-055 C O1 | 1 | 500 | 225 | 999 | 114.91 | 107.9 | AG2-055 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 153.63 | 158.1 | Z2-088 | BG_P7_CNSTN_NWEST2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.12 | 157.24 | Z2-088 | PJM_500_BG_P1_5013_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 162.12 | 157.24 | Z2-088 | PJM_500_BG_P4_5_CNSTN_M_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 151.94 | 156.77 | Z2-088 | BG_P7_GRCTN_RAPHEL_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 161.61 | 154.38 | Z2-088 | PECO_P4_PEACH255_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 148.58 | 153.12 | Z2-088 | BG_P7_NEAST_RPHLRD_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 155.7 | 150.54 | Z2-088 | PN_P1-2_PN-500-010T_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.42 | 149.51 | Z2-088 | PJM_500_BG_P4_5_CNSTN_13_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 146.35 | 149.44 | Z2-088 | PJM_500_BG_P4_5_CNSTN_6_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.04 | 148.26 | Z2-088 | AP_P2-3_PE-500-016_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 144.11 | 148.24 | Z2-088 | AP_P2-3_PE-500-015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.01 | 147.88 | Z2-088 | PJM_500_BG_P4_5_CNSTN_L_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.29 | 147.86 | Z2-088 | PECO_P4_NOTTI55_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.09 | 147.67 | Z2-088 | PECO_P2-2_NOTT230B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 153.12 | 147.66 | Z2-088 | PECO_P4_NOTTI785_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.85 | 147.46 | Z2-088 | PECO_P4_NOTTI85_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.79 | 147.44 | Z2-088 | PECO_P1-2_220-08_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.22 | 147.39 | Z2-088 | AP_P1-2_WP-500-DRT17_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.22 | 147.39 | Z2-088 | AP_P1-2_PE-500-001_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200064 | PCHBTM1S | 1 | 500 | 225 | 4030 | 152.72 | 147.38 | Z2-088 | PECO_P4_COOPR125_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200004 | CNASTONE | 1 | 500 | 225 | 3183 | 143.17 | 147.32 | Z2-088 | AP_P2-3_PE-500-018C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 221089 | WINDYED1 | 221090 | GLENARM2 | 1 | 115 | 232 | 176 | 96.51 | 104.7 | AG2-055 | Base Case |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.83 | 144.12 | Z2-088 | PECO_P4_PEACH025_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 150.68 | 144.01 | Z2-088 | PECO_P1-2_PBTIE1_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 208019 | MANO | 208071 | SAHA34TP | 1 | 230 | 229 | 911 | 149.1 | 143.23 | Z2-088 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 139.07 | 133.13 | Z2-088 | PECO_P4_PEACH205_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 138.96 | 132.8 | Z2-088 | PECO_P1-2_PBTIE2_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 138.02 | 131.93 | Z2-088 | PECO_P4_PEACH055_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z2 | 500 | 225 | 3022 | 133.33 | 127.51 | Z2-088 | PECO_P4_PEACH015_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 128.72 | 126.98 | Z2-088 | DVP_P4-2: 514T595_SRT-SW |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 132.01 | 126.19 | Z2-088 | PECO_P4_PEACH045_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 126.97 | 125.26 | Z2-088 | DVP_P4-2: 51482_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 126.97 | 125.16 | Z2-088 | AP_P1-2_PE-500-407T_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 126.97 | 125.16 | Z2-088 | DVP_P1-2: LN 514_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200003 | BRIGHTON | 200025 | W CHAPEL | 1 | 500 | 225 | 1732 | 123.77 | 121.98 | Z2-088 | PEPCO_P4_PP41_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200064 | PCHBTM1S | 200065 | PCHBTM2S | Z1 | 500 | 225 | 3277 | 122.91 | 117.54 | Z2-088 | PECO_P4_PEACH225_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 223937 | DICK 230 | 314290 | 6EDFERRY | 1 | 230 | 233/345 | 1508 | 117.17 | 115.25 | Z2-088 | AP_P2-3_PE-500-019C_SRT-W |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 99.58 | 103.53 | Z2-088 | PECO_P1-2_5012_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 99.58 | 103.53 | Z2-088 | PECO_P4_PEACH235_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 99.58 | 103.53 | Z2-088 | PJM_500_BG_P4_5_CNSTN_C_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200004 | CNASTONE | 200026 | HUNTERTN | 1 | 500 | 225 | 3024 | 98.65 | 102.2 | Z2-088 | PJM_500_BG_P4_5_CNSTN_B_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200762 | 26GARRETT | 235470 | 01GARRET | 1 | 115 | 226/201 | 190 | 98.21 | 100.27 | Z2-108 | PJM_500_BG_P4_5_CNSTN_J_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200762 | 26GARRETT | 235470 | 01GARRET | 1 | 115 | 226/201 | 190 | 98.21 | 100.27 | Z2-108 | PJM_500_BG_P1_5011_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome
N/A | 200762 | 26GARRETT | 235470 | 01GARRET | 1 | 115 | 226/201 | 190 | 98.04 | 100.11 | Z2-108 | PEPCO_P4_PP40_SRT-A |  | NO | Related to 2022 Window 3, pending window outcome